TABLE 17-2  SUMMARY OF SPRINKLER REQUIREMENTS

| Where Required Type of System | Automatic Sources Required | Partial System Permitted | Connection to Domestic Permitted | Alternate Permitted (§27-955) | Siamese Required (§27-959) | Centrala Station Required (§27-955) (§27-967) | Waterb Flow Alarm Required (§27-957) [(§3721 of RS17-2)] | Automatic Dry Sprinkler Permitted (§5212 of RS[-]17) | Dry Nonautomatic Sprinkler Permittedc |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| High Hazard Bldg. – Group A (§27-954(a)) | 2 | No | No §27-961(c) | No | Yes | Nonea | Yes | Yes | No |
| High Hazard Spaces – Group A (§27-954(b))b | 1 | Yes | No §27-961(c) | No | §27-959(a)(3) If over 36 heads in a fire section | Nonea | Yes If over 36 heads in a fire section | Yes | No |
| Storage Occupancy Bldg. - Group B1 (§27-954(c)) | 1 | No | No §27-961(c) | No | Yes | Nonea | Yes | Yes | No |
| Storage Occupancy Spaces [Bldg.] – Group B1 (§27-954(d)) | 1 | Yes | Yes §27-961(c) | No | §27-959(a)(3) If over 36 heads in a fire section | Nonea | Yesb If over 36 heads in a fire section | Yes | No |
| Storage Occupancy Spaces – Group B2 (§27-954(e)) | 1 | Yes | No | No | §27-959(a)(3) If over 36 heads in a fire section | Nonea | Yesb If over 36 heads in a fire section | Yes | No |
| Mercantile Occupancy Spaces – Group C Exceeding 7,500 sq. ft. (§27-954(f)) | 2 sources if exceeding 20,000 sq. ft. 1 source if not more than 20,000 sq. ft. | No | No | No | Yes | Nonea | Yes | Yes | No |
| Industrial Occupancy Bldg. - Group D-1, When required by Labor Law (§27-954(g)) | 1 source if not hazardous occupancy | No | No | No | Yes | Nonea | Yes | Yes | No |
| Industrial Occupancy Spaces. –Group D-1, exceeding 7,500 sq. ft. (§27-954(h)) | 1 | No | No | No | Yes | Nonea | Yes | Yes | No |
| Business Occupancy Spaces - Group E Showrooms when Required by (§27-954(i)) | 1 | Yes | Yes and/or Standpipe Riser | No | Yes | Nonea | Yes | Yes | No |
| Assembly Occupancy Spaces - Group F-1a (§27-954(j)) | 1 | Yes | Yes | No | §27-959(a)(3) If over 36 heads in a fire section | Nonea | Yesb | No | No |
| Institutional Occupancy Group H - Corridors and Exit Passageway (§27-954(k)) | 1 | Yes | Yes | No | §27-959(a)(3) If over 36 heads in a fire section | Nonea | Yes | No | No |
| Unventilated Areas Above or Below Grade (§27-954(l))d | 1 | Yes | Yes | No | §27-959(a)(3) If over 36 heads in a fire section | Nonea | §27-962 (e)(8) | Yes | No |
| Rubbish – Laundry and Similar Chutes (§27-954(m))d,e | 1 | Yes | Yes | No | No | [None] Yesa | None | Yes | No |
| Soiled Linen – Collection and Sorting Area (§27-954(n)) | 1 | Yes | Yes | No | §27-959(a)(3) If over 36 heads In a fire section | Nonea | Yes §27-962 (e)(8) | Yes | No |
| Workshops (§27-954(o))d | 1 | Yes | Yes | Yes | §27-959(a)(3) If over 36 heads In a fire section | Yes If smoke detector is used in lieu of sprinkler | Yes §27-962 (e)(8) | Yes | No |
| Refuse Collection and Disposal Areas (§27-954(p)) | 1 | Yes | Yes In Occupancy Groups E, G, J | No | §27-959(a)(3) If over 36 heads In a fire section | Nonea | Yes §27-962 (e)(8) | Yes | No |
| Drying Areas – Laundries or Similar Spaces (§27-954(q))d | 1 | Yes | Yes In Occupancy Groups E, G, J | Yes | §27-959(a)(3) If over 36 heads In a fire section | Yes If smoke detector is used in lieu of sprinkler | Yes §27-962 (e)(8) | No | No |
| Cooling Towers (§27-954(r)) | 1 | No | Yes | No | No | Nonea | Yes | Yes | No |
| Buildings and Spaces in Residential Occupancy Group J-1 (§27-954(t)) | 1 | No | Nof | No | Yes, except as provided in §27-959(a)(3) | No | Yes | No | No |
| Buildings and Spaces in Residential Occupancy Group J-2 with 4 or more Dwelling Units and not exceeding Six Stories or 75 Feet In Height (§27-954(t)) | 1 | No | Yesg | No | Yes, except as provided in §27-959(a)(1) and §27-959(a)(5) | No | Yes | No | No |
| Buildings and Spaces in Residential Occupancy Group J-2 with 4 or more Dwelling Units and Exceeding Six Stories or 75 Feet In Height (§27-954(t)) | 1 | No | Noh | No | Yes, except as provided in §27-959(a)(3) | No | Yes If over 36 heads | No | No |

Notes:

a.	Central Station supervision required only when booster pump is provided under §27-964 or when non-automatic sprinkler is permitted by the commissioner.

b.	Water flow alarms required when more than 36 heads are installed in a fire section or fire area.

c.	Only when permitted by the commissioner (§27-967(c)).

d.	[see] See §27-954(w) for requirements pertaining to these spaces located in a building classified in occupancy group J-1.

e.	See section 4-4.8 of reference standard RS 17-2.

f.	Except as provided in reference standard RS 17-2A.

g.	Notwithstanding section 27-962(i) of this chapter.

h.	Except as provided in section 27-962(i) of this chapter.