TABLE 17-2  SUMMARY OF SPRINKLER REQUIREMENTS

| Where Required Type of System | Automatic Sources Required | Partial System Permitted | Connection to Domestic Permitted | Alternate Permitted ((27-955) | Siamese Required ((27-959) | Centrala Station Required ((27-955) ((27-967) | Waterb Flow Alarm Required ((27-957) [((3721 of RS17-2)] | Automatic Dry Sprinkler Permitted ((5212 of RS[-]17) | Dry Non-automatic Sprinkler Permittedc |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| High Hazard Bldg. – Group A ((27-954(a)) | 2 | No | No (27-961(c) | No | Yes | Nonea | Yes | Yes | No |
| High Hazard Spaces – Group A ((27-954(b)) | 1 | Yes | No (27-961(c) | No | (27-959(a)(3) If over 36 heads in a fire section | Nonea | Yes If over 36 heads in a fire section | Yes | No |
| Storage Occupancy Bldg. – Group B1 ((27-954(c)) | 1 | No | No (27-961(c) | No | Yes | Nonea | Yes | Yes | No |
| Storage Occupancy Spaces Bldg. – Group B1 ((27-954(d)) | 1 | Yes | Yes (27-961(c) | No | (27-959(a)(3) If over 36 heads in a fire section | Nonea | Yesb If over 36 heads in a fire section | Yes | No |
| Storage Occupancy Spaces – Group B2 ((27-954(e)) | 1 | Yes | No | No | (27-959(a)(3) If over 36 heads in a fire section | Nonea | Yesb If over 36 heads in a fire section | Yes | No |
| Mercantile Occupancy Spaces – Group C Exceeding 7,500 sq. ft. ((27-954(f)) | 2 sources if exceeding 20,000 sq. ft. 1 source if not more than 20,000 sq. ft. | No | No | No | Yes | Nonea | Yes | Yes | No |
| Industrial Occupancy Bldg. – Group D-1, When required by Labor Law ((27-954(g)) | 1 source if not hazardous occupancy | No | No | No | Yes | Nonea | Yes | Yes | No |
| Industrial Occupancy Spaces – Group D-1 exceeding 7,500 sq. ft. ((27-954(h)) | 1 | No | No | No | Yes | Nonea | Yes | Yes | No |
| Business Occupancy Spaces – Group E Showrooms when Required by ((27-954(i)) | 1 | Yes | Yes and/or standpipe riser | No | Yes | Nonea | Yes | Yes | No |
| Assembly Occupancy Spaces – Group F-1a ((27-954(j)) | 1 | Yes | Yes | No | (27-959(a)(3) If over 36 heads in a fire section | Nonea | Yesb | No | No |
| Institutional Occupancy Group H – Corridors and Exit Passageway ((27-954(k)) | 1 | Yes | Yes | No | (27-959(a)(3) If over 36 heads in a fire section | Nonea | Yes | No | No |
| Unventilated Areas Above or below grade ((27-954(l))d | 1 | Yes | Yes | No | (27-959(a)(3) If over 36 heads in a fire section | Nonea | (27-962(e)(8) | Yes | No |
| Rubbish – Laundry and Similar Chutes ((27-954(m))d, e | 1 | Yes | Yes | No | No | [None] Yesa | None | Yes | No |
| Soiled Linen – Collection and Sorting Area ((27-954(n)) | 1 | Yes | Yes | No | (27-959(a)(3) If over 36 heads in a fire section | Nonea | Yes (27-962(e)(8) | Yes | No |
| Workshops ((27-954(o)) d | 1 | Yes | Yes | Yes | (27-959(a)(3) If over 36 heads in a fire section | Yes If smoke detector is used in lieu of sprinkler | Yes (27-962(e)(8) | Yes | No |
| Refuse Collection and Disposal Areas ((27-954(p)) d | 1 | Yes | Yes In Occupancy Groups E,G,J | No | (27-959(a)(3) If over 36 heads in a fire section | Nonea | Yes (27-962(e)(8) | Yes | No |
| Drying Areas – Laundries or Similar Spaces ((27-954(q)) d | 1 | Yes | Yes In Occupancy Groups E,G,J | Yes | (27-959(a)(3) If over 36 heads in a fire section | Yes If smoke detector is used in lieu of sprinkler | Yes (27-962(e)(8) | No | No |
| Cooling Towers ((27-954(r)) | 1 | No | Yes | No | No | Nonea | Yes | Yes | No |
| Buildings and Spaces in Residential Occupancy Group J-1 ((27-954(t)) | 1 | No | Nof | No | Yes, except as provided in (27-959(a)(3) | No | Yes | No | No |
| Buildings and Spaces in Residential Occupancy Group J-2 with 4 or more Dwelling Units and not exceeding 6 stories or 75 feet in height ((27-954(t)) | 1 | No | Yesg | No | Yes, except as provided in (27-959(a)(1) and (27-959(a)(5) | No | Yes | No | No |
| Buildings and Spaces in Residential Occupancy Group J-2 with 4 or more Dwelling Units and exceeding 6 stories or 75 feet in height ((27-954(t)) | 1 | No | Noh | No | Yes, except as provided in (27-959(a)(3) | No | Yes If over 36 heads | No | No |

Notes:

a  Central Station supervision required only when booster pump is provided under (27-964 or when non-automatic sprinkler is permitted by the commissioner.

b  Water flow alarms required when more than 36 heads are installed in a fire section or fire area.

c  Only when permitted by the commissioner ((27-967(c)).

d  [see] See (27-954(w) for requirements pertaining to these spaces located in a building classified in occupancy group J-1.

e  See section 4-4.8 of reference standard RS 17-2.

f  Except as provided in reference standard RS 17-2A.

g  Notwithstanding section 27-962(i) of this chapter.

h  Except as provided in section 27-962(i) of this chapter.