- Staff:	Terzah N. Nasser

Counsel to the Committee

Kamilla Sjödin

###### Legislative Attorney

Benjamin J. Goodman

Legislative Policy Analyst

THE COUNCIL

REPORT OF THE INFRASTRUCTURE DIVISION

ROBERT NEWMAN, LEGISLATIVE DIRECTOR

COMMITTEE ON HOUSING AND BUILDINGS

Erik Martin Dilan, Chair

October 25, 2006

INT. NO. 426-A:	By:	Council Members Dilan, Comrie, Gonzalez, Nelson, Seabrook, Stewart and Baez (by request of the Mayor).

TITLE:	A Local Law to amend the administrative code of the city of New York, in relation to the maintenance of sprinkler systems in certain residential occupancies.

ADMINISTRATIVE CODE:	Repeals section 27-2050 and amends subdivision (c) of section 27-4265.

BACKGROUND AND ANALYSIS:

On October 25, 2006 the Committee on Housing and Buildings, chaired by Council Member Erik Martin Dilan, conducted a hearing on Proposed Int. No. 426-A, A Local Law to amend the Administrative Code of the City of New York, in relation to the maintenance of sprinkler systems in certain residential occupancies.  The Committee conducted its first hearing on this legislation on October 18, 2006.

The Council is concerned about the maintenance of sprinkler systems and the City’s role in the inspection process.  Some property owners have expressed concerns about the current requirements imposed under the Housing Maintenance Code for the annual inspection of a sprinkler system in certain residences as enforced by the Department of Housing Preservation and Development (HPD), while the Fire Department (FDNY) required certain monthly inspections of the same sprinkler system.  As the two different agencies had different inspection timelines, some converted dwellings of more than 3 dwelling units were required to have two of the necessary “flow tests” of their sprinkler system conducted within six-months of the immediately preceding flow test, during every third year of a five-year cycle.  This bill, in part, would streamline the inspection requirements of these sprinkler systems to reduce the confusion, impose new flow testing requirements on certain occupancies and simplify the enforcement tools under one agency, the Fire Department.  This bill would require an inspection of the sprinkler system once every 30 months, if there is a pressure valve, and annually for those sprinkler systems that do not have a pressure valve.

During the first hearing, the Committee heard testimony from representatives of the Fire Department, representatives of the sprinkler industry, other professionals and members of the general public who are concerned with this topic.  HPD estimates that the jurisdictional shift from HPD to FDNY imposed under this bill would apply to roughly 7,500 buildings, mostly brownstones, that were converted from single family homes to multiple dwelling units.

Int. No. 426

Bill section one would repeal section 27-2050 of the Administrative Code of the City of New York to eliminate the requirements within the Housing Maintenance Code for the annual inspection of any sprinkler system installed pursuant to the requirements of the Multiple Dwelling Law in converted dwellings or in tenements used for single room occupancy.  Bill section two would amend subdivision (c) of section 27-4265 of the Administrative Code, which is contained within the Fire Prevention Code and enforced by the Fire Department, by amending paragraph (1) to exempt converted dwellings and tenements used for single room occupancy (regardless of occupancy classification), in which a sprinkler has been installed in accordance with requirements of the Multiple Dwelling Law from the maintenance and inspection requirements imposed pursuant to paragraph (1) upon buildings and spaces that are not classified in occupancy group J-2 and J-3.

Subparagraph (a) of paragraph (2) of subdivision (c) of section 27-4265 would be amended to provide that in converted dwellings or tenements used for single room occupancy (regardless of occupancy classification), in which a sprinkler has been installed in accordance with the requirements of the Multiple Dwelling Law and in buildings in occupancy group J-2, including those with three or more dwelling units, regardless of height, as amended by this provision, both automatic and non-automatic sprinkler systems shall be inspected once a month by a competent person employed by property owner who holds either a certificate of fitness issued by the FDNY, a fire suppression contractor license issued by the Department of Buildings (DOB), or a master plumber’s license issued by DOB when the sprinkler system does not have more than thirty sprinkler heads.  Current law covers buildings in occupancy group J-2 having four or more dwelling units and requires the inspection of sprinkler systems therein at least once every six months by a competent person in those buildings that both do not exceed six stories or seventy-five feet in height and that have a secondary means of egress.  Furthermore, the inspection requirements would be amended to require that a check of all control valves be conducted, including the main supply control valve, and to require a check of the static pressure in the sprinkler system from a pressure gauge, if installed.

Subparagraph (c) of paragraph (2) of subdivision (c) of such section would mandate that the Fire Commissioner order that a flow test of the sprinkler system be conducted at least once a year, rather than every thirty months.  However, the requirements of this subparagraph do not apply to converted dwellings or tenements used for single room occupancy (regardless of occupancy classification), in which a sprinkler has been installed due to the requirements of the Multiple Dwelling Law.  Alternatively, if the pressure is checked during the required monthly inspection described in subparagraph (a) of paragraph (2) of such section then the flow test must be conducted at least once every thirty months.

Paragraph (3) of subdivision (c) of section 27-4265 would be amended to make a conforming text change to still reflect that a system of automatic sprinklers in one- and two- family homes be maintained in perfect working order.  As such three-family homes will now be subject to the above requirements of sprinkler system testing described herein above.

Bill section three provides that this law would become effective 180 days after enactment, however, the Fire Commissioner may take any necessary actions to implement this local law before its effective date.

A-version

The A-version contains a text amendment to correct an incorrect internal cross-reference within the original bill.  At roughly the top of page 4, the reference within subparagraph c of paragraph 2 of subdivision c of section 27-4265 of Int. No. 426 referred to “... the required monthly inspection described in subparagraph a of this subdivision to make certain the system design pressure is being maintained, …” (emphasis added) and the A-version was amended to read “... described in subparagraph a of this paragraph ....” (emphasis added).

Update

On Wednesday, October 26, 2006, the Committee adopted this legislation by a vote of eleven in the affirmative, zero in the negative and no abstentions.

Accordingly, the Committee recommends its adoption.