Int. No. 268

By Council Members Lander, Barron, Brewer, Chin, Vann, Williams, Mark-Viverito, Lappin, Nelson, Garodnick, Recchia Jr., Arroyo, Rodriguez, Van Bramer and Gennaro

..Title

A Local Law to amend the administrative code of the city of New York, in relation to preventing water waste in buildings.

..Body

Be it enacted by the Council as follows:

Section 1.  Statement of findings and purpose.  Leaks and equipment malfunctions have the potential to waste a tremendous amount of water in New York City buildings and they can persist undetected for years.  The Council therefore finds that sub-meters attached to major water-using equipment will help building managers quickly detect such leaks and malfunctions, and save significant amounts of water from being wasted.

§2.  Section 606.5.4.1 of the New York city plumbing code, as added by local law number 33 for the year 2007, is amended to read as follows:

606.5.4.1 Water piping control and location. Water inlets to gravity house tanks shall be controlled by a ball cock or other automatic supply valve or emergency electrical cut-off so installed as to prevent the overflow of the tank in the event that the pumps filling the tanks do not shut off at the predetermined level or the street pressure rises to a point where it can fill the tank. The water inlet to a suction tank shall be controlled by a ball cock or other automatic supply valve. The inlet shall be terminated so as to provide an accepted air gap but in no case shall it be less than 4 inches (102 mm) above the top of the overflow. The outlet from a gravity tank to the distribution system shall be equipped with a strainer located at least 2 inches (51 mm) above the tank bottom to prevent solids from entering the piping system. All down-feed supplies from a tank cross connected in any manner with distribution supply piping in a building supplied by direct street or pump pressure, shall be equipped with a check valve on the main cold water down supply to prevent backflow of water into the roof tank. All roof tanks shall be provided with a high water level alarm, at or slightly below the overflow, designed to activate when the ball cock, automatic supply valve, or emergency electrical cut-off fails.

§3.  Section 606 of the New York city plumbing code, as added by local law number 33 for the year 2007, is amended by adding a new section 606.7 to read as follows:

606.7 Equipment and area sub-meters. Water sub-meters from a list promulgated by the department of environmental protection shall be installed on the makeup water lines for the following:

1.	evaporative cooling towers

2.	commercial cooking facilities

3.	commercial laundry facilities

4.	commercial gyms and spas

5.	swimming pools

Exception: Swimming pools accessory to Group R-3 occupancies

§4.  Section 608.16.2 of the New York city plumbing code, as added by local law number 33 for the year 2007, is amended to read as follows:

608.16.2 Connections to boilers. The potable supply to the boiler shall be equipped with a backflow preventer with an intermediate atmospheric vent complying with ASSE 1012 or CAN/CSA B64.3. Where conditioning chemicals are introduced into the system, the potable water connection shall be protected by an air gap or a reduced pressure principle backflow preventer, complying with ASSE 1013, CAN/CSA B64.4 or AWWA C511. Makeup water supplies to boilers serving buildings greater than six stories shall be equipped with a water sub-meter from a list promulgated by the department of environmental protection along with inlet and outlet isolation valves.

§5.   This local law shall take effect on January 1, 2011, except that the commissioner of buildings shall take such actions as are necessary for its implementation, including the promulgation of rules, prior to such effective date.

.

LS # 995

6-4-10 12 pm

DB

WE 3