Robert C. Calandra

### Counsel

William Hongach

Policy Analyst

## THE COUNCIL

# REPORT OF THE

# GOVERNMENTAL AFFAIRS DIVISION

Robert Newman, Legislative Director

Alix Pustilnik, Deputy Director, Governmental Affairs

COMMITTEE ON FIRE & CRIMINAL JUSTICE SERVICES

Hon. James Vacca, Chair

#### June 2, 2009

INT. NO. 986:	By Council Member Baez and the Speaker (Council Member Quinn) (in conjunction with the Mayor)

TITLE:	A Local Law to amend the administrative code of the city of New York and the New York city building code, in relation to hydrostatic pressure testing of standpipes and sprinklers.

ADMINSTRATIVE CODE:  	Amends subsection 1704.21 of section BC 1704 of 					 	chapter 17 of the New York city building code of 						chapter 7 of title 28 of the administrative code of 						the city of New York.

Adds subsection 1704.21.1

INT. NO. 1002:	By Council Member James and the Speaker (Council Member Quinn) (in conjunction with the Mayor)

TITLE:				..Title

A Local Law to amend the administrative code of the city of New York, in relation to prohibiting smoking at construction sites.

ADMINISTRTIVE CODE:		Adds section BC 3303.7.3

INT. NO. 1004:	By Council Member Sanders, Jr. and the Speaker (Council Member Quinn) (in conjunction with the Mayor)

TITLE:				..Title

A Local Law to amend the administrative code of the city of New York and the New York city building code, in relation to an air pressurized alarm system for standpipes.

ADMINISTRATIVE CODE:	Adds subsection BC 3303.8.

INT. NO. 1007:	By Council Member Vacca and the Speaker (Council Member Quinn) (in conjunction with the Mayor)

TITLE:				..Title

A Local Law to amend the administrative code of the city of New York, in relation to inter-agency notification.

ADMINISTRATIVE CODE:	Adds section 28-103.7.1

..Body

###### I.	INTRODUCTION:

On June 2, 2009, the Committee on Fire and Criminal Justice Services, chaired by Council Member James Vacca, will hold a hearing on the above-referenced legislation.  Those invited to testify include representatives of the New York City Fire Department (“FDNY”), the Department of Buildings (“DOB”), the Department of Environmental Protection (“DEP”), the Uniformed Fire Officers Association (“UFOA”), the Uniformed Firefighters (“UFA”), the New York Building and Construction Trades Council of Greater New York, the General Contractors Association of New York, the Environmental Contractors Association of New York City, the Real Estate Board of New York as well as various stakeholders and other interested parties.

II.	BACKGROUND:

On August 18, 2007, a fire in the former Deutsche Bank Building at 130 Liberty Street in Manhattan led to the deaths of New York City Firefighters Joseph Graffagnino and Robert Beddia and resulted in injuries to several others. 130 Liberty Street was a 26 story high-rise office building which was undergoing asbestos abatement and demolition at the time of the fire. As early as August 20, 2007 the FDNY announced it was investigating the possibility that the fire was caused by a discarded cigarette on the 17th floor, with later investigations concluding the cause of the fire was the careless discard of smoking material in the asbestos decontamination area on the south side of the building on the 17th floor. The FDNY also concluded shortly thereafter that the sprinkler system was damaged and out of service and that there was no working standpipe in the building on the day of the fire, which resulted in significant delay in getting water on the fire.  These and other findings led Council Members to pursue legislative solutions to the problems being uncovered and prompted the City of New York to undertake a comprehensive review of the way construction, demolition, and abatement operations are regulated and conducted in the City. The four bills before this Committee are part of a package of twelve bills that resulted from a collaborative process between the Administration and the Council. These bills combine the findings and recommendations of a Working Group (“the Working Group”) called for by the mayor on this subject with legislative proposals put forth by Council Members in the wake of the fire.  The bills are collectively intended to improve construction, demolition, and asbestos abatement procedures in the City of New York.

III. 	ANALYSIS OF INT. NO. 986

At the time of the 130 Liberty Street fire the Fire Prevention Code required the owners of occupied buildings to conduct a hydrostatic test of standpipes once every five years, a process that involves fully charging the system with water and utilizing pressure gauges to confirm its suitability for FDNY operations. However, while buildings being demolished were required to maintain an operational standpipe, no separate hydrostatic pressure test of the standpipe system was required by virtue of the fact the building was undergoing demolition.  The last hydrostatic test of the 130 Liberty Street standpipe and sprinkler systems on record was conducted on November 12 and 13, 1996, when both systems were deemed satisfactory. The next hydrostatic test was scheduled for November 2001, two months after the September 11 terrorist attacks.  That test did not occur due to the condition of the building. The New York City Building Code required buildings undergoing a demolition to maintain non-automatic systems unless a variance had been requested and approved by the FDNY. According to the FDNY investigation, no such variance had been granted at 130 Liberty Street at the time of the fire. Regarding newly constructed buildings, the Working Group reported that at the time of their report these buildings were only required to pressure test the standpipe at the end of construction.

Therefore, among other things aimed at ensuring that all buildings which require them have working standpipes, the Working Group recommended that DOB should amend its rules and/or seek legislation to require a licensed plumber or fire suppression contractor to pressure test standpipe systems every 75 feet for buildings under construction. Int. No. 986 requires hydrostatic pressure testing for new or altered sprinkler systems and for new or altered standpipe systems as detailed below.

Section 1 of Int. No. 986 amends subsection 1704.21 of section BC 1704 of chapter 17 of the New York City Building Code of chapter 7 of title 28 of the Administrative Code of the City of New York by providing that new or altered sprinkler systems shall be inspected in accordance with new section 1704.21.1 and clarifying that the special inspector need not witness the hydrostatic test when such test is witnessed by the DOB. Additionally, this section requires that the special inspector shall verify that any painting of the sprinkler system required by section 903.6 has been performed. Finally, section 1 adds a new subsection 1704.21.1 which provides that all new or altered sprinkler systems in buildings shall undergo successful hydrostatic pressure testing by a licensed master plumber or licensed fire suppression piping contractor in accordance with the requirements of the code, including Section 901.5, and NFPA 13 § 10.10.2.2, as modified in Appendix Q.

Section 2 amends subsection 1704.22 of section BC 1704 of chapter 17 of the New York City Building Code of chapter 7 of title 28 of the Administrative Code of the City of New York, and adds a new subsection 1704.22.1.

Subsection 1704.22 is amended to require that new or altered standpipe systems shall be inspected in accordance with new section 1704.22.1. Additionally, this section amends subsection 1704.22 by requiring the special inspector verify that any painting of the standpipe system required by section 905.11 has been performed and clarifies that the special inspector need not witness the hydrostatic test when such test is witnessed by the DOB.

New subsection 1704.22.1 requires that all new or altered standpipe systems in building shall undergo successful hydrostatic pressure testing by a licensed master plumber or licensed fire suppression piping contractor in accordance with NFPA 14 § 11.4 and the requirements of the code, including section 901.5 and new sections 1704.22.1.1 through 1704.22.1.5 described below.

Section 1704.22.1.1 requires an initial test be performed when a new building reaches a height of 75 feet (22 860 mm) and additional tests every 75 feet (22 860 mm) thereafter.  The permit holder shall also perform a final test of the system in accordance with the requirements of section 901.5.

Section 1704.22.1.2 requires hydrostatic tests be performed every 75 feet (22 860) where there is an enlargement that triggers a new standpipe system or where there is an addition to an existing standpipe system.

Section 1704.22.1.3 requires hydrostatic testing be performed on existing standpipes where stories are removed from a building, prior to the commencement of work, if the building is in violation of enumerated sections of the Fire Code.

Section 1704.22.1.4 requires the permit holder to perform a final test of the completed system in accordance with the requirements on section 901.5 for alterations not covered under sections 1704.22.1.2 or 1704.22.1.3.

Section 1704.22.1.5 provides that no standpipe system shall be considered in readiness until there has been a successful hydrostatic test.

Section 3 provides that this local law shall take effect six months after enactment except that the commissioner of buildings may promulgate rules or take other administrative actions for the implementation of this local law prior to such effective date.

IV.	ANALYSIS OF INT. NO. 1002

Currently, the New York City Fire Code prohibits smoking at construction sites and federal regulation and DEP rules prohibit smoking in asbestos work places. The Working Group recommended that the Citywide smoking ban at construction, demolition, and abatement sites should be strengthened and enforced with a zero-tolerance approach.  Specifically, the Working Group recommended that DOB should amend its rules and/or seek legislation to ban smoking in all areas within a construction or demolition site and should consider whether additional penalties or mechanisms are needed to enforce the prohibition.  Additionally, the Working Group recommended that DOB should amend its current protocols to prohibit smoking in construction sites, in furtherance of existing requirements for contractors to institute and maintain safety measures during construction and demolition. This legislation will enhance the existing smoking prohibitions by including them in the building code, which will increase awareness of the prohibitions and allow for greater enforcement and protection by building inspectors in the hope of preventing future fires from taking place.

Section 1 of Int. No. 1002 amends section BC 3303 of the building code of the City of New York by adding a new section 3303.7.3 which (i) prohibits smoking at all construction and demolition sites and (ii) requires signs to be posted in accordance with the provisions of Fire Code Section 310 and any rules promulgated thereunder.

Section 2 provides that this local law shall take effect take effect in 60 days.

V.	ANALYSIS OF INT. NO. 1004

At the time of the 130 Liberty Street fire there was no requirement that buildings undergoing construction or demolition had to have dry standpipe alarms that would sound if a standpipe were compromised. When the Working Group issued its report, they indicated that the FDNY Manhattan Borough Command had reacted favorably to pressurized standpipe alarms that were being piloted by private contractors. The Working Group recommended that the FDNY and DOB study the feasibility of requiring the installation of a pressurized standpipe alarm system (or other security measures) on new building and full demolition jobs, and make recommendations pertaining to the adoption of rules or proposal of legislation to implement such requirement. Subsequent to the 130 Liberty Street fire, a pressurized alarm was installed in the former Deutsche Bank building. On February 5, 2009 a standpipe at 130 Liberty Street was once again severed. An alarm sounded at 8:30 a.m. on that day, signaling the standpipe had lost pressure, which ultimately resulted in the evacuation of the building and the issuance of a stop work order until the standpipe was fixed.

Section 1 of Int. No. 1004 amends subsection 3303.8 of section BC 3308 of chapter 33 of the New York City Building Code of chapter 7 of title 28 of the Administrative Code of the City of New York and adds a new subsection 3303.8.1, which requires an air pressurized alarm system for dry standpipe systems during construction or demolition operations. Paragraph 1 of this new subsection requires that in vacant buildings undergoing demolition, existing standpipes shall be maintained in readiness as dry standpipes in accordance with section 3303.8 and shall be provided with an air pressurized alarm system. Paragraph 2 requires that a temporary standpipe shall be in readiness once a new building reaches 75 feet (22 860 mm) in height and shall contain an air pressurized alarm system. Paragraph 3 requires that an application to install an alarm system be filed by a registered design professional and that a licensed electrician obtain any required electrical permits in accordance with the code. Paragraph 4 establishes the specification for the required alarm systems such as such as; pressure, alarm activation, air compressor, alarm, power supply, check valves, locks and caps, FDNY connections, drainage, manual air release connection, construction documents, and signage.

Section 2 provides that this local law shall take effect six months after enactment except that the commissioner of buildings may promulgate rules or take other administrative actions for the implementation of this local law prior to such effective date.

VI.     ANALYSIS OF INT. NO. 1007

The Working Group found that the DOB, DEP and FDNY recorded inspection results in three different formats. Specifically: (i) DOB inspectors were recoding results for new buildings and full demolitions on paper inspection cards; (ii) FDNY inspectors were recording results in a sharable database for 15-day inspections and on paper inspection cards for 30-day and other field inspections; and inspections conducted by the Bureau of Fire Prevention were recorded on paper, then entered into a database; and (iii) DEP abatement inspectors were recording results in an internal database that was not being shared. As a result, individual inspectors across agencies did not have the means to know when a location had been inspected by another agency, or the results of that inspection. The Working Group recommended that the DOB, FDNY, and DEP implement a system to share relevant results of inspections of buildings that meet agreed-upon criteria. The Working Group recommended that the FDNY develop a computer-based process to share inspection data internally and with DOB and DEP. In the short term, it was recommended that the FDNY, DOB, and DEP implement a mechanism such as a common database which would enable them to share relevant inspection results that meet agreed-upon criteria.  Over the long term, it was recommended that the FDNY, DOB, and DEP develop a comprehensive data-sharing mechanism that would capture relevant inspection results that might include open stop work orders, violations, and other data. While the relevant agencies have already begun to implement some of the Working Group recommendations, Int. No. 1007 mandates that the Buildings Commissioner, the Fire Commissioner and the Commissioner of Environmental Protection shall establish procedures to share information regarding violations issues as a result of inspections of buildings meeting agreed upon criteria that are relevant to the responsibilities of each department as related below.

Int. No. 1007 amends the Administrative Code of the City of New York, in relation to inter-agency notification. Section 1 adds a new section 28-103.7.1 that requires the Building Commissioner, the FDNY Commissioner and DEP Commissioner to establish a procedure to share information regarding violations issued as a result of inspections of buildings meeting agreed-upon criteria that are relevant to the responsibilities of each department.

Section 2 amends Chapter 2 of title 29 of the Administrative Code of the City of New York, by adding a new subsection FC 106.4 that requires the Fire Commissioner, the Building Commissioner and the Commissioner of DEP to establish a procedure to share information regarding violations in accordance with the requirements of the new section 28-103.7.1.

Section 3 amends section 24-146.1 of the Administrative Code by adding a new subdivision (n) that requires the Commissioner of DEP, in coordination with the Commissioner of the FDNY and Commissioner of DOB, to establish a procedure to share information regarding violations in accordance with the requirements of section 28-103.7.

Section 4 provides that this law shall take effect six months after its enactment and that one year after enactment a copy of the procedure established in accordance with section 28-103.7.1 shall be provided to the City Council.

Int. No. 986

- By Council Member Baez and the Speaker (Council Member Quinn) (in conjunction with the Mayor)

..Title

A Local Law to amend the administrative code of the city of New York and the New York city building code, in relation to hydrostatic pressure testing of standpipes and sprinklers.

..Body

Be it enacted by the Council as follows:

Section 1.  Subsection 1704.21 of section BC 1704 of chapter 17 of the New York city building code of chapter 7 of title 28 of the administrative code of the city of New York, as added by local law number 33 for the year 2007, is amended and a new subsection 1704.21.1 is added to read as follows:

1704.21 Sprinkler system special inspection. New and altered sprinkler [system] systems shall be inspected in accordance with [Section] Sections 903 and 1704.21.1. The permit holder responsible for the sprinkler work shall perform all required acceptance tests, complete and sign the appropriate contractor’s material and test certifications. The special inspector shall witness all required tests, and shall verify that all installations of all materials, fittings, hangers, assemblies and signage are in accordance with the approved construction documents, that any painting of the sprinkler system required by Section 903.6 has been performed and that the contractor has transmitted required maintenance literature and instruction to the owner. The special inspector shall verify that the material and test certification forms have been transmitted to the Fire Department and the department.

Exception: [Special inspection of] The special inspector need not witness the hydrostatic test [shall not be required] when such test is witnessed by the department.

1704.21.1  Hydrostatic pressure testing.  All new or altered sprinkler systems in buildings shall undergo successful hydrostatic pressure testing by a licensed master plumber or licensed fire suppression piping contractor in accordance with the requirements of this code, including Section 901.5, and NFPA 13 § 10.10.2.2, as modified in Appendix Q.

§2.  Subsection  1704.22 of Section BC 1704 of chapter 17 of the New York city building code of chapter 7 of title 28 of the administrative code of the city of New York, as added by local law number 33 for the year 2007, is amended and a new subsection 1704.22.1 is added to read as follows:

1704.22 Standpipe system special inspection. New and altered standpipe systems shall be inspected in accordance with [Section] Sections 905 and 1704.22.1. The permit holder responsible for the standpipe work shall perform all required acceptance tests, complete and sign the appropriate contractor’s material and test certifications. The special inspector shall witness all required tests, verify that installation of all materials, fittings, hangers, assemblies and signage are in accordance with the approved construction documents, that any painting of the standpipe system required by Section 905.11 has been performed and that the contractor has transmitted required maintenance literature and instruction to the owner. The special inspector shall verify that the material and test certification forms have been transmitted to the Fire Department and the department.

Exception:  [Special inspection of] The special inspector need not witness the hydrostatic test [shall not be required]when such test is witnessed by the department.

1704.22.1  Hydrostatic pressure testing.  All new or altered standpipe systems in buildings shall undergo successful hydrostatic pressure testing by a licensed master plumber or licensed fire suppression piping contractor in accordance with the requirements of this code, including Section 901.5, Sections 1704.22.1.1 through 1704.22.1.5 and NFPA 14 §11.4.

1704.22.1.1  New buildings. An initial test shall be performed when the building reaches a height of 75 feet (22 860 mm) and additional tests shall be performed at every 75 feet (22 860 mm) thereafter.  The permit holder shall perform a final test of the completed system in accordance with the requirements of Section 901.5.

1704.22.1.2  Enlargements or additions to existing system.  Where there is an enlargement that triggers a new standpipe system or there is an addition to an existing standpipe system, hydrostatic tests shall be performed every 75 feet (22 860 mm).  The permit holder shall perform a final test of the completed system in accordance with the requirements of Section 901.5.

1704.22.1.3  Removal of stories.  Where stories are removed from a building served by an existing standpipe system, hydrostatic testing shall be performed prior to the commencement of work if the building is in violation of Sections 905.12, 905.12.1 and 912.6 of the New York City Fire Code.

1704.22.1.4  Alterations.  For alterations not covered under sections 1704.22.1.2 or 1704.22.1.3, above, the permit holder shall perform a final test of the completed system in accordance with the requirements of Section 901.5.

1704.22.1.5  Readiness. No standpipe system shall be considered in readiness until there has been a successful hydrostatic test.

§3.  This local law shall take effect six months after enactment except that the commissioner of buildings may promulgate rules or take other administrative actions for the implementation of this local law prior to such effective date.

RCC

BKH

5/14/09

1:30 p.m.

LS # 6583

Int. No. 1002

- By Council Member James and the Speaker (Council Member Quinn) (in conjunction with the Mayor)

..Title

A Local Law to amend the administrative code of the city of New York, in relation to prohibiting smoking at construction sites.

..Body

Be it enacted by the Council as follows:

Section 1.  Section BC 3303 of the building code of the city of New York is amended to add a new section 3303.7.3 to read as follows:

3303.7.3 Smoking.  Smoking shall be prohibited at all construction and demolition sites. Signs shall be posted in accordance with the provisions of Fire Code Section 310 and any rules promulgated thereunder.

§ 2.  This local law shall take effect in 60 days.

RCC

BKH

05/07/09

7:00 p.m.

LS #s 3857, 7084

Int. No. 1004

- By Council Member Sanders, Jr. and the Speaker (Council Member Quinn) (in conjunction with the Mayor)

- ..Title

- A Local Law to amend the administrative code of the city of New York and the New York city building code, in relation to an air pressurized alarm system for standpipes.

- ..Body

- Be it enacted by the Council as follows:

Section 1. Subsection 3303.8 of section BC 3308 of chapter 33 of the New York city building code of chapter 7 of title 28 of the administrative code of the city of New York, as added by local law number 33 for the year 2007, is amended by adding a new subsection 3303.8.1 to read as follows:

3303.8.1  Air pressurized alarm system for dry standpipe systems during construction or demolition operations.  Air pressurized alarm systems shall be provided as set forth in items 1 through 4. The provisions of NFPA 14, Chapter 12, as modified by Appendix Q, shall also apply.

- Demolitions.  In vacant buildings undergoing demolition, existing standpipes shall be maintained in readiness as dry standpipes in accordance with item 2 of Section 3303.8 and shall be provided with an air pressurized alarm system.

- New buildings.  A required or temporary standpipe shall be in readiness once the new building reaches 75 feet (22 860 mm) in height and shall contain an air pressurized alarm system.

- Submission of application.  An alteration application to install such system shall be filed by a registered design professional.  A licensed electrician shall obtain any required electrical permits in accordance with Chapter three of Title 27 of the Administrative Code.

- Specifications.  The following provisions shall apply to the alarm system:

4.1	Pressure.  Air pressure shall be maintained in the standpipe at all times and shall not exceed 25 psig (172.4 kPa gauge).  The supervisory pressure shall be as determined by a registered design professional.

4.2	Alarm activation.  The alarm shall be activated when the pressure drops below the supervisory pressure or rises above the maximum pressure of 25 psig (172.4 kPa gauge).  When the alarm is activated, repairs to the standpipe necessary to restore the required pressure shall be undertaken immediately.  All work at the site shall cease until the standpipe system is repaired and the appropriate pressure is restored.

4.3	Air compressor.  The air compressor shall be designed to automatically cut in and cut out at the supervisory pressure. The air compressor shall utilize an air dryer during times when freezing conditions exist to condition the air entering the dry standpipe system.

4.4	Alarm.  The standpipe alarm system shall utilize pressure switches and control equipment to annunciate a local audible alarm on site that can be heard during working and non-working hours.  The audible signal of the horn shall be at least 15 dBA above the ambient noise level but no more than 110 dBA.

4.5	Power supply.  The standpipe alarm system shall be connected to an active power supply at all times.

4.6	Check valves.  Check valves shall be installed to prevent water from entering the air compressor.

4.7	Locks and caps.  All control valves shall be chained and locked in the appropriate position and shall be provided with capped outlets.  All hose valves shall also be provided with capped outlets.

4.8	Fire Department connections.  Three-inch cast iron house threaded plugs with gaskets in Fire Department connection swivels shall be provided.

4.9	Drainage.  Provisions shall be made to drain water in any trapped sections of the dry standpipe system that are subject to freezing.

4.10	Manual air release connection.  A minimum 2.5-inch (63.5 mm) connection located immediately downstream of the Fire Department Siamese connection check valve shall be provided and  piped to a location immediately adjacent to the Siamese connections.  This line shall be fitted with a 2.5-inch (63.5 mm) hose valve and shall allow for release of the pressurized air from the dry standpipe system. The number of air release valves provided shall be such that the air pressure shall be released in no more than 3 minutes, which shall be verifiable by an actual air release test in conjunction with the final acceptance testing.

4.11	Construction documents.  Plans shall identify all standpipe risers, intermediate check valves that have to be removed, proposed location of the air release connections, and complete information regarding the alarm system.

4.12	Signage.  Signage shall be provided at all Siamese connections indicating that the dry standpipe system is pressurized and showing the location of the manual air release

§2.  This local law shall take effect six months after enactment except that the commissioner of buildings may promulgate rules or take other administrative actions for the implementation of this local law prior to such effective date.

RCC

BKH

05/07/09

7:00 p.m.

LS # 7085

Int. No. 1007

- By Council Member Vacca and the Speaker (Council Member Quinn) (in conjunction with the Mayor)

..Title

A Local Law to amend the administrative code of the city of New York, in relation to inter-agency notification.

..Body

Be it enacted by the Council as follows:

Section 1.  The administrative code of the city of New York is amended by adding a new section 28-103.7.1 to read as follows:

§ 28-103.7.1  Sharing results of buildings inspections.  The commissioner, the fire commissioner and the commissioner of the department of environmental protection shall establish a procedure, the implementation of which shall begin within six months of the effective date of this section, to share information regarding violations issued as a result of inspections of buildings meeting agreed-upon criteria that are relevant to the responsibilities of each department.

§2. Chapter 2 of title 29 of the administrative code of the city of New York is amended by adding a new subsection FC 106.4 to read as follows:

FC 106.4.  Sharing results of inspections.  The commissioner, in coordination with the Commissioner of Buildings and the Commissioner of Environmental Protection, shall establish a procedure to share information regarding violations in accordance with the requirements of Section 28-103.7.1 of the administrative code of the city of New York.

§3. Section 24-146.1 of the administrative code of the city of New York is amended by adding a new subdivision (n) to read as follows:

(n)  Sharing the results of inspections.  The commissioner, in coordination with the commissioner of the department of buildings and the fire commissioner, shall establish a procedure to share information regarding violations issued pursuant to this section, in accordance with the requirements of section 28-103.7.1 of the administrative code of the city of New York.

§4.  This local law shall take effect six months after its enactment. Upon the passage of one year after this local law’s enactment, a copy of the procedure established in accordance with the requirements of Section 28-103.7.1 of the administrative code of the city of New York shall be provided to the Council.

RCC

BKH

05/07/09

7:00 p.m.
LS # 6584

Fire Department City of New York Safety and Inspection Services Command, Investigative Report 130 Liberty Street, Volume 1, at pg. 5..

News from the BLUE ROOM, Multi-Agency Update on Fire at 130 Liberty Street, August 20, 2007.

Supra, note 1.

New from the BLUE ROOM, Update on Investigations of the Fire at 130 Liberty Street, August 22, 2007.

In the fall of 2007, Deputy Mayor Edward Skyler convened a Working Group that included representatives of the Department of Buildings , Department of Environmental Protection , New York City Fire Department, the Mayor’s Office of Operations, and the Law Department to review how the City regulates construction, demolition and abatement operations, including agency practices regarding enforcement, and the ways these operations are conducted in the field. See, Strengthening the Safety, Oversight and Coordination of Construction, Demolition and Abatement Operations, Report and Recommendations to Mayor Michael R. Bloomberg, July 2008.

Strengthening the Safety, Oversight and Coordination of Construction, Demolition and Abatement Operations, Report and Recommendations to Mayor Michael R. Bloomberg, July 2008.

Id.

Id.

Id.

Id.

Supra, note 1 at pg. 3.

Supra, note 6 at pg. 20.

Fire Code Section 1404.1, Federal Regulation 1910.1001(i)(4) and 1926.1101(j)(4).

Supra, note 6 at pg. 20.

Id at pg. 21.

Id.

Supra, note 6 at pg. 20.

Workers Sever Standpipe that Turned Deutsche into Deathtrap…Again, By Jonathan Lemire and Bill Hutchinson, Febraury 6, 2009 – New York Daily News.

Id.

Id.

Id.