Proposed Int. No. 1939-A

By Council Members Maisel, Kallos, Chin, Yeger, Powers, Rosenthal, Rivera and Cumbo

..Title

A Local Law to amend the New York city building code, in relation to requiring standby power for nursing homes, adult homes, enriched housing and certain assisted living facilities

..Body

Be it enacted by the Council as follows:

Section 1. Chapter 4 of the New York city building code is amended by adding a new section BC 426 to read as follows:

SECTION BC 426

NURSING HOMES, ADULT HOMES, ENRICHED HOUSING

AND ASSISTED LIVING FACILITIES

426.1 General. The provisions of Section 426.2 apply to I-1, I-2 and R-2 occupancies that are nursing homes, adult homes, enriched housing and assisted living facilities.

Exception:  This section does not apply to alcohol and drug abuse rehabilitation centers, halfway houses, congregate care facilities and social rehabilitation facilities.

426.2 Standby power. Nursing homes, adult homes, enriched housing and assisted living facilities shall be provided with standby power systems capable of providing power for at least 72 hours for the standby power loads specified in Section 426.2.1.

426.2.1 Standby power loads. The following loads are classified as standby power loads:

1.	In buildings having more than one occupied floor, at  least  one  elevator  serving  all  floors,  or  one  elevator  per  bank  where  different  banks  serve  different  portions  of  the building;

2.	Air conditioning, cooling, and heating systems sufficient to maintain temperature and humidity in accordance with Section 1204 in at least one common space which can accommodate all occupants of such facility or in all spaces used by occupants of such facility for sleeping purposes;

3. 	Refrigerators and freezers located in the facility; and

4. 	Lighting in all hallways.

§ 2. Section 2702.2 of the New York city building code is amended by adding a new section 2702.2.21 to read as follows:

2702.2.21 Nursing homes, adult homes, enriched housing and assisted living facilities. Standby power shall be provided in I-1, I-2 or R-2 occupancies that are nursing homes, adult homes, enriched housing and assisted living facilities, other than those excluded by exception pursuant to Section 426.1, in accordance with Section 426.2.

§ 3. This local law takes effect immediately.

NAB/APB

LS #11750

12/18/20 3:14 pm