TABLE 17-2  SUMMARY OF SPRINKLER REQUIREMENTS

| #### Where Required Type of System |  | Automatic Sources Required |  | Partial System Permitted |  | Connection to Domestic Permitted |  | Alternate Permitted (§27-955) |  | Siamese Required (§27-959) |  | Centrala Station Required (§27-955) (§27-967) |  | Waterb Flow Alarm Required (§27-957) [(§3721 of RS17-2)] |  | Automatic Dry Sprinkler Permitted (§5212 of RS[-]17) |  | Dry Nonautomatic Sprinkler Permittedc |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| High Hazard Bldg. – Group A (§27-954(a)) |  | 2 |  | No |  | No §27-961(c) |  | No |  | Yes |  | Nonea |  | Yes |  | Yes |  | No |
| High Hazard Spaces – Group A (§27-954(b))b |  | 1 |  | Yes |  | No §27-961(c) |  | No |  | §27-959(a)(3) If over 36 heads in a fire section |  | Nonea |  | Yes If over 36 heads in a fire section |  | Yes |  | No |
| Storage Occupancy Bldg. - Group B1 (§27-954(c)) |  | 1 |  | No |  | No §27-961(c) |  | No |  | Yes |  | Nonea |  | Yes |  | Yes |  | No |
| Storage Occupancy Spaces [Bldg.] – Group B1 (§27-954(d)) |  | 1 |  | Yes |  | Yes §27-961(c) |  | No |  | §27-959(a)(3) If over 36 heads in a fire section |  | Nonea |  | Yesb If over 36 heads in a fire section |  | Yes |  | No |
| Storage Occupancy Spaces – Group B2 (§27-954(e)) |  | 1 |  | Yes |  | No |  | No |  | §27-959(a)(3) If over 36 heads in a fire section |  | Nonea |  | Yesb If over 36 heads in a fire section |  | Yes |  | No |
| Mercantile Occupancy Spaces – Group C Exceeding 7,500 sq. ft. (§27-954(f)) |  | 2 sources if exceeding 20,000 sq. ft. 1 source if not more than 20,000 sq. ft. |  | No |  | No |  | No |  | Yes |  | Nonea |  | Yes |  | Yes |  | No |
| Industrial Occupancy Bldg. - Group D-1, When required by Labor Law (§27-954(g)) |  | 1 source if not hazardous occupancy |  | No |  | No |  | No |  | Yes |  | Nonea |  | Yes |  | Yes |  | No |
| Industrial Occupancy Spaces. –Group D-1, exceeding 7,500 sq. ft. (§27-954(h)) |  | 1 |  | No |  | No |  | No |  | Yes |  | Nonea |  | Yes |  | Yes |  | No |
| Business Occupancy Spaces - Group E Showrooms when Required by (§27-954(i)) |  | 1 |  | Yes |  | Yes and/or Standpipe Riser |  | No |  | Yes |  | Nonea |  | Yes |  | Yes |  | No |
| Assembly Occupancy Spaces - Group F-1a (§27-954(j)) |  | 1 |  | Yes |  | Yes |  | No |  | §27-959(a)(3) If over 36 heads in a fire section |  | Nonea |  | Yesb |  | No |  | No |
| Institutional Occupancy Group H - Corridors and Exit Passageway (§27-954(k)) |  | 1 |  | Yes |  | Yes |  | No |  | §27-959(a)(3) If over 36 heads in a fire section |  | Nonea |  | Yes |  | No |  | No |
| Unventilated Areas Above or Below Grade (§27-954(l))d |  | 1 |  | Yes |  | Yes |  | No |  | §27-959(a)(3) If over 36 heads in a fire section |  | Nonea |  | §27-962 (e)(8) |  | Yes |  | No |
| Rubbish – Laundry and Similar Chutes (§27-954(m))d,e |  | 1 |  | Yes |  | Yes |  | No |  | No |  | [None] Yesa |  | None |  | Yes |  | No |
| Soiled Linen – Collection and Sorting Area (§27-954(n)) | 1 |  | Yes |  | Yes |  | No |  | §27-959(a)(3) If over 36 heads In a fire section |  | Nonea |  | Yes §27-962 (e)(8) |  | Yes |  | No |  |
| Workshops (§27-954(o))d | 1 |  | Yes |  | Yes |  | Yes |  | §27-959(a)(3) If over 36 heads In a fire section |  | Yes If smoke detector is used in lieu of sprinkler |  | Yes §27-962 (e)(8) |  | Yes |  | No |  |
| Refuse Collection and Disposal Areas (§27-954(p)) | 1 |  | Yes |  | Yes In Occupancy Groups E, G, J |  | No |  | §27-959(a)(3) If over 36 heads In a fire section |  | Nonea |  | Yes §27-962 (e)(8) |  | Yes |  | No |  |
| Drying Areas – Laundries or Similar Spaces (§27-954(q))d | 1 |  | Yes |  | Yes In Occupancy Groups E, G, J |  | Yes |  | §27-959(a)(3) If over 36 heads In a fire section |  | Yes If smoke detector is used in lieu of sprinkler |  | Yes §27-962 (e)(8) |  | No |  | No |  |
| Cooling Towers (§27-954(r)) | 1 |  | No |  | Yes |  | No |  | No |  | Nonea |  | Yes |  | Yes |  | No |  |
| Buildings and Spaces in Residential Occupancy Group J-1 ##### (§27-954(t)) | 1 |  | # No |  | # Nof |  | # No |  | Yes, except as provided in §27-959(a)(3) |  | ### No |  | ## Yes |  | No |  | # No |  |
| Buildings and Spaces in Residential Occupancy Group J-2 with 4 or more Dwelling Units and not exceeding Six Stories or 75 Feet In Height (§27-954(t)) | 1 |  | # No |  | Yesg |  | # No |  | Yes, except as provided in §27-959(a)(1) and §27-959(a)(5) |  | # No |  | ##### Yes |  | # No |  | # No |  |
| Buildings and Spaces in Residential Occupancy Group J-2 with 4 or more Dwelling Units and Exceeding Six Stories or 75 Feet In Height (§27-954(t)) | 1 |  | # No |  | # Noh |  | # No |  | Yes, except as provided in §27-959(a)(3) |  | ### No |  | ###### Yes If over 36 heads |  | # No |  | # No |  |

Notes:

a.	Central Station supervision required only when booster pump is provided under §27-964 or when non-automatic sprinkler is permitted by the commissioner.

b.	Water flow alarms required when more than 36 heads are installed in a fire section or fire area.

c.	Only when permitted by the commissioner (§27-967(c)).

d.	[see] See §27-954(w) for requirements pertaining to these spaces located in a building classified in occupancy group J-1.

e.	See section 4-4.8 of reference standard RS 17-2.

f.	Except as provided in reference standard RS 17-2A.

g.	Notwithstanding section 27-962(i) of this chapter.

h.	Except as provided in section 27-962(i) of this chapter.

f

g