Int. No. 2261

By Council Members Cornegy, Levine, Gennaro and Louis (by request of the Mayor)

..Title

A Local Law to amend the administrative code of the city of New York, the New York city plumbing code, the New York city building code, the New York city mechanical code and the New York city fuel gas code,  in relation to bringing such codes and related provisions of law up to date with the 2015 editions of the international building, mechanical, fuel gas and plumbing codes, with differences that reflect the unique character of the city, clarifying and updating administration and enforcement of such codes and the 1968 code and repealing chapters 2 and  35, appendices K and M, section N102 of appendix N, appendices P and Q, and section R103.3 figures 1A and 1B of appendix R of the New York city building code, chapter 15 and appendix A of the New York city mechanical code and chapter 8 of the New York city fuel gas code in relation thereto

..Body

Be it enacted by the Council as follows:

Section 1.  Legislative intent. This local law implements sections 28-601.1, 28-701.1, 28-801.1 and 28-901.1 of the administrative code, which require regular updates of the New York city plumbing code, the New York city building code, the New York city mechanical code and the New York city fuel gas code to reflect changes in the International Plumbing, Building, Mechanical and Fuel Gas Codes. These amendments will bring the New York city codes up to date with the 2015 editions of the International Plumbing, Building, Mechanical and Fuel Gas Codes published by the International Code Council, with differences to accommodate the unique nature of construction in the City. The local law is divided into parts A through E. Part A contains amendments to chapters 1 through 5 of title 28 of the administrative code in separately numbered sections within part A. Chapters 1 through 5 contain general provisions governing administration and enforcement of all such codes and the 1968 code. Parts B, C, D and E contain amendments to chapters 6 through 9 of title 28 of the administrative code and to the codes within such chapters-- chapter 6, containing the New York city plumbing code (part B); chapter 7, containing the New York city building code, (part C); chapter 8, containing the New York city mechanical code, (part D); and chapter 9, containing the New York city fuel gas code, (part E). Each part amends the relevant chapters and appendices of the relevant code in separately numbered sections within the part.

Part A (Chapters 1 through 5 of Title 28)

§ 1.  Chapter 1 of title 28 of the administrative code of the city of New York, as added by local law number 33 for the year 2007, sections 28- 101.1, 28-101.2, 28-101.3.1,  28-101.4.5, 28-101.5 , 28-102.4.5, 28-102.5, 28-103.1, 28-103.16 , 28-103.20 , article 104, article 105, 28-107.1, 28-107.2, 28-107.3, 28-107.4, 28-107.5 , 28-113.1, 28- 113.3 , 28-113.4 , article 115, article 116, sections 28-117.1, 28-117.2, 28-117.5, 28-118.3.4.2, 28-118.16.2, 28-118.20, 218.21 amended by  local law number 141 for the year  2013, sections  28-101.3 , 28-102.7, 28-109.2, 28-109.3,  28-110.3 item 17, 20, 21, article 111, sections 28-112.1 exception item 1,  28-112.3, 28-112.7, 28-112.8, amended by local law number 108 for the year 2008, section 28-101.4.3 exception 19  added by local law number 13 for the year 2014, exception 20 added by local law number 15 for the year 2020, section 28-101.2.4  added by local law number 17 for the year  2014, section 28 -103.1 item 5 and section 28-103.1.1 amended by local law  number 195 for the year  2018, section 28-103.1.3 amended by local law number 80 for the year 2020, section 28-1103.7.1 added by local law number 39 for the year 2009, section 28-103.11 amended by local law number 10 for the year 2016,  section 28-103.21.1 amended by local law number 78 for the year 2017, 28-103.24 amended by local law number 80 fir the year 2020, section 28-103.23 added by local law number 82 for the year 2013, section 28-103.26 added by local law 68 of 2017, section 28-103.27 added by local law 158 of  2017, section 28-103.29 amended by local law number 219 for the year  2019, section 28-103.30.5 added by local law number 188 for the year  2017 and renumbered by local law number 233 for the year 2017, section 28-103.32 amended by local law number 80 for the year 2020, section 28-103.33 renumbered and amended by local law number 93 for the year 2019, section 28-103.35 added by local law number 59 for the year 2019, section 28- 103.36 added by local law number 15 for the year 2020, section 28-104.2 amended by chapter 217 of the laws of 2018, sections 28-104.2.1. 2, 28-104.2.1.3.2, 28-104.2.1.4 amended by local law number 108 for the year 2019, sections 28-104.7.16, 28-104.8 amended by local law number 106 for the year 2019, section 28-105.1.2, added by local law number 97 for the year 2017, sections 28-105.1.2 added by local law number 160 for the year 2017, section 28-105.1.3 added by local law number 104 for the year 1019, sections 28-105.1.4 and 28-105.1. 5 added by local law number 114 for the year 2019, section 28-105.2,item 3 amended by local law number 1 for the year 2011, item 10 amended by local law number 195 for the year 2018, section 28-105.4 subdivisions  7 and 8 added and subdivision 9 amended by local law 195 for the year 2018, section 28-105.5 amended by chapter 217 of the laws of 2018, section 28-105.10.1 amended by local law number 62 for the year 2019, section 28-105.11 amended by local law number 158 for the year 2017, section 105.12.7.1 amended by chapter 217 of the laws of 2018, section 28-12.8 amended by local law number 81 for the year 2017, 28-105.12.9 added by local law number 196 for the year  2017, section 28-105.12.10 added by local law 106 of 219, section 28- 105.12.11 added by local law number 111 for the year 2019, section 28-106.1 amended by local law 38 of 2015, section 28-106.2 added by local law 37 of 2009, sections 28-106.3 and 28-106.4 amended by local law 38 of 2015, section 28-109.1 amended by local law number 195 for the year 2018, table 112.2 amended by local law number 56 for the year 2016, section 28-112.10 added by local law number 4 for the year 2016, section 28-112.10.2 amended by local law number 51 for the year 2013, section 28-112.11 added by local law number 33  for the year 2014, section 28-112.12 added by local law number 196 for the year 2017, section  28-113.5 added by local law number 2 for the year 2012, section 116.2.1 amended by local law number 115 for the year 2019, sections 28-116.2.4 and 28-116.2.4.3 amended and added by local law number 151 for the year 2016, section 28-116.2.4.2 added by local law number 149 for the year 2017, section 28-116.7 added by local law number 97 for the year 2017, section 28-117.4.4 amended by local law number 80 for the year 2020, section 28-118.22 added by local law number 97 for the year 2017, section 28-119.4 added by local law number 154 for the year 2016, article 120 amended by local laws 118 for the year 2019, 106 for the year 2019, and 116 for the year 2019, sections 28-101.5, 28-118.4.2, 28-118.15, 28-118.17, 28-118.19 and table 28-112.8 amended by local law number 6 for the year 2021, is amended to read as follows:

CHAPTER 1

ADMINISTRATION

ARTICLE 101
GENERAL

§28-101.1 Title. The provisions of this chapter shall apply to the administration of the codes set forth in this title and the 1968 building code. This title shall be known and may be cited as the “New York city construction codes” and includes:

The New York city plumbing code.

The New York city building code.

The New York city mechanical code.

The New York city fuel gas code.

The New York city energy conservation code.

§28-101.2 Intent. The purpose of the New York city construction codes is to provide reasonable minimum requirements and standards, based upon current scientific and engineering knowledge, experience and techniques, and the utilization of modern machinery, equipment, materials, and forms and methods of construction, for the regulation of building construction in the city of New York in the interest of public safety, health, welfare and the environment, and with due regard for building construction and maintenance costs.

§28-101.3 Codes. Any reference in this title to “this code” or “the code” shall be deemed to be a reference to this title and all of the codes comprising the New York city construction codes unless the context or subject matter requires otherwise. Whenever a section or subsection of this code is cited or referred to, subordinate consecutively numbered sections and subsections of the cited provision are deemed to be included in such reference unless the context or subject matter requires otherwise.

§28-101.3.1 Occupancy classifications in prior codes. With regard to prior code buildings, references to occupancy classifications in this code shall be deemed to refer to the equivalent occupancy classification under the 1968 or prior building codes.

§28-101.4 Effective date. Except as otherwise provided in sections 28-101.4.1, 28-101.4.2, 28-101.4.3, [and] 28-101.4.4, and 28-101.4.5, on and after July 1, 2008, all work shall be performed in accordance with the provisions of this code.

§28-101.4.1 Permit issued or work commenced prior to July 1, 2008. If a permit for work was issued prior to July 1, 2008 or, if no permit was necessary, work was commenced prior to July 1, 2008, all of the provisions of chapter 1 of title 27 of the administrative code as heretofore in effect shall apply to such work.

§28-101.4.2 Applications for construction document approval submitted prior to and within twelve months after July 1, 2008. Any work for which an application for construction document approval was submitted to the department prior to July 1, 2008 and not thereafter abandoned, or for which an application for construction document approval is submitted to the department within a period of twelve months after such date may, at the option of the owner, be performed in its entirety in accordance with the provisions of this code, or in accordance with the 1968 building code, provided that such work is commenced within twelve months after the date of issuance of a permit [therefore] therefor and is diligently carried on to completion. The commissioner may, for good cause, extend the time period for commencement of the work beyond 12 months. Where the owner elects to perform the work in compliance with the 1968 building code, the following conditions shall apply:

1.	Except as otherwise limited by the commissioner, administration and enforcement of the 1968 building code shall be in accordance with this code, including but not limited to approval of construction documents, issuance of permits and certificates of occupancy, tests and inspections, penalties and enforcement. Controlled inspections and semi-controlled inspections as referenced in the 1968 building code shall be deemed to be special inspections and shall comply with the provisions of this code relating to special inspections. Materials regulated in their use by the 1968 building code shall be subject to applicable provisions of this code.

2.	Safety of public and property during construction operations including demolition shall be governed by chapter 33 of the New York city building code.

§28-101.4.3 Optional use of the 1968 building code for work on prior code buildings. At the option of the owner, and subject to applicable provisions of this code, work on prior code buildings may be performed in accordance with the requirements and standards set forth in the 1968 building code, or where the 1968 code so authorizes, the code in effect prior to December 6, 1968.

Exceptions:

1.	Fuel gas, plumbing and mechanical work. The installation of and work on all appliances, equipment and systems regulated by the New York city fuel gas code, the New York city plumbing code and the New York city mechanical code shall be governed by applicable provisions of those codes relating to new and existing installations.

2.	Fire protection systems. Alterations of buildings and changes of use or occupancy shall be governed by chapter 9 of the New York city building code, subject to special provisions for prior code buildings as set forth therein.

3.	Elevators, conveyors and amusement rides. The installation of and work on elevators, conveyors, and amusement rides shall be governed by chapter 30 and appendix K of the New York city building code and the rules of the department, subject to special provisions for prior code buildings as set forth therein. [.]

4.	Safety during construction operations. Safety of public and property during construction operations including demolition shall be governed by chapter 33 of the New York city building code.

5.	Accessibility. Alterations, including minor alterations, of buildings and changes of use or occupancy, shall be governed by chapter 11 of the New York city building code, subject to special provisions for prior code buildings as set forth therein.

6.	Encroachments into the public right of way. Encroachments onto the public right of way shall be governed by chapter 32 of the New York city building code.

7.	Administration and enforcement. Except as otherwise limited by the commissioner, administration and enforcement of the 1968 building code shall be in accordance with this code, including but not limited to approval of construction documents, issuance of permits and certificates of occupancy, tests and inspections, penalties and enforcement.

8.	Special inspections. Controlled inspections and semi-controlled inspections as referenced in the 1968 building code shall be deemed to be special inspections and shall be governed by the provisions of this code relating to special inspections.

9.	Materials. Materials regulated in their use by the 1968 building code shall be subject to applicable provisions of this code.

10.	Security grilles. The installation and replacement of security grilles shall comply with section [1008.1.4.5] 1010.1.4.4 of the New York city building code.

[8.] 11.	Energy efficiency. All work related to energy efficiency shall be regulated by the New York city energy conservation code.

12.	Roof recovering and replacements.

12.1.	Installation and materials. Work involving the recovering or replacing of an existing roof covering shall be governed by sections [1510.1] 1511.1 through [1510.6] 1511.7 of the New York city building code;

12.2.	Cool roofs. Work involving the recovering or replacing of an existing roof covering shall comply with section 1504.9 of the New York city building code unless the area to be recovered or replaced is less than fifty percent of the roof area and less than 500 square feet (46 m2).

12.3.	Green roofs. Notwithstanding the applicant’s election to use the 1968 building code or prior code, work involving green roof systems and container gardens shall be permitted to be performed pursuant to Chapter 15 of the New York city building code.

12.4.	Sustainable roofs. Work involving the replacing of an entire existing roof deck or roof assembly shall comply with section [1511.2] 1512.2 of the New York city building code.

13.	Handrails. Where the alteration of a building includes the addition or replacement of an entire stair enclosure including the stairs, handrails shall comply with section [1009.12] 1011.11 and section [1012] 1014 of the New York city building code. Where the alteration of a building includes the addition or replacement of ramps, handrails shall comply with section [1010.8] 1012.8 and section [1012] 1014 of such code.

14.	Guards. Where the alteration or repair of a building involves the addition or replacement of guards, such guards shall comply with sections [1013] 1015 and [1607.7] 1607.8 of the New York city building code.

15.	 [Areas of special flood] Flood hazard areas. Within [areas of special] flood hazard areas in accordance with section 28-104.9.4, all work for any activity regulated by Appendix G of the New York city building code shall be governed by such appendix.

16.	Structural. The use of load resistance factor design (LRFD), calculation of live loads, and applicability of seismic and wind loads shall be governed by special provisions for prior code buildings as set forth in section 1601.2 of the New York city building code.

17.	Emergency and standby power systems. The installation of and work on emergency and standby power systems shall comply with section 2702.1 of the New York city building code.

18.	Parking garages and open parking lots. Where an alteration of a parking garage or an open parking lot includes an increase in the size of the electric service, such alteration shall include provisions for the installation of electric vehicle charging stations in accordance with section [406.2.11] 406.4.10 or [406.7.11] 406.9.8 of the New York city building code, as applicable.

19.	Mold protection. Alterations shall comply with sections 2506 and 2509 of the New York city building code relating to areas subject to moisture or water damage.

§28-101.4.4 Reductions of fire safety or structural safety of prior code buildings prohibited. Notwithstanding any other provision of this code, where the alteration of any prior code building or structure in accordance with a provision of this code would result in a reduction of the fire safety or structural safety of such building, relevant provisions of the 1968 building code shall apply to such alteration unless there is full compliance with those provisions of this code that would mitigate or offset such reduction of fire protection or structural safety. Where the owner, having a choice to elect the 1968 building code or this code, chooses this code, the applicant shall submit a comparative analysis acceptable to the commissioner of the relevant fire safety and structural safety provisions under the 1968 building code and this code, demonstrating that the alteration does not result in a reduction to the fire and life safety of the building.

Exception: The use of automatic-closing by smoke detection for doors serving vertical exit enclosures in accordance with section [708.7] 713.7 of the New York city building code in a prior code building shall not be deemed to result in a reduction of the fire safety or structural safety of such a building.

§28-101.4.5 Work that increases existing floor surface area of a prior code building by more than 110 percent. Notwithstanding sections 28-101.4.3 and 28-102.4.3 or any other provision of this code that would authorize alterations of prior code buildings in accordance with the 1968 building code or prior codes, where the proposed work at the completion of construction will increase the amount of floor surface area of a prior code building by more than 110 percent, over the amount of existing floor surface area, such entire building shall be made to comply with the provisions of this code as if it were a new building hereafter erected. See Section 28-105.2 for permits for such work.

Exceptions: When determining the amount of existing floor surface area for the purposes of section 28-101.4.5, the following shall be excluded from the measured square footage of floor surface area:

- The square footage of floors removed during the course of the work when such floors are removed together with the supporting beams, joists, decking and slabs on grade.

- The square footage of any floor that was installed together with the supporting beams, joists, decking and slabs on grade less than 12 months prior to submission of the application for construction document approval for the proposed work. For the purposes of this exception, floors installed pursuant to a work permit signed off less than 12 months before such submission shall not be counted as existing floor surface area.

§28-101.4.5.1 Changes in scope of work. In cases where changes in the scope of work during the course of construction would result in increasing the floor surface area at the completion of construction by more than 110 percent over the amount of existing floor surface area as determined pursuant to section 28-101.4.5, such entire building shall be made to comply with the provisions of this code as if hereafter erected and such work shall be refiled as a new building application in accordance with the provisions of section 28-105.2.

Exception: Work to the extent necessary to relieve an emergency condition may be performed prior to amending plans or obtaining a new permit pursuant to sections 28-105.4.1 and 28-105.12.2.

§28-101.4.5.2 Definitions. As used in Section 28-101.4.5, the following term shall have the following meaning unless the context or subject matter requires otherwise.

FLOOR SURFACE AREA. Floor surface area is the gross square foot area of all horizontal floor and roof surfaces, including roofs of bulkheads and superstructures, of a building or structure at any level, including cellar, attic and roof.

§28-101.4.5.3 Effect on zoning resolution. The provisions of section 28-101.4.5 shall not be construed to affect the status of any nonconforming use or non-complying bulk otherwise permitted to be retained pursuant to the New York city zoning resolution.

§28-101.5 Definitions. As used in this chapter and elsewhere in this title, the following terms shall have the following meanings unless the context or subject matter requires otherwise:

1968 BUILDING CODE. Chapter 1 of title 27 of the administrative code as hereafter in effect.

1968 OR PRIOR CODE BUILDINGS OR STRUCTURES (PRIOR CODE BUILDINGS). (i) A building or structure in existence prior to July 1, 2008 or one for which a lawful building permit was issued for the erection of such building or structure prior to July 1, 2008. (ii) A building or structure erected in accordance with the 1968 building code under a lawful building permit issued for the erection of such building or structure on or after July 1, 2008 in accordance with section 28-101.4.2 of this code.

ACCEPTANCE OR ACCEPTED. In reference to construction documents, the endorsement by the department of construction documents with less than full examination by the department based on the professional certification of a registered design professional in accordance with a program established by the commissioner.

ADDITION. An alteration of a building in existence that increases its exterior dimensions including, but not limited to, an extension or increase in floor area or height (including an increase in height or area resulting from the construction of a rooftop structure or rooftop mechanical equipment) of the building.

ADMINISTRATIVE CODE. The administrative code of the city of New York.

ALTERATION. Any construction, addition, change of use or occupancy, or renovation to a building or structure in existence.

APPROVAL OR APPROVED. In reference to construction documents, the determination by the department after full examination that submitted construction documents comply with this code and other applicable laws and rules. In reference to materials, the determination by the commissioner that material is acceptable for its intended use.

APPROVED AGENCY. An established and recognized agency [, or other qualified person,] that is regularly engaged in conducting tests or furnishing inspection services, when approved pursuant to department rules as qualified to perform or witness identified testing or inspection services.

APPROVED FABRICATOR. An established and qualified person, firm or corporation approved by the commissioner to custom manufacture or build products or assemblies regulated by this code, including the production of concrete.

APPROVED INSPECTION AGENCY. An approved agency that is approved by the department as qualified to perform one or more of the inspections required by this code.

APPROVED TESTING AGENCY. An approved agency that is approved by the department as qualified to test and evaluate the performance of one or more of the materials regulated in their use by this code. Such term shall include, when approved pursuant to department rules, a third party testing or certification agency, evaluation agency, testing laboratory, testing service, licensed concrete testing laboratory, or other entity concerned with product evaluation.

ARCHITECT. A person licensed and registered to practice the profession of architecture under the education law of the state of New York.

BUILDING. Any structure used or intended for supporting or sheltering any use or occupancy. The term shall be construed as if followed by the phrase “structure, premises, lot or part thereof” unless otherwise indicated by the text.

CHARTER. The New York city charter.

CERTIFICATE OF COMPLIANCE. A certificate stating that materials and products  meet specified standards [,] or that work was done in compliance with approved construction documents and other applicable provisions of law, or with respect to specified service equipment, a certificate issued by the department authorizing the operation of such equipment.

CITY. The city of New York.

COMMISSIONER. The commissioner of buildings of the city of New York, or his or her duly authorized representative.

CONSTRUCTION DOCUMENTS. Plans and specifications and other written, graphic and pictorial documents, prepared or assembled for describing the design, location, physical characteristics, and other elements of the project necessary for obtaining a building permit.

DAY. A calendar day, computed in accordance with section 20 of the New York state general construction law, unless otherwise specified as a business day.

DEFERRED SUBMITTAL. Those portions of the design that are not submitted at the time of the application for construction document approval and that are to be submitted to the department within a specified period of time after the issuance of a permit.

DEMOLITION. Full or partial demolition.

DEMOLITION, FULL [:]. The dismantling, razing, or removal of all of a building or structure, including all operations incidental thereto.

DEMOLITION, PARTIAL [:]. The dismantling, razing, or removal of structural members, floors, interior bearing walls, and/or exterior walls or portions thereof, including all operations incidental thereto.

DEPARTMENT. The department of buildings of the city of New York.

ENGINEER. A person licensed and registered to practice the profession of engineering under the education law of the state of New York.

ENLARGEMENT. An addition.

ENVIRONMENTAL CONTROL BOARD or ECB. The environmental control board established pursuant to section 1049-a of the charter within the office of administrative trials and hearings.

EXISTING BUILDING OR STRUCTURE. A completed building or structure that is in existence at the time of an applicable reference in this code.

FABRICATED ITEM. Products and assemblies regulated by this code [,] that are custom manufactured [,] or built prior to their incorporation into the work at the construction site. Fabricated items shall not include listed, labeled or approved products or assemblies. Materials produced in accordance with standard specifications referenced by this code, such as rolled structural steel shapes, steel-reinforcing bars, masonry units, and wood structural panels, or in accordance with a referenced standard [,] listed in this code, which provides requirements for quality control done under the supervision of a third-party quality control agency, shall not be considered fabricated items.

FIRE PROTECTION PLAN. A report containing a narrative description of the life and fire safety systems and evacuation system for a structure.

HEREAFTER. On or after July 1, 2008.

HERETOFORE. Before July 1, 2008.

INSPECTION CERTIFICATE. Identification applied to a product by an approved agency containing the name of the manufacturer, the function and performance characteristics, and the name and identification of the approved agency that indicates that the product or material has been inspected and evaluated by such approved agency. An inspection certificate shall also mean a certificate issued by the department upon satisfactory completion of an inspection or test.

INTERIM CERTIFICATE OF OCCUPANCY.  A type of temporary certificate of occupancy authorizing occupancy of one or more floors of a building prior to the completion of all work needed to obtain a certificate of occupancy for the building, and that remains in effect until the issuance of a certificate of occupancy for the building.

LABEL. An identification applied [to material] on a product by the manufacturer that contains the name of the manufacturer, the function and performance characteristics of the product or material, and the name and identification of [the] an approved agency and that indicates that [the] a representative sample of the product or material has been tested and evaluated by an approved agency for compliance with nationally recognized standards or tests to determine suitable usage in a specific manner.

LABELED. Material to which has been attached a label, symbol or other identifying mark of the manufacturer that contains the name of the manufacturer, the function and performance characteristics of the product or material, and the name and identification of an approved agency and that indicates that a representative sample of the material has been tested and evaluated by an approved agency for compliance with nationally recognized standards or tests to determine suitable usage in a specified manner.

LAND SURVEYOR. A person licensed and registered to practice the profession of land surveying under the education law of the state of New York.

LANDSCAPE ARCHITECT. A person licensed and registered to practice the profession of landscape architecture under [the Education Law of the State of New York] the education law of the state of New York.

LETTER OF COMPLETION. A document issued by the department indicating that permitted work has been completed, including satisfactory final inspection in accordance with this code. A letter of completion is issued only in circumstances where a certificate of occupancy is not required upon completion of the permitted work.

LIMITED ALTERATION APPLICATION.  Application for limited oil-burning appliance alterations, limited plumbing alterations, limited sprinkler alterations, and limited standpipe alterations submitted pursuant to section 28-104.6, Exception 1. Such work shall not include any associated work that would otherwise require an alteration permit including, but not limited to, any construction of fire rated partitions and enclosures.

Category 1 work shall be limited to a new installation into an existing building or system. The utilization of this category shall be limited by an annual monetary cap.

Category 2 work shall include any existing system(s) or components that are replaced, repaired or altered. This category shall not be limited by a monetary cap.

LIMITED OIL-BURNING [BOILER] APPLIANCE ALTERATIONS. An alteration, installation, replacement or repair to an [oil-burner/boiler system] oil-burning appliance that is limited in scope, falling into one of the following categories [:]. Any construction or alteration to fire-rated partitions or enclosures, with the exception of through-penetrations that are firestopped, shall require a separate application filed with the department.

Category 1. An [alteration] addition to an [oil burner/boiler system] existing oil-burning appliance where the total cost of the proposed category 1 work in the building does not exceed [thirty-five] fifty thousand dollars in any 12-month period and where the proposed work is limited to the [replacement] installation of:

1.	oil equipment [or] ,

2.	oil-fired appliances, located within the same enclosure or room as the existing oil burning appliance,

3.	unit heaters, or

4. 	oil piping including no more than two above-ground oil tanks each with a capacity of no more than 330 gallons (1250 L) [or less capacity provided the replacement] provided such oil tanks also comply with the capacity limits established in section 1305.11 of the New York city mechanical code. The newly installed tanks shall have a UL listing, [or labeling] be labeled, or meet the alternative tank design and construction standards contained in section 1305.14 of the New York city mechanical code.

Category 2. An alteration [to] , repair or replacement of an [oil burner/boiler system] existing oil-burning appliance that is not subject to cost or duration limitations and that is limited to the following:

1.	Replacement of oil burners, oil-burning [boilers] appliances or water [heater with] heaters in which the heat input [of 1] per appliance does not exceed 3 million Btu/h ( [293] 879 kW) [or less].

[2.	Replacement of oil burners with heat input of 2.8 million Btu/h (821 kW) or less.]

[3.] 2.	Relocation of an oil burner or oil-burning [boiler] appliance or water heater within the same [, unaltered fire-rated] enclosure or room.

[4.] 3.	Placement of a temporary department of buildings registered oil fired mobile boiler and corresponding fuel oil storage tank with associated piping at a site for emergency heating.

4.	Placement of a temporary fuel oil storage tank with a capacity of 5,000 gallons (18 927 L) or less at a site for emergency use and connected to an existing oil-burning appliance.

5.	Repair, replacement or relocation of oil equipment, appliances or oil piping including two above-ground oil tanks with 330 gallons (1250 L) provided such oil tanks also comply with the capacity limitations of section 1305.11 of the New York City Mechanical Code. The replacement tanks shall have a UL listing or labeling or meet the alternative tank design and construction standards contained in section 1305.14 of the New York city mechanical code. Any such relocation shall be only within the same enclosure or room.

LIMITED PLUMBING ALTERATIONS. An installation, replacement, repair or alteration to a plumbing or fuel gas piping system, including fixtures and appliances, that is limited in scope, falling into one of the following categories:

Category 1. An [alteration] addition to [a] an existing plumbing or fuel gas piping system or service where the total cost of the proposed Category 1 work in the building does not exceed [thirty-five] fifty thousand dollars in any 12-month period and where the proposed work is limited to the following:

1.	The addition of not more than [5] five plumbing fixtures or fixture connections in a building within any 12-month period, including any associated plumbing necessary to serve such additional fixtures or fixture connections;

2.	The installation of new [plumbing or] fuel gas piping [, excluding work in Category 2] in conjunction with the addition of not more than five gas appliances or six unit heaters, limited to residential gas barbecue, Category 1 vented hot water heater, gas infrared heater, gas light, gas oil burner pilot, gas pool heater in conjunction with an R-3 occupancy group, one commercial gas appliance and gas unit heater, including any associated fuel gas piping necessary to serve such additional appliances;

3.	The installation of up to five new sprinkler heads off of an existing domestic water system within any 12-month period;

[4.	Rearrangement of not more than 20 sprinkler heads in areas classified in light hazard occupancy, as such term is defined in NFPA 13 as amended by appendix Q of the New York city building code, provided such areas are already sprinklered and such areas will remain in such occupancy, and provided further that all such sprinkler heads are off of a domestic water system;]

[5.	Rearrangement of not more than 20 sprinkler heads in restaurant service areas classified in Group 1 ordinary hazard occupancy, as such term is defined by NFPA 13 as amended by appendix Q of the New York city building code, provided such areas are already sprinklered and such areas will remain in such occupancy, and provided further that all such sprinkler heads are off of a domestic water system;]

[6.	Rearrangement of not more than 20 sprinkler heads in mercantile areas classified in Group 2 ordinary hazard occupancy, as such term is defined by NFPA 13 as amended by appendix Q of the New York city building code, provided such areas are already sprinklered and such areas will remain in such occupancy, and provided further that all such sprinkler heads are off of a domestic water system;]

[7.	In-kind replacement of piping and parts is required for the operation of a standpipe, provided that a sprinkler is not connected or is not now being connected to such system; and]

[8.	Replacement of parts required for the operation of a standpipe system that is not a combined standpipe system.]

4.	Installation of a new single domestic gas dryer that is vented directly through an exterior wall in buildings occupied exclusively as one- or two-family dwellings not more than three stories in height, as provided for in rules of the department.

Category 2. [An] The repair, replacement of or alteration to [a] an existing plumbing or fuel gas piping system that is not subject to cost or duration limitations and that is limited to the following:

- The [rerouting] repair, replacement of or alteration of existing plumbing or fuel gas [branch] piping to serve the same number of fixtures and appliances;

- The in-kind replacement of plumbing fixtures and gas appliances that do not provide heat or hot water when not constituting a minor alteration or ordinary repair under this code. This shall not preclude plumbing work that is a minor alteration or ordinary repair from being filed as a limited alteration application;

- The relocation and [mounting] replacement of [new] plumbing fixtures [on existing roughing] , other than the mere replacement of existing fixtures constituting a minor alteration or ordinary repair under this code. This shall not preclude the relocation and replacement of plumbing fixtures that is a minor alteration or ordinary repair from being filed as a limited alteration application;

- The installation or replacement of primary backflow preventers;

- [Replacement] In-kind replacement of gas-fired [boilers] appliances with a combined heat input of [1] 3 million Btu/h ( [293] 879kW) or less;

- Replacement of gas burners with heat input of [2.8] 3 million Btu/h ( [821] 879 kW) or less;

- Relocation of a gas burner/boiler within the same, unaltered fire-rated enclosure or room, with the exception of through-penetrations that are firestopped;

8.	In-kind replacement with the following direct-vent appliances with heat input of 350,000 Btu/h (103 kW) or less that are vented directly through exterior walls serving buildings occupied exclusively as one- or two-family dwellings not more than four stories in height [, as provided for in rules by the department, regarding gas-fired boilers, hot water heaters and furnaces;]:

8.1.	gas-fired boilers,

8.2.	hot water heaters and

8.3.	furnaces;

9.	[Installation of a new single domestic gas dryer that is vented directly through an exterior wall in buildings occupied exclusively as one- or two-family dwellings not more than four stories in height, as provided for in rules by the department] In-kind direct replacement of gas-fired boilers, hot water heaters and furnaces with heat input of 350,000 Btu/h (103 kW) or less; that are vented directly through exterior walls;

10.	Placement of a registered gas fired temporary boiler with associated gas piping at a site for emergency heating and/or hot water; [and]

11.	Replacement of up to thirty existing sprinkler heads providing that orifice sizes, type and deflector positions remain the same, and all such sprinkler heads are off of a domestic water system [.];

12.	Rearrangement of not more than 20 sprinkler heads in areas classified in light hazard occupancy, as such term is defined in NFPA 13 as amended by appendix Q of the New York city building code, provided such areas are already sprinklered and such areas will remain in such occupancy, and provided further that all such sprinkler heads were legally installed off of a domestic water system;

13.	Rearrangement of not more than 20 sprinkler heads in restaurant service areas classified in Group 1 ordinary hazard occupancy, as such term is defined by NFPA 13 as amended by appendix Q of the New York city building code, provided such areas are already sprinklered and such areas will remain in such occupancy, and provided further that all such sprinkler heads were legally installed off of a domestic water system; and

14.	Rearrangement of not more than 20 sprinkler heads in mercantile areas classified in Group 2 ordinary hazard occupancy, as such term is defined by NFPA 13 as amended by appendix Q of the New York city building code, provided such areas are already sprinklered and such areas will remain in such occupancy, and provided further that all such sprinkler heads were legally installed off of a domestic water system.

LIMITED SPRINKLER ALTERATIONS. An alteration, installation, replacement or repair to a sprinkler system that is limited in scope, falling into one of the following categories:

Category 1. An alteration to an existing sprinkler system where the total cost of the proposed Category 1 work in the building does not exceed [thirty-five] fifty thousand dollars in any 12-month period, the fire rating of the area where the new sprinkler heads are being installed is not being altered and [where] the proposed work is limited to [the following:] the installation of up to five new sprinkler heads off of an existing sprinkler system.

[1.	Replacement of parts required for the operation of a sprinkler system;]

[2.	Changes that do not alter the type of sprinkler system;]

[3.	Relocation of piping that does not affect the operation of the sprinkler system;]

[4.	Rearrangment of not more than 20 sprinkler heads in areas classified in light hazard occupancy, as such term is defined in NFPA 13 as amended by appendix Q of the New York city building code, provided such areas area already sprinklered and such areas will remain in such occupancy;]

[5.	Rearrangment of not more than 20 sprinkler heads in restaurant service areas classified in Group 1 ordinary hazard occupancy, as such term is defined in NFPA 13 as amended by appendix Q of the New York city building code, provided such areas are already sprinklered and such areas will remain in such occupancy;]

[6.	Rearrangment of not more than 20 sprinkler heads in mercantile areas classified in Group 2 ordinary hazard occupancy, as such term is defined in NFPA 13 as amended by appendix Q of the New York city building code, provided such areas are already sprinklered and such areas will remain in such occupancy; and]

[7.	The installation of up to five new sprinkler heads off of an existing sprinkler system.]

Category 2. An alteration, repair or replacement of [to] an existing sprinkler system or combined sprinkler standpipe system that is not subject to cost or duration limitations and that is limited to [the replacement of sprinkler heads, provided that orifice sizes, type and deflector positions remain the same.]:

1.	The replacement of sprinkler heads, provided that orifice sizes, type and deflector positions remain the same;

2.	Replacement of parts required for the operation of a sprinkler system or combined sprinkler standpipe system, provided that orifice sizes, type and deflector positions remain the same;

3.	Changes that do not alter the type of sprinkler system;

4.	Relocation of piping that does not affect the operation of the sprinkler system, provided that orifice sizes, type and deflector positions remain the same;

5.	Rearrangement of not more than 30 sprinkler heads in areas classified in light hazard occupancy, as such term is defined in NFPA 13 as amended by appendix Q of the New York city building code, provided such areas are already sprinklered and such areas will remain in such occupancy;

6.	Rearrangement of not more than 30 sprinkler heads in restaurant service areas classified in Group 1 ordinary hazard occupancy, as such term is defined in NFPA 13 as amended by appendix Q of the New York city building code, provided such areas are already sprinklered and such areas will remain in such occupancy;

7.	Rearrangement of not more than 30 sprinkler heads in mercantile areas classified in Group 2 ordinary hazard occupancy, as such term is defined by NFPA 13 as amended by appendix Q of the New York city building code, provided such areas are already sprinklered and such areas will remain in such occupancy;

8.	Rearrangement of sprinkler heads in a storage area under 200 square feet classified Group 1 ordinary hazard, as such term is defined by NFPA 13 as amended by appendix Q of the New York city building code, provided such areas are already sprinklered and such areas will remain in such occupancy;

9.	Unlimited cut and cap of an existing sprinkler system associated with a permitted demolition or gut renovation; and

10.	Relocation of a fire department connection as part of a combined system.

LIMITED STANDPIPE ALTERATIONS. Category 2. An alteration, replacement or repair to an existing standalone or combined standpipe system that is limited [in scope falling into the following category] to the following:

[Category 1. An alteration to an existing combined standpipe system where the total cost of the proposed work in the building does not exceed thirty five thousand dollars in any 12-month period and the proposed work is limited to one or more of the following:]

1.	Replacement or relocation of parts required for the operation of a standalone or combined standpipe system; [and]

2.	Relocation of standalone or combined standpipe auxiliary hose sources and cabinets within 10 feet (3048 mm) of their original location, provided that the existing covered area is not affected and provided that such relocation complies with this code for a  new installation [.]; and

3.	Unlimited cut and cap of an existing standalone or combined standpipe system for a demolition or gut renovation.

LISTED. Material identified in a list published by an approved agency that maintains periodic inspection of production of listed material or periodic evaluation services whose listing states either that the material meets identified nationally recognized standards or has been tested and found suitable for a specified purpose when installed in accordance with the manufacturer’s installation instructions.

MAIN USE OR DOMINANT OCCUPANCY (OF A BUILDING). Refers to a single occupancy classification assigned to a structure by the department according to such structure’s main use or dominant occupancy.

MANUFACTURER’S DESIGNATION. Identification applied to material by the manufacturer indicating that the material complies with a specified standard or set of rules (see “Label” and “Mark”).

MARK. Identification applied to a product by the manufacturer indicating the name of the manufacturer and the function of a product or material (see “Label” and “Manufacturer’s designation”).

MATERIALS. Materials, assemblies, appliances, equipment, devices, systems, products and methods of construction regulated in their use by this code or regulated in their use by the 1968 building code.

OCCUPANCY. The purpose or activity for which a building or space is used or is designed, arranged or intended to be used.

OWNER. Any person, agent, firm, partnership, corporation or other legal entity having a legal or equitable interest in, or control of the premises.

PARTY WALL. A fire division on an interior lot line common to two adjoining buildings.

PERMIT. An official document or certificate issued by the commissioner that authorizes performance of specified work or activity.

PERSON. An individual, partnership, corporation, or other legal entity.

PREMISES. Land, improvements thereon, or any part thereof.

PRIOR CODE BUILDING. See 1968 OR PRIOR CODE BUILDING OR STRUCTURE (PRIOR CODE BUILDING).

PROFESSIONAL CERTIFICATION. A personal verification of a registered design professional made under such professional’s signature and seal that accompanies construction documents and other related documents filed with the department and that attests that such documents do not contain false information and are in compliance with all applicable provisions of law.

PROGRESS INSPECTION. Inspection of permitted construction work in progress to verify compliance with the code and with approved construction documents.

PROJECT. A design and construction undertaking comprised of work related to one or more buildings or structures and the site improvements. A project is represented by one or more plan/work applications, including construction documents compiled in accordance with article 104 of this chapter, that relate either to the construction of new buildings or structures or to the demolition or alteration of existing buildings or structures. Applications for a project may have different registered design professionals and different application numbers, and may result in the issuance of one or more permits.

REGISTERED DESIGN PROFESSIONAL. An architect or engineer.

REGISTERED DESIGN PROFESSIONAL OF RECORD. The registered design professional who prepared or supervised the preparation of applicable construction documents filed with the department.

REQUIRED. Shall mean required by the provisions of this code.

RETAINING WALL. A wall designed to prevent the lateral displacement of soil or other materials.

SERVICE EQUIPMENT. Equipment or systems, and all components thereof, that provide sanitation, power, light, heat, ventilation, air conditioning, refuse disposal, fire-fighting, transportation or other facilities for buildings.

SIGN-OFF. The issuance by the department of a letter of completion or certificate of occupancy for permitted work indicating the satisfactory completion of all required inspections and receipt by the department of all required submittal documents.

SINGLE ROOM OCCUPANCY MULTIPLE DWELLING. See section 28-107.2.

SPECIAL INSPECTION. Inspection and testing of selected materials, equipment, installation, fabrication, erection or placement of components and connections, to ensure compliance with approved construction documents and referenced standards as required by chapter 17 of the New York city building code or elsewhere in this code or its referenced standards.

SPECIAL INSPECTION AGENCY. An agency employing one or more persons who are special inspectors and that meets the requirements of department rules.

SPECIAL INSPECTOR. An individual employed by a special inspection agency having required qualifications and authorized by [department] department rules to perform or witness particular special inspections required by this code or by the rules of the department, including but not limited to a qualified registered design professional so authorized.

STRUCTURE. That which is built or constructed, including among others: buildings, stadia, tents, reviewing stands, platforms, stagings, observation towers, radio towers, tanks, trestles, open sheds, shelters, fences, and display signs.

SUBMITTAL DOCUMENTS. Completed application forms, construction documents, reports and any other documents submitted in compliance with this code or other applicable laws and rules including but not limited to special inspection reports, certifications or approvals from other governmental agencies and other data required by this code or by the department.

SUPERINTENDENT OF CONSTRUCTION (CONSTRUCTION SUPERINTENDENT). An individual, when authorized pursuant to department rules as qualified to superintend permitted construction work on behalf of the owner.

USE (USED). The purpose for which a building, structure, or space is occupied or utilized, unless otherwise indicated by the text. Use (used) shall be construed as if followed by the words “or is intended, arranged, or designed to be used.”

UTILITY COMPANY OR PUBLIC UTILITY COMPANY. The term shall be construed to have the same meaning as that contained in section two of the New York state public service law.

UTILITY CORPORATION OR PUBLIC UTILITY CORPORATION. The term shall be construed to have the same meaning as that contained in section two of the New York state public service law.

WORK NOT CONSTITUTING MINOR ALTERATIONS OR ORDINARY REPAIRS. See section 28-105.4.2.1.

WRITING (WRITTEN). The term shall be construed to include handwriting, typewriting, printing, photo-offset, or any other form of reproduction in legible symbols or characters, including, in the discretion of the commissioner, electronic media.

WRITTEN NOTICE. A notification in writing delivered by hand to the person or parties intended, or delivered at or sent by mail or in the discretion of the commissioner by electronic media to the last address known to the party giving such notice.

ZONING RESOLUTION. The zoning resolution of the city of New York, adopted December fifteenth, nineteen hundred sixty-one, including all amendments thereto.

ARTICLE 102
APPLICABILITY

§28-102.1 General. Where, in any specific case, different sections of this code specify different materials, methods of construction or other requirements, the most restrictive shall govern. Where a general requirement conflicts with a specific requirement, the specific requirement shall govern. Where British and metric units of measurement conflict, the British units shall govern.

§28-102.2 Other laws. The provisions of this code do not presumptively provide for matters that are contained in the charter, the New York state labor law, the New York state multiple dwelling law, the zoning resolution, or the New York state general city law. Where there is conflict or inconsistency between the requirements of this code and other applicable laws and rules, unless otherwise required, such conflict shall be resolved in favor of the more restrictive requirement.

§28-102.3 Separability. If any clause, sentence, paragraph, section or part of this code shall be adjudged to be invalid, such judgment shall not affect, impair or invalidate the remainder thereof, but shall be confined in its operation to the clause, sentence, paragraph, or part thereof directly involved in the controversy in which such judgment shall have been rendered.

§28-102.4 Existing buildings. The lawful use or occupancy of any existing building or structure, including the use of any service equipment therein, may be continued unless a retroactive change is specifically required by the provisions of this code or other applicable laws or rules.

§28-102.4.1 Prior code buildings must comply with the applicable retroactive requirements of the 1968 building code. Prior code buildings must comply with the applicable retroactive requirements of the 1968 building code including those requiring the installation of fire safety and building safety systems and the filing of verifying reports with the department of such installations by the dates specified in section 27-228.5 of the administrative code or in other applicable provisions of such 1968 building code. A violation of such provisions shall be a violation of this code.

§28-102.4.2 Change in use or occupancy. Except as [otherwise] otherwise provided in sections 28-101.4.1, 28-101.4.2, 28-101.4.3 or 28-101.4.4 changes in the use or occupancy of any building or structure made after July 1, 2008 shall comply with the provisions of this code. Any changes made in the use or occupancy of a building or structure not in compliance with this code shall be prohibited and shall be a violation of this code. After a change in use or occupancy has been made in a building, the re-establishment of a prior use or occupancy that would not be lawful in a new building of the same construction class shall be prohibited unless and until all the applicable provisions of this code and other applicable laws and rules for such reestablished use or occupancy shall have been complied with. A change from a use prohibited by the provisions of this code, but which was permitted prior to July 1, 2008, to another use prohibited by the provisions of this code shall be deemed a violation of this code.

§28-102.4.3 Alteration of prior code buildings. Except as otherwise provided in sections 28-101.4.1, 28-101.4.2, 28-101.4.3 and 28-101.4.4, prior code buildings altered after July 1, 2008 shall comply with the provisions of this code. In accordance with subdivision eleven of section three of the New York state multiple dwelling law and article 4 of subchapter 1 of the 1968 building code, at the option of the owner, multiple dwellings erected prior to December 6, 1969 may be altered and buildings erected prior to December 6, 1969 may be converted to multiple dwellings in accordance with applicable provisions of the New York state multiple dwelling law and the building laws and regulations in effect prior to December 6, 1968, provided the general safety and public welfare are not thereby endangered. At a minimum, the application of sections 28-101.4.3, 28-101.4.4 and 28-101.4.5 to any such alteration shall be deemed necessary to protect the general safety and public welfare.

§28-102.4.4 Continuation of unlawful use or occupancy. The continuation of the unlawful use or occupancy of a building or structure contrary to the provisions of this code, or contrary to the provisions of prior codes or other applicable law or rule, shall be a violation of this code.

§28-102.4.5 Fire district maps. The boundaries of fire districts shall be in accordance with the maps set forth in Appendix D of the New York city building code.

§28-102.5 [Regulation of lots. The regulation of lots, in conformity with the street on which they are situated, shall be calculated at curb level. Where a lot has more than one street frontage, and is so situated that the street frontages intersect, the curb of the longest street frontage shall be used. When the street frontages do not intersect, the curb along each frontage shall be used to one-half the depth of the lot between street frontages. A lot as referred to in this section 28-102.5 shall mean a parcel of land twenty-five feet by one hundred feet, or less, in one ownership whether adjacent land be in the same or other ownership; but, for this purpose, no land in the same ownership may be divided into lots smaller than twenty-five feet by one hundred feet.] Reserved.

§28-102.6 Appendices. All enacted appendices are a part of the provisions of this code.

§28-102.7 References in other laws. References to provisions of the building code of the city of New York or to chapter 1 of title 27 of the administrative code in other laws shall be deemed to refer to equivalent provisions of the 1968 building code or the New York city construction codes as the context in which such references appear may require.

ARTICLE 103
DUTIES AND POWERS OF COMMISSIONER OF
BUILDINGS

§28-103.1 Jurisdiction. This code shall be enforced by the commissioner of buildings, pursuant to the provisions of section six hundred forty-three of the New York city charter. However, the commissioner of small business services may also enforce all of the provisions of this code with respect to buildings under the jurisdiction of the department of small business services and the fire commissioner may also enforce all the provisions of this code relating to:

1.	The approved number of persons in places of assembly (overcrowding);

2.	Obstruction of aisles, corridors, and exits;

3.	The posting and availability for inspection of certificates of occupancy or other authorization of lawful occupancy, certificates of compliance and place of assembly certificates of operation;

4.	The maintenance of fire, smoke and carbon monoxide detection and alarm systems, fire extinguishing systems, refrigerating systems, storage tanks and auxiliary storage tanks for oil-burning equipment, exit signs and path markings, and any fire or life safety system, equipment or device intended for use by fire fighting personnel or whose use or operation is subject to the New York city fire code or other law or rule enforced by the New York city fire department, and any related installation and signage;

5.	The installation and testing of fire alarm systems, smoke-detecting and carbon monoxide detecting devices that are interconnected with a fire alarm system or monitored by a central station, alternative automatic fire extinguishing systems, including but not limited to fire extinguishing systems for commercial cooking equipment, and fire protection plans;

6.	Fire fighting equipment, access to and within premises upon or in which construction and demolition work is being conducted, and the conduct of all construction or demolition work affecting fire prevention and fire fighting;

7.	Any exhaust system designed or used for commercial cooking equipment, when such commercial cooking equipment is required to be protected by a fire extinguishing system; and

8.	The installation and testing of natural gas distribution piping systems designed for or operated at a gas pressure of 15 psig (103 kPa gauge) or greater.

§28-103.1.1 Installation of equipment required by the New York city fire code. Where the installation of exit signs, emergency means of egress illumination, special mechanical ventilation, sprinkler systems, fire alarm systems and alternative automatic fire extinguishing systems is required by the New York city fire code, the fire commissioner shall require such installations to be in accordance with this code.

§28-103.1.2 Enforcement of New York city construction codes on property within the jurisdiction of the department of small business services. This code and the 1968 building code shall apply to property within the jurisdiction of the department of small business services pursuant to the New York city charter including, but not limited to, structures on waterfront property used in conjunction with and in furtherance of waterfront commerce and/or navigation. It shall be administered and enforced by the department of small business services in the same manner as property within the jurisdiction of the department.

§28-103.1.3 Innovation review board. There is hereby established within the department an innovation review board which shall include as members in addition to the commissioner, the commissioners of environmental protection, health and mental hygiene and design and construction and the chairperson of the city planning commission, or their respective designees. The commissioner shall also designate members from among the fire commissioner and the commissioners of transportation, parks and recreation, consumer affairs, emergency management, housing preservation and development and sanitation and the chairperson of the landmarks preservation commission, and non-governmental organizations and individuals, or their respective designees, with respect to specific matters being considered by the board where the commissioner determines it appropriate to do so.

§28-103.1.3.1 Meetings and recommendations. The commissioner shall convene the innovation review board at least quarterly, or more often as the commissioner may deem necessary to address issues in a timely manner to (i) review specific projects that propose to employ new technologies, design or construction techniques, materials or products, (ii) review proposals for approval of and to initiate reviews of such new technologies, design or construction techniques, materials or products in order to determine their environmental and sustainability benefits, (iii) make recommendations as to under what conditions and for what purposes each may be appropriately employed in New York city, and (iv) streamline approvals of specific innovative projects. If the board recommends that a technology, design or construction technique, material or product may appropriately be employed, the commissioner shall consider such recommendation and may by rule or other method as the commissioner deems appropriate, authorize the use of such technology, design or construction technique, material or product and under what conditions and for what purposes each may be appropriately employed. The commissioner shall state in writing to the interagency green team established pursuant to subdivision i of section twenty of the charter what action the commissioner shall take with respect to each such recommendation and the reasons for the action taken.

§28-103.2 Interpretation. This code shall be liberally interpreted to secure the beneficial purposes thereof.

§28-103.3 Variations. The requirements and standards prescribed in this code shall be subject to variation in specific cases by the commissioner, or by the board of standards and appeals, under and pursuant to the provisions of paragraph two of subdivision (b) of section six hundred forty-five and section six hundred sixty-six of the New York city charter, as amended.

§28-103.4 Appeals. An appeal from any decision or interpretation of the commissioner may be taken to the board of standards and appeals pursuant to the procedures of the board, except as provided in section 25-204 of the administrative code or as otherwise provided in this code.

§28-103.5 Seal; judicial notice. The commissioner may design and adopt a seal for the department for use in the authentication of the orders and proceedings of the department, and for such other purposes as the commissioner may prescribe. The courts shall take judicial notice of such seal, and of the signature of the commissioner, the deputy commissioners, and the borough superintendents of the department.

§28-103.6 Proofs, affidavits and oaths. Proofs, affidavits and examinations as to any matter arising in connection with the performance of any of the duties of the department may be taken by or before the commissioner, or a deputy commissioner, or such other person as the commissioner may designate; and such commissioner, deputy or other person may administer oaths in connection therewith.

§28-103.7 Cooperation of other departments. Upon request of the commissioner, it shall be the duty of all departments to cooperate with the department of buildings at all times, and to furnish to such department such information, reports and assistance as the commissioner may require.

§28-103.7.1 Sharing results of buildings inspections. The commissioner, the fire commissioner and the commissioner of the department of environmental protection shall [establish a procedure, the implementation of which shall begin within six months of the effective date of this section, to] share information regarding violations issued as a result of inspections of buildings meeting agreed-upon criteria that are relevant to the responsibilities of each department.

§28-103.8 Matters not provided for. Any matter or requirement essential for fire or structural safety or essential for the safety or health of the occupants or users of a structure or the public, and which is not covered by the provisions of this code or other applicable laws and rules, shall be subject to determination and requirements by the commissioner in specific cases.

§28-103.9 Additional tests. Whenever there is insufficient evidence of compliance with the provisions of this code, or evidence that a material or method of construction does not conform to the requirements of this code, or in order to substantiate claims for alternative materials or methods, the commissioner shall have the authority to require tests as evidence of compliance to be made at no expense to the city. Test methods shall be as specified in this code, or by other recognized test standards approved by the commissioner. In the absence of recognized and accepted test methods, the commissioner shall approve the testing procedures. Tests shall be performed as directed by the commissioner. Reports of such tests shall be retained by the department for the period required for retention of public records.

§28-103.10 Supporting documentation for materials. Whenever this code or the rules of the department permits the use of material regulated in its use by this code or the 1968 building code without the prior approval of the commissioner, the commissioner may, in the interest of public safety, require the submittal of supporting documentation that any material used or proposed to be used complies with the applicable code standard for such use. Such supporting documentation may consist of but shall not be limited to certification documents of an approved agency, test reports, analysis, computations or other evidence of such compliance.

§28-103.11 Applications and permits. The department shall receive and review applications, construction documents, and other related documents and shall issue permits, in accordance with the provisions of this code. The department shall, on a weekly basis, send council members and community boards, by electronic mail, a copy of all completed applications for a new building or an alteration that will require a new certificate of occupancy for a building, received during the prior week, disaggregated by community board. In addition, the department shall post such information on its website on a weekly basis.

§28-103.12 Identification. Department personnel shall carry metal badges with suitable inscriptions thereon or other prescribed identification when inspecting structures or premises or otherwise in the performance of their duties under this code.

§28-103.13 Right of entry. The commissioner or his or her authorized representatives, in the discharge of their duties, shall have the right to enter upon and inspect, at all reasonable times, any buildings, enclosure, premises, or any part thereof, or any signs or service equipment contained therein or attached thereto for the purpose of determining compliance with the provisions of this code and other applicable building laws and rules. Officers and employees of the department shall identify themselves by exhibiting the official badge or other identification prescribed by the department; and other authorized representatives of the commissioner shall identify themselves by producing and exhibiting their authority in writing signed by the commissioner. If access is not obtained, the commissioner shall have recourse to remedies provided by law to secure entry.

§28-103.14 Department records. The department shall keep official records of applications received, permits and certificates issued, fees collected, reports of inspections, and notices and orders issued. Such records shall be retained in the official records for the period required for retention of public records.

§28-103.14.1 List of permits for cellular antenna. The commissioner shall maintain a separate list of alteration permits issued for the erection or placement of antennae used to provide cellular telephone or similar service or any structure related to such service which shall, at a minimum, set forth the name, business address and business telephone number of the applicant, the date of the application, the date the permit was issued, the location for which the permit was issued, including the premises address and the zoning district, whether residential, commercial, or manufacturing, and the number of permits issued for such purpose at the same location. Such list shall be made available to the public upon request between regular business hours and shall be available to the public in electronic format on a 24-hour basis on the department’s website.

§28-103.15 Insurance. The commissioner may require applicants for permits to obtain and furnish proof of workers’ compensation, disability and general liability insurance in such amounts and in accordance with such specifications as shall be set forth in the rules of the department or as otherwise required by law.

§28-103.16 Inspections of existing buildings, structures, signs, service equipment and construction machinery and equipment. In addition to other required inspections, the commissioner may make or require inspections of existing buildings, structures, signs, service equipment installations and construction machinery and equipment to ascertain compliance with the provisions of this code and other laws that are enforced by the department. Such inspections may be made on behalf of the department by officers and employees of the department and other city departments and governmental agencies; and by approved agencies, special inspectors or other persons when the commissioner is satisfied as to their qualifications and reliability. The commissioner may accept inspection and test reports from persons authorized by this code or by the commissioner to perform such inspections. Such reports shall be filed with the department.

§28-103.17 Certain outside work, employment and financial interests of department employees prohibited. It shall be unlawful for any officer or employee of the department to be engaged in conducting or carrying on business as an architect, engineer, carpenter, plumber, iron worker, mason or builder, or any other profession or business concerned with the construction, alteration, sale, rental, development, or equipment of buildings. It shall also be unlawful for such employees to be engaged in the manufacture or sale of automatic sprinklers, fire extinguishing apparatus, fire protection devices, fire prevention devices, devices relating to the means or adequacy of exit from buildings, or articles entering into the construction or alteration of buildings, or to act as agent for any person engaged in the manufacture or sale of such articles, or own stock in any corporation engaged in the manufacture or sale of such articles.

§28-103.18 Investigation of complaints. The commissioner shall cause all complaints to be investigated. For purposes of investigating complaints of violations of law enforced by the department, the commissioner may by rule establish a program to classify structures based on their enforcement history and may create criteria for such classification and assign enforcement resources accordingly.

§28-103.18.1 Complaint records. The department shall keep records of complaints made by any person in reference to any building or other matter under the jurisdiction of the department. Recorded complaints shall include the name and residence of the complainant, the name of the person complained of, the date of the entry of the complaint and any suggested remedies. Except for entries of names and residences of the complainants, such records shall be made available for public examination.

§28-103.19 Addition, modification, and deletion of referenced standards. The standards referenced in this code may be added to, deleted or modified pursuant to local law or by rule of the department. Every such rule adding, deleting or modifying a referenced standard shall indicate the promulgating agency of the standard, the standard identification, the effective date and title and the section or sections of this code to which such standard applies. The commissioner shall act in consultation with the fire commissioner on matters relating to fire safety.

[Exception: Referenced standards in the New York city plumbing code, other than referenced national standards contained in chapter 13 of such code, shall not be added to, deleted, or modified by rule.]

§28-103.20 Existing rules continued. Rules promulgated by the department in accordance with the law in effect [prior to July 1, 2008] when such rules were promulgated shall remain in effect for the matters covered to the extent that such rules are not inconsistent with this code unless [and], until and to the extent that such rules are amended or repealed by the department.

§28-103.21 Incident lists. The commissioner shall, [by January 2018 and] on a monthly basis [thereafter] , post on the department’s website, in a machine-readable format, a list of every incident, reported to the department in accordance with section 28-103.21.1, that occurred on every construction site where construction work subject to permitting by the commissioner resulted in (i) a fatality to any individual, including a member of the general public or a construction worker, or (ii) an injury to any individual, including a member of the general public or a construction worker, that requires transport by emergency medical services or requires immediate emergency care at a hospital or offsite medical clinic, regardless of whether such incident involved a violation of this code or any other law or rule. Such list shall identify, at a minimum, the following information for each incident that the department is required to report on pursuant to this section:

1.	The owner of the site where the incident occurred;

2.	If the incident involved a construction worker, the name of the general contractor or the subcontractor who employed such worker at the time of the incident;

3.	A detailed description of the incident, including the nature of the work being performed at the time of the incident;

4.	Violations issued by the department as a result of the incident and to whom such violations were issued;

5.	The number of persons injured and/or killed in the incident, and whether such persons were members of the public, construction workers or other persons;

6.	If the incident involved an injury, a description of the type of injury;

7.	Whether the incident involved a fatality;

8.	The date and time of the incident;

9.	The address where the incident occurred;

10.	The total square footage of the site where the incident occurred;

11.	The number of floors and height of the building involved where the incident occurred or, in the case of a new building, the proposed number of floors and proposed height;

12.	A list of active permits issued by the department associated with the construction site where an incident occurred, disaggregated by type;

13.	If the incident involved a construction worker, the length of time the injured or deceased worker had been employed by their employer at the time of the incident;

14.	If the incident involved a construction worker, the number of hours the injured or deceased worker had been working when the incident occurred;

15.	If the incident involved a construction worker, whether or not the injured or deceased worker was a union member; and

16.	Whether or not the construction site where the incident occurred was a union site.

§28-103.21.1 Reporting. Where construction work subject to permitting by the commissioner that results in a fatality or injury to any individual, including a member of the general public or a construction worker, occurs on a construction site within the city, the owner or person otherwise in control of the site at which such incident occurred, or, if the incident involved a construction worker, the general contractor or subcontractor that employed such worker, shall report to the department, within three business days after the occurrence of such incident, the information required by section 28-103.21.

§28-103.22 Outreach on security grille visibility requirements. The commissioner shall, through or in cooperation with the department of small business services, the department of consumer affairs, and other city agencies deemed appropriate, develop an outreach program to manufacturers and installers of security grilles, business improvement districts, local development corporations, chambers of commerce and community boards to alert these groups and the businesses that utilize security grilles of the permit requirements and the requirements of this section, the penalties associated with violation thereof and the availability of any business loans, grants or tax subsidies related to the installation or use of such security grilles.

§28-103.23 Manual on flood construction and protection standards. The commissioner shall create and make publicly available, in print and on the department’s website, a manual explaining in detail the flood construction and protection requirements and standards applicable to the city. Such manual shall be made available in plain English and Spanish and in other languages as determined by the commissioner and shall be updated as necessary to reflect changes to applicable flood construction requirements and standards. Such manual shall include, but need not be limited to, a description and explanation of the following:

1.	The materials requirements imposed by applicable flood construction requirements and standards, including the elements of structures subject to such material requirements;

2.	The manner in which specific utilities and attendant equipment must be protected from flooding; and

3. 	The application of the flood construction and protection requirements and standards to existing structures.

§28-103.24 Electronic submissions. The commissioner shall have the discretion to require that any document or payment submitted to the department be submitted and/or signed electronically.

§28-103.25 Hotel development plans. Where the development receives applications for new construction of or conversions to transient hotels, as defined in the zoning resolution, the department shall provide written notice, or notice by electronic mail, of the proposed construction or conversion to:

1.	The borough president of the borough in which such proposed construction is located:

2.	The council member in whose district such proposed construction is located;

3.	The community board of the community district in which such proposed construction is located; and

4.	If such proposed construction involves land within two or more community districts in a borough, the borough board.

§28-103.26[.] Reporting to the federal occupational safety and health administration. As soon as practicable after the issuance of [(i)] an immediately hazardous or major violation of chapter 33 of the New York city building code [or (ii) a violation of section 3310.10.2 of the New York city building code], the commissioner shall report such violation to the federal occupational safety and health administration.

§28-103.27 Disclosure of building occupancy status for buildings subject to permit. For each building for which a permit for work has been issued, the commissioner shall post on the department’s website a statement of whether the construction documents relating to such permit indicate that one or more dwelling units within such building will be occupied during such work.

§28-103.28 Site safety training (SST) task force. The commissioner shall convene and provide staff for an SST task force in accordance with the following:

1.	Such task force shall be composed as follows:

1.1.	The commissioner, or the designee of such commissioner, shall serve as the chairperson of such task force.

1.2.	The task force shall consist of 14 members, in addition to the chairperson. Seven of the additional members of such task force shall be appointed by the mayor or the mayor’s designee, and seven of the additional members of such task force shall be appointed by the speaker of the council. Such task force shall include members who represent (i) parts of the construction industry that are represented by labor unions or labor organizations, (ii) parts of such industry that are not represented by such unions or organizations, (iii) minority-owned business enterprises or women-owned business enterprises that are certified in accordance with section 1304 of the New York city charter and primarily engaged in construction work and (iv) day laborers.

1.3	All members of the task force shall have significant experience (i) in a construction or demolition related field or (ii) developing or providing construction site safety training, except that one of the members appointed by the mayor pursuant to Item 1.2 may be a municipal officer with experience related to the program to be established pursuant to section 22-509 of the code.

2.	Such task force shall meet at least quarterly each year for the first two years of its existence and at least annually for three years thereafter.

3.	Such task force shall from time to time on its own initiative or upon request of the commissioner provide the commissioner with recommendations relating to training required by section 3321 of the New York city building code.

4.	Such task force shall establish a mechanism for receiving and reviewing recommendations from the public relating to training required by such section.

5.	By no later than March 1, 2018, such task force shall provide the commissioner with recommendations relating to the amount of additional SST credits required for satisfying item 1.1 of the definition of limited SST card and the topics that such additional SST credits must cover. Such task force shall consider, but need not include in its recommendations, the following topics insofar as such topics relate to safeguarding the public from potential dangers posed by building sites:

5.1.	Fall protection.

5.2.	Personal protection equipment.

5.3.	Safely working with machines.

5.4.	Working with hazardous chemicals or other materials.

5.5.	OSHA and its role in construction industry safety and health.

5.6.	Handling heavy materials and proper lifting techniques.

5.7.	Exit routes, emergency action plans, fire prevention and fire protection.

5.8.	Confined space awareness.

5.9.	Walking and working surfaces.

5.10.	Electrical safety.

5.11.	Hazard communication.

5.12.	Concrete operations.

5.13.	Demolition work.

5.14.	Excavation work.

5.15.	Construction and demolition work at major building sites.

5.16.	Material handling.

5.17.	Material hoisting.

5.18.	Site perimeter protection.

5.19.	Sidewalk sheds and fences.

5.20.	Steel erection.

5.21.	Tenant and occupant protection.

5.22.	Ladders and stairs.

5.23.	Drug and alcohol awareness.

5.24.	Asbestos awareness.

5.25.	Lead awareness.

5.26.	First aid, including cardiopulmonary resuscitation (CPR) and automated external defibrillator (AED) use.

§28-103.29 Reporting regarding implementation of section 3321 of the New York city building code. No later than three months after the end of each fiscal year, the commissioner shall report to the mayor and the speaker of the council, and make publicly available online, a report on implementation of section 3321 of the New York city building code. In addition to any information the commissioner deems relevant, such report shall include:

1.	The number of SST providers in existence at the end of such fiscal year. Such number shall also be disaggregated by which condition of item 1 of the definition of “site safety training (SST) provider” set forth in [section 3302.1] Chapter 2 of the New York city building code is satisfied by each such provider.

2.	The number of SST cards issued in such fiscal year.

3.	The number of temporary SST cards issued in such fiscal year.

4.	The number of violations of such section issued in such fiscal year, disaggregated by violation type.

5.	A list of building sites where violations of such section were issued and, for each such site, the following information disaggregated by violation type:

5.1.	The number of follow-up inspections conducted pursuant to section 28-204.1.1.

5.2.	The average frequency of such follow-up inspections.

5.3.	The number of violations of section 3321 of the New York city building code issued as a result of such inspections.

6.	A description of the enforcement mechanisms used by the department to ensure the integrity of training provided by SST providers in connection with section 3321 of the New York city building code and that such training satisfies the requirements of such section and any rules or department requirements relating to such training.

§28-103.29.1 Audits of training provided in connection with section 3321 of the New York city building code. In addition to any other enforcement mechanisms, the department shall periodically audit SST providers and training provided in connection with section 3321 of the New York city building code by such providers in order to ensure the integrity of such training and compliance with such section and any rules or department requirements relating to such training.

§28-103.30 Real Time Enforcement Unit. There is hereby established within the department a real time enforcement unit. Such unit and an agency that is delegated authority by the commissioner shall be responsible for enforcing the construction codes with respect to:

1.	occupied multiple dwellings with complaints related to work without a permit; and

2.	occupied multiple dwellings with valid permits for (i) the alteration of 10 percent or more of the existing floor surface area of the building or (ii) an addition to the building.

§28-103.30.1 Tracking complaints related to work without a permit. The real time enforcement unit shall receive and track all complaints related to work without a permit in occupied multiple dwellings. The unit shall retain records of such complaints.

§28-103.30.2 Monitoring occupied multiple dwellings with permits for alteration or addition. The real time enforcement unit shall monitor all occupied multiple dwellings with valid permits for (i) the alteration of 10 percent or more of the existing floor surface area of the building or (ii) an addition to the building. Owners of such buildings shall notify the department in writing at least 72 hours prior to the commencement of any work pursuant to such permits.

§28-103.30.3 Inspections. For immediately hazardous complaints related to work without a permit in occupied multiple dwellings, the real time enforcement unit shall conduct inspections of such occupied multiple dwellings within 12 hours of the receipt of such complaints, except that complaints received after 8:00 p.m. shall be inspected by 10:00 a.m. on the following day. For all other complaints related to work without a permit in occupied multiple dwellings, such unit shall conduct inspections of such multiple dwelling within ten days of receipt of such complaints. The real time enforcement unit shall also conduct initial inspections of no fewer than five percent of occupied multiple dwellings with valid permits for alteration or addition as described in section [28-103.26.2] 28-103.30.2, within 20 days of commencement of work for such alterations or additions and shall conduct periodic unannounced inspections thereafter until such work is complete. The unit shall be available to conduct inspections seven days a week, between the hours of 8:30 a.m. and 10:00 p.m.

§28-103.30.4 Violations. The real time enforcement unit shall issue notices of violation or stop work orders as necessary.

§28-103.30.5 Report. The department shall publish online an annual report with the following information related to the effectiveness of the real time enforcement unit: (i) the number of complaints received disaggregated by building; (ii) the average time taken to respond to complaints; (iii) the number of monitored occupied multiple dwellings with valid permits for alteration or addition as described in section [28-103.26.2] 28-103.30.2; (iv) the number of initial and periodic inspections conducted disaggregated by building; and (v) the number and type of violations issued disaggregated by building.

§28-103.31 Report on site safety manager and coordinator certifications. [The] In October of each year, the commissioner shall [, in October of 2018 and each year thereafter,] electronically submit to the city council and post on the department’s website a report that includes the following information regarding site safety managers and site safety coordinators:

1.	The (i) number of active site safety manager certificates and (ii) number of active site safety coordinator certificates;

2.	The (i) number of active site safety manager certificates on the last day of the preceding year and (ii) number of active site safety coordinator certificates on the last day of the preceding year;

3.	The (i) number of sites for which a site safety manager was required by this code during the preceding year and (ii) number of such sites for which a site safety manager was required by this code but for which a site safety coordinator may be designated in lieu of such manager pursuant to the exception to section 3310.5 of the New York city building code;

4.	The (i) number of site safety manager certificates issued in the preceding year and (ii) number of site safety coordinator certificates issued in the preceding year;

5.	The (i) number of applicants for site safety manager certificates who submitted applications during the preceding year and (ii) number of applicants for site safety coordinator certificates who submitted applications during the preceding year;

6.	The (i) average length of time for an applicant who submitted an application for a site safety manager certificate during the preceding year to receive such certificate, measured from the date a completed application is submitted to the department and (ii) average length of time for an applicant who submitted an application for a site safety coordinator certificate during the preceding year to receive such certificate, measured from the date a completed application is submitted to the department; and

7.	The (i) average length of time for an applicant who submitted an application for a site safety manager certificate during the preceding year to complete a background check, if any, for such certificate, measured from the date such applicant submitted all documentation necessary to complete such check, (ii) average length of time for an applicant who submitted an application for a site safety coordinator certificate during the preceding year to complete a background check, if any, for such certificate, measured from the date such applicant submitted all documentation necessary to complete such check (iii) the main three reasons for completions of background checks for applicants who submitted applications for site safety manager certificates during the preceding year exceeding the average length of time for completion of such background checks and (iv) the main three reasons for completions of background checks for applicants who submitted applications for site safety coordinator certificates during the preceding year exceeding the average length of time for completion of such background checks.

§28-103.32 Education and outreach regarding single-occupant toilet room requirements. The department, in conjunction with (i) the mayor’s office of immigrant affairs, (ii) the commission on human rights, (iii) the department of consumer affairs, (iv) the department of health and mental hygiene, (v) the department of small business services, (vi) the department of citywide administrative services and (vii) any other office or agency designated by the mayor, shall conduct education and outreach to increase awareness of sections 403.2.1 and 403.4 of the New York city plumbing code, regarding single-occupant toilet room requirements. Such education and outreach shall be tailored to business owners, and shall, at a minimum, include educational materials concerning such single-occupant toilet room requirements and the related posting and signage requirements, including samples of acceptable signage. Such materials and sample signage shall be available in the designated citywide languages as defined in section 23-1101. Information concerning such requirements shall also be made available on the department’s website.

§28-103.32.1 Reporting. [By no later than April 1, 2019, and annually thereafter] In April of each year until April 1, 2023, the commissioner of buildings shall submit to the mayor and the speaker of the council, and post on the department’s website, a report on:

1.	The education and outreach conducted as required by section 28-103.32 including a description of how such outreach was conducted and the number of business owners reached through the outreach;

2.	The number of complaints related to sections 403.2.1 and 403.4 of the New York city plumbing code reported to 311, disaggregated by online complaints and phone complaints;

3.	The number of violations issued as a result of such complaints;

4.	The total amount of penalties imposed as a result of such violations for the immediately preceding year; and

5.	Whether subsequent inspections were conducted by the department to ensure future compliance with such sections of the New York city plumbing code. The reports required pursuant to this section shall remain permanently accessible on the department’s website.

§28-103.33 Office of alternative energy. There is hereby established within the department an office of alternative energy.

§28-103.33.1 Definitions. As used in this section, the following terms have the following meaning:

ALTERNATIVE ENERGY PROJECT. Construction work on a building that will result in such building having at least 50 kilowatts of alternative energy capacity installed onsite from:

- A qualified energy resource, as such term is defined in section 45 of title 26 of the United States code; or

2. A source that is determined to be renewable by the commissioner or the head of another agency designated by the mayor.

GREEN ROOF SYSTEM. See [section 1502.1] chapter 2 of the New York city building code.

§28-103.33.2 Duties of the office of alternative energy. The duties of the office of alternative energy include, but need not be limited to:

1.	Establishing a program to (i) assist with the technical review and approval of applications and other documents submitted to the department in connection with alternative energy projects, (ii) provide guidance to applicants in connection with such projects, (iii) support technical research for advancing energy legislation and policy within the city and (iv) receive and respond to comments, questions and complaints with respect to such program;

2.	Coordinating with the office of long-term planning and sustainability, fire department, department of small business services, department of housing preservation and development, and other relevant agencies to ensure that policies are in place to encourage the installation and maintenance of alternative energy projects, and seeking cooperation and assistance from the city university of New York with respect to such policies; and

3.	Making recommendations to the commissioner and the heads of other agencies with respect to streamlining the process for obtaining the necessary approvals to install and maintain alternative energy projects.

§28-103.33.3 Reporting. The head of the office of the alternative energy shall submit an annual report to the commissioner and to the head of any other relevant agency providing (i) a description of the most commonly received comments, questions and complaints received with respect to such office, (ii) a description of actions undertaken by such office to coordinate with other agencies and the results of such coordination, (iii) recommendations made pursuant to section [28-103.31.2] 28-103.33.2 and (iv) recommendations with respect to expanding the definition of alternative energy project. By no later than three months after the end of each fiscal year, such office shall submit a report to the mayor and the speaker of the city council that includes a summary of the actions taken by any agency as a result of any comment, question, complaint or recommendation from or forwarded by such office.

§28-103.33.4 Posting of information. The office of alternative energy shall maintain a website and shall post on such website the contact information for such office and a statement indicating that any person may contact such office if such person has a comment, question or complaint with respect to such office.

§28-103.33.4.1 Information regarding installation of green roof systems. The office of alternative energy shall further post and maintain links on its website to information regarding the installation of green roof systems and other resources and materials regarding green roof systems.

§28-103.34 Electronic mail address.  All applicants, licensees, permit holders, and any other person or entity that submits any report or certification or seeks or receives any approval or authorization from the department shall provide to the department an active electronic mail address for purposes of receiving communications from the department, except where another method of communication is authorized by the commissioner. It shall be the responsibility of the applicant, licensee, permit holder, or other  person or entity to monitor and maintain an electronic email address and notify the department of any changes.

§28-103.34.1 Electronic notification. The commissioner may send written notices, documents or other correspondence to the electronic address provided pursuant to this section. Upon consent of such applicant, licensee, permit holder, or other person or entity, the commissioner may serve an order to such electronic address.

§28-103.35 E-mail notice of construction project updates. The department shall provide, free of charge, a service allowing users to register to receive an automated e-mail notification each time a change in status is recorded with respect to one or more construction projects, selected by such user. Such email notifications shall include any update to work permits issued by the department for each such selected construction project, including issuance of any stop work order issued pursuant to section 28-207.2.

§28-103.36 Bird friendly design and construction requirements. The department shall issue, and update as necessary, bird friendly building design and construction requirements. No later than October 1, 2020, the department shall post on its website such requirements and information about compliance with section 1403.8 of the New York city building code.

ARTICLE 104
CONSTRUCTION DOCUMENTS

§28-104.1 General. The department shall not issue a permit pursuant to this code, or a place of assembly operation certificate pursuant to this code unless and until it approves all required construction documents for such work. The department shall not issue an electrical work permit pursuant to the New York city electrical code for fire and emergency alarm systems, solar panels and wind turbines unless and until it approves all required construction documents for such work. Such construction documents shall be prepared by or under the supervision of a registered design professional as required by this code. An application for an associated work permit shall not be submitted to the department until all required construction documents have been approved.

§28-104.1.1 Construction documents subject to the New York city fire code. Except as the New York city fire code may otherwise provide, the construction documents for facilities and systems for which the fire code provides design and installation requirements, including but not limited to fire alarm systems, flammable and combustible liquids, compressed gases, explosives and other hazardous materials; flammable spraying systems and facilities; automatic water sprinkler systems for hazardous material and combustible material storage, and non-water fire extinguishing systems, shall be subject to the review and approval of the fire commissioner in accordance with the New York city fire code. Approval by the department of construction documents for new or existing buildings containing such facilities and systems shall not be construed as approval of such systems and facilities.

§28-104.2 Application for approval of construction documents. The department shall assign an application number to and docket all applications for approval of construction documents and any amendments thereto filed with it. The department shall examine the construction documents promptly after their submission. The examination shall be made under the direction of the commissioner for compliance with the provisions of this code and other applicable laws and rules. The personnel employed for the examination of construction documents shall be qualified registered design professionals[,] experienced in building construction and design or persons working under the supervision of such registered design professionals. The department shall provide written notification to owners of adjoining property at the time such application is submitted.

§28-104.2.1 Less than full examination of applications for construction and related document approval based on professional certification. The commissioner may, in the commissioner’s discretion, establish a program whereby construction and related documents may be accepted with less than full examination by the department based on the professional certification of an applicant who is a registered design professional. On a monthly basis, the commissioner shall audit no less than 25 percent of construction documents which are for multiple dwellings where 25 percent or more of the dwelling units are occupied and such multiple dwellings, in whole or in part, either (i) are subject to rent regulation, (ii) are being rehabilitated or maintained as affordable housing through a department of housing preservation and development program, (iii) are subject to a city regulatory agreement mandating the creation or preservation of a certain number of affordable units, (iv) contain affordable housing units created, sponsored or preserved through other city programs or initiatives, or (v) where the department knows or has reason to know, are the subject of a rent overcharge application which is in the process of being investigated by the New York State division of housing and community renewal.

Exceptions:

1.	Construction or related documents may not be subject to less than full examination if the building is listed on the department of housing preservation and development’s website pursuant to paragraph 6 of subdivision m of section 27-2115.

2.	Where a penalty is imposed pursuant to article 213 of chapter 2 of this title for work that has been performed without a permit on a building (i) construction and related documents for work at such building shall not be accepted with less than full examination by the department for one year after such imposition or (ii) if such work without a permit was performed on only part of such building and the owner of such part is not the owner of such building, construction and related documents for work on such part shall not be accepted with less than full examination by the department for one year after such imposition or until the date such part of such building changes owners, whichever is sooner.

§28-104.2.1.1 Effect of acceptance. Except as otherwise specified in this code or in the rules of the department, for the purposes of this code, the acceptance of construction and related documents in accordance with such program shall have the same force and effect as the approval of construction and related documents after full examination by the department. Except as otherwise specified in this code or in the rules of the department, references in this code to approved construction and/or related documents or to the approval of construction and/or related documents shall also be deemed to refer to accepted construction and related documents or to the acceptance of construction and related documents, as applicable.

§28-104.2.1.2 Program requirements. The commissioner may establish qualifications and requirements for registered design professionals to participate in such program and may exclude, suspend or otherwise sanction participants for cause. The commissioner shall send an annual notification to registered design professionals who are currently participating in this program notifying them, in a manner to be determined by the commissioner, of the grounds upon which they may be excluded, suspended or otherwise sanctioned.

§28-104.2.1.3 Mandatory program requirements. Registered design professionals participating in such program shall be subject to sections 28-104.2.1.3.1 through 28-104.2.1.3.2.

§28-104.2.1.3.1 Probation. A registered design professional shall not be eligible to participate in the program during any period of probation imposed as a sanction by the board of regents pursuant to section 6511 of the New York State education law.

§28-104.2.1.3.2 Mandatory sanctions. The commissioner shall, after the opportunity for a hearing before the office of administrative trials and hearings in accordance with department rules, exclude, suspend or otherwise condition the participation of a registered design professional who (i) knowingly or negligently submits a professional certification of an application and/or construction and other related document that contains false information or is not in compliance with all applicable provisions of law, (ii) submits two professionally certified applications for construction document approval within any 12-month period containing errors that result in revocation of an associated permit or that otherwise demonstrate incompetence or a lack of knowledge of applicable laws, or (iii) knowingly orders or directs another registered design professional to submit a professional certification of an application and/or construction and any other related document that contains false information or is not in compliance with all applicable provisions of law or that otherwise demonstrates incompetence or a lack of knowledge of applicable laws, or with knowledge of such specific conduct, ratifies or assents to such conduct or with knowledge of such specific conduct and while acting as a supervisor otherwise fails to prevent it.[.] The commissioner may, after the opportunity for a hearing before the office of administrative trials and hearings in accordance with department rules, exclude, suspend, or otherwise condition the participation of a registered design professional who submits two professionally certified applications for construction document approval within any 12-month period containing errors that result in a stop work order. The term “otherwise condition” shall mean limitations on such professional’s participation in the program, such as, but not limited to, audits and monitoring of the registered design professional’s applications and other submissions. For the purposes of this section, a professionally certified application shall include the professional certification of construction and other related documents and the satisfaction of objections issued at plan examination.

§28-104.2.1.3.2.1 Reinstatement. A registered design professional who is excluded from the program in accordance with section 28-104.2.1.3 may apply for reinstatement one year or more after such exclusion. An applicant who the commissioner finds is qualified to resume participation in the program shall be on probation for a period of not less than 6 months after reinstatement and during that time shall as a condition of such reinstatement attend one or more training or continuing education courses, approved by the department, related to compliance with the New York city building code and related laws and rules and the zoning resolution. The professional shall submit satisfactory proof of the successful completion of such training or continuing education courses to the department.

§28-104.2.1.3.2.2 Mandatory permanent revocation. The commissioner (i) shall permanently revoke, without the opportunity of restoration, the professional certification privileges of [an engineer or architect] the registered design professional who, while on probation, professionally certifies an application, plans, construction or other related document that contains false information or is not in compliance with all applicable provisions of law or who otherwise demonstrates incompetence or a lack of knowledge of applicable laws and (ii) may permanently revoke the professional certification privileges of [an engineer or architect] the registered design professional who knowingly orders or directs another registered design professional to, while on probation, professionally certify an application, plans, construction or other related document that contains false information or is not in compliance with all applicable provisions of law or that otherwise demonstrates incompetence or a lack of knowledge of applicable laws, or with knowledge of such specific conduct, ratifies or assents to, or with knowledge of such specific conduct and while acting as a supervisor otherwise fails to prevent it.

§28-104.2.1.3.2.3 Construction. Nothing herein shall be construed to limit the commissioner’s power, consistent with state and local law, to adopt rules that include additional grounds to limit the filing privileges of or otherwise sanction registered design professionals, after the opportunity for a hearing, who it determines, knowingly or negligently submit applications or other documents to the department that contain false information or are not in compliance with all applicable provisions of law or that otherwise demonstrate incompetence or a lack of knowledge of applicable law or standards.

§28-104.2.1.4 Database. The department shall create and maintain a database of all registered design professionals who have been excluded, suspended or otherwise sanctioned by the department, all current firms of employment or affiliation of such professionals, if known or readily ascertainable, and the firm that employed such professionals, or with which such professional was affiliated, at the time such professionals were sanctioned, and the status of such sanction or sanctions. Within 7 business days of the date a sanction is imposed, the department shall post on its website, in a non-proprietary machine-readable format that permits automated processing, and shall make available upon request, the name of the registered design professional, and the firm that employed such professionals, or with which such professionals were affiliated, at the time such professionals were sanctioned, and a description of the sanction, the initial date of the sanction, the reinstatement date, if applicable, the address of the premises for which the application associated with the sanction was submitted, and whether the sanction was imposed after a hearing or a settlement. The department shall provide requested information concerning the exclusion, suspension or other sanction of a specific registered design professional and the firm of employment of such professionals, or the firm with which such professionals were affiliated, when such professionals were sanctioned, within 30 days of such request.

§28-104.2.1.5 Applicant requirement. The program shall include a condition that the applicant remain with the project until it is signed [-] off by the department and that if the applicant withdraws from or is unable to continue a project before the issuance of a letter of completion or certificate of occupancy, as applicable, all work shall stop and no permit, letter of completion or certificate of occupancy shall be issued until a successor registered design professional is designated as applicant of record and such person:

1.	Completes a thorough review and evaluation of the previously filed and accepted construction and other related documents to determine that they conform to the applicable laws and rules in accordance with rules of the board or regents, 8 NYCRR 29.3(a)3;

2.	Inspects any built work to confirm that the observable conditions are consistent with the previously filed and accepted construction documents; [and]

3.	Performs or reviews the results of any tests or inspections required by this code to confirm that all required tests and inspection have been performed and that the results of such tests and inspections are consistent with the accepted and/or approved construction documents; and

4.	Based on the result of the evaluation and inspections, secures department approval after examination of construction and other related documents submitted by and under signature and seal of the successor. All deficiencies shall be addressed by the successor in such documents.

§28-104.2.1.6 Notice to the state department of education. The department shall provide written notice to the New York state department of education of any registered design professional who was the subject of any disciplinary proceeding where there has been an adverse determination or sanction by the department including any settlement agreement that is reached between the parties that resulted in a sanction of privileges being imposed by the department. Such notice shall be sent within ten business days after a determination is made in any such disciplinary proceeding or after a settlement of such proceeding has been reached, and shall include the name, and business firm name and address of such registered design professional, as well as any supporting documentation for the sanction imposed. The department shall also provide such notice to the state department of education of any registered design professional that has been the subject of any disciplinary proceeding where there has been an adverse determination or sanction by the department within the five calendar years immediately preceding the effective date of this section.

§28-104.2.2 Approval or acceptance to be indicated on construction documents. All construction documents, when approved, shall be stamped or endorsed “approved” under the official method of the department, followed by a notation of the date except that construction documents accepted with less than full examination by the department shall be stamped or endorsed “accepted” instead of “approved”. [One set of “approved” or “accepted” construction documents shall be retained by the department and another set shall be maintained at the project site until the work authorized by the permit is completed and signed-off by the department.]

§28-104.2.3 Time limitation of application. An application for approval of construction documents shall be deemed to have been abandoned 12 months after the date of its submission, unless such application has been diligently prosecuted after rejection in whole or in part, or unless a permit shall have been issued pursuant to this code, except that the commissioner may upon application, for reasonable cause, grant extensions of time for additional 12-month periods, including for reasons such as, the diligent prosecution of related applications at other agencies, including but not limited to, the board of standards and appeals, the city planning commission, the landmarks preservation commission and the department of environmental protection. Any such extension shall not serve to avoid compliance with section 28-104.2.4 with respect to any subsequent laws and rules in effect at the time of issuance of the associated work permit or place of assembly certificate of operation.

Exception: Where, subsequent to the filing of an application, the department determines that such application is incomplete and the department has notified the applicant that the application is incomplete, the commissioner may deem such application abandoned after 90 days from the date of such notification.

§28-104.2.4 Conditions of approval. All construction documents approved by the commissioner shall be conditioned upon and subject to compliance with the requirements of this code and other applicable laws and rules in effect at the time of issuance of the associated work permit or place of assembly certificate of operation, including, but not limited, to intervening amendments to this code or the zoning resolution, and designations by the landmarks preservation commission.

§28-104.2.5 Phased or partial approval. In the case of construction documents for the construction of new buildings or the alteration of buildings, the commissioner may grant partial approval of construction documents before the construction documents for the entire building or structure have been submitted. The approval of such partial applications will be subject to the submittal and approval of construction documents, filed together, comprising:

1.	The lot diagram showing the exact location of the lot and dimensions to the nearest corner;

2.	A complete zoning analysis showing compliance of the proposed work with the zoning resolution;

3.	The foundation plans, as provided for in section [106.7.1] 107.7.1 of the New York city building code, as well as a loading diagram and column schedule for the entire building or structure;

4.	Earthwork plans, as provided for in section 107.8 of the New York city building code; [and]

5.	The floor and roof plans showing compliance with exit requirements, as provided for in this code. Structural calculations that justify the foundation design shall be made available to the department when requested by the department. Following the partial approval of such construction documents, the issuance of a foundation and earthwork permit shall be subject to submission of required submittal documents, including related support of excavation documents in accordance with section 28-105.2.1. The owner and the holder of such a foundation and earthwork permit shall proceed at their own risk with the construction operation and without assurance that a permit for the entire structure will be granted. In the event that the project does not proceed, any open excavation shall be filled and graded in accordance with chapter 33 of the New York city building code[.]; and

6.	Other documents the department determines are necessary.

The issuance of such foundation and earthwork permit is subject to submission of required submittal documents. The owner and the holder of such foundation and earthwork permit shall proceed at their own risk with the construction operation and without assurance that a permit for the entire structure will be granted.

§28-104.2.6 Deferred submittal. With the prior approval of the department, the applicant may defer submittal of portions of the design until a specified period of time after the issuance of a permit. The applicant shall list the deferred submittal items on the initial application for construction document approval. The deferred submittal items shall not be constructed or installed until the design and submittal documents for the item have been approved by the department. The owner and permit holder shall proceed at their own risk with the construction operation and without assurance that a permit for the entire structure will be granted and the approval of all construction documents shall be conditioned upon and subject to compliance with the requirements of this code and other applicable laws and rules in effect at the time of issuance of the associated permit or place of assembly certificate of operation.

§28-104.2.7 Time period for review. Completed construction documents complying with the provisions of this code and other applicable laws and rules shall be approved by the commissioner and written notice of approval shall be given the applicant promptly and no later than 40 calendar days after the submission of a complete application.

Exceptions:

1.	On or before the fortieth day, the commissioner may, for good cause shown and upon notification to the applicant, extend such time for an additional 20 calendar days.

2.	Such time period for review shall commence in accordance with article 107 for single room occupancy multiple dwellings.

§28-104.2.7.1 Notification of approval. The department shall, on a weekly basis, send council members and community boards, by electronic mail, and post on its website, a [copy] report of all [notices of approval for] applications [sent to applicants] that were approved during the prior week, disaggregated by community board, for:

1.	A new building or an alteration that will require a new certificate of occupancy for a building; and

2.	Work at a building or part thereof for which construction and related documents shall not be accepted with less than full examination by the department pursuant to the exception to section 28-104.2.1.

§28-104.2.8 Notification of rejection. Applications failing to comply with the provisions of this code and other applicable laws and rules shall be rejected and written notice of rejection, stating the grounds of rejection, shall be given the applicant promptly and not later than the date required in section 28-104.2.7. The department shall, on a weekly basis, send council members and community boards, by electronic mail, a [copy] report of all [notices of a first rejection for] rejections of applications for a new building or an alteration that will require a new certificate of occupancy for a building, [sent to applicants] during the prior week, disaggregated by community board. In addition, the department shall post such information on its website on a weekly basis.

§28-104.2.9 Resubmission. Whenever an application has been rejected and is thereafter revised and resubmitted to meet the stated grounds of rejection, the revised application and construction documents shall be approved if they meet the stated grounds of rejection and otherwise comply with the provisions of this code and other applicable laws and rules or shall be rejected if they fail to meet the stated grounds of rejection or otherwise fail to so comply. Written notice of approval or written notice of rejection, stating the grounds of rejection, shall be given the applicant promptly and not later than 20 calendar days after the resubmission of such documents.

§28-104.2.10 Revocation of approval. The commissioner may, on notice to the applicant, revoke the approval of construction documents for failure to comply with the provisions of this code or other applicable laws or rules; or whenever there has been any false statement or any misrepresentation as to a material fact in the submittal documents upon the basis of which such approval was issued; or whenever an approval has been issued in error and conditions are such that approval should not have been issued. Such notice shall inform the applicant of the reasons for the proposed revocation and that the applicant has the right to present to the commissioner or his or her representative within 10 business days of personal service or electronic delivery or 15 [calendar] business days of the posting of service by mail, information as to why the approval should not be revoked.

§28-104.2.10.1 Effect on work permit. The effect of revocation of approval of construction documents is the automatic revocation of all work permits that may have been issued based on such construction documents.

§28-104.3 Amended construction documents. Subject to the time limitations set forth in this code, amendments to approved construction documents shall be submitted, reviewed and approved before the work or equipment is completed; and such amendments when approved shall be deemed part of the original construction documents. The department may allow minor revisions of construction documents to be made and submitted to the department after the completion of work but prior to sign-off of the work [in accordance with department rules]. All other revisions of construction documents shall be submitted and approved prior to commencing the work effectuating such revisions.

§28-104.4 Place of filing. Except as otherwise provided by rule, applications for construction document approval shall be filed in the department office in the borough in which the work or equipment is located or at the discretion of the commissioner shall be submitted electronically.

§28-104.5 Fees. Filing fees shall be paid as required by article 112.

§28-104.6 Applicant. The applicant for approval of construction documents shall be the registered design professional who prepared or supervised the preparation of the construction documents on behalf of the owner.

Exception: The applicant may be other than a registered design professional for:

1.	Limited [oil burner/boiler] oil-burning appliance alterations, limited plumbing alterations, limited sprinkler alterations, and limited standpipe alterations (limited alteration application), where the applicant is licensed to perform such work pursuant to this code;

2.	Demolition applications other than those specified in section 3306.5 of the New York city building code, where the applicant is the demolition contractor performing such demolition. In such cases, the commissioner may require structural plans designed by a registered design professional to address any critical structural, sequencing or site safety items;

3.	Elevator applications;

4.	Applications for work falling within the practice of landscape architecture as defined by the New York state education law, including but not limited to landscaping and vegetation plans, tree protection plans, erosion and sedimentation plans, grading and drainage plans, curb cuts, pavement plans, and site plans for urban plazas and parking lots, where the applicant is a landscape architect. Landscape architects shall not file plans for stormwater management and plumbing systems;

5.	 Other categories of work consistent with rules promulgated by the commissioner.

§28-104.6.1 Verification of professional qualification required. The department shall not accept construction documents or other documents submitted in connection with applications for construction document approval or work permits under this code by any person representing that he or she is a registered design professional or landscape architect without verifying, by means of lists compiled and made available by the New York state department of education pursuant to paragraph e-1 of subdivision four of section sixty-five hundred seven of the New York state education law, that such person meets the qualifications established by law to practice as an architect or engineer in New York state.

§28-104.7 Submittal of construction documents. All construction documents submitted to the department shall contain such information and shall be in such form as shall be set forth in this section 28-104.7 and the rules of the department. Construction documents shall also conform to standards as may be prescribed in the applicable sections of the construction codes.

§28-104.7.1 Scope. Construction documents shall be complete and of sufficient clarity to indicate the location and entire nature and extent of the work proposed, and shall show in detail that they conform to the provisions of this code and other applicable laws and rules; if there exist practical difficulties in the way of carrying out the strict letter of the code, laws or rules, the applicant shall set forth the nature of such difficulties.

§28-104.7.2 Forms. The applicant shall submit construction documents on or accompanied by forms provided by the department.

§28-104.7.3 Media. Construction documents shall be printed upon suitable material, or presented as electronic media documents as determined by the commissioner. Plans shall be drawn to suitable scale, resolution and file format as determined by the commissioner.

§28-104.7.4 Quantities. The applicant shall submit the number of copies of construction documents as the commissioner shall require.

§28-104.7.5 Citations to code sections required. In no case shall terms such as “code compliant”, “approved”, “legal” or similar terms be used in the construction documents as a substitute for specific reference to a particular code section, approval or standard in order to show compliance with code requirements or other applicable laws and rules.

§28-104.7.6 City datum. All elevations noted in the construction documents shall be referred to and clearly identified as the North American vertical datum of 1988 (“NAVD”) as established and maintained by National Geodetic Survey of the National Ocean Service, National Oceanic and Atmospheric Administration or successor agency, which is hereby established as the city datum. Neither the United States coast and geodetic survey mean sea level datum of 1929 (national geodetic vertical datum, (“NGVD”) nor any of the five borough data as established by the former Board of Estimate and Apportionment shall be referred to in construction documents except as may be required for the purpose of demonstrating conversion to the NAVD. Conversions to NAVD shall be performed by registered design professionals or surveyors. Conversion to and from borough data, [and] NGVD and NAVD shall be performed using tables 104.7.6.1 through 104.7.6.5.

| TABLE 104.7.6.1a |
| --- |
| BRONX ELEVATIONS | TO OBTAIN EQUIVALENCY: | NGVD ELEVATIONS | TO OBTAIN EQUIVALENCY: | NAVD ELEVATIONS |
| 8.422 to 8.495 | →add 2.608→ | 11.030 to 11.083 | →subtract between 1.030 and 1.083→ | 10.000 |
| 10.000 | →add 2.608→ | 12.608 | →subtract between 1.030 and 1.083→ | 11.525 to 11.578 |
| 7.392 | →add 2.608→ | 10.000 | →subtract between 1.030 and 1.083→ | 8.917 to 8.970 |

a.	Conversions to and from NAVD as indicated in this table represent the likely range. The precise conversion depends on the latitude and longitude of the location in question, as determined by a surveyor.

| TABLE 104.7.6.2a |
| --- |
| BROOKLYN ELEVATIONS | TO OBTAIN EQUIVALENCY: | NGVD ELEVATIONS | TO OBTAIN EQUIVALENCY: | NAVD ELEVATIONS |
| 8.546 to 8.572 | →add 2.547→ | 11.093 to 11.119 | →subtract between 1.093 and 1.119→ | 10.000 |
| 10.000 | →add 2.547→ | 12.547 | →subtract between 1.093 and 1.119→ | 11.428 to 11.454 |
| 7.453 | →add 2.547→ | 10.000 | →subtract between 1.093 and 1.119→ | 8.881 to 8.907 |

a.	Conversions to and from NAVD as indicated in this table represent the likely range. The precise conversion depends on the latitude and longitude of the location in question, as determined by a surveyor.

| TABLE 104.7.6.3a |
| --- |
| MANHATTAN ELEVATIONS | TO OBTAIN EQUIVALENCY: | NGVD ELEVATIONS | TO OBTAIN EQUIVALENCY: | NAVD ELEVATIONS |
| 8.288 to 8.357 | →add 2.752→ | 11.040 to 11.109 | →subtract between 1.040 and 1.109→ | 10.000 |
| 10.000 | →add 2.752→ | 12.752 | →subtract between 1.040 and 1.109→ | 11.643 to 11.712 |
| 7.248 | →add 2.752→ | 10.000 | →subtract between 1.040 and 1.109→ | 8.891 to 8.960 |

a.	Conversions to and from NAVD as indicated in this table represent the likely range. The precise conversion depends on the latitude and longitude of the location in question, as determined by a surveyor.

| TABLE 104.7.6.4a |
| --- |
| QUEENS ELEVATIONS | TO OBTAIN EQUIVALENCY: | NGVD ELEVATIONS | TO OBTAIN EQUIVALENCY: | NAVD ELEVATIONS |
| 8.361 to 8.381 | →add 2.725→ | 11.086 to 11.106 | →subtract between 1.086 and 1.106→ | 10.000 |
| 10.000 | →add 2.725→ | 12.725 | →subtract between 1.086 and 1.106→ | 11.619 to 11.639 |
| 7.275 | →add 2.725→ | 10.000 | →subtract between 1.086 and 1.106→ | 8.914 to 8.894 |

a.	Conversions to and from NAVD as indicated in this table represent the likely range. The precise conversion depends on the latitude and longitude of the location in question, as determined by a surveyor.

| TABLE 104.7.6.5a |
| --- |
| STATEN ISLAND ELEVATIONS | TO OBTAIN EQUIVALENCY: | NGVD ELEVATIONS | TO OBTAIN EQUIVALENCY: | NAVD ELEVATIONS |
| 7.835 to 7.917 | →add 3.192→ | 11.027 to 11.109 | →subtract between 1.027 and 1.109→ | 10.000 |
| 10.000 | →add 3.192→ | 13.192 | →subtract between 1.027 and 1.109→ | 12.083 to 12.165 |
| 6.808 | →add 3.192→ | 10.000 | →subtract between 1.027 and 1.109→ | 8.891 to 8.973 |

a.	Conversions to and from NAVD as indicated in this table represent the likely range. The precise conversion depends on the latitude and longitude of the location in question, as determined by a surveyor.

§28-104.7.7 Identification of special and progress inspections. Whenever work or materials are subject to special inspection, as provided in this code, such work or materials shall be listed on the title sheet of the construction documents, or the sheet immediately following, as subject to special or progress inspection.

§28-104.7.8 Identification of materials. Construction documents shall identify all materials proposed to be used, including identification of the test standard to which they conform, and where applicable, supporting information or test data from the manufacturer attesting to such conformance.

§28-104.7.9 Energy conservation code. The application shall contain all information required to demonstrate compliance with the New York city energy conservation code. This information shall include signed and sealed construction drawings, including electrical drawings, to the extent that they demonstrate such energy code compliance, as required by such energy code and rules.

§28-104.7.10 Preparer. Each plan or drawing shall contain the license number, seal, signature (or equivalent as approved by the commissioner) and address of the registered design professional or landscape architect who prepared or supervised the preparation of the plans.

§28-104.7.11 Additional information. In addition to the data and information specified in this code and the rules of the department, the commissioner is authorized to require the submission of additional plans, surveys, computations, analyses, test reports, photographs, special inspection and such other data and information as may be necessary to determine compliance with this code and other applicable laws and rules.

§28-104.7.12 Waiver of certain documents. The commissioner is authorized to waive the submission of any of the required construction documents and other data if review of such documents is not necessary to ascertain compliance with this code or not required for the phase of work for which a permit is sought.

§28-104.7.13 Identification of work involving raising or moving a building. Where the lowest above-grade floor or the lowest subgrade floor of a building is to be raised, lifted, elevated or moved, such work shall be listed on the title sheet of the construction documents as subject to special inspection.

§28-104.7.14 Identification of certain I-1 and I-2 occupancies and of certain adult homes, enriched housing, community residences and intermediate care facilities as exempt from temporary external generator connection requirements. The title sheet of construction documents for the following buildings shall list whether the building is exempt from the requirement to provide connections for temporary external generators pursuant to any exception contained in Sections G304.5.1 or G304.5.2 of appendix G of the New York city building code, as applicable:

1.	A new or substantially improved building, as such term is defined in appendix G of the New York city building code, that contains space classified in occupancy group I-1 or I-2 or space that is an adult home, enriched housing, community residence or intermediate care facility classified as occupancy group R pursuant to an exception to section [308.2.1] 308.3.1 or [308.2.2] 308.3.2 of the New York city building code, and that is located in [an area of] a special flood hazard area, as such term is defined in appendix G of the New York city building code; and

2.	A new or substantially improved building that contains space classified as an occupancy group I-2 hospital and that is located in a shaded X-Zone, as such terms are defined in appendix G of the New York city building code.

§28-104.7.15 Identification of certain hospitals as exempt from temporary external boiler or chiller connection requirements. The title sheet of construction documents for a new or substantially improved building, as such term is defined in appendix G of the New York city building code, that contains space classified as an occupancy group I-2 hospital and that is located in [an area of special] a flood hazard [or shaded X-Zone] area, as such [terms are] term is defined in appendix G of the New York city building code, shall list whether the requirement to provide connections for temporary external boilers and chillers pursuant to Item 2 of section G304.5.2 is inapplicable as a result of such building having its boiler and chiller plants located at or above the applicable design flood elevation.

§28-104.7.16 Tenant protection plan. The title sheet of construction documents shall contain a statement requiring a tenant protection plan be submitted in accordance with the requirements of article 120 prior to the issuance of a permit for alteration, construction or partial demolition work in a building containing one or more occupied dwelling units.

§28-104.7.17 Amended certificates of occupancy. For amended certificates of occupancy subject to section 28-118.16.2, the term construction documents, as used in section 28-116.2.4.1, shall mean an accurate and complete final lot survey made by a land surveyor, and floor and roof plans showing, at a minimum, compliance with exit requirements in accordance with this code.

§28-104.7.18 Multiple tax lots on a zoning lot. For applications that will result in a new building or an enlargement to an existing building, construction documents shall, on forms provided by the department:

1.	Identify whether the zoning lot consists of a single tax lot or multiple tax lots;

2.	In the case of multiple tax lots on a zoning lot:

2.1.	state whether each tax lot does or does not have a current certificate of occupancy;

2.2.	for each tax lot that has a certificate of occupancy, state whether:

2.2.1.	the address of the building or open lot use on  each such certificate of occupancy is consistent with the current lawful street address;

2.2.2.	the block and/or tax lot numbers on  each such certificate of occupancy is consistent with the current tax maps as published by the Department of Finance;

2.2.3.	the certificate of occupancy indicates metes and bounds of a zoning lot and whether such metes and bounds are inconsistent with the metes and bounds of the zoning lot in the application; and

2.2.4.	there is an existing building or an open lot use without a certificate of occupancy.

2.3.	Following a change in the metes and bounds of a zoning lot, construction documents shall be filed by the owner of each tax lot with a certificate of occupancy that indicates inconsistent metes and bounds to reflect the change in metes and bounds of the zoning lot, in accordance with the requirements of section 28-118.3.2.1.

2.4.	Following a change in the metes and bounds of a zoning lot, construction documents shall be filed by the owner of each tax lot without a certificate of occupancy or where the certificate of occupancy does not indicate inconsistent metes and bounds,  in accordance with the requirements of section 28-118.3.3.

§28-104.7.18.1 Obligations of owners of other tax lot. Within one year from the approval of construction documents for a new building or enlargement on a zoning lot consisting of multiple tax lots, the owners of all tax lots on the zoning lot shall comply with sections 28-118.3.2.1, 28-118.3.3 and 28-118.3.5.1 as applicable.

Exception. For the purpose of this section, condominium tax lots and air parcel tax lots shall not be deemed to be multiple tax lots.

§28-104.8 Applications. All applications shall comply with sections 28-104.8.1 through 28-104.8.3.

§28-104.8.1 Applicant statements. The application shall contain the following signed and sealed statements by the applicant:

1.	A statement certifying that the applicant is authorized by the owner to make the application and certifying that, to the best of the applicant’s knowledge and belief, the construction documents comply with the provisions of this code or the 1968 building code, if applicable, and other applicable laws and rules; if there exist practical difficulties in the way of carrying out the strict letter of the code, laws or rules, the applicant shall set forth the nature of such difficulties in such signed statement;

2.	A professional certification; and

3.	A statement certifying compliance with the New York city energy conservation code.

§28-104.8.2 Owner statements. The application shall contain a signed statement by the owner, and, in the case of cooperative or condominium forms of ownership, the application shall also contain a statement by the cooperative or condominium board, affirming that the applicant is authorized to make the application and, if applicable, acknowledging that construction and related documents will be accepted with less than full examination by the department based on the professional certification of the applicant. Such statement shall list the owner’s full name and address, as well as the names of the principal officers, partners or other principals if a corporation, partnership or other entity. Principal officers of a corporation shall be deemed to include the president, vice presidents, secretary and treasurer. Where a current deed holder with a valid property interest or a court appointed entity or equivalent in charge of the property, or in the case of a cooperative or condominium unit, the cooperative or condominium board, notifies the department in writing that the applicant does not have authority to make the application, the department is authorized pursuant to section 28-104.2.10 to revoke approval of construction documents. In addition, the application shall contain the following:

1.	A signed statement certifying whether the building to be altered, constructed or demolished contains one or more occupied dwelling units;

2.	A signed statement indicating whether the building to be altered, constructed or demolished contains housing accommodations subject to rent control or rent stabilization under chapters 3 and 4 of title 26 of the administrative code or rent regulation under [Article] article 7-C of the [Multiple Dwelling Law] New York state multiple dwelling law; and

3.	If the building to be altered, constructed or demolished contains occupied housing accommodations subject to rent control under chapter 3 of title 26 of the administrative code, the application shall contain a signed statement indicating that the owner has notified the New York state division of homes and community renewal that the owner has complied with all requirements imposed by the regulations of such agency as preconditions for such filing; or that the owner has not notified such agency because the nature and scope of the work proposed, pursuant to such regulations, does not require notification; or, if the building is subject to [Article] article 7-C of the [Multiple Dwelling Law] New York state multiple dwelling law, the application shall contain a signed statement indicating that the owner will notify the [New York City Loft Board] loft board of the filing of the construction documents and will comply with all requirements imposed by [Multiple Dwelling Law Article] New York state multiple dwelling law article 7-C and the [Loft Board’s] loft board’s rules.

§28-104.8.3 Information of applicant, filing representative, and owner. The application shall set forth the full names, addresses, telephone numbers, and [where available,] e-mail addresses of the following persons and where any of such persons are corporations, partnerships or other business entities, the names and addresses of the principal officers, partners or other principals of such entity:

1.	The applicant;

2.	The filing representative;

3.	The owner, and, in the case of cooperative or condominium forms of ownership, cooperative owners’ corporation, or condominium owners’ association; and

4.	Where a person other than the owner has engaged the applicant, such cooperative unit shareholder, condominium unit owner, lessee, or mortgagee.

§28-104.9 Coastal zones and water-sensitive inland zones. Construction documents shall comply with sections 28-104.9.1 through 28-104.9.6 relating to work in coastal zones and water-sensitive inland zones.

§28-104.9.1 Definitions. As used in section 28-104.9 the following terms shall have the following meanings:

COASTAL [AREAS OF] SPECIAL FLOOD HAZARD AREAS. Areas of land as identified on the flood insurance rate maps referenced in New York city building code section G402 pursuant to article 36 of the New York state environmental conservation law.

COASTAL EROSION HAZARD AREAS. Areas of land as identified on the final map issued by the New York state department of environmental conservation in accordance with section 34-0104 of the New York state environmental conservation law.

COASTAL ZONES AND WATER-SENSITIVE INLAND ZONES. Areas of land comprising tidal wetlands, freshwater wetlands, coastal erosion hazard areas, coastal [areas of] special flood hazard areas or rivervine and other inland [areas of] special flood hazard areas.

FRESHWATER WETLANDS. Areas of land as identified on the final map issued by the New York state department of environmental conservation in accordance with section 24-0301 of the New York state environmental conservation law, as well as any adjacent areas as such term is defined in section 662.1 of title six of the New York code of rules and regulations.

RIVERVINE AND OTHER INLAND [AREAS OF] SPECIAL FLOOD HAZARD AREAS. Areas of land, including floodways, as identified on the flood insurance rate maps referenced in section G402 of the New York city building code pursuant to article 36 of the New York state environmental conservation law.

STRUCTURE. Any object constructed, installed or placed in, on or under land or water, including, but not limited to, a building, permanent shed, deck, in-ground or aboveground swimming pool, garage, mobile home, paving, road, public utility service distribution, transmission and collection system, storage tank, pier, dock, wharf, groin, jetty, seawall, revetment, bulkhead or breakwater.

TIDAL WETLANDS. Areas of land as identified on the tidal wetland inventory issued by the New York state department of environmental conservation in accordance with section 25-0201 of the New York state environmental conservation law, as well as any adjacent areas as such term is defined in section 661.4 of title six of the New York code of rules and regulations.

§28-104.9.2 Statement and submission by applicant. It shall be the duty of an applicant for construction document approval to determine whether the proposed work is located within a coastal zone or a water-sensitive inland zone subject to section 28-104.9.3 and/or section 28-104.9. Applications for construction document approval shall include a statement by the applicant indicating whether the proposed work is located within a coastal zone or water-sensitive inland zone subject to such sections. The failure to disclose that proposed work is within a coastal zone or water-sensitive inland zone subject to such sections shall be a violation of this code.

§28-104.9.3 Coordination with department of environmental conservation and other agencies. The commissioner shall not approve construction documents for construction of a new structure, the horizontal enlargement of a structure or to excavate or fill any land, within a tidal wetland, a tidal wetland adjacent area, freshwater wetland, freshwater wetland adjacent area, or coastal erosion hazard area, without documentation satisfactory to the commissioner that the New York state department of environmental conservation, and such other governmental agencies as are applicable, have issued any applicable permits or other approvals for such construction, excavation or fill.

§28-104.9.4 Compliance with special flood hazard area requirements mandated within special flood hazard areas. Within coastal [areas of] special flood hazard areas and [areas of] special flood hazard areas, the commissioner shall not approve construction documents for construction or alteration of buildings or structures, including alterations pursuant to section 28-101.4.3, or for any other activity regulated by section G201 of the New York city building code, unless the application complies with the requirements of Appendix G of the New York city building code.

§28-104.9.5 False statement or omission. No person shall submit an application for construction document approval for any structure within a coastal zone or water-sensitive inland zone [which] that falsely avers or by omission causes the department to determine that the subject property is not located within such zone or that the New York state department of environmental conservation and other appropriate agencies have issued the appropriate permits or approvals when they did not.

§28-104.9.6 Revocation of approval of construction documents. Where the department determines that work is located within a coastal zone or water-sensitive inland zone after construction documents have been approved for such work and/or that the documentation required by sections 28-104.9.2 through 28-104.9.4 has not been submitted, the department shall revoke such approval and any associated work permits that may have been issued for such work in accordance with section 28-104.2.10.

§28-104.10 [Construction documents for sites near subways or tunnels.]  Notification to the New York City Transit Authority, the Metropolitan Transportation Authority, and the Port Authority of New York and New Jersey.  Construction documents shall not be approved unless all applicable agency approvals [regarding nearby subways or tunnels]  from the New York City Transit Authority, the Metropolitan Transportation Authority, or the Port Authority of New York and New Jersey, as provided for in [sections 3304.3.3 and] section 3304.3.5 of the New York city building code have been submitted to the department.

§28-104.11 Construction documents for sites that are covered development projects as defined in section 24-541 of the administrative code. Construction documents for sites that are covered development projects as defined in section 24-541 of the administrative code shall comply with section 28-104.11.1 through 28-104.11.4.

§28-104.11.1 Definitions. As used in this code in connection with provisions relating to the jurisdiction of the department of environmental protection, the terms covered development project, development activity, post-construction stormwater management facility, stormwater construction permit, stormwater maintenance permit, and stormwater pollution prevention plan or SWPPP shall have the same definitions as such terms are defined in subchapter 1 of chapter 5-A of title 24 of the administrative code.

§28-104.11.2 Disclosure required. It shall be the duty of an applicant for construction document approval to determine whether the site of the proposed work is part of a covered development project and to disclose such information on construction documents. Failure to disclose such information on construction documents shall be a violation of this code.

§28-104.11.3 Required documentation. Applications for construction document approval shall include copies of any required stormwater construction permit issued by the department of environmental protection and the stormwater pollution prevention plan for the covered development project.

§28-104.11.4 Revocation of approval of construction documents. Where the department finds after the approval of construction documents that the applicant failed to disclose the information required by this section, the department may revoke such approval and any associated work permits in accordance with the provisions of sections 28-104.2.10 and 28-104.2.10.1.

§28-104.12 Retention of construction and submittal documents. An applicant shall retain one set of approved construction documents, submittal documents, and any other documents required by department rule for a period of not less than six years from the date of completion of the permitted work.

§28-104.13 Construction documents for extension, alteration or relocation of an existing chimney or vent. Where an owner of a new or altered taller building is required by section 2113 of the New York city building code, section 801 of the New York city mechanical code or section 501 of the New York city fuel gas code to extend, alter or relocate an existing chimney or vent on an affected building, such work shall be filed under a separate application for the affected building.

ARTICLE 105
PERMITS

§28-105.1 General. It shall be unlawful to construct, enlarge, alter, repair, move, demolish, remove or change the use or occupancy of any building or structure in the city, to change the use or occupancy of an open lot or portion thereof, or to erect, install, alter, repair, or use or operate any sign or service equipment in or in connection therewith, or to erect, install, alter, repair, remove, convert or replace any gas, mechanical, plumbing, fire suppression or fire protection system in or in connection therewith or to cause any such work to be done unless and until a written permit [therefore] therefor shall have been issued by the commissioner in accordance with the requirements of this code, subject to such exceptions and exemptions as may be provided in section 28-105.4.

§28-105.1.1 Notification to fire department. The commissioner, in consultation with the fire commissioner, shall establish a procedure for notifying the fire department of the issuance of any permit that will result in the issuance of a new or amended certificate of occupancy or other change in the use or occupancy of the premises. In no instance shall the required notice be given to the fire department more than one business day after the date of the issuance of the permit.

§28-105.1.2 Projects for which a stormwater construction permit is required. It shall be a violation of this code to engage in any development activity with respect to a covered development project without a stormwater construction permit issued by the department of environmental protection. The issuance of a permit pursuant to this code shall not be construed to be permission for any activity that requires a stormwater construction permit issued by the department of environmental protection pursuant to chapter 5-A of title 24 of the administrative code. The issuance of a stormwater construction permit by the department of environmental protection shall not be construed as permission for work that requires a permit from the department of buildings pursuant to this code.

[§28-105.1.2 Denial of permits for certain arrears. The commissioner shall not issue a permit for a new building, demolition, place of assembly or major alteration that will change the use, egress or occupancy for a property if $25,000 or more in covered arrears is owed to the city with respect to such property or if the owners of such property owe, in aggregate, $25,000 or more in covered arrears to the city, provided that, where a dwelling unit within a property is owned as a condominium or held by a shareholder of a cooperative corporation under a proprietary lease, covered arrears owed to the city for such unit shall not be considered covered arrears owed to the city for such property. For the purposes of this section, the term “covered arrears” may include any of the following, but shall not include any such items that are currently in the appeals process:]

[1.	Unpaid fines, civil penalties or judgments entered by a court of competent jurisdiction or the environmental control board pursuant to chapter 2 of this title or chapter 2 of title 28 of the code; and]

[2.	Unpaid and past due fees or other charges lawfully assessed by the commissioner.]

[Exceptions:]

[1.	The commissioner may issue a permit for a property if the applicant submits a certification from the department of finance that binding agreements are in force requiring payment of all covered arrears owed by the owners of such property, and such owners are in compliance with such agreement.]

[2.	The commissioner may issue a permit for a property where the issuance of such permit is necessary to correct an outstanding violation of this code, the housing maintenance code or any other applicable provisions of law or rule or where the commissioner determines that issuance of such permit is necessary to perform work to protect public health and safety.]

[3.	The commissioner may issue a permit for a portion of a property occupied by a tenant who is not an owner of such property or responsible for any covered arrears owed with respect to such property.]

[4.	The commissioner may issue a permit, for a dwelling unit within a property that is owned by a condominium or held by a shareholder of a cooperative corporation under a proprietary lease, if the owners of record for such unit do not owe, in aggregate, $25,000 or more in covered arrears to the city.]

[5.	The commissioner may issue a permit where a property was the subject of an in rem foreclosure judgment in favor of the city and was transferred by the city to a third party pursuant to section 11-412.1 of the code.]

[6.	The commissioner may issue a permit where a property is the subject of a court order appointing an administrator pursuant to article 7-a of the real property actions and proceedings law in a case brought by the department of housing preservation and development.]

[7.	The commissioner may issue a permit where a property is the subject of a loan provided by or through the department of housing preservation and development or the New York city housing development corporation for the purpose of rehabilitation that has closed within the five years preceding the application for such permit.]

[8.	The commissioner may issue a permit for a property where the department of housing preservation and development or the New York city housing development corporation notifies the commissioner that the permit is required for participation in a program that involves rehabilitation of such property.]

§28-105.1.3 Denial of permits for excessive violations. The commissioner shall, no less than once every six months, compile a list of multiple dwellings that includes: (i) all multiple dwellings containing fewer than 35 units that have a ratio of open hazardous or immediately hazardous New York city housing maintenance code violations or immediately hazardous or major construction code violations that equal in the aggregate three or more such violations for every dwelling unit in such multiple dwelling; and (ii) all multiple dwellings containing 35 units or more that have a ratio of open hazardous or immediately hazardous New York city housing maintenance code violations or immediately hazardous or major construction code violations that equal in the aggregate two or more such violations for every dwelling unit in such multiple dwelling. The commissioner shall not issue permits for multiple dwellings on such list. If the owner of a multiple dwelling on such list corrects open hazardous or immediately hazardous New York city housing maintenance code violations or immediately hazardous or major construction code violations in such multiple dwelling so that the ratio of such violations to the number of dwelling units in such multiple dwelling falls below those outlined in this section, the commissioner shall remove such multiple dwelling from such list. Such denial shall not apply where a dwelling unit within such multiple dwelling is owned as a condominium or held by a shareholder of a cooperative corporation under a proprietary lease.

Exceptions:

1.	Where the issuance of such permit is necessary to correct an outstanding violation of this code, the New York city housing maintenance code or any other applicable provisions of law or rule.

2.	Where the issuance of such permit is necessary to perform work to protect public health and safety.

3.	For a portion of a property occupied by a tenant who is not an owner of such property or responsible for any existing violations in such property.

4.	Where a property was the subject of an in rem foreclosure judgment in favor of the city and was transferred by the city to a third party pursuant to section 11-412.1 of the administrative code.

5.	Where a property is the subject of a court order appointing an administrator pursuant to article 7-a of the New York state real property actions and proceedings law in a case brought by the department of housing preservation and development.

6.	Where a property is the subject of a loan provided by or through the department of housing preservation and development or the New York city housing development corporation for the purpose of rehabilitation that has closed within the five years preceding the application for such permit.

7.	For a property where the department of housing preservation and development or the New York city housing development corporation notifies the commissioner that the permit is required in connection with the implementation of a program of such department or corporation.

§28-105.1.4 Denial of permits for false statements on applications for construction document approval. The commissioner shall not issue a permit for an occupied building for at least one year following the date of a determination by the commissioner that a false statement about the occupancy status of such building has been made in an application for construction document approval. Such denial shall not apply where a dwelling unit within such multiple dwelling is owned as a condominium or held by a shareholder of a cooperative corporation under a proprietary lease.

Exceptions:

1.	Where the issuance of such permit is necessary to correct an outstanding violation of this code, the New York city housing maintenance code or any other applicable provisions of law or rule.

2.	Where the issuance of such permit is necessary to perform work to protect public health and safety.

3.	For a portion of a property occupied by a tenant who is not an owner of such property or responsible for any existing violations in such property.

4.	Where a property was the subject of an in rem foreclosure judgment in favor of the city and was transferred by the city to a third party pursuant to section 11-412.1 of the administrative code.

5.	Where a property is the subject of a court order appointing an administrator pursuant to article 7-a of the New York state real property actions and proceedings law in a case brought by the department of housing preservation and development.

6.	Where a property is the subject of a loan provided by or through the department of housing preservation and development or the New York city housing development corporation for the purpose of rehabilitation that has closed within the five years preceding the application for such permit.

7.	For a property where the department of housing preservation and development or the New York city housing development corporation notifies the commissioner that the permit is required in connection with the implementation of a program of such department or corporation.

§28-105.1.5 Denial of permits for work without permit on occupied building. The commissioner shall not issue a permit for a building for at least one year following the date of a determination by the commissioner that work has been performed without a permit in such building and such building was occupied at the time such work was being performed. Such denial shall not apply where a dwelling unit within such multiple dwelling is owned as a condominium or held by a shareholder of a cooperative corporation under a proprietary lease.

Exceptions:

1.	Where the issuance of such permit is necessary to correct an outstanding violation of this code, the New York city housing maintenance code or any other applicable provisions of law or rule.

2.	Where the issuance of such permit is necessary to perform work to protect public health and safety.

3.	For a portion of a property occupied by a tenant who is not an owner of such property or responsible for any existing violations in such property.

4.	Where a property was the subject of an in rem foreclosure judgment in favor of the city and was transferred by the city to a third party pursuant to section 11-412.1 of the administrative code.

5.	Where a property is the subject of a court order appointing an administrator pursuant to article 7-a of the New York state real property actions and proceedings law in a case brought by the department of housing preservation and development.

6.	Where a property is the subject of a loan provided by or through the department of housing preservation and development or the New York city housing development corporation for the purpose of rehabilitation that has closed within the five years preceding the application for such permit.

7.	For a property where the department of housing preservation and development or the New York city housing development corporation notifies the commissioner that the permit is required in connection with the implementation of a program of such department or corporation.

§28-105.1.6 Denial of permits for certain arrears. The commissioner shall not issue a permit for a new building, demolition, place of assembly or major alteration that will change the use, egress or occupancy for a property if $25,000 or more in covered arrears is owed to the city with respect to such property or if the owners of such property owe, in aggregate, $25,000 or more in covered arrears to the city, provided that, where a dwelling unit within a property is owned as a condominium or held by a shareholder of a cooperative corporation under a proprietary lease, covered arrears owed to the city for such unit shall not be considered covered arrears owed to the city for such property. For the purposes of this section, the term “covered arrears” may include any of the following, but shall not include any such items that are currently in the appeals process:

1.	Unpaid fines, civil penalties or judgments entered by a court of competent jurisdiction or the environmental control board pursuant to chapter 2 of this title; and

2.	Unpaid and past due fees or other charges lawfully assessed by the commissioner.

Exceptions:

1.	The commissioner may issue a permit for a property if the applicant submits a certification from the department of finance that binding agreements are in force requiring payment of all covered arrears owed by the owners of such property, and such owners are in compliance with such agreement.

2.	The commissioner may issue a permit for a property where the issuance of such permit is necessary to correct an outstanding violation of this code, the New York city housing maintenance code or any other applicable provisions of law or rule or where the commissioner determines that issuance of such permit is necessary to perform work to protect public health and safety.

3.	The commissioner may issue a permit for a portion of a property occupied by a tenant who is not an owner of such property or responsible for any covered arrears owed with respect to such property.

4.	The commissioner may issue a permit, for a dwelling unit within a property that is owned by a condominium or held by a shareholder of a cooperative corporation under a proprietary lease, if the owners of record for such unit do not owe, in aggregate, $25,000 or more in covered arrears to the city.

5.	The commissioner may issue a permit where a property was the subject of an in rem foreclosure judgment in favor of the city and was transferred by the city to a third party pursuant to section 11-412.1 of the administrative code.

6.	The commissioner may issue a permit where a property is the subject of a court order appointing an administrator pursuant to article 7-a of the New York state real property actions and proceedings law in a case brought by the department of housing preservation and development.

7.	The commissioner may issue a permit where a property is the subject of a loan provided by or through the department of housing preservation and development or the New York city housing development corporation for the purpose of rehabilitation that has closed within the five years preceding the application for such permit.

8.	The commissioner may issue a permit for a property where the department of housing preservation and development or the New York city housing development corporation notifies the commissioner that the permit is required for participation in a program that involves rehabilitation of such property.

§28-105.2 Classification of work permits. For the purposes of this code, work permits shall be classified as follows:

1.	New building permits: for the construction of new buildings, including as provided for in section 28-101.4.5.

2.	Alteration permits: for the alteration of buildings or structures, including new and existing sign structures and partial demolition in conjunction with such buildings or structures.

3.	Foundation and earthwork permits: for the construction or alteration of foundations, including earthwork, excavation, fill, and foundation insulation.

4.	Earthwork permits: for work solely involving earthwork, excavation, or fill operations.

5.	Full demolition permits: for the full demolition and removal of buildings or structures.

6.	Plumbing permits: for the installation or alteration of plumbing and plumbing systems, including gas piping. Such permits shall include permits for limited plumbing alterations.

7. 	Sign permits: for the erection, installation, display or alteration of signs.

8.	Service equipment permits: for the installation or alteration of service equipment, including but not limited to air conditioning and ventilating systems, boilers, elevators, escalators, moving walkways, dumbwaiters, mobile boilers and mobile oil tanks. Such permits shall include permits for limited [oil burner/boiler] oil-burning appliance alterations.

9.	Temporary construction [equipment] installation permits: for the erection, installation and use of temporary [structures] construction installations to facilitate construction and/or safety during construction, including but not limited to temporary fences, railings, catch platforms, over-the-sidewalk chutes, footbridges, sidewalk sheds, and scaffolds.

10.	Fire protection and suppression system permits: for the installation and alteration of fire protection and suppression systems, including sprinkler systems and standpipe systems. Such permits shall include permits for limited sprinkler alterations and limited standpipe alterations.

11.	Crane and derrick permits: for the use of power operated cranes and derricks during construction.

12.	Temporary structure permits and temporary use authorizations: for temporary structures and uses, see article 111.

§28-105.2.1 Submittal documents required for foundations and earthwork. Prior to the issuance of any permit for work that includes foundations and/or earthwork, submittal documents clearly illustrating support of excavation design, including but not limited to stepping, sheeting, sloping, shoring, and bracing, and any protective railings or equipment required by chapter 33 of the New York city building code shall be required.

§28-105.2.2 Submittal documents required for partial and full demolition. Prior to the issuance of any permit for work that includes full or partial demolition, submittal documents shall be required in accordance with chapter 33 of the New York city building code.

§28-105.3 Separate permits required. Separate work permits shall be required, as provided above, except that separate permits for foundations and earthwork, or for the installation or alteration of air conditioning systems, ventilation systems, and heating systems shall not be required whenever such work is included in and forms a part of the construction documents filed for the construction of a new building or the alteration of a building or structure.

§28-105.4 Work exempt from permit. Exemptions from permit requirements of this code shall not be deemed to grant authorization for any work to be done in any manner in violation of the provisions of this code, the zoning resolution or any other law or rules enforced by the department. Such exemptions shall not relieve any owner of the obligation to comply with the requirements of or file with other city agencies. Unless otherwise indicated, permits shall not be required for the following:

1.	Emergency work, as set forth in section 28-105.4.1.

2.	Minor alterations and ordinary repairs, as described in section 28-105.4.2.

3.	Certain work performed by a public utility company or public utility corporation, as set forth in section 28-105.4.3.

4.	Ordinary plumbing work, as set forth in section 28-105.4.4.

5.	Permits for the installation of certain signs, as set forth in section 28-105.4.5.

6.	Geotechnical investigations, as set forth in section 28-105.4.6.

7.	The installation, alteration or removal of alternative automatic fire extinguishing systems, including but not limited to fire extinguishing systems for commercial cooking equipment, subject to the approval of the fire department in accordance with section 105 of the New York city fire code.

8.	The installation, alteration or removal of fire alarm systems, emergency alarm systems and fire department in-building auxiliary radio communication systems, subject to the approval of the fire department in accordance with the requirements of this code. Such work shall be submitted in accordance with the rules and regulations of the fire department.

9.	Other categories of work as described in department rules, consistent with public safety.

§28-105.4.1 Emergency work. Work that would otherwise require a permit may be performed without a permit to the extent necessary to relieve an emergency condition. An application for a permit shall be submitted within 2 business days after the commencement of the emergency work and shall include written description of the emergency condition and the measures undertaken to mitigate the hazard. Emergency work may include but shall not be limited to:

1.	Erection of sidewalk sheds, fences, or other similar structures to protect the public from an unsafe condition.

2.	Stabilization of unsafe structural conditions.

3.	Repair of gas leaks.

4.	Repair or replacement of heating or hot water equipment servicing education or residential occupancies during the heating season, which is between October 1st and May 31st, as established by the New York city housing maintenance code [or education occupancies between [November 1st and May 1st].

5.	Replacement of parts required for the operation of a combined standpipe or sprinkler system.

§28-105.4.2 Minor alterations and ordinary repairs. A permit shall not be required for minor alterations and ordinary repairs.

§28-105.4.2.1 Definitions. The following words and terms shall, for the purposes of this section 28-105.4.2 and as used elsewhere in this code, have the meanings shown herein.

MINOR ALTERATIONS. Minor changes or modifications in a building or any part thereof, excluding additions thereto, that do not in any way affect health or the fire or structural safety of the building or the safe use and operation of the service equipment therein. Minor alterations shall not include any of the work described as “work not constituting minor alterations or ordinary repairs.”

ORDINARY REPAIRS. Replacements or renewals of existing work in a building, or of parts of the service equipment therein, with the same or equivalent materials or equipment parts, that are made in the ordinary course of maintenance and that do not in any way affect health or the fire or structural safety of the building or the safe use and operation of the service equipment therein. Ordinary repairs shall include the repair or replacement of any plumbing fixture, piping or faucets from any exposed stop valve to the inlet side of a trap. Ordinary repairs shall not include any of the work described as “work not constituting minor alterations or ordinary repairs.”

WORK NOT CONSTITUTING MINOR ALTERATIONS OR ORDINARY REPAIRS. Minor alterations or ordinary repairs shall not include:

1.	The removal or cutting away of any load bearing or required fire rated wall, fire door, floor, or roof construction, or any portion thereof [.];

2.	The removal, cutting, or modification of any beams or structural supports;

3.	The removal, change, or closing of any required exit;

4.	The addition, rearrangement, relocation, removal or replacement of any parts of the building affecting loading or exit requirements, or light, heat, ventilation, or elevator requirements or accessibility requirements, or any fire suppression or fire protection system;

5.	Additions to, alterations of, or rearrangement, relocation, replacement, repair or removal of any portion of a standpipe or sprinkler system, water distribution system, house sewer, private sewer, or drainage system, including leaders, or any soil, waste or vent pipe, or any gas distribution system;

6.	Any plumbing work other than the repair or replacement of plumbing fixtures, piping or faucets from the exposed stop valve to the inlet side of a trap;

7.	The alteration or repair of a sign for which a permit is required; or

8.	Any other work affecting health or the fire or structural safety of the building or the safe use and operation of the service equipment therein.

§28-105.4.3 Public utility company or public utility corporation. A permit shall not be required for:

1.	The installation or alteration of gas service piping or gas meter piping including meters, valves, regulators, and related equipment, when such work is to be performed and serviced and maintained by utility corporations subject to the jurisdiction of the New York state public service commission [;].

2.	The emergency repair of gas distribution piping when such work is performed by licensed master plumbers or by utility corporations subject to the jurisdiction of the New York state public service commission, in order to alleviate hazardous conditions, provided that a written report describing the details of such repairs shall be filed with the commissioner upon completion of the work.

§28-105.4.4 Ordinary plumbing work. The following ordinary plumbing work may be performed without a permit, provided that the licensed plumber performing such work: (i) provides a monthly report listing completed work and work in progress during the preceding month, including the block, lot and address of each job, a description of the work performed or in progress at each address, and the location in each building where the work was performed or is in progress; (ii) pays the fees for such work in accordance with this code; and (iii) submits to the department a certification that the work was performed in accordance with this code and all applicable laws and rules. Ordinary plumbing work shall include:

1.	The removal of a domestic plumbing system not connected to a fire suppression or fire protection system, or the removal of a portion of such system.

2.	The relocation of up to two plumbing fixtures within the same room to a maximum of 10 feet (3048 mm) distant from the original location, except in health care facilities.

3.	The installation, replacement or repair of a food waste grinder (food waste disposal) or secondary back flow preventer and the replacement or repair of a sump pump.

4.	The replacement of closet bends.

5.	In buildings in occupancy group R2 occupied by fewer than six families or in buildings in occupancy group R3, the replacement of a gas water heater or a gas fired boiler with a capacity of 350,000 BTU or less where the existing appliance gas cock is not moved, provided that the plumber has inspected the chimney and found it to be in good operational condition.

6.	The repair or replacement of any non-gas, non-fire suppression piping not longer than 10 feet (3048 mm) inside a building, or connected piping previously repaired or replaced under this provision.

7.	The repair or replacement of non-fire suppression branch piping after the riser shutoff valve, including the replacement of fixtures, limited to two bathrooms and one kitchen per building per monthly reporting period.

8.	The replacement of flexible gas tubing no greater than 4 feet (1219 mm) in length located downstream of the existing gas cock to an appliance, provided such gas tubing does not penetrate a wall.

§28-105.4.5 Sign permits. A sign permit shall not be required where the sign is:

[1.	Painted directly on the exterior wall surface of a building or on the surface of a fence;]

[2.] 1.	A wall sign of not more than six square feet (0.56 m2) in area;

[3.] 2.	Erected by employees of a city agency, including traffic and other similar signs;

[4.] 3.	A ground sign offering the sale or rental of the premises on which it is erected, provided the sign does not exceed 12 square feet (1.1 m2) in area, and is removed immediately upon such sale or rental;

[5.] 4.	Temporary and erected during construction work [and related thereto] as required by chapter 33 of the New York city building code or other applicable law;

[6.] 5.	Temporary for special decorative display use for holidays, public demonstrations, or the promotion of civic, welfare or charitable purposes, except that signs that utilize streets or cross streets shall be subject to the requirements of the department of transportation; or

[7.] 6.	Temporary signs offering the sale or rental of real property when erected on the premises offered for sale or rent, and is removed immediately upon such sale or rental.

§28-105.4.6 Geotechnical investigations. A permit shall not be required for excavation performed for a geotechnical investigation required by section [1802.4] 1803.4 of the New York city building code provided such excavation does not exceed 10 feet (3048 mm) in length, width, or diameter and is conducted under the supervision of a registered design professional. All excavation activity, including backfilling of excavations, shall comply with all relevant code provisions, including but not limited to sections 1803 and 3304 of the New York city building code.

§28-105.5 Application for permit. All applications for permits shall be submitted on forms furnished by the department. Applications shall include all information required by this code, other applicable law or the rules of the department. The applicant shall list any portions of the design that have been approved for deferred submittal in accordance with section 28-104.2.6. The application shall set forth an inspection program for the project. An application for a permit shall be submitted no later than 12 months after the approval of all required construction documents (other than those documents approved for deferred submittal). The department shall provide written notification to owners of adjoining property at the time such application is submitted.

§28-105.5.1 Applicant for permit. The applicant for a permit shall be the person who performs the work or who retains a subcontractor to do the work.

Exception: For permits issued for plumbing work, fire protection and suppression work, and [oil burner/boiler] oil-burning appliance work, the applicant for such permits shall be the licensed master plumber, licensed master fire suppression piping contractor, or licensed oil-burning equipment installer, respectively, who performs the work.

[§28-105.5.1] §28-105.5.2 Application for permit where a building is occupied. All applications for permits for work on a building having more than three dwelling units shall state (i) the total number of units in the building at the time the application is filed, [and] (ii) the number of units occupied at the time the application is filed, and (iii) the number of units to be occupied during the course of the work. The work permit application shall be amended prior to occupancy of any units that were not initially counted as being occupied during the course of the work.

[§28-105.5.2] §28-105.5.3 Owner statement. All applications for permits shall include a certification by the owner of the property for which the permit is sought stating the following:

1.	A statement as to whether $25,000 or more in covered arrears, that are not currently in the appeals process, are owed to the city with respect to such property;

2.	A statement as to whether the owners of the property owe, in aggregate, $25,000 or more in covered arrears to the city;

3.	For each owner of the property:

3.1.	The person’s full name and business address;

3.2.	A list of properties in the city for which the person owes covered arrears to the city and, for each such property, the amount of such covered arrears owed; and

3.3.	A list of properties in the city for which the person is an owner;

4.	If an exception to section [28-105.1.2] 28-105.1.6 of the code applies to such owner, a description of such exception.

[§28-105.5.2.1] §28-105.5.3.1 Audit. The commissioner shall each year, in consultation with the department of finance and each other appropriate city agency, audit at least 25 percent of the statements submitted under section [28-105.5.2] 28-105.5.3 of the code.

§28-105.6 Fees. Applications for permits shall be accompanied by the payment of appropriate fees as provided for in article 112.

§28-105.7 Time limitation of applications. An application for a permit shall be deemed to have been abandoned 12 months after the date of its submission, unless such application has been diligently prosecuted after rejection in whole or in part, or a permit shall have been issued except that the commissioner may, for reasonable cause, and upon payment of all reinstatement fees as provided for in this code, grant extensions of time for additional 12-month periods.

§28-105.8 Validity of permit. The issuance or granting of a permit shall not be construed to be a permit for, or an approval of, any violation of any of the provisions of this code or of any other law or rule. Permits presuming to give authority to violate or cancel the provisions of this code or other law or rule shall not be valid. The issuance of a permit based on construction documents and other data shall not prevent the commissioner from requiring the correction of errors in the construction documents and other data. The commissioner is authorized to prevent any occupancy, use or work in violation of this code, the zoning resolution or other law or rule enforced by the department.

§28-105.8.1 Duration of permit. Permits may be issued for a period of up to two years unless otherwise limited by law.

§28-105.8.2 Signature of commissioner on permit. Every permit issued by the commissioner shall have his or her signature affixed thereto; but the commissioner may authorize any subordinate to affix such signature, including by the use of electronic means.

§28-105.9 Expiration. All permits issued by the commissioner shall expire by limitation and become invalid if the permitted work or use is not commenced within 12 months from the date of issuance of the permit. Subsequent to the 12-month period following the issuance of the initial permit, all permits shall expire if the permitted work is suspended or abandoned for a continuous period of 12 months unless such permits expire earlier pursuant to applicable provisions of this code. The permit shall automatically expire upon the expiration of required insurance or, if the applicant holds a license issued by the department, upon the expiration or revocation of such license during the term of the permit or if the permit is not renewed.

Exception: All permits for work in [an area of special] a flood hazard area shall [comply with] expire in accordance with the timeframes established by section G104 of appendix G of the New York city building code.

§28-105.9.1 Reinstatement. The commissioner may at any time reinstate a work permit solely for the purpose of sign-off, including the correction of defects noted in a final inspection as provided in section 28-116.2.4 of this code or reinstate a work permit within a period of two years from the date of issuance of the original permit. Except in the case of a permit reinstated solely for the purpose of sign-off, the work shall comply with all the requirements of this code and other applicable laws and rules in effect at the time application for reinstatement is made. The applicant for reinstatement shall pay all reinstatement fees as required by article 112.

§28-105.10 Suspension or revocation of permit. The commissioner is authorized to suspend or revoke a permit issued under the provisions of this code.

§28-105.10.1 Notice of proposed revocation. The commissioner may, on written notice to the permit holder, revoke any permit for failure to comply with the provisions of this code or other applicable laws or rules; or whenever there has been any false statement or any misrepresentation as to a material fact in the application or submittal documents upon the basis of which such approval was issued; or whenever a permit has been issued in error and conditions are such that the permit should not have been issued. Such notice may be accompanied by a stop work order pursuant to section 28-207.2 of this code and shall inform the permit holder of the reasons for the proposed revocation and that the applicant has the right to present to the commissioner or his or her representative within 10 business days of delivery of the notice by hand or electronic delivery or 15 [calendar] business days of the posting of notice by mail, information as to why the permit should not be revoked.

§28-105.10.2 Immediate suspension in cases of imminent peril. The commissioner may immediately suspend any permit without prior notice to the permit holder when the commissioner has determined that an imminent peril to life or property exists. The commissioner shall forthwith notify the permit holder that the permit has been suspended and the reasons [therefore] therefor, that it is proposed to be revoked, and that the permit holder has the right to present to the commissioner or his or her representative within 10 business days of delivery of the notice by hand or electronic delivery or 15 [calendar] business days of the posting of notice by mail information as to why the permit should not be revoked.

§28-105.11 Posting of permit. The building permit or a copy thereof shall be posted in a conspicuous place at the work site, visible to the public for the duration of the work, or the use and operation of the equipment, or until the expiration of the permit. No such permit shall be posted or displayed at any location other than the location of the premises or equipment for which the permit was issued. Where the permit is exposed to the weather, it shall be laminated or encased in a plastic covering to protect it from the elements. The permit shall identify whether any dwelling unit within such building will be occupied during the work. If dwelling units within such building will be occupied during the work, the permit shall indicate the total number of dwelling units that will be occupied.

Exception: Where a project information panel is required by section 3301.9.1, of the New York city building code, the permit shall be posted in accordance with such section, and no other permits shall be posted in any location readily visible to the public, except as provided in section 3301.9.5 of the New York city building code.

§28-105.12 Conditions of permit. Permits shall be subject to the following conditions:

§28-105.12.1 Compliance with code. Permits shall be deemed to incorporate the provisions that the applicant, the owner, their agents, employees, and contractors shall carry out the permitted work in accordance with the provisions of this code and other applicable laws or rules, whether specified or not, except as variations have been legally permitted or authorized.

§28-105.12.2 Compliance with construction and submittal documents. All work shall conform to the approved construction and submittal documents, and any approved amendments thereto. Changes and revisions during the course of construction shall conform to the amendment requirements of this code.

§28-105.12.2.1 Construction documents maintained on site. One set of current “approved” or “accepted” construction documents shall be maintained at the project site no later than the commencement of the work and until the work authorized by the permit is completed and signed off by the department.

Exception: Construction documents filed in connection with the issuance of a temporary construction installation permit shall be maintained at the site until such temporary construction installation is removed.

§28-105.12.3 Adherence to lot diagram. All work shall be strictly located in accordance with the lot diagram approved in accordance with this code and no lot or plot shall be changed, increased or diminished in area from that shown on the approved lot diagram, unless and until a revised diagram showing such changes, accompanied by the necessary statement of the owner or applicant, shall have been submitted to and approved by the commissioner.

§28-105.12.4 Compliance with safety requirements. All work shall be conducted in accordance with and subject to the safety requirements of this code and other applicable laws or rules, including any order or requirement of the commissioner that the building or structure under construction or alteration be vacated, in whole or in part, during the progress of the work and until the issuance of a certificate of occupancy. Adjoining lots and properties shall be protected in accordance with this code.

§28-105.12.5 Compliance with noise control code required. All work shall be performed in compliance with the provisions of the New York city noise control code as set forth in chapter 2 of title 24 of the administrative code. Failure to comply with sections 24-222 and 24-223 of the administrative code shall be a violation of this code.

§28-105.12.6 Deferred submittals. Where permits are issued subject to deferred submittal of portions of the design as provided for in section 28-104.2.6, the deferred submittal items shall not be installed until the construction and submittal documents for such portions have been approved by the department and, where applicable, new or amended permits have been issued.

§28-105.12.7 Insurance. Where workers compensation, employee disability or liability insurance is required by law or department rule, the applicant for the work permit shall obtain and include proof of such insurance with the work permit application. The permit shall expire by operation of law if the insurance upon which the permit was conditioned lapses, expires or is cancelled, unless the permit holder files proof of alternate insurance before such event.

§28-105.12.7.1 Insurance coverage for adjacent properties. A person who obtains a permit for construction or demolition operations shall, at such person’s own expense, procure and maintain for the duration of the operations, insurance of a kind and in an amount specified by rule of the department, to insure any and all adjacent property owners and their lawful occupants fully for all risks of loss, damage to property or injury to or death of persons, arising out of or in connection with the performance of the proposed work. Such person shall submit proof of insurance to the department when applying for a permit for construction or demolition work. The department shall provide such proof of such insurance together with the permit to the owners of adjoining property thirty days prior to the commencement of the construction or demolition work, except in the event that emergency work is authorized as defined in section 28-105.4.1 of this code. If such emergency work is necessary, the permit and proof of insurance shall be provided to owners of adjoining property within a reasonable timeframe.

§28-105.12.8 Site safety plan. Where a site safety plan is required by this code or by the department, all work shall adhere to the site safety plan. Site safety plans shall require approval of the department where specified in this code or the New York city building code.

§28-105.12.9 Safety training required. No permit for construction or demolition work for which training is required by section 3321 of the New York city building code shall be issued or renewed until the applicant has certified that all workers who will be working under such permit will have the requisite training throughout the duration of such permit.

§28-105.12.10 Tenant protection plan required. Where a tenant protection plan is required by article 120, all work shall adhere to the tenant protection plan.

§28-105.12.11 Inspections. Upon issuance of a permit and at any time during such permit period, the commissioner or his or her authorized representatives, in the discharge of their duties, shall have the right to enter, in accordance with applicable law, upon any buildings, enclosures, premises, or any part thereof, or attached thereto for the purposes of an inspection of work pursuant to such permit to ensure that such work is not occurring in an unsafe or dangerous manner, and that such work is being performed in compliance with applicable code provisions. If the commissioner or his or her authorized representative is unable to gain access to such property expeditiously for the purposes of an inspection of work pursuant to such permit and there is a reason to believe that the work is being done in violation of the law, the commissioner shall issue a stop work order. Such stop work order may be rescinded in accordance with section 28-207.2.3.

ARTICLE 106
ASBESTOS

§28-106.1 Asbestos certification required. The commissioner shall not issue a permit for the demolition or alteration of a building constructed pursuant to plans submitted for approval on or before April 1, 1987, unless the applicant submits such certification relating to asbestos as may be required by the rules of the New York city department of environmental protection or the commissioner of environmental protection has issued a variance.

§28-106.1.1 Full demolition permit. The commissioner shall not issue a full demolition permit unless the owner of the building provides certification in a form and manner to be provided in the rules of the department of environmental protection that (i) the building is free of asbestos containing material, or (ii) the commissioner of environmental protection, has issued a variance from this requirement in accordance with subdivision (m) of section 24-136 of the administrative code and the rules of the department of environmental protection, subject to the requirement that demolition work will be performed only in parts of the building that are certified free of asbestos containing material. The full demolition permit shall be subject to such additional conditions as the department of buildings may require of the permittee based on the size and complexity of the demolition work.

Exception: This section 28-106.1.1 shall not apply to full demolition performed as emergency work pursuant to article 215 of chapter 2 of this title where the emergency warrants immediate commencement of the work or full demolition with asbestos in place authorized pursuant to 12 NYCRR 56-11.5.

§28-106.1.2 Alteration permit for the removal of one or more stories. The commissioner shall not issue an alteration permit for the removal of one or more stories of a building unless the owner of the building provides certification in a form and manner to be provided in the rules of the department of environmental protection that (i) the stories to be removed are free of asbestos containing material and that no abatement activities will be performed anywhere in the building concurrently with the removal work authorized by such permit or (ii) the commissioner of environmental protection has issued a variance from these requirements in accordance with subdivision (m) of section 24-136 of the administrative code and the rules of the department of environmental protection, subject to the requirement that work authorized by the alteration permit will be performed only in parts of the building that are certified free of asbestos containing material. The alteration permit shall be subject to such additional conditions as the department of buildings may require of the permittee based on the size and complexity of the work.

Exception: This section 28-106.1.2 shall not apply to removal of one or more stories performed as emergency work pursuant to article 215 of chapter 2 of this title where the emergency warrants immediate commencement of the work.

§28-106.2 Construction and maintenance of asbestos containment structures and other temporary structures or work required for asbestos abatement activities. Notwithstanding any other provision of this code, the construction and maintenance of asbestos containment structures, decontamination system enclosures and other temporary structures or work performed in the course of and only for the purpose of asbestos abatement activities shall comply with this section and the rules of the New York city department of environmental protection relating to such temporary structures and work and with article 30 of the New York state labor law and rules adopted pursuant to such article.

§28-106.2.1 Materials. The rules of the New York city department of environmental protection relating to materials used in the construction of temporary structures for asbestos abatement activities shall contain a provision requiring such structures to be non-combustible or flame resistant in compliance with reference standard NFPA 255-06 or NFPA 701-99, as such standards may be modified by local law or by the department of buildings pursuant to applicable rules.

§28-106.3 Permit exemption. Except as otherwise provided by rule, work performed in the course of and only for the purpose of an asbestos project that is required to be permitted pursuant to section 24-138 of the administrative code shall be exempt from the permit requirements of this code.

§28-106.4 Definitions. For the purposes of this article, the terms "asbestos" and "asbestos project" shall have the meanings as are ascribed in section 24-136 of the administrative code.

ARTICLE 107
ALTERATION OR DEMOLITION OF SINGLE ROOM
OCCUPANCY MULTIPLE DWELLINGS

§28-107.1 General. The commissioner shall not approve construction documents, nor issue an initial or reinstated permit in connection therewith, for the alteration or demolition of a single room occupancy multiple dwelling except as set forth in this article. Applications for post approval amendments to construction documents are subject to this article where the application proposes a change within a covered category of work as set forth in section 28-107.3.

§28-107.2 Definitions. The following words and terms shall, for the purposes of this article and elsewhere in the code, have the meanings shown herein.

CLASS A MULTIPLE DWELLING, CLASS B MULTIPLE DWELLING, FURNISHED ROOM HOUSE, ROOMING UNIT AND SINGLE ROOM OCCUPANCY. Shall have the meanings set forth in section 27-2004 of the New York city housing maintenance code.

SINGLE ROOM OCCUPANCY MULTIPLE DWELLING. A single room occupancy multiple dwelling means:

1.	A “class A multiple dwelling” used in whole or part as a “rooming house” or “furnished room house,” or for “single room occupancy” pursuant to section 248 of the New York state multiple dwelling law;

2.	A “class A multiple dwelling” containing “rooming units”; or

3.	A “class B multiple dwelling.”

Exception: The term single room occupancy multiple dwelling shall not include:

1.	College or school dormitories;

2.	Clubhouses;

3.	Luxury hotels, as such term is defined by the commissioner of housing preservation and development; or

4.	Residences whose occupancy is restricted to an institutional use such as housing intended for use by the employees of a single company or institution;

5.	City-owned multiple dwellings; or

6.	Any multiple dwelling, other than a lodging house, containing fewer than nine sleeping rooms, rooming units, single room occupancy units, or hotel units unless the total number of such units is more than fifty percent of the total number of dwelling units in such multiple dwelling; or

7.	Any multiple dwelling that:

7.1.	Is the subject of a program approved by the commissioner of housing preservation and development and related to the rehabilitation or preservation of a single room occupancy multiple dwelling or the provision of housing for persons of low or moderate income, other than a program consisting solely of real property tax abatement or tax exemption; and

7.2.	Has been exempted from the provisions of this article by the commissioner of housing preservation and development.

8.	Any building erected after May 5, 1983.

9.	Any building lawfully altered pursuant to the provisions of this article after May 5, 1983, such that the building no longer meets the definition of single room occupancy multiple dwelling.

§28-107.3 Covered categories of work. Applications for the approval of construction documents for the following categories of work are covered by this article:

1.	Demolition of a single room occupancy multiple dwelling;

2.	Alteration of a single room occupancy multiple dwelling to a class A multiple dwelling to be used in whole or in part for other than single room occupancy purposes;

3.	Alteration of a single room occupancy multiple dwelling resulting in the removal or addition of kitchen or bathroom facilities; and

4.	Such other types of alteration work to a single room occupancy multiple dwelling as shall be prescribed by rule of the commissioner of housing preservation and development, in consultation with the commissioner.

Exceptions:

1.	Work solely for the purpose of either (i) making the public areas of a multiple dwelling accessible to persons with disabilities without altering the configuration of any dwelling unit or rooming unit or (ii) making the interior or the entrance to a dwelling unit or a rooming unit accessible to persons with disabilities shall not be covered by this article.

2.	Repairs, demolition or any other work performed by a city agency or by a contractor pursuant to a contract with a city agency shall not be covered by this article.

§28-107.4 Required submittal documents. The commissioner shall not approve any construction documents, nor issue an initial or reinstated permit in connection therewith, for a single room occupancy multiple dwelling for the covered categories of work unless the applicant provides:

1.	A sworn affidavit by or on behalf of all the owners, as the term owner is defined in section 27-2004 of the New York city housing maintenance code, of such multiple dwelling that there will be no harassment of the lawful occupants of such multiple dwelling by or on behalf of such owners during the construction period;

2.	A tenant protection plan as provided for in this code; and

3.	One of the following documents from the commissioner of housing preservation and development:

3.1.	A current certification that there has been no harassment of the lawful occupants of such multiple dwelling within the 36 month period prior to submission of an application for such certification to the department of housing preservation and development, provided, however, that such certification shall except any portion of such 36 month period during which title was vested in the city; or

3.2.	A waiver of such certification.

§28-107.5 Filing process. Applications for a certification of no harassment shall be made pursuant to section 27-2093 of the New York city housing maintenance code.

§28-107.6 Time period for acceptance or rejection. The time period in which the commissioner is required to approve or reject an application for construction document approval or resubmission thereof pursuant to this code shall commence from the date that the commissioner receives either the certification or waiver pursuant to this article.

§28-107.7 Denial of certification. Where the commissioner of housing preservation and development denies the certification required by this article, the commissioner shall reject the application for construction document approval.

§28-107.8 Request for stop-work or rescission. The commissioner shall be empowered to issue a stop-work notice or order with respect to an alteration or demolition permit and/or to rescind approval of construction documents at the request of the commissioner of housing preservation and development pursuant to section 27-2093 of the New York city housing maintenance code.

§28-107.9 Effect of denial or rescission. Where the commissioner rejects or rescinds the approval of construction documents pursuant to this article, no further application for the covered categories of work shall be considered by the commissioner for a period of 36 months following the date of the denial of the certification of no harassment by the commissioner of housing preservation and development or the date of the rescission of such certification of no harassment by such commissioner.

ARTICLE 108
PAVEMENT PLAN

§28-108.1 General. The commissioner shall not issue a permit for the erection of a new building, use of an open lot or for alterations that will require the issuance of a new or amended certificate of occupancy without a statement that no certificate of occupancy shall be issued unless the sidewalk, curb and/or roadway in front of or abutting such building, including but not limited to the intersection quadrants for corner properties, shall have been paved, [or] repaired or installed by the owner, at his or her own cost, in the manner, of the materials, and in accordance with the [standard specifications] New York city building code, the New York city zoning resolution, and the standards prescribed by the New York city department of transportation pursuant to sections 19-113 and 19-115 of the administrative code.

Exceptions:

1.	Application for the erection of an accessory building appurtenant to an existing one- or two-family dwelling.

2.	Where the commissioner determines, in consultation with the commissioner of transportation, that a sidewalk is not required, provided that such determination shall not affect the obligations of the owner under subdivision a of section 19-152 of the administrative code, nor relieve the owner of any such obligations, nor impair or diminish the rights of the city or its agencies to enforce such obligations.

3.	Where [the extent of the change in use or occupancy, or] the cost of the alteration, including enlargements, does not exceed a total cost of 30 percent of the building value [threshold established pursuant to rule of the commissioner].

§28-108.2 Pavement plan required. Construction documents shall include a pavement plan processed and approved under guidelines established by the department. The pavement plan shall include documentation sufficient to show compliance with the New York city building code, the New York city zoning resolution, and the standards [and specifications of] prescribed by the New York city department of transportation pursuant to sections 19-113 and 19-115 of the administrative code.

Exception: No pavement plan shall be required with respect to an alteration application for a building where the applicant certifies that there is a sidewalk in existence in front of or abutting such building, including but not limited to the intersection quadrants for corner properties, complying with the specifications of the New York city department of transportation, and that the nature of such alteration work will neither remove such existing sidewalk nor cause damage to such existing sidewalk such that the damage could not be corrected as minor repairs prior to issuance of the certificate of occupancy.

§28-108.3 Improvement of streets. The commissioner shall insure that streets are suitably improved in accordance with the standards [and specifications of] prescribed by the department of transportation as required by subdivision two of section thirty-six of the New York state general city law and shall otherwise carry out the provisions of such subdivision.

ARTICLE 109
FIRE PROTECTION PLAN

§28-109.1 Fire protection plan required for covered buildings. New building and alteration applications for covered buildings as set forth in section 28-109.2 shall include a fire protection plan prepared by or under the supervision of a registered design professional who shall professionally certify such plan. Such plan shall be submitted for review and approval by  the fire department for compliance with this code prior to issuance of a certificate of occupancy, a temporary certificate of occupancy or a letter of completion, as applicable. The fire protection plan shall be submitted in accordance with the rules and regulations of the fire department.

Exception: No fire protection plan shall be required for an alteration that meets all three of the following requirements:

1.	The alteration does not involve a change of use or occupancy;

2.	The alteration does not exceed one million dollars; and

3.	The alteration does not create an inconsistency with a previously approved fire protection plan.

§28-109.2 Covered buildings. Covered buildings include:

1.	High-rise buildings as described in section 403 of the New York city building code.

2.	Occupancy groups B, E, F, H, M, or S occupying two or more stories with over 20,000 gross square feet (1858 m2) of floor area per floor, or occupying two or more stories in a building with a total floor area exceeding 50,000 gross square feet (4645 m2).

3.	Any building containing an assembly occupancy having an occupant load of 300 or more persons.

4.	Occupancy group I or R-1 occupying two or more stories and containing sleeping accommodations for 30 or more persons.

5.	Occupancy group R-2 occupancies containing 30 or more dwelling units in a building where over 10,000 gross square feet (929 m2) of floor area is occupied by occupancy group A, E, M, or I.

6.	Covered mall buildings and open mall buildings designed pursuant to section 402 of the New York city building code.

§28-109.3 Scope. The plan shall include the following information, where applicable:

1.	A description of the building including: address; block and lot numbers; number of stories; height in feet; occupancy group; construction classification; occupancy load and department of buildings application number;

2.	All floors, exits, doors, corridors, and partitions serving as fire barriers, fire partitions, fire walls; locations and ratings of required enclosures and fire areas; stairs with pressurization; roof access; exit discharges; and locations of any required frontage space; and

3.	In narrative form, a description of safety systems and features, including:

3.1.	Communications systems.

3.2.	Alarm systems.

3.3.	Smoke and carbon monoxide detection equipment.

3.4.	Location of fire command station.

3.5.	Elevator recall.

3.6.	Emergency lighting and power.

3.7.	Standpipes.

3.8.	Sprinklers.

3.9.	Emergency and standby power systems.

3.10.	Mechanical ventilation and air conditioning.

3.11.	Smoke control systems and equipment.

3.12.	Furnishings types and materials.

3.13.	Places of assembly.

3.14.	Fire department access.

3.15.	Photoluminescent pathway markings.

3.16.	Other safety related systems, required and voluntary, to be installed.

ARTICLE 110
SITE SAFETY PLAN

[§28-110.1 Site safety plan. Where a site safety plan is required by chapter 33 of the New York city building code, such plan shall include the following:]

[1.	Location of all construction fences around work site;]

[2.	Location of all gates in construction fences;]

[3.	Location of standard guardrails around excavations, when required;]

[4.	Horizontal and vertical netting program, including details of the initial installation, schedule of horizontal jumps and vertical installations, and designated crane and derrick lifting areas where horizontal netting is omitted. The program shall include as an attachment any department approval obtained regarding required safety netting during construction or demolition operations; the revised site safety plan shall be approved;]

[5.	Location of all sidewalk sheds, including appropriate department application numbers and department of transportation permit numbers and expiration dates;]

[6.	Location of all temporary walkways, including appropriate department application numbers and department of transportation permit numbers and expiration dates;]

[7.	Location of foot bridges and motor vehicle ramps, including appropriate department application numbers and department of transportation permit numbers and expiration dates;]

[8.	Protection of side of excavation, when required, including appropriate department application numbers and department of transportation permit numbers and expiration dates;]

[9.	Location of all street and sidewalk closing(s), including appropriate department application numbers and department of transportation permit numbers and expiration dates;]

[10.	Approximate location of material and personnel hoist(s) and loading areas, including appropriate department application numbers and department of transportation permit numbers and expiration dates;]

[11.	Approximate location of all crane and derrick loading areas;]

[12.	Location of all surrounding buildings, indicating occupancy, height and type of any required roof protection;]

[13.	Location of all standpipe system and siamese hose connections;]

[14.	Location of all temporary elevators for fire department use when building is above 75 feet (22 860 mm) in height;]

[15.	Location of all exterior contractors’ sheds;]

[16.	All required safety netting and scaffolding;]

[17.	Widths of all sidewalks and roadways; all traffic information; all exits from the work site;]

[18.	A copy of the proposed site safety manager or site safety coordinator’s certificate, as applicable, including the certificate for any alternate site safety manager or site safety coordinator;]

[19.	Such features requiring special sequencing in order to maintain safe conditions with a written description of those sequences;]

[20.	A statement that prior to performing any work on the project all workers have successfully completed the training required by section 3310.10.2 of the New York city building code; and]

[21.	A statement that all workers employed on the construction site will receive a site-specific orientation program required by section 3310.10.1 of the New York city building code.]

§28-110.1 Site safety plan. Where a site safety plan is required by chapter 33 of the New York city building code, such plan shall include the following, as applicable:

1.	Site conditions and surrounding property, utilities, and infrastructure;

2.	Streets, sidewalks, pedestrian protection, fences, gates, and pedestrian and traffic control;

3.	Adjoining property protection;

4.	Unenclosed perimeter protection;

5.	Excavations;

6.	Fire protection;

7.	Temporary construction installations;

8.	Means of egress from the jobsite, both permanent and temporary;

9.	Location of security guard and watchperson stations;

10.	Means of securing controlled access zones;

11.	Debris and material storage areas/loading zones;

12.	Material handling plan for crane operations if crane operations come into conflict with hoist operations;

13.	In occupied buildings, means and methods employed to protect all tenants from the adverse effect of construction operations;

14.	For work related to the alteration, maintenance, or repair of a façade, means and methods of getting material and debris to and from the work area.  Means to separate debris and materials from occupants of the building must be indicated;

15.	For work related to the alteration, maintenance, or repair of a façade, means and methods, including ladders, used by workers to access scaffolds, sidewalk sheds, and the work area;

16.	Features requiring special sequencing in order to maintain safe conditions, with a written description of those sequences;

17.	A note indicating that prior to performing any work on the project all workers must successfully complete the training required by section 3321 of the New York city building code; and

18.	A note indicating that all workers employed on the construction site must receive a site-specific orientation program as required by section 3301.11 of the New York city building code.

§28-110.2 Phased site safety plans. Multiple layouts of the site safety features enumerated in section 28-110.1 may be submitted at any time during construction operations to show phased site safety designs consistent with the phase of anticipated work.

ARTICLE 111
TEMPORARY STRUCTURES AND USES

§28-111.1 General. The erection of certain temporary structures and temporary uses may be authorized as set forth in sections 28-111.1.1 and 28-111.1.2.

§28-111.1.1 Permits for the erection and use of temporary structures. The commissioner is authorized to issue a permit for the erection of temporary structures including but not limited to tents, grandstands, platforms, reviewing stands, outdoor bandstands, stages and similar miscellaneous structures and equipment, and for the temporary use of such structures. Such permits shall be limited as to time of service or use, but in no event shall be permitted for more than 90 days. The commissioner may grant extensions for demonstrated cause.

Exception: No permit shall be required for:

1.	The erection and use of temporary tents of less than 400 gross square feet (37 m2) for not more than 30 days.

2.	The erection and use of temporary platforms, reviewing stands, outdoor bandstands and similar miscellaneous structures that cover an area less than 120 square feet (11.16 m2), including connecting areas or spaces with a common means of egress or entrance, for not more than 30 days.

§28-111.1.2 Letters authorizing temporary uses. The commissioner is authorized to issue a letter authorizing the temporary use of outdoor or indoor spaces provided the space shall be occupied in a manner that will not endanger public safety, health, or welfare. Such letters authorizing the temporary use shall be limited as to time of service or use, but shall not be permitted for more than 90 days. The commissioner may grant extensions for demonstrated cause.

§28-111.2 Conformance. Temporary structures and uses shall conform to the structural strength, fire safety, means of egress, accessibility, light, ventilation and sanitary requirements of this code as necessary to ensure the public health, safety and general welfare.

§28-111.3 Termination of approval. The commissioner is authorized to terminate such permit or letter of authorization [and] and to order the temporary structure or use to be discontinued.

§28-111.4 Application processing. Application for such structures and uses shall be submitted to the department no later than 15 business days prior to the construction of the temporary structure or the commencement of the temporary use.

§28-111.5 Fees. Applications for such permits shall be accompanied by the applicable fees in accordance with article 112. Fees for subsequent requests for renewals shall be paid upon approval of such requests.

§28-111.6 Place of assembly. Notwithstanding any inconsistent provision of this article, the use of a temporary structure or the temporary use of space as a place of assembly shall require a temporary place of assembly certificate of operation issued pursuant to section 28-117.2.

ARTICLE 112
FEES

§28-112.1 Payment of fees. A permit, inspection, or other service or privilege as regulated in this code shall not be valid until the fees prescribed herein or in rules have been paid, nor shall a renewal of a permit or other service or privilege or an amendment to a permit be released until the fee has been paid. In addition, an approval required to be reissued due to a change in product name, company name and/or address, contact information or principals, shall not be reissued until a reissuance fee, if any, has been paid. The department shall adopt such rules and shall prescribe such forms as may be necessary to carry out the provisions of this article.

Exceptions:

1.	A permit, inspection or other service or privilege as regulated in this code shall not be subject to this provision if the current deed holder of the building or property affected is a corporation or association organized and operated exclusively for religious, charitable or educational purposes, or for one or more such purposes, no part of the earnings of which inures to the benefit of any private shareholder or individual, and provided that the property affected is to be used exclusively by such corporation or association for one or more of such purposes.

2.	A permit, inspection or other service or privilege as regulated in this code shall not be subject to this provision if the work proposed is emergency work performed by a city agency or by a contractor pursuant to a contract with a city agency.

§28-112.2 Schedule of permit fees. Permits for new buildings, structures, mechanical, and plumbing systems or alterations requiring a permit shall be accompanied by a fee for each permit in accordance with the fee schedule of Table 28-112.2. Fifty percent of the total fee for the work permit, but not less than one hundred dollars, or the total fee for the work permit where such fee is less than one hundred dollars, shall be paid and shall accompany the first application for the approval of construction documents; and the whole or remainder of the total fee shall be paid before the work permit may be issued. The commissioner may require reasonable substantiation of any statement or other form that may be required by the department.

| TABLE 28-112.2 |
| --- |
| PERMIT TYPE | FILING FEE | RENEWAL FEE | COMMENTS |
| New Buildings |  |  |  |
| New building work permit: One-, two- or three-family dwelling, where no existing building elements are to be retained in place as part of the new building. | $0.06 for each square foot, or fraction thereof, of the total floor area of the new building, but not less than $100 for each structure. The rates and fees set forth above shall be subject to increases as provided by department rules. | [$100] $130 per work type | For the purposes of this fee schedule item, “building elements” means any portion of an existing building or structure, including but not limited to party walls, foundations, footings, piles and slabs on grade. |
| Subsequent applications related to initial new building work permit application, filed prior to the first temporary certificate of occupancy (TCO), or the final certificate of occupancy if no TCO is issued. | [$100] $130 | [$100] $130 per work type |  |
| New building work permit: One-, two- or three-family dwelling, where any existing building elements are to be retained in place as part of the new building, pursuant to section 28-101.4.5. | Minimum Filing Fee - $100 Minimum filing fee for the first five thousand dollars or fraction thereof, of the cost of alteration; plus $2.60 for each one thousand dollars, or fraction thereof, of cost of alterations in excess of five thousand dollars. The rates and fees set forth above shall be subject to increases as provided by department rules. | [$100] $130 per work type | For the purposes of this fee schedule item, “building elements” means any portion of an existing building or structure, including but not limited to party walls, foundations, footings, piles and slabs on grade. |
| New building work permit: Garage for not more than three cars when accessory to and filed with plans for one-, two- or three-family dwelling to which it is accessory on the same lot. | [$100] $130 | [$100] $130 per work type |  |
| New building work permit: All other new buildings fewer than 7 stories and less than 100,000 square feet, where no existing building elements are to be retained in place as part of the new building. | $0.26 for each square foot, or fraction thereof, of the total floor area of the new building, but not less than $280 for each structure. The rates and fees set forth above shall be subject to increases as provided by department rules. | [$100] $130 per work type | For the purposes of this fee schedule item, “building elements” means any portion of an existing building or structure, including but not limited to party walls, foundations, footings, piles and slabs on grade. |
| Subsequent applications related to initial new building work permit application, filed prior to the first temporary certificate of occupancy (TCO), or the final certificate of occupancy if no TCO is issued. | [$100] $130 | [$100] $130 per work type |  |
| New building work permit: All other new buildings fewer than 7 stories and less than 100,000 square feet, where any existing building elements are to be retained in place as part of the new building, pursuant to section 28-101.4.5. | Minimum Filing Fee - $280 Minimum filing fee for the first three thousand dollars, or fraction thereof, of the cost of alteration; plus $10.30 for each one thousand dollars, or fraction thereof, of the alteration cost in excess of three thousand dollars. The rates and fees set forth above shall be subject to increases as provided by department rules. | [$100] $130 per work type | For the purposes of this fee schedule item, “building elements” means any portion of an existing building or structure, including but not limited to party walls, foundations, footings, piles and slabs on grade. |
| New building work permit: All other new buildings 7 stories or more or 100,000 square feet or more, classified in occupancy group R-2, where at least 50 percent of the occupancy units are affordable to households whose income is less than 165 percent of the area median income for New York city, as determined by the United States department of housing and urban development or successor agency, which are financed entirely or in part by a grant or loan from the city of New York or the New York city housing and development corporation, and where no existing building elements are to be retained in place as part of the new building. | $0.26 for each square foot, or fraction thereof, of the total floor area of the new building, but not less than $100 for each structure, The rates and fees set forth above shall be subject to increases as provided by department rules. | [$100] $130 per work type | For the purposes of this fee schedule item, "building elements" means any portion of an existing building or structure, including but not limited to party walls, foundations, footings, piles and slabs on grade. |
| Subsequent applications related to initial new building work permit application, filed prior to the first temporary certificate of occupancy (TCO), or the final certificate of occupancy if no TCO is issued | [$100] $130 | [$100] $130 per work type |  |
| New building work permit: All other new buildings 7 stories or more 100,000 square feet or more, classified in occupancy group R-2, where at least 50 percent of the occupancy units are affordable to households whose income is less than 165 percent of the area median income for New York city, as determined by the United States department of housing and urban development or successor agency, which are financed entirely or in part by a grant or loan from the city of New York or the New York city housing and development corporation, and where any existing building elements are to be retained in place as part of the new building, pursuant to section 28-101.4.5. | Minimum Filing Fee - $280 Minimum filing fee for the first $3,000 or fraction thereof, of the cost of alteration; plus $10.30 for each one thousand dollars, or fraction thereof, of the alteration cost in excess of [thee] three thousand dollars. The rates and fees set forth above shall be subject to increases as provided by department rules. | [$100] $130 per work type | For the purposes of this fee schedule item, "building elements" means any portion of an existing building or structure, including but not limited to party walls, foundations, footings, piles and slabs on grade. |
| New building work permit: All other new buildings 7 stories or more, or 100,000 square feet or more, where no existing building elements are to be retained in place as part of the new building. | $0.45 for each square foot, or fraction thereof, of the total floor area of the new building, but not less than $290 for each structure. The rates and fees set forth above shall be subject to increases as provided by department rules. | [$100] $130 per work type | For the purposes of this fee schedule item, "building elements" means any portion of an existing building or structure, including but not limited to party walls, foundations, footings, piles and slabs on grade. |
| Subsequent applications related to initial new building work permit application, filed prior to the first temporary certificate of occupancy (TCO), or the final certificate of occupancy if no TCO is issued | [$100] $130 | [$100] $130 per work type |  |
| New building work permit: All other new buildings 7 stories or more, or 100,000 square feet or more, where any existing building elements are to be retained in place as part of the new building, pursuant to section 28-101.4.5. | Minimum Filing Fee - $290 Minimum filing fee for the first three thousand, or fraction thereof, of the cost of alteration; plus $17.75 for each one thousand dollars, or fraction thereof, of the alteration cost in excess of three thousand dollars. The rates and fees set forth above shall be subject to increases as provided by department rules. | [$100] $130 per work type | For the purposes of this fee schedule item, "building elements" means any portion of an existing building or structure, including but not limited to party walls, foundations, footings, piles and slabs on grade. |
| Alterations |  |  |  |
| Alteration work permit: One-, two- or three-family dwelling |  | [$100] $130 per work type |  |
| Alteration Type 1 | Minimum Filing Fee - $170 |  |  |
| Alteration Type 2 | Minimum Filing Fee - $130 |  |  |
| Alteration Type 3 | Minimum Filing Fee - $130 |  |  |
| Limited Alteration Application | Minimum Filing Fee - $130 |  |  |
|  | Minimum filing fee for the first five thousand dollars, or fraction thereof, of the cost of alteration; plus $2.60 for each one thousand dollars, or fraction thereof, of cost of alterations in excess of five thousand dollars. The rates and fees set forth above shall be subject to increases as provided by department rules. |  |  |
| Alteration work permit: Alterations in all other buildings and structures fewer than 7 stories and less than 100,000 square feet, including but not limited to aerial towers and masts, tank structures, fire escapes, etc., which are unoccupied and not easily valued by area. |  | [$100] $130 per work type | Such alterations work shall include: Applications related to new building work permit application, filed after the first temporary certificate of occupancy (TCO), or the final certificate of occupancy if no TCO is issued. Installation or alteration of elevators, escalators, amusement devices and other devices regulated under this code, except those filed under a new building application. |
| Alteration Type 1 | Minimum Filing Fee - $280 |  |  |
| Alteration Type 2 | Minimum Filing Fee - $225 |  |  |
| Alteration Type 3 | Minimum Filing Fee - $195 |  |  |
| Limited Alteration Application | Minimum Filing Fee - $195 |  |  |
|  | Minimum filing fee for the first three thousand dollars, or fraction thereof, of the cost of alteration; plus $10.30 for each one thousand dollars, or fraction thereof, of the alteration cost in excess of three thousand dollars. The rates and fees set forth above shall be subject to increases as provided by department rules. |  |  |
| Alteration work permit: Alterations in all other buildings and structures 7 stories or more, or 100,000 square feet or more, classified in occupancy group R-2, which are unoccupied and not easily valued by area, where at least 50 percent of the occupancy units are affordable to households whose income is less than 165 percent of the area median income for New York city, as determined by the United States department of housing and urban development or successor agency, and which are financed entirely or in part by a grant or loan from the city of New York or the New York city housing and development corporation. |  | [$100] $130 per work type | Such alterations work shall include: Applications related to new building work permit application, filed after the first temporary certificate of occupancy (TCO), or the final certificate of occupancy if no TCO is issued. Installation or alteration of elevators, escalators, amusement devices and other devices regulated under this code, except those filed under a new building application. |
| Alteration Type 1 | Minimum Filing Fee - $280 |  |  |
| Alteration Type 2 | Minimum Filing Fee - $280 |  |  |
| Alteration Type 3 | Minimum Filing Fee - $195 |  |  |
| Limited Alteration Application | Minimum Filing Fee - $195 |  |  |
|  | Minimum filing fee for the first three thousand dollars, or fraction thereof, of the cost of alteration; plus $10.30 for each one thousand dollars, or fraction thereof, of the alteration cost in excess of three thousand dollars. The rates and fees set forth above shall be subject to increases as provided by department rules. |  |  |
| Alteration work permit: Alterations in all other buildings and structures 7 stories or more, or 100,000 square feet or more, including but not limited to aerial towers and masts, tank structures, fire escapes, etc., which are unoccupied and not easily valued by area. |  | [$100] $130 per work type | Such alterations work shall include: Applications related to new building work permit application, filed after the first temporary certificate of occupancy (TCO), or the final certificate of occupancy if no TCO is issued. Installation or alteration of elevators, escalators, amusement devices regulated under this code, except those filed under a new building application. |
| Alteration Type 1 | Minimum Filing Fee - $290 |  |  |
| Subsequent or related filings | Minimum Filing Fee - $290 |  |  |
|  | Minimum filing fee for the first three thousand dollars, or fraction thereof, of the cost of alteration; plus $17.75 for each one thousand dollars, or fraction thereof, of the alteration cost in excess of three thousand dollars. The rates and fees set forth above shall be subject to increases as provided by department rules. |  |  |
| Alteration work permit: Alterations in all other buildings and structures 7 stories or more, or 100,000 square feet or more, including but not limited to aerial towers and masts, tank structures, fire escapes, etc., which are unoccupied and not easily valued by area. |  | [$100] $130 per work type | Such alterations work shall include: Applications related to new building work permit application, filed after the first temporary certificate of occupancy (TCO), or the final certificate of occupancy if no TCO is issued. Installation or alteration of elevators, escalators, amusement devices and other devices regulated under this code, except those filed under a new building application. |
| Alteration Type 2 | Minimum Filing Fee - $225 |  |  |
| Alteration Type 3 | Minimum Filing Fee - $195 |  |  |
| Limited Alteration Application | Minimum Filing Fee - $195 |  |  |
|  | Minimum filing fee for the first three thousand dollars, or fraction thereof, of the cost of alteration; plus $10.30 for each one thousand dollars, or fraction thereof, of the alteration cost in excess of three thousand dollars. The rates and fees set forth above shall be subject to increases as provided by department rules. |  |  |
| Permit to install or alter service equipment except plumbing and fire suppression piping service equipment. | [Filing] Filing fee calculated as for respective building alteration. | [$100] $130 |  |
| Permit to install, alter or replace oil-burning equipment [:] , gas or electric heating or any other energy source equipment. | $130 (Per Type, Device, or Equipment) | $130 (Per Type, Device or Equipment) |  |
| Where the storage tank exceeds two hundred seventy-five gallon capacity; or where the storage tank is less than two hundred seventy-five gallons and is to be buried, or is to be installed in a multiple dwelling or a place of assembly or in a building along the line of a subway, or is to deliver fuel oil to a burner installed above the lowest floor of a building with a primary Business Group B. occupancy. | [$130] | [$100] |  |
| In all other conditions.] | [$65] | [$100] |  |
| Other |  |  |  |
| Permit for foundation, earthwork or open space without roof, whether enclosed or unenclosed, on sites such as parking lots, gasoline or oil-selling stations, storage yards, sales or exhibition or show spaces used for generally similar purposes. | $10 for each two thousand square feet of area or fraction thereof, but not less than $130. | [$100] $130 |  |
| Permit for golf driving range. | $7.50 for each twenty thousand square feet of area or fraction thereof, but not less than $130. | [$100] $130 |  |
| Accessory building to golf driving range, not to exceed one hundred forty-four square feet. | $130 | [$100] $130 |  |
| Permit for demolition and removal. | Multiply building frontage in feet or fraction thereof × number of stories of the building × $2.60, but not less than $260. For corner lot, use the longer building frontage. | [$100] $130 |  |
| Curb cut, private dwelling | $3 for each linear foot including splay; minimum $130 |  |  |
| Curb cut, other | $6 for each linear foot including splay; minimum $130 |  |  |
| Amendments |  |  |  |
| Filing of [post-approval] amendments to [existing] active applications and active permits. | [The greater of $100 or the fees for the additional scope or cost of work as calculated pursuant to this Table 28-112.2.] As provided by rule. |  |  |
| Signs |  |  |  |
| Permit to erect, install or alter sign: Ground sign, wall sign, or any sign mounted to the wall or any other structure. | Filing fee calculated as for respective building alteration, plus $5 for each one hundred square feet of surface area or fraction thereof, but not less than $35. | [$100] $130 | Each face of any sign, when fronting on different streets, shall be treated as a separate sign. |
| Permit to erect, install or alter sign: Roof sign having a tight, closed or solid surface. | Filing fee calculated as for respective building alteration; plus $15 for each one hundred square feet of surface area, or fraction thereof, but not less than $70. | [$100] $130 | Each face of any sign, when fronting on different streets, shall be treated as a separate sign. |
| Permit to erect, install or alter sign: Roof sign without a tight, closed or solid surface, extending to a height of not more than thirty-one feet above roof level. | Filing fee calculated as for respective building alteration; plus $15 for each one hundred square feet of surface area, or fraction thereof, but not less than $100. | [$100] $130 | Each face of any sign, when fronting on different streets, shall be treated as a separate sign. |
| Permit to erect, install or alter sign: Roof sign without a tight, closed or solid surface, extending to a height over thirty-one feet above roof level. | Filing fee calculated as for respective building alteration; plus $25 for each one hundred square feet of area, or fraction thereof, but not less than $135. | [$100] $130 | Each face of any sign, when fronting on different streets, shall be treated as a separate sign. |
| Permit to erect, install or alter sign: Illuminated sign on storefront or wall or any other structure projecting beyond street line having thirty square feet or less on one side. | Filing fee calculated as for respective building alteration. | $100] $130 | Illuminated sign is subject to annual use fee: $45. |
| Permit to erect, install or alter sign: Illuminated sign on storefront or wall or any other structure projecting beyond street line having more than thirty square feet but no more than fifty square feet on one side. | Filing fee calculated as for respective building alteration. | $100] $130 | Illuminated sign is subject to annual use fee: $70. |
| Permit to erect, install or alter sign: Illuminated sign on storefront or wall or any other structure projecting beyond street line and having more than fifty square feet on one side. | Filing fee calculated as for respective building alteration. | $100] $130 | Illuminated sign is subject to annual use fee: $.075 for each square foot or part thereof annually, but not less than [$100] $130. |
| Maintenance permit for outdoor signs. | As provided by department rules. |  |  |
| Temporary Structures and Construction Installations |  |  |  |
| Sidewalk shed | $160 for the first twenty-five feet or fraction thereof in the length of the shed; plus $10 for each additional twenty-five feet or fraction thereof. | [$100] $130 |  |
| Scaffold | $160 | [$100] $130 |  |
| Construction Fence | $160 | [$100] $130 |  |
| Permit for temporary shed, railing, footbridge, catch platform, building sidewalk shanty, over-the-sidewalk chute. | $160 for each permit. | [$100] $130 |  |
| Permit for temporary structure other than those [temporary structures] listed above, including but not limited to tents, grandstands, stages. | For the initial 30 days of permit duration: $130 for the first one thousand square feet or fraction thereof; plus $0.10 for each square foot or fraction thereof in excess of one thousand square feet; [$100] $130 for each additional 30 day period of permit duration. | [$100] $130 for each additional 30 days. |  |
| Reinstatement of Applications/Permits |  |  |  |
| Application [/permit] reinstatement fees: |  |  |  |
| [ Prior to first permit.] | [Full fee at the rate in effect on the date of reinstatement.] |  |  |
| Following first permit issuance but prior to commencing work. | Full fee at the rate in effect on the date of reinstatement. |  |  |
| Following first permit, with work partially complete. | Full fee at the rate in effect on the date of reinstatement. |  |  |
| Reinstatement of an abandoned application. | Based upon the full fee at the rate in effect on the date of reinstatement, the percentage of the fee equal to the percentage of work remaining, as determined by the department inspector. |  |  |
| Permit reinstatement fees: |  |  |  |
| Following first permit issuance but prior to commencing work and more than 1 year since filing. | Full fee at the rate in effect on the date of reinstatement. |  |  |
| Following first permit, but more than 1 year with work partially complete. | Based upon the full fee at the rate in effect on the date of reinstatement, the percentage of the fee equal to the percentage of work remaining as determined by the department inspector, plus the renewal fee. |  |  |
| Following first permit, more than 1 year after work suspended or abandoned. | Based upon the full fee at the rate in effect on the date of reinstatement, the percentage of the fee equal to the percentage of work remaining as determined by the department inspector, plus the renewal fee. |  |  |
| Work permit within a period of 2 years from the date of issuance, solely for the purpose of sign-off, including correction of defects noted in a final inspection as provided in section 28-116.2.4. | Based upon the full fee at the rate in effect on the date of reinstatement, the percentage of the fee equal to the percentage of work remaining as determined by the department inspector, plus the renewal fee. |  |  |
| More than 2 years with code/zone change during this period (e.g., job application was originally filed under 1968 Code and job must be filed in 2014 Code). | Re-file job application and pay full filing fee. |  |  |

§28-112.3 Building permit valuations. An estimate of the cost of construction shall be provided at the time of application for construction document approval or, where no construction documents are required, at the time of application for a permit. Such costs shall include the total value of work proposed, including but not limited to materials, equipment and labor, with reasonable allowances for profit and overhead. If, in the opinion of the department, the cost is underestimated, the application shall be denied, unless the applicant can show detailed estimates to meet the approval of the department. A final [affidavit] statement with the total actual cost of construction, as built or installed, shall be submitted prior to [sign off] sign-off. The initial, amended and final building permit valuation shall be set by the department.

§28-112.4 Work commencing before permit issuance. Any person who commences any work before obtaining the necessary permits shall be subject to a penalty as specified in this code that shall be in addition to the required permit fees.

Exception: Emergency work performed pursuant to section 28-105.4.1.

§28-112.5 Related fees. The payment of the fee for the construction, alteration, removal or demolition for work done in connection or concurrently with the work authorized by a building permit shall not relieve the applicant or holder of the permit from the payment of other fees that are prescribed by law.

§28-112.6 Refunds and rebates. Upon application to the comptroller of the city of New York, and upon verification of claim by the commissioner, refunds or rebates of partial or full fees shall be provided as set forth in sections 28-112.6.1 through 28-112.6.3.

§28-112.6.1 Withdrawal of work permit applications. In the event that an owner withdraws an application, the owner may obtain a refund of all or a portion of the fee paid as follows:

1.	If an application for construction document approval is withdrawn prior to the commencement of examination of the application all but forty dollars of the deposit fee paid shall be refunded.

2.	If an application for construction document approval is withdrawn during the progress of examination of the application, the comptroller shall retain a percentage of the deposit fee paid, which the department shall certify is the equivalent percentage of the examination completed, but not less than one hundred dollars. The remainder of the deposit fee shall be refunded to the owner.

3.	If an application for construction document approval is withdrawn after examination of construction documents and/or construction document approval and before issuance of permit, there shall be refunded by the comptroller 50 percent of the total computed fee for the permit, except that not less than one hundred dollars shall be retained by the comptroller.

§28-112.6.2 Withdrawal of cranes and derricks applications. If the applicant withdraws his or her application for a certificate of approval for a power-operated crane, derrick or cableway, such applicant may obtain a refund of a portion of the fees as follows:

1.	If the application is withdrawn prior to the commencement of examination by the department, the entire fee shall be refunded except one hundred dollars.

2.	If the application is withdrawn after the examination has commenced, the comptroller shall retain a percentage of the fee paid, which the department shall certify is the equivalent percentage of the examination performed, but not less than one hundred dollars. The remainder of the fee shall be refunded to the applicant.

3.	If the application is withdrawn after the department has performed its examination, whether or not the application has been approved no part of the fee shall be returned to the applicant.

§28-112.6.3 Incentive rebates. With respect to the rebates under this section 28-112.6, the commissioner may, at his or her discretion, issue a rebate of application fees as follows and as established by rule.

§28-112.6.3.1 Renewable energy rebates. Owners who demonstrate the production on a zoning lot of five percent or more of the annual energy consumption on the zoning lot through renewable energy sources may receive a fee rebate as established by rule.

§28-112.6.3.2 Rebate for energy use reduction. Owners who demonstrate a reduction in energy use from that allowed at the time of permit by the New York state energy conservation construction code as a result of the permitted work may receive a fee rebate as established by rule.

§28-112.6.3.3 Rebate for water conservation systems. Owners who demonstrate conservation of water taken from the city supply by providing evidence of achieving the water-recycling discount authorized by the New York city water board may receive a fee rebate as established by rule.

§28-112.6.3.4 Rebate for redevelopment, remediation and reuse of contaminated properties known as brownfields. Owners who demonstrate that their site was contaminated and has been certified as remediated by the United States environmental protection agency or the New York state department of environmental conservation, or has received a notice of satisfaction from the New York city department of environmental protection, may receive a fee rebate as established by rule.

§28-112.6.3.5 Rebate for recycling construction and demolition waste. Owners who demonstrate the recycling of construction and demolition waste may receive a fee rebate as established by rule.

§28-112.6.3.6 Rebate for bicycle storage facilities. Except for R-3 occupancy, owners who demonstrate that they have provided secured indoor bicycling facilities accessible to all building occupants may be rebated their fees as set out in rule. Such facilities shall be identified on approved plans and shall be noted on the certificate of occupancy with a statement that the bicycling accommodations dedicated to such facilities were provided in accordance with this section.

§28-112.6.3.7 Rebate for LEED or other environmental design certification. Owners who demonstrate certification of their project, which was signed off following the effective date of this code, by the United States Green Building Council based upon the Council’s Leadership in Energy and Environmental Design (LEED) rating system or as otherwise provided by rule, may be rebated their fees as set out in rule.

§28-112.6.3.8 Other rebates. The commissioner is authorized to promulgate rules to rebate fees following sign-off based upon the installation of energy-conserving systems.

§28-112.7 Inspection and report filing fees. Aside from the fees covered under permit fees above, the following inspection and report filing fees shall be paid according to requirements of this code and as promulgated in rules.

§28-112.7.1 Fees for the testing, approval, inspection and use of power-operated cranes, derricks and cableways. The owner of any crane or derrick shall renew the certificate of operation each year. See Table 28-112.7.1.

| TABLE 28-112.7.1 |
| --- |
| EQUIPMENT TYPE | FILING FEE | RENEWAL FEE | COMMENTS |
| Prototype approval of one configuration of a mobile crane. One configuration shall be comprised of the crane with a main boom, one fixed jib and one set of counterweights. | $2500 when testing has been monitored and certified by a competent individual or group, other than the manufacturer, acceptable to the commissioner; $4000 when, in lieu of monitoring and certification of tests, the commissioner shall require design calculations for such items as the commissioner deems necessary to supplement the tests. |  | Additional configurations shall be subject to the same fee as the original configuration. |
| Amendment to a configuration. | One-half the original configuration fee. |  |  |
| Prototype approval of a mobile crane with a hydraulic boom. | $4000 |  |  |
| Certificate of approval for mobile crane with a boom less than two hundred feet in length; fee also includes initial certificate of operation. | $500 | $250 annually | The boom length as herein specified shall include the jibs and any other extensions to the boom. |
| Certificate of approval for mobile crane with a boom two hundred feet or more in length, but less than three hundred feet in length; fee also includes initial certificate of operation. | $1000 | $250 annually | The boom length as herein specified shall include the jibs and any other extensions to the boom. |
| Certificate of approval for mobile crane with a boom three hundred feet or more in length but less than four hundred feet in length; fee also includes initial certificate of operation. | $2000 | $400 annually | The boom length as herein specified shall include the jibs and any other extensions to the boom. |
| Certificate of approval for mobile crane with a boom four hundred feet or more in length; fee also includes initial certificate of operation. | $3000 | $400 annually | The boom length as herein specified shall include the jibs and any other extensions to the boom. |
| Certificate of approval for master climber and tower cranes and derricks, regardless of length; fee also includes initial certificate of operation. | $3000 | $400 annually |  |
| Certificate of approval for all other cranes; fee also includes initial certificate of operation. | $1000 | $250 annually |  |
| Certificate of approval required for a mobile crane with a boom not exceeding fifty feet in length with a maximum rated capacity not exceeding three tons; fee also includes initial certificate of operation. | $300 | $200 annually | The boom length as herein specified shall include the jibs and any other extensions to the boom. |
| Certificate of operation-sign hanger, fifty-one feet to one-hundred thirty five feet with capacity of 3 tons or less. | $250 | $200 annually |  |
| New certificate of approval, when the boom or extension thereof is replaced or altered. | The fee shall be the full fee required for testing a new crane or derrick with a boom or extension of the same size and design as the replacement boom or extension thereof. |  |  |
| Review only of engineering calculations for mobile crane with a boom exceeding 250 feet to be erected by a licensed master or special rigger, for which a certificate of on-site inspection is not required under this code or rules of the department. | [$100] $130 |  |  |
| On-site inspection of up to three models of mobile cranes with boom, including jibs and other extensions to the boom two hundred fifty feet or more in length, or derrick. | $250 during business hours; $750 outside business hours; upon written request of the applicant. | [$100] $130 |  |
| All other on-site inspections of cranes. | $150 | [$100] $130 |  |
| Amendment to an application for certificate of on-site inspection. | [$100] $130 |  |  |
| Application for waiver of on-site inspection of mobile crane or derrick. | [$100] $130 |  |  |
| Notification of Outrigger Beam Installation or dismantling | As provided by department rules |  |  |
| Notification of use, installation or dismantle of all cranes | As provided by department rules |  |  |

§28-112.7.2 Report filing fees. See Table 28-112.7.2.

| TABLE 28-112.7.2 |
| --- |
| REPORT TYPE | FILING FEE | RENEWAL FEE | COMMENTS |
| Filing fee for report of critical examination of exterior walls and appurtenances thereof. | As provided by department rules. |  |  |
| Filing fee for inspection report of potentially compromised buildings or structures. | As provided by department rules. |  |  |
| Filing fee for report of condition assessment of retaining walls. | As provided by department rules. |  |  |
| Filing fee for periodic boiler inspection report. | [$30 for each boiler.] As provided by department rules. |  |  |
| Filing fee for report of periodic inspections and category tests of elevator and other devices [(Category 1)]. | [$30 for each device.] As provided by department rules. |  |  |

§28-112.7.3 Other inspection fees. See Table 28-112.7.3.

| TABLE 28-112.7.3 |
| --- |
| INSPECTION TYPE | FILING FEE | RENEWAL FEE | COMMENTS |
| Each inspection of a temporary amusement device | $100 |  |  |
| Marquee inspection. | $15 annually for each one hundred square feet or fraction thereof. |  | --- |
| Place of assembly inspection, including following a violation. | $100 each inspection, each place of assembly. |  | --- |
| Search inspection of a building with a frontage of twenty-five feet or less and a depth of one hundred feet or less. | $20 for each floor for the first three floors; $10 for each additional floor; $100 minimum total. |  | A basement or a cellar shall count as a floor. Where both a basement and a cellar exist, the cellar shall not count as a floor in computing fee. |
| Additional fee for building with frontage exceeding twenty-five feet. | Increase above fee by 40% for each floor for each additional twenty-five feet or fraction thereof. |  |  |
| Additional fee for building with depth exceeding one hundred feet. | Increase above fee by 25% for each floor for each additional twenty-five feet or fraction thereof. |  |  |

§28-112.7.4 Equipment inspection fees. See Table 28-112.7.4.

| TABLE 28-112.7.4 |
| --- |
| EQUIPMENT INSPECTION TYPE | FILING FEE | RENEWAL FEE | COMMENTS |
| High-pressure boiler periodic inspection. | $65 for each inspection, for each boiler. As provided by department rules, $100 for each inspection, for each device. |  |  |
| Reinspection fee following a violation. |  |  |  |
| Equipment inspection fee: Each elevator or other device regulated by this code. |  |  |  |

§28-112.8 Special fees. Special fees are charged for services that are not covered in the fees for permits, equipment, reports and inspection. The department shall be entitled to charge the following special fees in accordance with Table 28-112.8:

| TABLE 28-112.8 |
| --- |
| SERVICE TYPE | FILING FEE | [RENEWALS] RENEWAL FEE | COMMENTS |
| Accelerated plan review | As provided by department rules |  |  |
| Accelerated inspection | As provided by department rules |  |  |
| Certificate of occupancy request | As provided by department rules |  |  |
| Accelerated certificate of occupancy request | As provided by department rules |  |  |
| Application for temporary certificate of occupancy Application for interim certificate of occupancy | [$100] $130 $130 | [$100] $130 |  |
| Application to amend a temporary certificate of occupancy | $130 |  |  |
| Reinspection made necessary by a failure to correct a condition or respond to a request to correct that results in issuance of a violation or other order | As provided by department rules |  |  |
| Temporary place of assembly certificate of operation | [$100] $130 | [$100] $130 |  |
| Temporary use letter (does not include fees for any associated temporary structure) | For the initial 30 days of duration $100. [$100] $130 for each additional 30 day period of permit duration. | [$100] $130 for each additional 30 days |  |
| Temporary use letter for place of assembly | $250 |  | Application shall be submitted at least ten work days prior to the event; late fees shall be imposed at $100 for each day following required submission date that the application is received by the department. |
| Subpoena | As provided by applicable state or federal law |  |  |
| Place of assembly certificate of operation | $200 |  | [$100] $130 amendment |
| Ordinary plumbing work | [$100] $130 for each report |  |  |
| Limited plumbing alteration | Filing fee as calculated for respective building alteration |  |  |
| Limited sprinkler and/or standpipe alteration | Filing fee as calculated for respective building alteration |  |  |
| Limited [oil burner/boiler] oil-burning appliance alteration | Filing fee as calculated for respective building alteration |  |  |
| Approval or acceptance of materials, assemblies and equipment |  |  |  |
| Application for approval of materials | $600 |  |  |
| Application for amendment of prior approval of materials | $500 |  |  |
| Application for change of identification (change of ownership, corporate name or name of product) of prior approval | $350 |  |  |
| Application for approval of materials evaluated by an approved testing agency | $200 |  |  |
| Other fees |  |  |  |
| Certificate of pending violation: Multiple and private dwellings | As provided by department rules |  |  |
| Certificate of pending violation: All other buildings | As provided by department rules |  |  |
| Certified copy of license | As provided by department rules |  |  |
| Records Management of applications for new buildings and alterations and associated documentation for certificates of occupancy, temporary certificates of occupancy, “compliance reports” and/or letters of completion, as required by rule of the commissioner | As provided by department rules |  |  |
| Preparing only or preparing and certifying a copy of a record or document filed in the department | As provided by department rules |  |  |
| Notification of, the installation or removal of an adjustable suspended scaffold | $35 |  |  |
| Issuance of a core certificate of completion, which indicates completion of the building structure, the elevator systems, stairs, and all fire safety systems | [$100] $130 |  |  |
| Issuance of letter of no objection to or classification of a specified occupancy of a premises, as follows: |  |  |  |
| 1, 2, or 3 family homes | $25 |  |  |
| All other premises | [$100] $130 |  |  |
| Fees for after-hours work variances. |  |  |  |
| The initial application fee for an after-hours variance | [$100] $130 |  |  |
| The renewal application fee for an after-hours variance | [$100] $130 |  |  |
| For each day for which such variance is granted or renewed | $80 |  |  |
| Application for approved agency approval | As provided by department rules |  |  |
| Application for special inspector authorization | As provided by department rules |  |  |
| Failure to keep a scheduled plan examination appointment | As provided by department rules |  |  |
| Failure to keep a scheduled inspection appointment | As provided by department rules |  |  |

§28-112.9 Lien on premises for unpaid fee or other charge. Any unpaid fee or charge for an inspection, reinspection, examination or service performed by the department or other unpaid amount owed to the department, and all permits issued by the department, pursuant to law shall constitute a lien upon the land and buildings upon or in respect to which such inspection, reinspection, examination or service was performed or permit issued, as hereinafter provided.

§28-112.9.1 Filing of fees. The department shall maintain a record of all unpaid fees and other charges. Such records shall be kept on a building by building basis and shall be accessible to the public during business hours. An entry of an unpaid amount on the records of the department shall constitute notice to all parties.

§28-112.9.2 Lien. All such unpaid amounts shall constitute a lien upon the land and building upon, or in respect to which, such inspection, reinspection, examination or service was performed or permit issued when the amount thereof shall have been definitely computed as a statement of account by the department and the department shall file such statement with the department of finance for entry in the records of such department against the premises. Such lien shall have a priority over all other liens and encumbrances except for the lien of taxes and assessments. However, no lien created pursuant to this section 28-112.9 shall be enforced against a subsequent purchaser in good faith or mortgagee in good faith unless the requirements of section 28-112.9.1 are satisfied.

§28-112.9.3 Notice. A notice, stating the amount due and the nature of the charge, shall be mailed by the department of finance [,] to the last known address of the person whose name appears on the records in the office of the department of finance as being the owner or agent or as the person designated by the owner to receive tax bills or, where no name appears, to the premises [,] addressed to either the owner or the agent.

§28-112.9.4 Interest. If such charge is not paid within 30 days from the date of entry, it shall be the duty of the department of finance to receive interest thereon at the rate of 15 percent per annum, to be calculated to the date of payment from the date of entry.

§28-112.9.5 Tax lien. Such charge and the interest thereon shall continue to be, until paid, a lien on the premises. Such lien shall be deemed a tax lien within the meaning of sections 11-319 and 11-401 of the administrative code and may be sold, enforced or foreclosed in the manner provided in chapter three or four of title eleven of such code or may be satisfied in accordance with the provisions of section thirteen hundred fifty-four of the New York state real property actions and proceedings law.

§28-112.9.6 Reference. The notice mailed by the department of finance pursuant to this section 28-112.9 shall have stamped or printed thereon a reference to this section 28-112.9.

§28-112.9.7 Validity not subject to challenge in enforcement proceeding. In any proceedings to enforce or discharge a lien created pursuant to this section 28-112.9, the validity of the lien shall not be subject to challenge based on:

- The lawfulness of the inspection, reinspection, examination, service or permit; or

- The propriety and accuracy of the fee for which a lien is claimed, except as provided in this section 28-112.9.

§28-112.9.8 Standing to challenge. No such challenge may be made except by (i) the owner of the property, or (ii) a mortgagee or lien or whose mortgage or lien would, but for the provisions of this section 28-112.9, have priority over the department’s lien.

§28-112.10 Waiver of application, permit and inspection fees for certain work arising out of the storm that occurred on October 29 and 30, 2012. The commissioner shall waive the fees that would otherwise be required to be paid by this code, the electrical code or the rules of the department for applications, permits and inspections for certain work arising out of the storm that occurred on October 29 and 30, 2012 as provided in subsections 28-112.10.1 and 28-112.10.2.

§28-112.10.1 Eligible buildings. For the purposes of this article, eligible buildings that, following the storm and pursuant to an inspection program established by the department under an emergency order of the Mayor, are designated by the department after inspection through a notation on the department’s records and/or by the posting of a red placard warning on the building or premises as seriously damaged and unsafe to enter or occupy or completely demolished and/or washed away. With respect to eligible buildings, fees associated with applications, permits and inspections shall be waived for alteration work, demolition work, construction of new buildings and associated work, including but not limited to associated electrical and plumbing work. The commissioner may request the applicant to submit additional information relating to the damage. Waiver of such fees pursuant to this section shall be applicable for jobs where the initial application for construction document approval or, if no construction documents are required, application for permit is submitted on or after October 30, 2012 and on or before October 31, 2014.

§28-112.10.2 Storm related damage to electrical and plumbing systems. In buildings other than eligible buildings, fees shall be waived only for applications, permits and inspections for work related to plumbing and electrical systems damaged by such storm. Applicants must submit certification by a licensed master electrician or a licensed master plumber or fire suppression piping contractor that the proposed work is related to such storm damage. The commissioner may request the applicant to submit additional information relating to the damage. Waiver of such fees pursuant to this section shall be applicable for jobs where the initial application for construction document approval or, if no construction documents are required, application for permit is submitted on or after October 30, 2012 and on or before December 31, 2013.

§28-112.11 Waiver of application, permit and inspection fees for work funded under the “Build It Back” program. The city has implemented a disaster recovery program known as the Build It Back program that uses federal Community Development Block Grant Disaster Recovery funds to aid in the recovery of residential property damaged or destroyed in the severe storm known as Sandy that occurred on October 29 and 30, 2012. To assist in such recovery, the commissioner shall waive fees, which would otherwise be required to be paid to the department by this code, the electrical code or the rules of the department, in connection with applications, permits and inspections for work that is officially approved and funded under the Build It Back program. The waiver provided for in this section shall apply only to work performed on property that is classified as residential and to fees payable on or after July 1, 2014. With respect to work on a mixed use building, fees payable on or after such date may only be waived for work on the residential units of such building and portions of such building that serve the residential units.

§28-112.12 Reduction in fees or penalties for sponsoring site safety training. The commissioner shall establish by rule a program for reducing the amount of any fee to be imposed upon a person or any civil penalty to be imposed upon a person for a violation, other than an immediately hazardous violation, where one or more of the following conditions is satisfied:

1.	Such person demonstrates, in a form and manner established by the commissioner, that such person has paid, either directly or indirectly, for the costs of one or more workers to obtain the training needed to comply with section 3321 of the New York city building code or has otherwise arranged for such workers to receive such training at no cost to such workers, provided that this shall not include any worker trained pursuant to an agreement that such person was required to enter into pursuant to section 28-204.1.1 or any worker trained under a program developed pursuant to section 22-509 of the administrative code.

2.	The fee or penalty to be imposed upon such person relates to a building site for which the owner of such site, or a person acting on such owner’s behalf, demonstrates, in a form and manner established by the commissioner, that such owner or such person acting on such owner’s behalf has paid, either directly or indirectly, for the costs of one or more workers to obtain the training needed to comply with section 3321 of the New York city building code or has otherwise arranged for such workers to receive such training at no cost to such workers, provided that this shall not include any worker trained pursuant to an agreement such person was required to enter into pursuant to section 28-204.1.1 or any worker trained under a program developed pursuant to section 22-509 of the administrative code.

ARTICLE 113
MATERIALS

§28-113.1 General. Materials shall be used, tested and approved for use in accordance with the specific provisions of this code and department rules, except that the commissioner shall have the power to limit or prohibit the use of any material to protect public safety. Materials shall be identified or described on construction documents and other related documents.

§28-113.2 Use of materials. Except as set forth in sections 28-113.2.1 through 113.2.6 materials specifically prescribed by this code or department rules may be used as prescribed without the prior approval of the commissioner.

§28-113.2.1 Approved material. Whenever this code or the rules of the department requires the use of an approved material, such material shall not be used without the prior approval of the commissioner for such use and may be used only to the extent set forth in such approval.

§28-113.2.2 Alternative materials. Except as otherwise specifically limited by this code, the provisions of this code are not intended to prevent the installation of any material or to prohibit any alternative engineered design or method of construction not specifically prescribed by this code, provided that the use of such alternative material has been previously approved by the commissioner and may be used only to the extent set forth in such approval. The use of an alternative material, design, method of construction or equipment shall be approved where the commissioner finds that the proposed design is satisfactory and complies with the intent of the provisions of this code, and that the material, method or work offered is, for the purpose intended, at least the equivalent of that prescribed in this code in quality, strength, effectiveness, fire resistance, durability and safety.

§28-113.2.3 Listed or labeled. Whenever this code or the rules of the department requires that material used be listed or labeled to a standard, material that is so listed or labeled may be used in accordance with such list or label without the prior approval of the commissioner. However, the commissioner reserves the right to require that information be submitted with regard to the testing and evaluation of any material so listed or labeled including but not limited to inspection certificates, test or evaluation reports, analysis, computations or other information used to determine that the material so listed or labeled complies with the applicable standard.

§28-113.2.4 Material not listed or labeled. Whenever this code or the rules of the department requires that material be listed or labeled to a standard and material proposed to be used is not so listed or labeled, the use of such material shall be subject to prior approval by the commissioner and such material shall be used only to the extent set forth in such approval.

§28-113.2.5 Reuse. The use of used material that meets the requirements of this code for new material is permitted unless otherwise provided in this code. Used equipment and devices shall not be reused without the prior approval of the commissioner and may be used only to the extent set forth in such approval.

§28-113.2.6 Previously issued approvals. Materials that were previously approved by the board of standards and appeals or by the department before July 1, 2008 may continue to be used to the extent that such approval is not inconsistent with the requirements or standards of this code, unless specifically amended or repealed by the commissioner.

§28-113.3 Approval procedure. Approval of materials pursuant to section 28-113.2 shall be in accordance with procedures set forth in this code and the rules of the department. The cost offsets, reports and investigations required under these provisions shall be paid by the applicant.

§28-113.3.1 Performance. When required by the commissioner, specific information consisting of test reports conducted by an approved testing agency in accordance with standards referenced in the construction codes or other such information as necessary, shall be provided for the commissioner to determine whether the material will perform for the use intended.

§28-113.3.2 Research and investigation. When required by the commissioner, sufficient technical data shall be submitted to the commissioner to substantiate the proposed use of any material. If it is determined that the evidence submitted is satisfactory proof of performance for the use intended, the commissioner shall approve the use of the material subject to the requirements of this code.

§28-113.3.3 Retesting of materials. All materials tested and accepted for use shall be subject to periodic retesting as determined by the commissioner; and any material that upon retesting is found not to comply with the code requirements or the requirements set forth in the approval of such material shall cease to be acceptable for the use intended. During the period for such retesting, the commissioner may require the use of such material to be restricted or discontinued if necessary to secure safety.

§28-113.3.4 New materials. New materials not provided for in this code, and any material of questioned suitability proposed for use in the construction of a building or structure, shall be subjected to the tests prescribed in this code or in the rules of the department to determine character, quality and limitations of use.

§28-113.3.5 Research reports. Supporting data, where necessary to assist in the approval of materials not specifically provided for in this code, shall consist of valid research reports from approved sources or other equivalent approved supporting documentation.

§28-113.3.6 Conflicting test results. Whenever there is evidence of conflicting results in the test of any material, the commissioner shall determine the acceptability of the material and/or the acceptable rating for such material.

§28-113.3.7 Amendment and repeal. The commissioner shall have the power to amend or repeal the approval of any material, including materials previously approved by the board of standards and appeals.

§28-113.3.8 Maintenance of records of approved material. For any material that has been approved, a record of such approval, including the conditions and limitations of the approval, shall be posted on the department’s website or shall be made available for public inspection at appropriate times.

§28-113.4 Labeling. Materials required to be labeled shall be labeled in accordance with the procedures set forth in this code or the recognized referenced standards.

§28-113.4.1 Testing. An approved agency shall test a representative sample of the material being labeled to the relevant standard or standards. The approved agency shall maintain a record of the tests performed. The record shall provide sufficient detail to verify compliance with the test standard.

§28-113.4.2 Inspection and identification. The approved agency shall at regular intervals perform surveillance inspections, which shall be in-plant if necessary, of the material that is to be labeled. The inspection shall verify that the labeled material is representative of the material tested.

§28-113.4.3 Label information. The label shall contain the manufacturer’s or distributor’s identification, model number, serial number or definitive information describing the material’s performance characteristics and the approved agency’s identification.

§28-113.4.4 Shipment and delivery certification of materials listed, labeled or approved. In the case of the shipment or delivery of material listed or labeled to a standard, such material shall be appropriately labeled or accompanied by the inspection certificate of an approved agency that the material is the same as that which was tested and evaluated by such agency. In the case of the shipment or delivery of material previously approved by the commissioner, the material shall be identified by a tag or certificate indicating that the material is the same that was approved for its intended use by the commissioner or, if applicable, previously approved by the board of standards and appeals, and containing the applicable approval number or calendar number under which the material received such approval.

§28-113.5 Volatile organic compounds emissions in carpet and carpet cushion. On and after July 1, 2013 carpet and carpet cushion as defined in section 17-1401 of the administrative code shall comply with the limits on volatile organic compound emissions set forth in chapter 14 of title 17 of such code.

ARTICLE 114
APPROVED AGENCIES

§28-114.1 General. Approved agencies shall satisfy the provisions of this article and the rules of the department as to qualifications and operations. The commissioner may revoke or suspend the commissioner’s approval of or otherwise sanction an approved agency for cause.

§28-114.1.1 Independent. An approved agency shall perform its authorized duties objectively and competently. The agency shall disclose possible conflicts of interest so that objectivity can be confirmed.

§28-114.1.2 Testing equipment. An approved agency shall have adequate testing equipment to perform required tests. The equipment shall be periodically calibrated.

§28-114.1.3 Personnel. An approved agency shall employ experienced personnel qualified to conduct, supervise and evaluate the tests or inspections that it undertakes. Special inspections may be performed only by employees of such agency who are special inspectors qualified pursuant to department rules to perform or witness the particular test or inspection. The commissioner may require proof of the qualifications of employees.

§28-114.1.4 Background. The commissioner may require an approved agency to submit to an investigation of its background and of the background of its principals as a condition of approval.

§28-114.1.5 Insurance. An approved agency shall maintain liability insurance as required by department rules.

§28-114.2 Written evaluation by approved agency. An agency’s evaluation of material or report of an inspection shall be in writing after satisfactory completion of the required inspection or test.

§28-114.3 Records. The approved agency shall maintain records of inspection and test reports for at least six years or for such period as the commissioner shall determine and shall make such records available to the department upon request.

§28-114.4 Re-authorization of approved agencies. An approved agency shall have its approval re-authorized in accordance with rules of the department.

§28-114.5 Disqualification. The commissioner may disqualify an approved agency or inspector from performing inspections pursuant to this code for cause. The approved agency or inspector shall be given prior notice of the proposed disqualification and the opportunity to contest such action. A list of approved agencies and inspectors who have been disqualified from performing inspections shall be maintained and made available to the public on the department’s website.

ARTICLE 115
SPECIAL INSPECTION AGENCIES AND SPECIAL INSPECTORS

§28-115.1 General. Special inspection agencies are approved agencies and shall be subject to the provisions of article 114 of this chapter. Special inspection agencies and special inspectors shall satisfy the provisions of this article and the rules of the department as to qualifications in order to perform special inspections required by chapter 17 of the New York city building code or elsewhere in this code or department rules.

§28-115.2 Disqualification. The commissioner may disqualify a special inspection agency or a special inspector from performing special inspections pursuant to this code for cause. The special inspection agency or special inspector shall be given prior notice of the proposed disqualification and the opportunity to contest such action. A list of special inspection agencies and special inspectors who have been disqualified from performing special inspection shall be maintained and made available to the public upon request.

§28-115.3 Records. A special inspector shall maintain records of special inspections on a building by building basis for at least 6 years or for such period as the commissioner shall determine and shall make such records available to the department upon request.

ARTICLE 116
INSPECTIONS AND SIGN-OFF OF COMPLETED
WORK

§28-116.1 General. Construction or work for which a permit is required shall be subject to inspection in accordance with this code and such construction or work shall remain accessible and exposed for inspection purposes until the required inspection is completed. A satisfactory inspection by the department or the acceptance by the department of a satisfactory report of an inspection by an approved agency shall not be construed to be an approval by the department of a violation of the provisions of this code or of any other provision of law. It shall be the duty of the permit holder to cause the work to remain accessible and exposed for inspection purposes. The permit holder shall be liable for any expense entailed in the removal or replacement of any material required to allow inspection. The inspector shall supply a report of the results of each inspection.

§28-116.1.1 Defective work and discrepancies with approved construction documents. An approved agency conducting inspections shall report defective work and discrepancies with the approved construction documents to the contractor and, when applicable, to the superintendent of construction, for correction. The approved agency shall report uncorrected discrepancies and defective work to the registered design professional of record and the owner in writing.

§28-116.1.2 Hazardous conditions. The approved agency shall report all conditions noted as hazardous to life, safety or health that are not immediately corrected to the immediate attention of the commissioner.

§28-116.2 Types of inspections. The inspections set forth in sections 28-116.2.1 through 28-116.2.4 are required or authorized by this code.

§28-116.2.1 Preliminary inspection. Before approving construction documents, the commissioner is authorized to examine or cause to be examined structures or premises for which an application has been filed. The department shall conduct preliminary inspections of no less than 20 percent of buildings containing six or more units where (i) an application for construction documents is submitted to the department and (ii) the applicant has indicated that the building that is the subject of such application is unoccupied, in order to verify the occupancy status of such sites.

§28-116.2.1.1 Preliminary inspection reporting. By January 1, 2021 and no later than January 1 annually thereafter, the department of buildings shall submit to the mayor and the speaker of the council a report describing the findings of preliminary inspections performed pursuant to section 28-116.2.1 in the preceding year. Such report shall include, but not be limited to: (i) the total number of applications found to have falsely indicated that a building was unoccupied; and (ii) for each application found to have falsely indicated that a building was unoccupied, the location of the associated building and date of filing for such application.

§28-116.2.2 Compliance inspections. In addition to the inspections specified in this code, the commissioner is authorized to make or require other inspections of any construction work to ascertain compliance with the provisions of this code and other laws that are enforced by the department.

§28-116.2.3 Special inspections, progress inspections and other inspections required during the progress of work. After the issuance of a work permit, special inspections, progress inspections and other inspections required by this code to be made during the progress of the work shall be made at such times or at such stages of the work and in such manner as shall be provided by this code or as otherwise required by the commissioner. The permit application shall set forth an inspection program for the work. Such inspections may be made by approved agencies or by the department as provided in this code or in the rules of the department. Special inspections shall be performed only by individuals who are special inspectors. The commissioner may accept inspection and test reports from approved agencies and the work may, unless otherwise specifically provided by code provisions or directed by the commissioner, proceed without any verifying inspection or test by the department. The names and business addresses of special inspectors and approved agencies shall be set forth in the work permit application. All inspection reports shall be in writing and signed by the person or entity performing the inspection. A record of all inspections shall be kept by the person performing the inspection. The commissioner may require inspection reports to be filed with the department. Records of inspections made by approved agencies and special inspectors shall be maintained by such persons for a period of six years after sign-off of the work or for such other period of time as the commissioner may require and shall be made available to the department upon request.

§28-116.2.3.1 Special and progress inspection of fabricated items. Where fabrication of regulated products is performed on the premises of a fabricator’s shop, special [or] and progress [inspection] inspections of the fabricated items [is] are required as provided in this code. The approved agency shall verify that the fabricator maintains detailed fabrication and quality control procedures that provide a basis for inspection control of the workmanship and the fabricator’s ability to conform to approved construction documents and referenced standards. The approved agency shall review the procedures for completeness and adequacy relative to the code requirements for the fabricator’s scope of work.

Exceptions:

1.	Work that is subject to progress inspections and performed on the fabricator’s premises shall not be subject to progress inspections where the fabricator is approved by the commissioner in accordance with section 28-116.6.

2.	Work that is subject to special inspections and performed on the fabricator’s premises shall be inspected by the special inspection agency in accordance with Section 1704.2.2.3 of the New York city building code where the fabricator is approved by the commissioner in accordance with section 28-116.6.

§28-116.2.3.2 Special inspection of raising and moving of a building. Where the lowest above-grade floor or the lowest subgrade floor of a building is to be raised, lifted, elevated or moved, special inspection of such work is required. The permit holder shall notify the department in writing at least 48 hours before the commencement of such work.

§28-116.2.4 Final inspection. There shall be a final inspection of all permitted work. Final inspections shall comply with sections 28-116.2.4.1 through 28-116.2.4.3.

§28-116.2.4.1 Final inspection prior to certificate of occupancy. In all cases where the permitted work requires the issuance of a new or amended certificate of occupancy, the final inspection shall be performed by the department in the presence of the permit holder, the registered design professional of record or the superintendent of construction. Such inspection shall be performed after all work authorized by the building permit is completed and before the issuance of the certificate of occupancy. All failures to comply with the provisions of this code or approved construction documents shall be noted and the owner promptly notified thereof in writing. All defects noted in such inspection shall be corrected. Reports of such final inspections shall be maintained by the department. The final inspection report shall confirm that defects noted have been corrected, that the work is in substantial compliance with the approved construction documents and with this code and with other applicable laws and rules and that all required inspections were performed.

Exception: For amended certificates of occupancy subject to section 28-118.16.2, the term construction documents, as used in section 28-116.2.4.1, shall consist of an accurate and complete final lot survey made by a land surveyor, and floor and roof plans showing, at a minimum, compliance with exit requirements in accordance with this code.

§28-116.2.4.2 Final inspection prior to letter of completion. In all cases where the permitted work does not require the issuance of a certificate of occupancy, the final inspection shall be performed by [the department or at the option of the owner by] an approved agency on behalf of the owner or by the department as directed by the commissioner. [Whenever the department performs a final inspection, the department shall charge a fee for such inspection.] The applicant shall take all reasonable and necessary steps to ensure that the final inspection is performed within one year after the expiration of the last permit. The inspection shall be performed after all work authorized by the building permit is completed. The approved agency performing the inspection shall report defective work and discrepancies with the approved construction documents to the contractor and, when applicable, to the superintendent of construction, for correction. The approved agency shall report uncorrected discrepancies and defective work to the registered design professional of record and the owner in writing. The approved agency shall report all conditions noted or observed as hazardous to life, safety or health that are not immediately corrected to the immediate attention of the commissioner. All defects noted in such inspection shall be corrected. The final inspection report shall confirm that defects noted have been corrected, that the work is in substantial compliance with the approved construction documents and with this code and other applicable laws and rules and that all required inspections were performed. Final inspection reports shall be filed with and maintained by the department. Records of final inspections made by approved agencies shall be maintained by such persons for a period of six years after sign-off or for such other period as the commissioner shall require and shall be made available to the department upon request.

Exception: Final inspection shall be performed by the department for permitted work in R-2 occupancies if the building is listed on the department of housing preservation and development’s website pursuant to paragraph 6 of subdivision m of section 27-2115 of the administrative code. The department shall charge a fee for such inspection.

§28-116.2.4.3 Final inspection of gas piping systems. The final inspection of gas piping systems shall be performed by the department in the presence of the permit holder, the registered design professional of record or the superintendent of construction. Such inspection shall be performed after all work authorized by the building permit is completed. All failures to comply with the provisions of this code or approved construction documents shall be noted and the owner promptly notified thereof in writing. All defects noted in such inspection shall be corrected. Reports of such final inspections shall be maintained by the department. The final inspection report shall confirm that defects noted have been corrected, that the work is in substantial compliance with the approved construction documents and with this code and with other applicable laws and rules and that all required inspections were performed.

§28-116.3 Inspection requests. It shall be the duty of the permit holder to notify the department or the person or entity designated to perform the inspection when work requiring inspection is ready to be inspected. It shall be the duty of the permit holder to provide access to and means for inspection of such work for any inspections that are required by this code.

§28-116.3.1 Additional notifications for special inspections. The permit holder shall also notify the relevant special inspection agency in writing at least 72 hours prior to the commencement of any work requiring special inspection.

§28-116.4 Sign-off of completed work. Upon submission of a satisfactory report of final inspection and all required submittal documents, the department shall document the sign-off of the project and issue a letter of completion, or, if applicable, a certificate of occupancy for the work. The owner shall take all necessary steps required by the department for the issuance of such letter of completion or certificate of occupancy within 1 year following the expiration of the last permit.

§28-116.4.1 Issuance of certificate of compliance. The following types of service equipment shall not be operated until the department issues a certificate of compliance after submission of a satisfactory report of inspection and testing of such equipment in accordance with this code and all required submittal documents:

1.	Air-conditioning, ventilation and exhaust systems.

2.	Elevators, escalators, moving walkways and dumbwaiters.

3.	Fuel burning and fuel-oil storage equipment.

4.	Refrigeration systems.

5.	Heating systems.

6.	Boilers.

Exception: A certificate of compliance shall not be required in connection with work specifically exempted from permit requirements in accordance with this code or department rules.

§28-116.5 Payment of outstanding penalties. The department may refuse to issue a letter of completion or certificate of occupancy pending payment of all outstanding fines or civil penalties imposed for violations of this code, the 1968 building code or other laws enforced by the department at the same building.

§28-116.6 Fabricator approval. Approval of fabricators by the department shall be based upon review of the fabricator’s written procedural and quality control manuals and periodic auditing of fabrication practices by an approved agency.

§28-116.6.1 Certificate of intent to fabricate. For all work where approval is sought based upon section 28-116.6, the approved fabricator shall submit a certificate of intent to fabricate such work to the department identifying the work to be performed as an approved fabricator, and that such work shall be performed in accordance with the approved construction documents, referenced standards and applicable provisions of law and for which site the work is being fabricated prior to fabricating any items for such project.

§28-116.6.2 Fabricator’s certificate of compliance. For all fabricated items, the approved fabricator shall submit a certificate of compliance to the department stating that the work was performed in accordance with the approved construction documents, referenced standards and applicable provisions of law.

§28-116.7 Post-construction stormwater management facilities. The department shall not issue a certificate of occupancy or letter of completion with respect to a building or premises that is part of a covered development project unless the applicant submits proof that the department of environmental protection has issued a stormwater maintenance permit for any post-construction stormwater management facilities serving such building or premises.

ARTICLE 117
PLACES OF ASSEMBLY

§28-117.1 Place of assembly certificate of operation. It shall be unlawful to use or occupy any building or space, including an outdoor space, as a place of assembly without a certificate of operation issued by the commissioner. An application for a certificate of operation shall be made to the department in such form and containing such information as the commissioner shall provide. The department shall inspect every place of assembly space prior to the issuance of a certificate of operation. The commissioner shall not issue a certificate of operation unless the department determines that the space conforms substantially to the approved construction documents and to this code or the 1968 building code as applicable and that the certificate of occupancy authorizes such use. A certificate of operation shall not be issued to a place of assembly providing seating or other moveable furnishings unless the commissioner approves a plan conforming to this code or the 1968 building code as applicable and the rules of the department. Seating and other moveable furnishings shall be maintained at all times during occupancy in accordance with the approved plan. Any amendment of such plan shall be subject to the prior approval of the commissioner.

§28-117.1.1 Contents of the place of assembly certificate of operation. The certificate of operation shall contain the place of assembly certificate number, the number of persons who may legally occupy the space and any other information that the commissioner may determine. Such certificate of operation shall be framed and mounted in a location that is conspicuously visible to a person entering the space. For the purposes of this article, a department issued place of assembly permit or place of assembly certificate of operation shall be valid until its expiration, at which time a new place of assembly certificate of operation shall be required in accordance with the provisions of this article and with the filing requirements of the department.

§28-117.1.2 New certificate required. The following changes to a place of assembly shall require a new place of assembly certificate of operation instead of an amendment filed in accordance with section 28-117.1.3:

1.	For a department issued place of assembly permit or place of assembly certificate of operation that does not have a nine-digit job number, any change of zoning use group, assembly occupancy group A-1 through A-5, or any of the changes set forth in section 28-117.1.3.

2.	For all other department issued place of assembly permits or place of assembly certificates of operation, any change of zoning use group or assembly occupancy group A-1 through A-5.

§28-117.1.3 Amendments. No change shall be made to a place of assembly that is inconsistent with the most recently issued place of assembly certificate of operation or renewal unless an amendment to such certificate is filed with and approved or accepted by the department. Changes that require an amendment include any of the following:

1.	Any physical change requiring an alteration permit to be issued by the department.

2.	Any amendment to the plan for seating and other moveable furnishing, in accordance with section 28-117.1.

3.	Any change to the name of the establishment.

§28-117.2 Temporary place of assembly certificate of operation. At the commissioner’s discretion, a temporary certificate of operation may be issued for a place of assembly space upon request by the applicant in accordance with this code provided that public safety is not jeopardized thereby. The applicant shall notify the fire department when a temporary place of assembly certificate of operation is issued.

Exception. Applications for temporary certificates of operation for place of assembly space in prior code buildings shall be permitted to comply with the 1968 building code provided that public safety is not jeopardized thereby.

§28-117.3 Duration of certificate. A place of assembly certificate of operation shall be issued by the department and shall be effective for one year after its issuance. Thereafter, such certificate shall be effective only for periods of time during which there is in effect an annual place of assembly permit issued by the fire department pursuant to section 105.6 of the New York city fire code.

§28-117.4 Security guards. In the case of a certificate holder that offers for sale food and/or beverages for on-premises consumption, but not including establishments operated by a not-for-profit corporation, and employs or uses the services of a security guard, as that term is defined in subdivision six of section eighty-nine of the general business law, such certificate holder shall comply with the provisions of article 7-A of the general business law, shall obtain proof that such security guard is registered pursuant to article 7-A of the general business law, shall maintain such proof in a readily available location, in accordance with rules promulgated by the commissioner during all hours in which such place of assembly is open to the public, shall maintain a roster of all security guards working at any given time when such place of assembly is open to the public, and shall require each security guard to maintain on his or her person proof of registration at all times when on the premises.

§28-117.4.1 Presumption. For purposes of this section, there shall be a rebuttable presumption that a person employed or whose services are retained at a place of assembly is a security guard if his or her job functions include:

1.	The monitoring or guarding of the entrance or exit of such place of assembly to manage ingress and egress to such place of assembly for security purposes during the hours of operation of such establishment; and/or

2.	Protection of such place of assembly from disorderly or other unlawful conduct by patrons of such place of assembly.

§28-117.4.1.1 Presumption not applicable to owner. The rebuttable presumption in section 28-117.4.1 shall not apply to an individual who is an owner of the establishment as described in section 28-117.4 that has received a place of assembly certificate of operation.

§28-117.4.2 Responsibility for violations. Notwithstanding any provision of this section, only the holder of a certificate of operation shall be liable for violations of this article that relate to such holder’s obligations regarding security guards.

§28-117.4.3 Enforcement. In addition to employees of the department, employees of the police department and the department of consumer affairs shall have the authority to enforce the provisions of this article regarding security guards.

§28-117.4.4 State liquor authority reporting. The enforcement agency shall report any violation of the provisions of this section relating to security guards to the state liquor authority if the holder of the certificate of operation holds a license pursuant to the alcoholic beverage control law.

§28-117.5 Outdoor places of assembly. The commissioner shall not issue a certificate of operation to an outdoor temporary or permanent place of assembly, including, but not limited to, tents, platforms, stages and outdoor assembly seating, unless the department determines that the space complies with the provisions of the code.

ARTICLE 118
CERTIFICATES OF OCCUPANCY

§28-118.1 General provisions. No building or open lot shall be used or occupied without a certificate of occupancy issued by the commissioner. Issuance of a certificate of occupancy shall not be construed as an approval of a violation of the provisions of this code or of other applicable laws and rules.

§28-118.2 New buildings or open lots. No building hereafter constructed or open lot shall be occupied or used, in whole or in part, unless and until a certificate of occupancy shall have been issued certifying that such building or open lot conforms substantially to the approved construction documents and the provisions of this code and other applicable laws and rules.

§28-118.3 Completed buildings or open lots. The provisions of sections 28-118.3.1 through 28-118.3.4 shall apply to completed buildings or open lots.

Exception: The provisions of sections 28-118.3.1 and 28-118.3.2 shall not be interpreted to require an issuance of a new or amended certificate of occupancy for a change from a mercantile establishment to a business establishment, or from a business establishment to a mercantile establishment, provided all the following criteria are met:

1.	Such alteration is limited to a change within the same zoning use group;

2.	The maximum occupant load for the individual establishment, both as existing and proposed, does not exceed 74 persons based on occupant load calculations in accordance with Table 6-2 of the 1968 building code or Table 1004.1.3 of the New York city building code, as applicable;

3.	The establishment is located on the ground floor, accessed by the public directly from the exterior of the building;

4.	The establishment undergoing alteration complies or is made to comply with any other requirements that would be applicable to the alteration, including but not limited to accessibility, and fire protection requirements pursuant to sections 901.9.2 and 1101.3.1 of the New York city building code;

5.	Such alteration does not require a change in the required exits. Relocation of exit doors of the same size or larger shall not constitute a change in the required exits; and

6.	Such alteration does not require a change in the live load from that stated on the existing certificate of occupancy.

§28-118.3.1 Change of occupancy or use. No building, open lot or portion thereof hereafter altered so as to change from one occupancy group to another, or from one zoning use group to another, either in whole or in part, shall be occupied or used unless and until the commissioner has issued a certificate of occupancy certifying that the alteration work for which the permit was issued has been completed substantially in accordance with the approved construction documents and the provisions of this code and other applicable laws and rules for the new occupancy or use.

§28-118.3.2 Changes inconsistent with existing certificate of occupancy. No change shall be made to a building, open lot or portion thereof inconsistent with the last issued certificate of occupancy or, where applicable, inconsistent with the last issued certificate of completion for such building or open lot or which would bring it under some special provision of this code or other applicable laws or rules, unless and until the commissioner has issued a new or amended certificate of occupancy.

§28-118.3.2.1 Changes in the address, block, lot, or zoning lot. When changes are made in the address of [the structure] a building or open use, the block and/or lot numbers, or the metes and bounds of the zoning lot that are inconsistent with that indicated on a certificate of occupancy, the owner shall obtain a new or amended certificate of occupancy within one year of such change.  For purposes of this section:

1.	The date of change in the metes and bounds of the zoning lot shall be the date of the approval of construction documents for any new building or enlargement on the zoning lot, as per article 104 following the reporting required in section 28-104.7.18;

2.	The date of the change of the address or the block and/or lot numbers shall be the date such change is made effective by the borough president or the department of finance.

§28-118.3.3 Zoning lot change not inconsistent with existing certificate of occupancy. Where metes and bounds of the zoning lot have been changed after the effective date of the local law that added this section and construction documents are approved for a new building or enlargement within such metes and bounds, an owner of a tax lot within such metes and bounds with a certificate of occupancy that does not indicate zoning lot metes and bounds, shall file an application with the department notifying it of the amended metes and bounds, including the city registration file number (CRFN) numbers of the related zoning lot exhibits, and obtain approval and sign off within one year from the date of such change in metes and bounds. For purposes of this section, the date of change in the metes and bounds of the zoning lot, shall be the date of the approval of construction documents for any new building or enlargement on the zoning lot, in accordance with article 104 following the reporting required in section 28-104.7.18.

[§28-118.3.3] §28-118.3.4 Changes to exits. No building hereafter altered so as to cause a major alteration to existing exits shall be occupied or used unless and until the commissioner has issued a certificate of occupancy certifying that the alteration work for which the permit was issued has been completed substantially in accordance with the approved construction documents and the provisions of this code and other applicable laws and rules.

[§28-118.3.4] §28-118.3.5 Existing buildings or open lots without certificates of occupancy. A building or open lot in existence prior to January 1, 1938 and heretofore legally used or occupied without a certificate of occupancy or, if applicable, a certificate of completion, and subject to the provisions of section 28-102.4 (continuation of lawful existing use), may continue to be used or occupied without a certificate of occupancy or, if applicable, a certificate of completion, [pursuant to the requirements of section six hundred forty five of the New York city charter, this code and other applicable laws and rules] provided such use or occupancy is not inconsistent with the records of the department relating to the lawful use of such building or open lot, and complies with applicable laws and rules, and provided there is no change in the existing use or occupancy classification of the building, open lot or portion thereof.

§28-118.3.5.1 Zoning lot change. Where metes and bounds of a zoning lot have been changed after the effective date of this code for a building or open lot in existence prior to January 1, 1938 and heretofore legally used or occupied without a certificate of occupancy, the owner shall file an application with the department notifying it of such change in metes and bounds, including the CRFN numbers of the related zoning lot exhibits, and obtain approval and sign off, within one year from the date of the change in metes and bounds of the zoning lot.  For purposes of this section, the date of change in the metes and bounds of the zoning lot, shall be the date of the approval of construction documents for any new building or enlargement on the zoning lot, as per article 104 following the reporting required in section 28-104.7.18.

[§28-118.3.4.1] §28-118.3.5.2 Application for certificate of occupancy. Upon application by the owner of such a building or open lot in existence prior to January 1, 1938, the commissioner shall issue a certificate of occupancy for such building, provided that at the time of issuing such certificate, such existing building is in compliance with all retroactive requirements of the 1968 building code applicable to such building and no notices of violation or other notices or orders affecting the building as they relate to the provisions of this code or the 1968 building code are pending before the department, and provided further that it is established to the satisfaction of the commissioner, after inspection and investigation, that the alleged use and occupancy of the building has heretofore legally existed.

[§28-118.3.4.2] §28-118.3.5.3 Partial certificates of occupancy. Partial certificates of occupancy may be issued pursuant to section [28-118.16] 28-118.20.

§28-118.4 Applications for certificates of occupancy. All applications for certificates of occupancy shall be submitted on forms furnished by the department. Applications for new buildings or additions to buildings shall be accompanied by an accurate and complete final lot survey made by a land surveyor showing such information as prescribed by the commissioner. The commissioner may waive the requirement of such survey in the case of small sheds, stands, temporary structures, signs, and similar small structures.

§28-118.4.1 Applicant. The application for a certificate of occupancy shall be made by or on behalf of the owner of the building or open lot; and if made by a person other than the owner, the application shall be accompanied by a signed statement of the applicant stating that the applicant is authorized by the owner to make the application. The full names and addresses of the owner, and applicant, and of the principal officers thereof, if a corporation, shall be stated in the application.

§28-118.4.2 Statement of compliance. When a certificate of occupancy for a new or altered building is applied for, the application shall be accompanied by a signed statement of the registered design professional of record or permittee, stating that such person has examined the approved construction documents and specifications of the building for which the certificate of occupancy is sought, and that, to the best of his or her knowledge and belief, the building has been erected or altered in accordance with the approved construction documents and specifications and, as erected or altered, complies with the provisions of this code and all other applicable laws and rules, except insofar as variations or variances therefrom have been legally permitted or authorized, specifying such variations or variances in such required statement.

28-118.4.3 Timeframe for application. The application for the certificate of occupancy must be submitted within six months of the final construction inspection. The department may refuse to issue a certificate of occupancy where the final inspection was completed more than six months prior to such application.

§28-118.5 Review of applications for certificates of occupancy. All applications for certificates of occupancy and accompanying submittal documents shall be examined promptly after their submission. If the building is entitled to the certificate of occupancy applied for, the application shall be approved and the certificate of occupancy issued by the commissioner within 10 calendar days after submission of a complete application. Otherwise, the application shall be rejected and written notice of rejection, stating the grounds of rejection, shall be given to the applicant within 10 calendar days of the submission of the application. Wherever an application has been rejected and proof is thereafter submitted establishing that the grounds of rejection have been met and that the building is entitled to the certificate of occupancy applied for, the application shall be approved and the certificate of occupancy issued within 10 calendar days after submission of such proof.

§28-118.6 Issuance of certificate of occupancy. After the commissioner inspects the building or open lot and determines that the building or open lot conforms substantially to the approved construction documents and to the provisions of this code and other applicable laws and rules, the commissioner shall issue a certificate of occupancy that shall contain information including, but not limited to:

1.	The building permit number.

2.	The address of the structure.

3.	Block and lot numbers pertaining to the zoning lot as of the date of issuance, as defined in section 12-10 of the New York city zoning resolution.

4.	The description of the structure for which the certificate is issued.

5.	A statement that the described portion of the structure has been inspected for compliance with the requirements of this code.

6.	The name and signature of the commissioner.

7.	The code under which the permit was issued.

8.	The use and occupancy, in accordance with this code and the zoning resolution.

9.	The type of construction as defined in this code.

10.	The design occupant load of floors and spaces, including roofs.

11.	Types of major fire suppression or alarm systems.

12.	Any special stipulations and conditions of the building permit.

13.	The maximum permissible live loads on the [several floors of the building] building floors and roofs.

14.	The number of parking spaces.

§28-118.7 Pavement plan. No certificate of occupancy shall be issued for any building or open lot requiring a pavement plan pursuant to article 108 unless and until an inspection has been made to show that all work necessary for compliance with the pavement plan has been completed.

§28-118.7.1 Certification. No certificate of occupancy shall be issued for any building or open lot requiring a certification pursuant to article 108 unless and until the applicant, after completion of construction work, inspects the sidewalk and certifies that the sidewalk is free from defects.

Exception: The commissioner may issue a certificate of occupancy if in lieu of such certification the owner furnishes to the department prior to the issuance of the certificate of occupancy security satisfactory to the department that the sidewalk will be installed and paved or repaired within the time specified by the department.

§28-118.8 Sanitary/storm water drainage. No certificate of occupancy shall be issued until the department confirms by inspection that all work relating to the installation of the part of the sanitary/storm water drainage system which lies outside of such property, if and as required by section 24-526 of the administrative code, has been satisfactorily completed.

§28-118.9 Fire protection plan. No certificate of occupancy shall be issued until a fire protection plan, if required pursuant to article 109, has been filed and accepted.

§28-118.10 Electrical work. No certificate of occupancy shall be issued unless compliance with the New York city electrical code is certified by the commissioner.

§28-118.11 Certificates of compliance. No certificate of occupancy shall be issued until certificates of compliance are issued for the following types of service equipment:

1.	Air conditioning and ventilation systems.

2.	Elevators, escalators, moving walkways and dumbwaiters.

3.	Fuel burning and fuel oil storage equipment.

4.	Refrigeration systems.

5.	Heating systems.

6.	Boilers.

§28-118.12 Place of assembly certificate of operation. The issuance of a certificate of occupancy shall not authorize the use of any space as a place of assembly unless and until the commissioner thereafter issues a place of assembly certificate of operation.

§28-118.13 Certificates of occupancy for air-inflated structures, air-supported structures, and tents. Certificates of occupancy for air-inflated structures, air-supported structures, and tents shall be issued for a period not exceeding one year. Such certificates may be renewed for one-year periods upon demonstration that the structure complies with all laws and rules in effect at the time of the request for renewal.

§28-118.14 Payment of outstanding fees and penalties. The department may refuse to issue a certificate of occupancy for a building pending payment of all outstanding fees, or fines or civil penalties imposed for violations of this code, the 1968 building code or other laws enforced by the department at the same building.

§28-118.15 Temporary certificates of occupancy. Upon application, the commissioner is authorized to issue a temporary certificate of occupancy before the completion of the entire work covered by the permit, provided that the subject portion or portions of the building may be occupied and maintained in a manner that will not endanger public safety, health, or welfare. The commissioner may refuse to issue a temporary certificate of occupancy for a building pending payment of all outstanding fees, or fines or civil penalties imposed for violations of this code, the 1968 building code or other laws enforced by the department at the same building. The commissioner shall set a time period during which the temporary certificate of occupancy is valid. The provisions of section 28-118.15.1 apply only to interim certificates of occupancy.  Nothing in section 28-118.15.1 is intended to affect, alter or amend the commissioner’s power to issue or to set time periods for the expiration of temporary certificates of occupancy that are not interim certificates of occupancy.

§ 28-118.15.1 Interim certificate of occupancy. An interim certificate of occupancy may be issued authorizing occupancy of a specific floor or floors of a building prior to the completion of the entire work covered by a permit in accordance with this section and rules of the department, subject to the following conditions:

1.	The building is of noncombustible construction and protected with an automatic sprinkler system;

2. 	Adequate means of egress are provided;

3. 	There are no outstanding objections relating to or affecting the occupancy of such portion of the building; and

4.	Upon inspection, the portion of the building is deemed safe for occupancy without reliance upon temporary measures.

Exceptions: Section 28-118.15.1 shall not apply to:

1. Residential buildings with fewer than eight stories or fewer than four dwelling units; or

2. Non-residential buildings with fewer than five stories; or

3. Mixed-use buildings with fewer than four dwelling units; or

4. Parking structures.

§ 28-118.15.1.1 Issuance, contents and posting of interim certificate of occupancy. An interim certificate of occupancy shall be issued after an inspection by the commissioner determines that the floor or floors of the building conform substantially to the approved construction documents and to the provisions of this code and other applicable laws and rules. Such interim certificate of occupancy shall contain the same information as a certificate of occupancy issued pursuant to section 28-118.6 and shall be posted while it is in effect in accordance with section 28-118.19 and replaced when necessary in accordance with section 28-118.19.1.

§ 28-118.15.1.2 Effective period. An interim certificate of occupancy shall remain in effect until the issuance of a certificate of occupancy for the building in accordance with section 28-118.6.

§ 28-118.15.2 Revocation and suspension. The commissioner may revoke or suspend a temporary certificate of occupancy, including an interim certificate of occupancy, that was issued in error, or on the basis of incorrect information provided to the department, or based on discontinuance of a nonconforming use pursuant to Article V of the New York city zoning resolution, in accordance with the procedures set forth in sections 28-105.10.1 and 28-105.10.2 for the suspension or revocation of a permit.

§28-118.16 Amended certificate of occupancy. The provisions of sections 28-118.16.1 through 28-118.16.2 shall apply to amended certificates of occupancy.

§28-118.16.1 Buildings exceeding three stories in height and change does not exceed 20 percent of total floor area. Where a building exceeds three stories in height and the change does not exceed 20 percent of the total floor area, an amendment to the existing certificate of occupancy for such new use shall be issued by the commissioner certifying that the proposed new occupancy and use conforms to the provisions of the laws governing building construction and that the proposed use will not be in conflict with any provisions of the New York state labor law, New York state multiple dwelling law or the zoning resolution.

§28-118.16.2 Change in address of the structure, block and lot numbers or metes and bounds of a zoning lot subsequent to the issuance of a certificate of occupancy. Where no change is made to a building, open lot or portion thereof inconsistent with the last issued certificate of occupancy, an amended certificate of occupancy may be issued to reflect a change in the address of the structure, block and lot numbers or the metes and bounds of the zoning lot. Notwithstanding any other provisions of law, removal of violations and payments of outstanding penalties are not required prior to issuance of an amended certificate of occupancy in accordance with this section 28-118.16.2.

§28-118.17 Revocation of certificates of occupancy. The commissioner is authorized to request, in writing, pursuant to section six hundred forty five of the New York city charter that the board of standards and appeals or a court of competent jurisdiction revoke, vacate, or modify a certificate of occupancy issued under the provisions of this code whenever the certificate is issued in error, or on the basis of incorrect information provided to the department, or the nonconforming use reflected on the certificate of occupancy is no longer permitted pursuant to Article V of the New York city zoning resolution. This section shall not be construed to apply to interim certificates of occupancy and other temporary certificates of occupancy.

§28-118.18 Record of certificates. A record of all certificates of occupancy shall be kept by the department; and copies thereof shall be furnished by the department upon request, and on the payment of the fee prescribed in article 112 of this chapter. The certificate of occupancy or a copy thereof shall be available for inspection at the building at all reasonable times.

§28-118.19 Posting of certificates of occupancy. The owner shall post a copy of the building’s certificate of occupancy, partial certificates of occupancy or temporary, including interim, certificates of occupancy in accordance with this section 28-118.19, except buildings occupied entirely by group R3. [Buildings] Owners of buildings that are not required to have a certificate of occupancy shall [be posted by the owner with] post a sign or placard in a form prescribed by the commissioner. The certificate of occupancy or sign, as applicable, shall be permanently affixed to the structure in a conspicuous location in a public hall, corridor, management office of the building or as otherwise prescribed by the commissioner.

§28-118.19.1 Replacement of posted certificates of occupancy and signs. All posted certificates of occupancy, partial certificates of occupancy, temporary, including interim, certificates of occupancy or signs, as applicable, shall not be removed or defaced and, if lost, removed or defaced, shall be immediately replaced. The commissioner may inspect or cause to be inspected periodically all buildings for compliance with the provisions of this code in regard to posting; and the inspection reports shall specify any violation thereof.

§28-118.20 Partial certificate of occupancy. A partial certificate of occupancy may be issued to a specific floor or floors of an existing building erected prior to January 1, 1938 subject to the following conditions:

1.	The building does not have and is not otherwise required to have a certificate of occupancy or certificate of completion, if applicable.

2.	The floor or floors for which a certificate of occupancy is issued shall not constitute more than 50 percent of the gross floor area of the building.

3.	The building is of noncombustible construction and protected with an automatic sprinkler system.

4.	Adequate means of egress are provided from all floors.

5.	Upon inspection, the building is deemed safe for occupancy.

§28-118.21 Live loads posted. Where the live loads for which each floor or portion thereof of a commercial or industrial building is or has been designed to exceed 50 psf (2.40 kN/m2), a certificate of occupancy required by this article shall not be issued until such design loads shall be conspicuously posted by the owner in that part of each story in which they apply, using durable signs. It shall be unlawful to remove or deface such signs.

Exception: This section 28-118.21 shall not apply to prior code buildings.

§28-118.22 Post-construction stormwater management facilities. The department shall not issue a certificate of occupancy with respect to a building or premises that is part of a covered development project unless the applicant submits proof that the department of environmental protection has issued a stormwater maintenance permit for any post-construction stormwater management facilities serving such building or premises.

§28-118.23 Extension, alteration or relocation of chimneys and vents. No certificate of occupancy shall be issued until all chimneys and vents required to be extended, altered or relocated by section 2113 of the New York city building code, section 801 of the New York city mechanical code or section 501 of the New York city fuel gas code have been so modified.

Exceptions:

- A certificate of occupancy may be issued to the new or altered taller building where access is granted and conditions are observed that result in a determination that chimney or vent alteration is not required and a revised chimney or vent plan is submitted pursuant to section 107.18 of the New York city building code.

2.	A certificate of occupancy may be issued to the new or altered taller building where one or more of the chimneys or vents requiring alteration has not been altered nor proven to comply with the applicable requirements of the New York city fuel gas code or New York city mechanical code as required when the following conditions have been met:

2.1.	The owners of the affected buildings have provided their refusal of consent in writing, or the owner of the affected buildings failed to grant consent after the owner of the new or altered taller building has made all the required notifications to the affected building owners; and

2.2.	The owner of the new or taller building demonstrates to the department in the form of a written statement from a registered design professional that there is no hazard to the occupancy in whole or in part of the new or altered building from the continued operation of the chimneys or vents in question.

ARTICLE 119
SERVICE UTILITIES

§28-119.1 Connection of service utilities. It shall be unlawful for any utility company or utility corporation to supply gas to a building, place or premises in which new meters other than replacement are required until a certificate of approval of gas installation from the department is filed with such utility company or utility corporation. When new gas service piping has been installed, it shall be locked-off by the utility company or utility corporation either by locking the gas service line valve or by installing a locking device on the outside gas service line valve. The lock shall not be removed until the gas meter piping (other than utility owned) and gas distribution piping have been inspected and certified as required by the department of buildings as being ready for service.

§28-119.1.1 Gas shut-off for alterations to gas piping systems. When alterations, extensions or repairs to existing gas meter piping or gas distribution piping require the shut-off of gas flow to a building, the utility company shall be notified by the owner or his or her authorized representative.

§28-119.2 Temporary connection. The commissioner shall have the authority to authorize the temporary connection of the building or system to the gas service utility.

§28-119.3 Authority to disconnect utility service. The commissioner may authorize disconnection of gas service to the building, structure or system regulated by this code and the codes referenced in case of emergency where necessary to eliminate an immediate hazard to life or property. The department shall notify the local gas utility company, and wherever possible the owner and occupant of the building, structure or service system of the decision to disconnect prior to taking such action.

§28-119.4 Notification of gas shut-off or non-restoration after inspection. Within 24 hours after gas service to a building is shut off by a utility company or utility corporation because of a class A or class B condition, as described in part 261 of title 16 of the New York codes, rules and regulations, and within 24 hours after gas service is, after an inspection by such a company or corporation, not restored because of such a condition, such company or corporation and the owner of such building shall each provide notice to the department in a form and manner prescribed by the department.

ARTICLE 120
TENANT PROTECTION PLAN

§28-120.1 Tenant protection plan. A tenant protection plan shall be prepared and submitted for the alteration, construction, or partial demolition of buildings in which any dwelling unit will be occupied during construction, including newly constructed buildings that are partially occupied where work is ongoing. The tenant protection plan shall be prepared by a registered design professional and filed with the department. The registered design professional preparing the tenant protection plan shall be retained by the general contractor performing the alteration, construction, or partial demolition work. No permit shall be issued for work that requires a tenant protection plan unless such plan is approved by the department. Such plan shall contain a statement signed by the owner and signed by the applicant affirming that the building contains dwelling units that will be occupied during construction and shall identify in sufficient detail the specific units that are or may be occupied during construction, the means and methods to be employed to safeguard the safety and health of the occupants throughout the construction, including, where applicable, details such as temporary fire-rated assemblies, opening protectives, or dust containment procedures. Such means and methods shall be described with particularity and in no case shall terms such as “code compliant,” “approved,” “legal,” “protected in accordance with law” or similar terms be used as a substitute for such description. The tenant protection plan must be site specific. The elements of the tenant protection plan may vary depending on the nature and scope of the work but at a minimum, must comply with all applicable laws and regulations, including the New York city construction codes, the New York city housing maintenance code, the New York city noise control code and the New York city health code, and shall make detailed and specific provisions for:

1.	Egress. At all times in the course of construction, provision shall be made for adequate egress as required by this code and the tenant protection plan shall identify the egress that will be provided. Required egress shall not be obstructed at any time except where approved by the commissioner.

2.	Fire safety. All necessary laws and controls, including those with respect to occupied dwellings, as well as additional safety measures necessitated by the construction shall be strictly observed.

3.	Health requirements. Specification of means and methods to be used for control of dust, disposal of construction debris, pest control and maintenance of sanitary facilities shall be included.

3.1.	There shall be included a statement of compliance with applicable provisions of law relating to lead and asbestos, and such statement shall describe with particularity what means and methods are being undertaken to meet such compliance.

4.	Compliance with housing standards. The requirements of the New York city housing maintenance code, and, where applicable, the New York state multiple dwelling law shall be strictly observed.

5.	Structural safety. No structural work shall be done that may endanger the occupants.

6.	Noise restrictions. Specification of means and methods to be used for the limitation of noise to acceptable levels in accordance with the New York city noise control code shall be included. Where hours of the day or the days of the week in which construction work may be undertaken are limited pursuant to the New York city noise control code, such limitations shall be stated.

7.	Maintaining essential services. Where heat, hot water, cold water, gas, electricity, or other utility services are provided in such building or in any dwelling unit located therein, the tenant protection plan shall specify the means and methods to be used for maintaining such services during such work in accordance with the requirements of the New York city housing maintenance code. If a disruption of any such service is anticipated during the work, then such plan shall specify the anticipated duration of such disruption and the means and methods to be employed to minimize such disruption, including the provision of sufficient alternatives for such service during such disruption. Notification of the disruption must be given to all affected occupants of occupied dwelling units.

Exception: In the following instances, the tenant protection plan may be prepared and filed by the registered design professional of record for the alteration, construction, or partial demolition work as part of the underlying application:

1.	Work in occupied one- and two-family homes.

2.	Work limited to the interior of a single dwelling unit of an occupied multiple dwelling with no disruption to the essential services of other units, where such dwelling is owner-occupied. For a dwelling unit within a property that is owned by a condominium or held by a shareholder of a cooperative corporation under a proprietary lease, the unit must be occupied by the owners of record for such unit.

§28-120.1.1 Public availability of tenant protection plan. Upon issuance of a permit for work containing a tenant protection plan, the department shall make the tenant protection plan publicly available on its website.

§28-120.1.2 Provision of copy of tenant protection plan to occupants upon request. The owner of a building undergoing work for which a tenant protection plan is required by section 28-120.1 shall, upon request from an occupant of a dwelling unit within such building, provide such occupant with a paper copy of the tenant protection plan approved by the department.

§28-120.1.3 Notice to occupants. Upon issuance of a permit for work containing a tenant protection plan, the owner shall (i) distribute a notice regarding such plan to each occupied dwelling unit and (ii) post a notice regarding such plan in a conspicuous manner in the building lobby, as well as on each floor within ten feet of the elevator, or in a building where there is no elevator, within ten feet of or in the main stairwell on such floor. The notice shall be in a form created or approved by the department and shall include:

1.	A statement that occupants of the building may obtain a paper copy of such plan from the owner and may access such plan on the department website;

2.	The name and contact information for the site safety manager, site safety coordinator or superintendent of construction required by section 3301.3 of the New York city building code, as applicable, or, if there is no site safety manager, site safety coordinator or superintendent of construction, the name and contact information of the owner of the building or such owner’s designee; and

3.	A statement that occupants of the building may call 311 to make complaints about the work.

§28-120.2 Phased tenant protection plans. Multiple layouts of the tenant protection features enumerated in section 28-120.1 may be submitted at any time during construction operations to show phased tenant protection plan designs consistent with the phase of anticipated work. Layouts submitted subsequent to a previously approved tenant protection plan shall constitute an amendment to such plan. Such amended plan shall be approved by the department prior to the commencement of the work requiring such amended plan.

§28-120.3 Contractor statement. The permit holder for the underlying alteration, construction, or partial demolition shall sign a statement certifying that the tenant protection plan submitted by the registered design professional coordinates with the scope of work intended.

Exception: This statement shall not be required for:

1.	Work in occupied one- and two-family homes.

2.	Work limited to the interior of a single dwelling unit of an occupied multiple dwelling with no disruption to the essential services of other units, where such dwelling is owner -occupied. For a dwelling unit within a property that is owned by a condominium or held by a shareholder of a cooperative corporation under a proprietary lease, the unit must be occupied by the owners of record for such unit.

§ 2.  Chapter 2 of title 28 of the administrative code of the city of New York, as added by local law number 33 for the year 2007, section 28-201.2.1 as amended by, and section 28-204.1.1 as added by, local law 196 for the year 2017, section 28-201.2.2 as amended by local law 33 for the year 2018, section 28-201.2.3 as added by local law 47 for the year 2012, sections 28-201.3.1, 28-204.3, 28-204.4, 28-204.6.3, 28-205.1.2.3, 28-207.4.2, 28-207.4.3, 28-207.5, 28-207.5.1, 28-211.1, 28-211.2, 28-212.10, 28-214.1, 28-215.1, 28-215.4, 28-215.6, 28-215.8, 28-216.2, 28-216.3, 28-216.3.1, 28-216.4, 28-216.5, 28-216.6.1, 28-216.6.3, 28-216.6.4, 28-216.7.3, 28-216.8.3.1, 28-216.8.3.3, 28-216.8.4, 28-216.9, 28-217.1, 28-217.1.1, 28-217.1.2, 28-217.1.3, 28-217.1.4, 28-217.1.5, 28-217.1.6, 28-217.1.7, 28-218.1, 28-218.2, 28-218.3, 28-218.4, 28-218.5, 28-218.6, 28-216.7 as amended by, and sections 28-207.2.5 and 28-207.4.4 as added by, local law 141 for the year 2013, section 28-202.1 as amended by, and sections 28-202.4 and 28-202.4.1 as added by, local law 70 for the year 2018, sections 28-202.3 and 28-202.3.1 as added by local law 205 for the year 2017, section 28-203.1 as amended by local law 203 for the year 2017, sections 28-204.2 as amended by local law 34 for the year 2008, section 28-204.6 as amended by local law 153 for the year 2017, section 28-204.6.1 as added by local law 152 for the year 2017, section 28-207.2.6 as amended by local law 157 for the year 2017, sections 28-207.2.4, 28-207.2.4.1, and 28-211.1.2 as added by local law 8 for the year 2008, section 28-207.4  as amended by local law 150 for the year 2017, section 28-210.1.1 as added by local law 94 for the year 2017, section 28-210.2 as added by local law 37 for the year 2007, section 28-210.3 as added by local law 45 for the year 2012, section 28-210.3.1 as added by local law 87 for the year 2017, sections 28-213.1.1 and 28-213.1.2 as amended by local law 156 for the year 2017, sections 28-213.5, 28-213.5.1, 28-213.5.2, and 28-213.5.3 as added by local law 155 for the year 2017, sections 28-213.6 and 28-213.7 as added by local law 158 for the year 2017, sections 28-219.1, 28-219.2, 28-219.2.1, 28-219.2.2, and 28-219.3 as amended by local law 51 for the year 2014, and section 28-219.4 as added by local law 101 for the year 2015, is amended to read as follows:

CHAPTER 2

ENFORCEMENT

ARTICLE 201
GENERAL

§28-201.1 Unlawful acts. It shall be unlawful to erect, construct, alter, extend, repair, fail to maintain, move, remove, demolish, occupy, use or operate any building, structure, premises, or equipment, or to conduct any subject matter regulated by this code or by the zoning resolution, or to cause same to be done, in conflict with or in violation of any of the provisions of this code, the zoning resolution, or the rules of the department or, with regard to existing buildings, any applicable provision of the 1968 building code or any other law or rule enforced by the department. It shall be unlawful to fail to comply with an order of the commissioner or to violate any order of the commissioner issued pursuant to this code, the 1968 building code, the zoning resolution or any law or rule enforced by the department.

§28-201.2 Classification of violations. The commissioner shall promulgate rules classifying all violations of this code, the zoning resolution or, with regard to existing buildings, the 1968 building code or other laws or rules enforced by the department as immediately hazardous violations, major violations or lesser violations unless the classification of such violations is specifically directed by this code. Such classification shall be based on the effect of the violation on life, health, safety or the public interest or the necessity for economic disincentive.

§28-201.2.1 Specified immediately hazardous violations. The commissioner shall classify the following violations as immediately hazardous:

- With respect to violations of article 210 of this chapter:

1.1.	A violation of section 28-210.1 in which a building legally approved for occupancy as a one-family or two-family dwelling (as set forth in the certificate of occupancy or if no certificate of occupancy is required, as evidenced by official records) is illegally converted to or maintained as a dwelling for occupancy by four or more families [;]; or

1.2.	A violation of sections 28-210.1 and 28-210.2 in any building involving the illegal conversion, maintenance or occupancy of three or more dwelling units than are legally authorized by the certificate of occupancy or if no certificate of occupancy is required as evidenced by official records.

- Any violation of section 28-211.1 false statement;

- Any violation of a stop work order or of a cease use order;

- Any violation of a vacate order or order to seal, secure and close, or closure order;

- Unlawful demolition;

- Falsely impersonating an employee or authorized representative of the department;

- Occupancy without a required certificate of occupancy;

- Intentional disobedience or violation of any provision of a closure order;

- Submittal of a materially false or misleading professional certification.

- A violation of section 28-212.11.

- A violation of section 28-307.1.

- A violation by a licensed rigger or person performing the functions and duties of a licensed rigger of the provisions of sections 28-404.1 or 28-401.9 of this code or such person’s failure to ensure that workers have certificates of fitness required pursuant to this code or applicable rule or any person’s violation of the provisions of [section] sections 3314.4.3.1 and 3314.4.3.4 of the New York city building code.

- A violation of any provision of chapter 4 of this title for engaging in any business or occupation without a required license or other authorization or a violation of section 27-3017 for performing electrical work without a required license.

[13.2	The minimum civil penalty that shall be imposed for a violation of section 27-3017 of this code and the minimum fine that shall be imposed for a violation of such section shall be $4,800. The maximum fine that shall be imposed for a violation of such section shall be $25,000. Such violation may also be punished, in addition to or instead of such fine, by imprisonment of not more than one year.]

- Any person who knowingly permits or causes a violation of [paragraph] section 3314.4.5 or [paragraph] section 3314.4.6 [of subdivision 3314.4 of section BC 3314] of the New York city building code.

- A violation of sections 3303.4.5 and 3303.4.6 of the building code.

- A violation of section 28-210.3 that involves more than one dwelling unit or a second or subsequent violation of section 28-210.3 by the same person at the same dwelling unit or multiple dwelling.

- A violation of sections 28-119.1 or 28-119.1.1.

- A violation of section [105.2] 106.2 of the New York city fuel gas code relating to work on a gas piping system.

- A violation of sections 406.6.2, 406.6.2.1, 406.6.2.2, 406.6.2.3, or 406.6.3 of the New York city fuel gas code.

- A second or subsequent violation of section 3321.1 of the New York city building code.

21.	A violation of sections 28-401.19(1), 28-401.19(2), 28-401.19(3), 28-401.19(4), 28-401.19(6), 28-401.19(7), 28-401.19(10), 28-401.19(11) or 28-401.19(15).

§28-201.2.2 Specified major violations. The commissioner shall classify the following violations as major violations:

- A violation of section 28-210.1 or 28-210.2 other than a violation that is directed to be classified as immediately hazardous.

- Failure to perform required façade, retaining wall, elevator and boiler inspections, or tests, structural inspections of buildings and structures that are potentially compromised as defined in section 28-217.1, and to file required reports within the applicable time period.

- Failure to provide the notice required by section [3314.1.1] 3314.4.1.5 of the New York city building code.

- A violation of the zoning resolution by any person for causing damage to or removing a tree within a Special Natural Area District, as defined in the zoning resolution.

4.1.	The fine or civil penalty for a violation described in item 4 shall be not less than seven hundred fifty dollars for each tree damaged or removed.

5.	Notwithstanding the provisions of section 28-204.2 of this code, a violation of item 3 or item 4 of section [1008.1.3.5] 1010.1.4 of the New York city building code except that no penalty for such violation shall be imposed if the respondent corrects the condition constituting the violation and files a certificate with the department that the condition has been corrected within ninety days from the date set forth in the notice of violation. It shall be an affirmative defense that the nonconforming security grille was installed prior to July 1, 2011.

5.1.	The fine or civil penalty for a violation described in item 5 shall be not less than two hundred fifty dollars for the first offense and not less than one thousand dollars for each subsequent offense.

6.	A violation of a condition, restriction or requirement established pursuant to the zoning resolution, section 197-d of the charter or section 25-114, related to a privately owned public space as such term is defined in section 25-114.

7.	A violation of section 28-309.12.

§28-201.2.3 Specified lesser violations. The commissioner shall classify the following violations as lesser violations:

1.	A violation of item 5 of section [1110.1] 1111.1, of section [1110.2] 1111.2, or of item 7 of section [1110.3] 1111.3 of the New York city building code, or a violation of section 28-313.1, 28-313.2 or 28-313.3 of the administrative code of the city of New York.

§28-201.3 Methods of enforcement. The commissioner may use any of the methods set forth in this code to enforce compliance with this code, the 1968 building code, the zoning resolution, other laws or rules enforced by the department and orders of the commissioner issued pursuant thereto including but not limited to:

- Proceedings for the recovery of civil penalties for immediately hazardous, major and lesser violations before the environmental control board or other administrative tribunal.

- Civil judicial proceedings for the recovery of civil penalties or injunctive relief or both for immediately hazardous, major and lesser violations.

- Criminal judicial proceedings for the imposition of criminal fines or imprisonment or both for immediately hazardous, major and lesser violations.

- The issuance and enforcement of peremptory orders for immediately hazardous, major and lesser violations.

- The issuance of a commissioner’s request for correction of an unlawful use or condition or order to correct an unlawful use or condition.

- Other special remedies as set forth in this code, the zoning resolution or other law or rule.

§28-201.3.1 Issuance. Officers and employees of the department and of other city agencies designated by the commissioner shall have the power to issue summonses, appearance tickets, orders and notices of violation based upon violations of this code, the 1968 building code, the zoning resolution or other laws or rules enforced by the department, orders, and requests for corrective action.

§28-201.4 Aggravating and mitigating factors. Civil penalties and criminal fines and imprisonment shall be imposed within the ranges set forth in this code or as otherwise specified in this code or other law, with due regard for mitigating and aggravating factors.

ARTICLE 202
CIVIL PENALTIES

§28-202.1 Civil penalties. Except as otherwise specified in this code or other law, violations of this code, the 1968 building code, the zoning resolution or other laws or rules enforced by the department shall be punishable by civil penalties within the ranges set forth below:

- For immediately hazardous violations, a civil penalty of not less than [one thousand dollars] $2,500 nor more than $25,000 may be imposed for each violation. In addition to such civil penalty, a separate additional penalty may be imposed of not more than $1,000 for each day that the violation is not corrected. The commissioner may by rule establish such specified daily penalties.

- For major violations, a civil penalty of not less than $1,000 nor more than $10,000 may be imposed for each violation. In addition to such civil penalty, a separate additional penalty may be imposed of not more than $250 for each month that the violation is not corrected. The commissioner may by rule establish such specified monthly penalties.

- For lesser violations, a civil penalty of not more than $500 may be imposed for each violation.

[Exceptions:] Exceptions:

1.	The owner, lessee, occupant, manager or operator of a building affected by a natural or man-made disaster, as determined by the commissioner, shall not be subject to a civil penalty for a violation involving such building if (i) notice of such violation is issued by the department during the 90-day period immediately after such disaster or, in the case of a major natural or man-made disaster as determined by the commissioner, during the six-month period immediately after such disaster, and (ii) such violation is corrected on or before 40 days after such disaster period or such greater amount of time as determined by the commissioner for such violation. The notice of such violation shall state that such violation is subject to this exception and shall set forth the procedure and time period for correcting such violation without incurring a civil penalty. This exception shall not apply to immediately hazardous violations, violations charged as aggravated violations or violations without connection to such disaster, as determined by the department.

2.	The owner, lessee, occupant, manager or operator of a building where a violation occurs shall not be subject to a civil penalty for such violation if (i) such violation was connected to a natural or man-made disaster, as determined by the commissioner, and (ii) such building is undergoing, or scheduled or under evaluation for, work or acquisition through a city-operated disaster recovery program responding to such disaster.

3.	The owner, lessee, occupant, manager or operator of a building shall not be subject to a civil penalty for a violation resulting from work done by a city employee, or by a third party under contract with the city, in response to a natural or man-made disaster, provided that such violation is corrected on or before 60 days after the issuance of such violation, or such greater amount of time as determined by the commissioner for such violation. If such owner, lessee, occupant, manager or operator of a building can demonstrate to the satisfaction of the department that a city employee or third party under contract with the city has committed to correcting such violation then such violation shall be rescinded, without penalty. The notice of such violation shall state that such violation is subject to this exception and shall set forth the procedure and time period for correcting such violation without incurring a civil penalty. This exception shall not apply to immediately hazardous violations or violations charged as aggravated violations.

4.	The minimum civil penalty for a violation of section 28-408.1 or section 28-410.1 of this code shall be $2,500 for a first violation and $5,000 for a second violation, in addition to any separate daily penalty imposed pursuant to item 1 of this section.

[4.	The minimum civil penalty for a violation of section 28-408.1 or section 28-410.1 of this code shall be $2,500 for a first violation and $5,000 for a second violation, in addition to any separate daily penalty imposed pursuant to item 1 of this section.]

5.	The minimum civil penalty for a violation of section 28-103.21.1 of this code shall be $2,500, in addition to any separate daily or monthly penalty imposed pursuant to item 1 or 2 of this section.

6.	The minimum civil penalty for a violation of section 3321.1 of the New York city building code shall be $5,000. The department may by rule provide that, for a first violation of such section or a first set of such violations that occur substantially at the same time, the minimum penalty may be reduced to $2,500.

7.	The minimum civil penalty for a violation of section 3321.2 of the New York city building code shall be $2,500.

8.	A violation of a condition, restriction or requirement established pursuant to the zoning resolution, section 197-d of the charter or section 25-114, related to a privately owned public space as such term is defined in section 25-114, shall be subject to a civil penalty of not less than $4,000 for the first offense and not less than $10,000 for each subsequent offense, in addition to any separate monthly penalty imposed pursuant to item 2 of this section.

9.	For a violation of section 28-210.1:

9.1.	Unless exception [5.2] 9.2 applies, the minimum civil penalty for a violation of section 28-210.1 in any building involving the illegal conversion, maintenance or occupancy of three or more dwelling units above the number of dwelling units that is legally authorized by the certificate of occupancy or if no certificate of occupancy is required as evidenced by official records shall be $15,000. Each dwelling unit above the number that is legally authorized by the certificate of occupancy or if no certificate of occupancy is required as evidenced by official records shall constitute a separate offense that shall be charged separately and shall be punishable by a separate civil penalty. Provided, however, that the penalties for multiple violations of this exception may be based on the same evidence; and

9.2.	The owner of a building shall not be subject to a civil penalty for a violation of section 28-210.1 in such building if such owner can show the following:

9.2.1.	Such violation was the first such violation issued for such building or was issued within 30 days after such first violation;

9.2.2.	At the time such violation was issued or, if such violation was issued within 30 days after such first violation was issued, the time such first violation was issued, a registration for such building has been properly filed with the department of housing preservation and development in accordance with article two of subchapter 4 of the housing maintenance code; and

9.2.3.	At the time such violation was issued or, if such violation was issued within 30 days after such first violation was issued, the time such first violation was issued, such owner reasonably did not know of, or could not reasonably have known of such illegal conversion, the maintenance thereof or occupancy thereof and takes lawful immediate and diligent steps to cure said violation.

10.	For violations of article 110 of this chapter or chapter 33 of the New York city building code:

10.1.	The minimum civil penalty for an immediately hazardous violation of such article or chapter shall be $2,000, in addition to any separate daily penalty imposed pursuant to item 1 of this section; and

10.2.	The minimum civil penalty for a major violation of such article or chapter shall be $1,000, in addition to any separate monthly penalty imposed pursuant to item 2 of this section.

11.	For (i) a violation of section 28-211.1 or (ii) where a tenant protection plan is required pursuant to section 28-120.1, but has not been submitted to the department, the minimum civil penalty for a first offense shall be no less than $10,000 and, for each subsequent offense, no less than $25,000.

12.	The minimum civil penalty that shall be imposed for a violation of section 27-3017 of this code and the minimum fine that shall be imposed for a violation of such section shall be $4,800. The maximum fine that shall be imposed for a violation of such section shall be $25,000. Such violation may also be punished, in addition to or instead of such fine, by imprisonment of not more than one year.

§28-202.2 Continuing violations. Notwithstanding the assessment of daily penalties, each day that a violation continues shall be a separate and distinct offense.

§28-202.3 Increased civil penalties for construction sites with excessive violations. Subject to the limitations of section 28-202.1, for any violation of this code, the 1968 building code, the zoning resolution or other laws or rules enforced by the department issued to a person who has an existing immediately hazardous or major violation with respect to the construction site for which the violation is being issued, that occurs at a construction site with a violation ratio, at the time of the issuance of such violation, that exceeds the threshold violation ratio for such site, the civil penalty imposed shall be at least twice the civil penalty that would be imposed if such site were not subject to this section 28-202.3. This section 28-202.3 shall have no effect on additional monthly or daily penalties imposed pursuant to section 28-202.1.

Exceptions:

1.	Sites that are the subject of an in rem foreclosure judgment in favor of the city and were transferred by the city to a third party pursuant to section 11-412.1 of the code.

2.	Sites that are the subject of a court order appointing an administrator pursuant to article 7-a of the real property actions and proceedings law in a case brought by the department of housing preservation and development.

3.	Sites that are the subject of a loan provided by or through the department of housing preservation and development or the New York city housing development corporation for the purpose of rehabilitation.

§28-202.3.1 Definitions. The following words and terms shall, for the purposes of section 28-202.3, have the meanings shown herein.

THRESHOLD VIOLATION RATIO. For a major building site, the ninetieth percentile of violation ratios for major building sites in the city as of December 31 of the immediately preceding calendar year. For a construction site that only involves work on a one-, two- or three-family building, the ninetieth percentile of violation ratios for construction sites that only involve work on a one-, two- or three-family building in the city as of December 31 of the immediately preceding calendar year. For a construction site that is not a major building site and that does not only involve work on a one-, two- or three-family building, the ninetieth percentile of violation ratios for construction sites that are not major building sites and that do not only involve work on a one-, two- or three-family building in the city as of December 31 of the immediately preceding calendar year.

VIOLATION RATIO. With respect to a construction site, (i) the number of immediately hazardous violations and major violations issued against such site in the preceding 12 months, excluding any violations that have been dismissed or that are currently in the appeals process, divided by the square footage of the footprint of such site or (ii) an alternative ratio established by department rule and that the department determines is appropriate for identifying construction sites with high rates of immediately hazardous violations, major violations or unsafe conditions for the purposes of this section 28-202.3, provided that such rule is promulgated on or after January 1, 2020.

§28-202.4 Maximum civil penalty for immediately hazardous violation of chapter 33 of the New York city building code that results in death or serious physical injury. Notwithstanding any inconsistent provision of this article, an immediately hazardous violation of a provision of chapter 33 of the New York city building code that results in death or serious physical injury, as such term is defined in article 10 of the New York state penal law, shall be punishable by a civil penalty of not more than $500,000, or not more than $150,000 if such violation is issued to an individual, which may be recovered in a civil action brought by the corporation counsel in the name of the city in any court of competent jurisdiction where:

- There was a substantial probability that the violating condition would cause death or serious physical injury, as such term is defined in article 10 of the New York state penal law;

- The defendant knew, or with reasonable diligence should have known, (i) of the existence of such violation and (ii) was in a position to remedy such violation or lessen the danger posed thereby; and

3.	Such violation resulted in the death or serious physical injury, as such term is defined in article 10 of the New York state penal law, of a person.

§28-202.4.1 Determining the amount of the civil penalty to be imposed. In determining the amount of the civil penalty to be imposed the court shall consider:

- The extent and severity of injury to persons and property;

- The history of violations by the defendant of laws or rules enforced by the department;

- The degree of willfulness, recklessness or negligence displayed by the defendant in committing the violation; and

- The defendant’s financial resources.

ARTICLE 203
CRIMINAL PENALTIES

§28-203.1 Criminal fines and imprisonment. Except as otherwise specified in this code or other law, violations of this code, the 1968 building code, the zoning resolution or other laws or rules enforced by the department shall be punishable by criminal fines and imprisonment within the ranges set forth below:

- Every person convicted of violating a provision of this code, the 1968 building code, the zoning resolution or other law or rule enforced by the department or an order of the commissioner issued pursuant thereto that is classified by the commissioner or the code as an immediately hazardous violation shall be guilty of a misdemeanor punishable by [(i)] a fine of not more than $25,000 or by imprisonment of not more than one year or by both such fine and imprisonment.

- Every person convicted of violating a provision of this code, the 1968 building code, the zoning resolution or other law or rule enforced by the department or an order of the commissioner issued pursuant thereto that is classified by the commissioner or the code as a major violation shall be guilty of a violation punishable by a fine of not more than $10,000 or imprisonment for not more than 15 days or both such fine and imprisonment.

- Every person convicted of violating a provision of this code, the zoning resolution or other law or rule enforced by the department or an order of the commissioner issued pursuant thereto that is classified by the commissioner or the code as a lesser violation shall be guilty of a violation punishable by a fine of not more than $500.

Exceptions:

1. The owner, lessee, occupant, manager or operator of a building affected by a natural or man-made disaster, as determined by the commissioner, shall not be subject to a criminal fine or imprisonment if notice of such violation was issued during the 90-day-period immediately after such disaster or, in the case of a major natural or man-made disaster as determined by the commissioner, during the six-month period immediately after such disaster. This exception shall not apply to immediately hazardous violations, violations charged as aggravated violations or violations without connection to such disaster.

2. The owner, lessee, occupant, manager or operator of a building where a violation occurs shall not be subject to a criminal fine or imprisonment for such violation if (i) such violation was connected to a natural or man-made disaster, as determined by the commissioner, and (ii) such building is undergoing, or scheduled or under evaluation for, work or acquisition through a city operated disaster recovery program responding to such disaster.

3. The owner, lessee, manager or operator of a building shall not be subject to criminal fines or imprisonment for a violation resulting from work done by a city employee or third party under contract with the city, in response to a natural or man-made disaster. This exception shall not apply to immediately hazardous violations or violations charged as aggravated violations.

4. The minimum fine for an immediately hazardous violation of article 110 of this chapter or chapter 33 of the New York city building code shall be $2,000.

5. The minimum fine for a major violation of article 110 of this chapter or chapter 33 of the New York city building code shall be $1,000.

6.	For (i) a violation of section 28-211.1 or (ii) where a tenant protection plan is required pursuant to section 28-120.1, but has not been submitted to the department, the minimum fine shall be no less than $10,000 and, for each subsequent offense, no less than $25,000.

§28-203.2 Continuing violations. In the case of continuing violations each day’s continuance shall be a separate and distinct offense.

ARTICLE 204
ENVIRONMENTAL CONTROL BOARD

§28-204.1 General. Any person who shall violate or fail to comply with any of the provisions of this code, the 1968 building code, the zoning resolution or other laws or rules enforced by the department or with any order issued pursuant thereto shall be liable for a civil penalty that may be recovered in a proceeding before the environmental control board. Such proceeding shall be commenced by the service of a notice of violation returnable before the board. Such notice of violation may be issued by employees of the department or of other city agencies designated by the commissioner and may be served by such employees or by a licensed process server.

§28-204.1.1 Violations of section 3321 of the New York city building code. In addition to any other penalties or remedies provided by law or rule, the following items shall apply to violations of section 3321 of the New York city building code:

- Upon determining that a worker at a building site is not in compliance with section 3321.1 of the New York city building code:

  - The commissioner shall issue a notice of violation to the owner of such site, each permit holder responsible for ensuring that such worker complies with such section at such site and the person who employed or otherwise engaged such worker at such site if such person can reasonably be identified. Each such worker shall constitute a separate violation that shall be noticed and charged separately and shall be punishable by a separate civil penalty. It shall be an affirmative defense to such a violation that such worker provided such owner, permit holder or the person who employed or otherwise engaged such worker at such site with an SST card, SST supervisor card, limited SST card, temporary SST card or documentation establishing training in compliance with such section, as appropriate, that reasonably appeared to be valid and applicable to such worker and such owner, permit holder or such person reasonably relied thereon.

  - In addition to the requirements of any other law or rule, such violation shall not be deemed corrected until the commissioner determines that, for each such worker, the recipient of such violation shows, in a form and manner established by the commissioner, that such owner, a person acting on behalf of such owner, a permit holder responsible for ensuring that such worker complies with such section at such site or the person who employed or otherwise engaged such worker at such site has entered into a binding agreement that satisfies each of the following conditions:

    - Pursuant to such agreement, such owner, a person acting on behalf of such owner or a permit holder responsible for ensuring that such worker complies with such section at such site or the person who employed or otherwise engaged such worker at such site shall pay, either directly or indirectly, for the costs of such worker to obtain the training required to comply with such section or will otherwise arrange for such worker to receive such training at no cost to such worker.

    - Pursuant to such agreement, and provided that such worker is diligently endeavoring to complete the training required by such section, such worker shall continue to be employed or otherwise engaged under the same terms and conditions that applied before such determination by the commissioner until (i) such worker successfully completes the training required to comply with such section, (ii) work for which such worker was employed or otherwise engaged at such site concludes or (iii) 60 days elapses after such determination, whichever occurs earlier, except that, during such period, such worker shall be paid as if such worker were working at such site 40 hours each week at the same hourly or effective hourly wage such worker was paid before such determination by the commissioner.

- Upon determining that a permit holder at a building site has not maintained a daily log in compliance with section 3321.2 of the New York city building code, a notice of violation shall be issued to the owner of such site and such permit holder. Failure to maintain such a log establishes a rebuttable presumption that each worker for whom such permit holder is responsible for ensuring compliance with section 3321 of the New York city building code is not compliant with such section and shall result in the issuance of notices of violation under Item 1.

- Upon a finding by the office of administrative trials and hearings, acting pursuant to section 1049-a of the New York city charter, or a court of competent jurisdiction that a second or subsequent violation of section 3321 of the New York city building code has occurred at a building site, the commissioner shall conduct at least one unannounced inspection of such site at least once every three months to determine compliance with such section. Such inspections shall continue until at least two consecutive inspections do not result in the issuance of a notice of violation of such section.

- Upon a finding by the office of administrative trials and hearings, acting pursuant to section 1049-a of the New York city charter, or a court of competent jurisdiction that the owner of a building site, a permit holder at such site or a person employing or otherwise engaging workers at such site has violated section 3321 of the New York city building code and such violation is a second or subsequent violation of such section by such owner, permit holder or person, the commissioner shall conduct at least one unannounced inspection of (i) each building site owned by such owner, if such violation is a second or subsequent violation by such owner, (ii) each building site where such permit holder works, if such violation is a second or subsequent violation by such permit holder and (iii) each building site where such person works, if such violation is a second or subsequent violation by such person.

§28-204.1.2 Notice of violating conditions outside of occupied dwelling units. An owner must post a copy of a notice of violation that relates to a violating condition outside of an occupied dwelling unit, including in a common area or affecting all residents, of such owner’s building in a conspicuous manner in the building’s lobby until such violation has been closed. In addition, such owner shall post a flyer or pamphlet, created by the department, with information about the adjudication process. Such notice of violation and flyer or pamphlet shall be posted as soon as practicable, but no later than five calendar days after it has been served.

§28-204.1.3 Notice to occupants of violating conditions in occupied dwelling units. An owner must distribute a copy of a notice of violation to the resident of an occupied dwelling unit where such violation relates to a violating condition that is present within such dwelling unit, and to residents of occupied dwelling units adjacent to such dwelling unit. In addition, such owner shall provide such residents with a flyer or pamphlet, created by the department, with information about the adjudication process. Such notice of violation and flyer or pamphlet shall be distributed to such occupied dwelling units as soon as practicable, but no later than five calendar days after it has been served.

§28-204.2 Order to certify correction. Each such notice of violation shall contain an order of the commissioner directing the respondent to correct the condition constituting the violation and to file with the department electronically or in such other manner as the department may authorize by rule a certification that the condition has been corrected. Unless otherwise provided by rule, such order shall require that violations classified as major or lesser be corrected within 30 days from the date of the order, that violations classified as immediately hazardous be corrected forthwith. Such order shall also require that certification of the correction of the violation shall be filed with the department in a manner and form and within such period of time as shall be established by the department. In any proceeding before the environmental control board, no civil penalty shall be imposed for a lesser violation if the respondent complies with the commissioner’s order to correct and to certify correction of the violation within the applicable time period. However, such violation may serve as a predicate for purposes of assessing aggravating factors attributable to multiple offenses.

§28-204.3 Failure of proof. In any proceeding before the environmental control board, if [the board finds] it is found that the commissioner has failed to prove the violation charged, the order requiring the respondent to correct the condition constituting the violation and to file a certification of correction shall be deemed dismissed.

§28-204.4 Failure to certify the correction of a violation. Failure to comply with an order of the commissioner issued pursuant to section 28-204.2 or pursuant to any provision of law or rule enforced by the department in effect at the time the order was issued to correct and to certify correction of a violation within the applicable time period shall be a violation of this code for which penalties may be imposed in addition to the penalties that may be or have been imposed for the violation referred to in such order. Upon application, for good cause, the commissioner may extend the time for filing the certification of correction of a violation, but not for more than 30 days for each extension.

§28-204.5 False statements in certification of correction. For the purposes of this section [28-204.5] , if the environmental control board finds that a certification of correction filed pursuant to section 28-204.2 contained material false statements relating to the correction of a violation, such certification of correction shall be null and void and the penalties set forth in this code for the violation may be imposed as if such false certification had not been filed with and accepted by the department. It shall be an affirmative defense that the respondent neither knew nor should have known that such statements were false.

§28-204.6 Enforcement of environmental control board judgments as a [Tax] tax lien. [Enforcement of] Notwithstanding any provision of law to the contrary, environmental control board judgments [against owners] for certain building code violations shall be entered against the owner and enforced as a tax lien against the property, as provided below. [Notwithstanding any provision of law to the contrary, an] An environmental control board judgment against an owner for a building code violation with respect to (i) a private dwelling, a wooden-framed single room occupancy multiple dwelling, or a dwelling with a legal occupancy of three or fewer dwelling units, (ii) a violation of section 28-210.1 involving the illegal conversion, maintenance or occupancy of three or more dwelling units than are legally authorized by the certificate of occupancy or if no certificate of occupancy is required as evidenced by official records, (iii) a building that contains twenty or more dwelling units, or that contains any space classified in an occupancy group other than occupancy group R, where the total value of all such judgments against such building is $60,000 or more, or (iv) a building that contains only space classified in occupancy group R and no fewer than six and no more than nineteen dwelling units, where the total value of all such judgments against such building is $30,000 or more, shall [constitute a tax lien on the] result in a tax lien being entered against the property named in the violation [with respect to] for which such judgment was rendered, as hereinafter provided. [Such liens shall be entered and enforced as provided in this section 28-204.6.]

Exception. Notwithstanding any provision of law to the contrary, an environmental control board judgment shall not constitute a tax lien on the property named in the violation with respect to which such judgment was rendered where:

- Such property was the subject of an in rem foreclosures judgment in favor of the city and was transferred by the city to a third party pursuant to section 11-412.1 of the administrative code within five years of such judgment.

- Such property is the subject of a court order appointing an administrator pursuant to article 7-A of the real property actions and proceedings law in a case brought by the department of housing preservation and development.

- Such property is the subject of a loan provided by or through the department of housing preservation and development or the New York city housing development corporation for the purpose of rehabilitation that had closed within five years before such judgment.

§28-204.6.1 Record of unpaid judgments. [There shall be filed in the office of the] The department of finance shall keep a record of all such unpaid judgments. Such records shall be kept by tax lot and block number and shall be accessible to the public during business hours. An entry of a judgment on the records of the department shall constitute notice to all parties.

[§28-204.6.1 Tax lien reporting. On December 31, 2018, the department of finance shall submit a report to the mayor and the council on tax lien activities as a result of environmental control board judgment debt. Such report shall include: (i) the number of buildings subject to tax liens for environmental control board judgment debts, disaggregated by whether the tax lien was a result of an illegal conversion, more than $60,000 in debt, or more than $30,000 in debt; (ii) the location of such buildings disaggregated by council district; (iii) the number of dwelling units in each building which is subject to a tax lien; and (iv) recommendations for whether a 25 percent lien to value ratio is an appropriate threshold for a property to be considered distressed and if it is not, such report shall contain recommendations for what an appropriate threshold would be.]

§28-204.6.2 Lien. All such unpaid judgments shall constitute a lien upon the property named in the violation with respect to which such judgment was rendered when the amount shall have been definitely computed as a statement of account by the department, and the department shall file such statement with the department of finance for entry against the property. Such lien shall have a priority over all other liens and encumbrances except for the lien of taxes and assessments. However, no lien created pursuant to this section 28-204.6 shall be enforced against a subsequent purchaser in good faith or mortgagee in good faith unless the requirements of section 28-204.6.1 are satisfied.

§28-204.6.3 Notice. A notice, stating the amount due and the nature of the charge, shall be mailed by the department of finance to the last known address of the person whose name appears on the records of the department of finance as being the owner or agent of the property or as the person designated by the owner to receive tax bills or, where no name appears, to the property, addressed to either the “owner” or the “agent.”

§28-204.6.4 Mailing. Such notice mailed by the department of finance pursuant to this section 28-204.6.4 shall have stamped or printed thereon a reference to section [204.6] 28-204.6.

§28-204.6.5 Failure to pay charge. If such charge is not paid within 30 days from the date of entry, it shall be the duty of the department of finance to receive interest thereon at the same rate as unpaid real property taxes, to be calculated to the date of payment from the date of entry.

§28-204.6.6 Enforcement of lien. Such charge and the interest thereon shall continue to be, until paid, a lien on the property. Any remedy or procedure available for the enforcement of tax liens against such property, including, but not limited to, any sale of a tax lien or any foreclosure of a tax lien, shall be available with respect to such tax lien. In addition, such tax lien may be satisfied in accordance with the provisions of section 1354 of the real property actions and proceedings law.

§28-204.6.7 Validity of lien. In any proceeding to enforce or discharge a lien created pursuant to this section 28-204.6, the validity of the lien shall not be subject to challenge based on the lawfulness of the judgment, except as provided in this section 28-204.6.

§28-204.6.8 Challenge. No such challenge may be made except by the owner of the property or a mortgagee or lienor whose mortgage or lien would, but for the provisions of this section 28-204.6, have priority over the department’s lien.

§28-204.6.9 Notice to mortgagees and lienors. Notwithstanding the foregoing provisions, no such judgment shall be entered and enforced as a tax lien against any property unless at the time of the issuance of the notice of violation a copy of such notice was also served on all mortgagees and lienors of record of such property by mail addressed to the recorded addresses of such mortgagees and lienors.

§28-204.6.10 Non-exclusive remedy. The procedures provided in this section 28-204.6 for the enforcement of environmental control board judgments against owners shall be in addition to any other methods provided under any other provision of law for the enforcement of such judgments.

§28-204.6.11 Tax lien reporting. On December 31, 2018, the department of finance shall submit a report to the mayor and the council on tax lien activities as a result of environmental control board judgment debt. Such report shall include: (i) the number of buildings subject to tax liens for environmental control board judgment debts, disaggregated by whether the tax lien was a result of an illegal conversion, more than $60,000 in debt, or more than $30,000 in debt; (ii) the location of such buildings disaggregated by council district; (iii) the number of dwelling units in each building which is subject to a tax lien; and (iv) recommendations for whether a 25 percent lien to value ratio is an appropriate threshold for a property to be considered distressed and if it is not, such report shall contain recommendations for what an appropriate threshold would be.

ARTICLE 205
CIVIL JUDICIAL PROCEEDINGS

§28-205.1 Civil judicial enforcement. The owner, lessee, person in charge, or occupant of any building, structure, premises, equipment or part thereof, where a violation of this code, the 1968 building code, the zoning resolution or of other laws or rules enforced by the department or any order issued by the commissioner shall exist or the agent, architect, builder, contractor, engineer, or any other person who commits or assists in any such violation or who maintains any building, structure, premises, equipment or part thereof where any such violation shall exist shall be subject to an action or proceeding to restrain, correct or abate such violation, or to compel compliance with such order. Upon request of the commissioner, the corporation counsel may institute judicial actions or proceedings seeking such relief. In addition to any other remedies, in any such action or proceeding the defendant or respondent shall be subject to the payment of civil penalties as provided in this code.

§28-205.1.1 Corporation counsel. Such actions and proceedings may be instituted by the corporation counsel in the name of the city in any court of competent jurisdiction in the city and shall be given preference over pending causes therein. In such actions or proceedings, the city may apply for restraining orders, preliminary injunctions or other provisional remedies, with or without notice; and no undertakings shall be required as a condition to the granting or issuing of any such order, injunction or remedy, or by reason thereof. No court shall lose jurisdiction of any action or proceeding hereunder by reason of a plea that the title to real estate is involved if the object of the action is to recover a penalty for the violation of any of the provisions of this code.

§28-205.1.1.1 Naming the building as a defendant. The corporation counsel shall name as defendants the building, structure, or premises where the violation shall exist by describing it by block, lot number, and street address and at least one of the owners of some part of or interest in the building, structure, or premises.

§28-205.1.1.2 In rem jurisdiction over the building. In rem jurisdiction over the building, structure, or premises where the violation shall exist shall be complete by affixing the summons to the door of the building, structure, or premises and by mailing the summons by certified or registered mail, return receipt requested, to one of the owners of some part of or interest in the building, structure, or premises. Proof of service shall be filed within two days thereafter with the clerk of the court designated in the summons. Service shall be complete upon such filing.

§28-205.1.1.3 Service on other defendants. Defendants, other than the building, structure, or premises where the violation shall exist, shall be served with the summons as provided in the civil practice law and rules.

§28-205.1.2 Presumptive evidence. In any action or proceeding founded upon a claim by the commissioner that any law or rule enforceable by the department has been violated, or that a lawful order issued by such commissioner has not been complied with, the following presumptions shall apply:

§28-205.1.2.1 Presumption of commissioner certificate. A certificate in writing by the commissioner, or his or her authorized representative, shall be presumptive evidence of any matter stated therein.

§28-205.1.2.2 Presumption of ownership. The person in whose name the real estate affected by the action is recorded in the office of the city register or the county clerk, as applicable, shall be presumed to be the owner thereof.

§28-205.1.2.3 Presumption of employment or agency. Whenever there is evidence that a person was the manager, operator, or supervisor or, in any other way, in charge of the premises, at the time the violation occurred, such evidence shall be presumptive that he or she was an agent or employee of the owner and/or lessee of the building, structure, or premises.

§28-205.1.2.4 Presumption of electronic signature and electronic submission. Anyone who receives access to an account for electronic filing from the department shall be presumed to have personally submitted or authorized the submission of all documents submitted to the department from that account and to have personally electronically signed all documents required to be electronically signed from such account.

§28-205.1.3 Costs. In no case shall the department, or any officer or employee thereof, be liable for costs in any such action or proceeding; and officers and employees of the department, acting in good faith and without malice, shall be free from liability for acts done in any such action or proceeding.

§28-205.1.4 Lien. Any judgment rendered in any such action or proceeding shall be and become a lien upon the premises named in the complaint in such action or proceeding, if any, the lien to date from the time of filing a notice of pendency in the office of the clerk of the county in which the premises is located, and to have priority before any mortgage or other lien existing prior to such filing, except tax and assessment liens.

§28-205.1.5 Notice of pendency. The notice of pendency referred to in this section 28-205.1.5 may be filed at the commencement of judicial proceedings; provided the commissioner may deem such action to be necessary. Any notice of pendency filed pursuant to the provisions of this code may be vacated and cancelled of record upon an order of a justice of the court in which such action or proceeding was instituted or is pending, or upon the consent in writing of the corporation counsel. The clerk of the county where the notice is filed is hereby directed and required to mark any such notice of pendency, and any record or docket thereof, as vacated and cancelled of record upon the presentation and filing of a certified copy of such order or consent.

ARTICLE 206
CRIMINAL JUDICIAL PROCEEDINGS

§28-206.1 Criminal judicial enforcement. The owner, lessee, person in charge, or occupant of any building, structure, premises, equipment or part thereof, where a violation of this code, the 1968 building code, the zoning resolution or of other laws or rules enforced by the department or any order issued by the commissioner shall exist or the agent, architect, builder, contractor, engineer, or any other person who commits or knowingly assists in any such violation or who maintains any building, structure, premises, equipment or part thereof where any such violation shall exist shall be guilty of a criminal offense punishable by a fine or imprisonment or both a fine and imprisonment in accordance with this code.

§28-206.1.1 Other penalties. The criminal penalties provided by this code shall be in addition to or alternative to any civil sanctions authorized to be imposed for an unlawful use or condition cited in this code.

ARTICLE 207
PEREMPTORY ORDERS

§28-207.1 Contents and service. Peremptory orders issued by the commissioner shall contain a description of the building, structure, premises, equipment or subject matter affected, and shall be designated by address where applicable. Such orders may be served personally or by posting at the premises followed by regular mail, by any officer or employee of the department, or by any person authorized by the commissioner.

§28-207.2 Stop work orders. Whenever the commissioner has issued a notice of proposed revocation pursuant to section 28-105.10.1 of this code or finds that any building work is being executed in violation of the provisions of this code, the 1968 building code, the zoning resolution or of any laws or rules enforced by the department, or in a dangerous or unsafe manner, the commissioner or his or her authorized representative may issue a stop work order.

§28-207.2.1 Issuance. Upon issuance of a stop work order by the commissioner, all work shall immediately stop unless otherwise specified. Such order may require all persons to forthwith vacate the premises pursuant to the provisions of section 28-207.4 and may also require such work to be done as, in the opinion of the commissioner, may be necessary to remove any danger therefrom. The police department or other law enforcement agency or officer shall, upon the request of the commissioner, assist the department in the enforcement of [this] section 28-207.2. The stop work order may be given verbally or in writing to the owner, lessee or occupant of the property involved, or to the agent of any of them, or to the person or persons executing the work. A verbal order shall be followed promptly by a written order and shall include the reason for the issuance of the stop work order. All written orders issued pursuant to section 28-207.2 shall be posted upon the premises and made available to the public.

§28-207.2.2 Unlawful continuance. No person shall with knowledge or notice of a stop work order allow, authorize, promote, continue or cause to be continued any work covered by the stop work order, except such work that may be required by order of the commissioner.

§28-207.2.3 Rescission. Upon application, the commissioner shall rescind the stop work order when the condition that gave rise to its issuance has been corrected and either all civil penalties or criminal fines assessed for any violation of such order have been paid or, where a violation is pending, security for the payment of such penalties or fines has been posted in accordance with department rules, or where the stop work order was issued in error or conditions are such that it should not have been issued. The commissioner may by rule require the payment of a fee in the amount of the expense of additional inspection and administrative expense related to such stop work order.

§28-207.2.4 Mandatory stop work orders. The commissioner shall issue stop work orders in the circumstances set forth below. Upon issuance of such stop work order, the work shall immediately stop and shall not resume until the stop work order is rescinded by the department. The stop work order shall not be rescinded less than two business days after the date of issuance of such order. Nothing in the following sections shall be construed to limit the commissioner’s power to issue stop work orders in other circumstances.

§28-207.2.4.1 Scaffold safety. A stop work order shall be issued if a permit holder or person directly in charge of any suspended scaffold supported by c-hooks or outrigger beams fails to notify the department prior to the installation or use of such equipment as required by section [3314.1.1] 3314.4.1.5 of the New York city [Building] building code and either:

- The rigger does not hold a license required by this code, or

- The workers lack certificates of fitness as required by this code or applicable rule, or

- The rigger failed to file with the department satisfactory evidence of insurance required by this code.

§28-207.2.5 Tampering. It shall be unlawful to tamper with, remove or deface a written posted stop work order from the location where it was affixed unless and until such stop work order has been rescinded by the commissioner. The owner or other person in control of the location shall ensure that the stop work order remains posted until rescinded by the commissioner.

§28-207.2.6 Penalties. In addition to the penalties provided for in this chapter, any person who fails to comply with a stop work order shall be liable for a civil penalty in the amount of $6,000 for the initial violation and $12,000 for every subsequent violation, to be paid to the department prior to the rescission of the stop work order; provided, however, this shall not apply to any work performed to remedy an unsafe or hazardous condition as authorized by order of the commissioner.

§28-207.3 Public nuisance. Whenever any building, structure, place or premises is or may be perilous to life or property by reason of the nature or condition of its contents, its use, the overcrowding of persons therein, defects in its construction, or deficiencies in fire alarm, fire extinguishing equipment or fire escape equipment, or by reason of any condition in violation of law or order of the commissioner, the commissioner may declare that the same, to the extent that the commissioner may specify, is a public nuisance and may order the same to be removed, sealed, abated, repaired, altered or otherwise improved.

§28-207.3.1 Rescission. Upon application, the commissioner shall rescind such order when the condition that gave rise to its issuance has been corrected or where the declaration was issued in error or conditions are such that it should not have been issued. The commissioner may by rule require the payment of a fee in the amount of the expense of additional inspection and administrative expense related to such order.

§28-207.4 Vacate order. [In case any order to remedy] Where there is a condition that is or may be imminently perilous, dangerous or detrimental to life, public safety or property, [issued by the commissioner is not] or where an order to remedy such condition has not been immediately complied with, or the commissioner determines that an emergency exists requiring such action, the commissioner may order and immediately cause any building, structure, place or premises to be vacated. The vacate order may be given verbally or in writing to the owner, lessee or occupant of the property involved, or to the agent of any of them, or to the person or persons executing the work. [A] Any verbal order to vacate shall be followed promptly by a written order and shall include the reason for the issuance of the vacate order. The written vacate order shall include the date by which the owner shall certify the correction of any and all violations giving rise to such vacate order.

§28-207.4.1 Basis for vacate. Conditions for which the commissioner may issue a vacate order shall include but shall not be limited to the following conditions that create a hazard to life, public safety, or property:

- Danger of structural failure;

- Danger of façade failure;

- Inadequate fire protection, detection, or  suppression;

- Inadequate egress; [or]

5.	Improper storage of hazardous [materials] , combustible or toxic [.] materials; or

6.	Defective or unlawful gas work.

§28-207.4.2 Enforcement of vacate order. All orders issued pursuant to this section 28-207.4 shall be posted upon the premises and made available to the public. Upon the posting of an order upon the premises, officers and employees of the police department, the department, and other authorized officers and employees of the city shall immediately act upon and enforce such order. The police department shall provide all reasonable assistance to the department and other authorized officers and employees necessary to carry out the provisions of [this] section 28-207.4. A copy of the vacate order may be filed with the county clerk of the county in which the premises is located and shall be filed with the department and accessible to the public. Such filing shall be notice of the vacate order to any subsequent owner and such owner shall be subject to such order.

§28-207.4.3 Penalties. In addition to the penalties provided for in this chapter, the owner of a premises where the terms of a vacate order are violated shall be liable for a civil penalty in the amount of $6,000 for the initial violation and $12,000 for every subsequent violation, to be paid to the department prior to the rescission of the vacate order.

[§28-207.4.3] §28-207.4.4 Rescission. Upon application, the commissioner may rescind the vacate order when the condition that gave rise to its issuance has been corrected [and either all civil penalties or criminal fines assessed for any violation of such order have been paid or, where a violation is pending, security for the payment of such penalties or fines has been posted in accordance with department rules], any civil penalty pursuant to section 28-207.4.3 has been paid, or where the vacate order was issued in error or conditions are such that it should not have been issued. The commissioner may by rule require the payment of a fee in the amount of the expense of additional inspection and administrative expense related to such vacate order.

[§28-207.4.4] §28-207.4.5 Tampering. It shall be unlawful to remove or deface a written posted vacate order from the location where it was affixed unless and until such vacate order has been rescinded by the commissioner. The owner or other person in control of the location shall ensure that the vacate order remains posted until rescinded by the commissioner.

§28-207.4.6 Unlawful continuance. No person shall with knowledge or notice of a vacate order allow, authorize, promote, continue or cause to be continued any occupancy or use covered by the vacate order.

§28-207.5 Cease use orders for service equipment. Whenever the commissioner determines that the operation of any service equipment is or may be dangerous to life, health or safety, the commissioner may issue a cease use order requiring such equipment to be shut down or sealed or otherwise made inoperable. Upon the issuance of such order a tag or notice shall be affixed to the device warning that the equipment is unsafe for operation. It shall be unlawful to operate such equipment or to remove or deface such tag unless and until the cease use order is rescinded by the commissioner. The owner or other person in control of the service equipment shall ensure that such tag or notice remains affixed until rescinded by the commissioner.

§28-207.5.1 Rescission of cease use order. Upon application, the commissioner may rescind the cease use order when the condition that gave rise to its issuance has been corrected and either all civil penalties or criminal fines assessed for any violation of such order have been paid or, where a violation is pending, security for the payment of such penalties or fines has been posted in accordance with department rules or where the cease use order was issued in error or conditions are such that it should not have been issued. The commissioner may by rule require the payment of a fee in the amount of the expense of additional inspection and administrative expense related to such cease use order.

ARTICLE 208
COMMISSIONER’S REQUEST FOR CORRECTIVE ACTION

§28-208.1 Commissioner’s request for corrective action. As an alternative to the issuance of an order or notice of violation, the commissioner may issue a request for corrective action to any person responsible for any claimed unlawful use or condition in any premises. Each request for corrective action shall have the commissioner’s signature affixed thereto; but the commissioner may authorize any subordinate to affix such signature, including an electronic signature.

§28-208.1.1 Contents and delivery. The request for corrective action shall contain a description of the building, structure, premises, equipment or subject matter affected, shall be designated by address, where applicable, shall be sent by regular mail or upon consent by electronic means to the owner, lessee, person in charge, or occupant of the building, structure, premises, equipment or to any person responsible for the unlawful use or condition at the last known address for such person. Requests for corrective action may be sent to a managing agent or other person specifically designated by the owner to attend to such requests on behalf of the owner. Each such request shall describe the unlawful use or condition, call upon the person addressed to correct it and to inform the department of the action taken. A time for correction or response shall be specified. A request for corrective action may be given orally, followed within a reasonable time by a writing as described in this section 28-208.1.1. A request for corrective action shall provide notice that failure to respond to such a request may result in the imposition of a fee for any subsequent inspection that results in the issuance of a notice of violation for the condition.

§28-208.1.2 Public record. The department shall keep a record, available to the public, of requests for corrective action issued pursuant to this article. The record of a request for corrective action shall be reflected as withdrawn upon submission to the department of a statement in a form prescribed by rule indicating that the use or condition has been corrected or did not exist or following an inspection by the department that confirms correction. A request for corrective action may be issued in response to a complaint or inspection.

§28-208.1.3 Other remedies not precluded. Nothing in this article shall be construed to limit the power of the commissioner to take any other action authorized by this code with respect to any unlawful use or condition including, but not limited to, the commencement of an action or proceeding in a court or before the environmental control board or other administrative tribunal or the issuance of a peremptory order or to require that the commissioner issue a request for corrective action as a prerequisite to any other enforcement action.

ARTICLE 209
COMMISSIONER’S ORDER TO CORRECT UNLAWFUL USE OR CONDITION

§28-209.1 General. The commissioner may issue an order to the persons responsible for any unlawful use or condition in any premises directing such person to correct the unlawful use or condition. Each such order shall have the commissioner’s signature affixed thereto; but the commissioner may authorize any subordinate to affix such signature, including an electronic signature.

§28-209.2 Contents and service of order. All orders issued by the commissioner shall contain a description of the building, structure, premises, equipment or subject matter affected, and shall be designated by address where applicable. All such orders shall be served by regular mail or, upon consent, electronically. Such orders may be served by any officer or employee of the department, or by any person authorized by the commissioner. An order may be given orally, followed within a reasonable time by a written order as described in this section 28-209.2. Failure to comply with a commissioner’s order within the stated time period shall be a violation of this code punishable by civil penalties or criminal fines and imprisonment as set forth in this code. Proof of compliance with a commissioner’s order shall consist of certification as prescribed by the rules of the department.

ARTICLE 210
ILLEGAL CONVERSIONS

§28-210.1 Illegal residential conversions. It shall be unlawful, except in accordance with all requirements of this code, to convert any dwelling for occupancy by more than the legally authorized number of families or to assist, take part in, maintain or permit the maintenance of such conversion. Upon the finding of such violation and the imposition of punishment for such violation as set forth in this code the department or if applicable the environmental control board shall forward to the internal revenue service, the New York state department of taxation and finance and the New York city department of finance the name and address of the respondent or defendant, the address of the building or structure with respect to which the violation occurred and the time period during which the violation was found to have existed.

§28-210.1.1 Inspection; failure to gain access to premises. Upon receiving a complaint of a condition relating to a building or part thereof that would, if observed by the commissioner, be identified by the commissioner as a violation of section 28-210.1 involving the illegal conversion, maintenance or occupancy of three or more dwelling units than are legally authorized by the certificate of occupancy or if no certificate of occupancy is required as evidenced by official records, the commissioner shall attempt to enter and inspect such building or part thereof. After two unsuccessful attempts to gain access to such building or part thereof, the commissioner shall request the corporation counsel to make an application in any court of competent jurisdiction for an ex parte administrative warrant directing the entry and inspection of such premises or location and to issue violations found upon access to such premises or locations. In preparing such requests, priority may be given by the commissioner to requests based on the degree of hazard to safety or property that the commissioner believes present. Such counsel shall promptly consider such request, and where such counsel determines that there is appropriate basis to obtain such an order, shall seek such an order. The commissioner shall promptly execute any such order in accordance with its terms.

§28-210.2 Illegal industrial or manufacturing conversions. Except as otherwise provided by section 42-03 of the zoning resolution and the multiple dwelling law, it shall be unlawful, except in accordance with all requirements of this code, to convert to residential use any space legally authorized for occupancy for industrial or manufacturing use or to assist, take part in, maintain or permit the maintenance of such conversion. Upon the finding of such violation and the imposition of punishment for such violation as set forth in this code the department, or, if applicable, the environmental control board shall forward to the internal revenue service, the New York state department of taxation and finance and the New York city department of finance the name and address of the respondent or defendant, the address of the building or structure with respect to which the violation occurred and the time period during which the violation was found to have existed.

§28-210.3 Illegal conversions of dwelling units from permanent residences. Except as otherwise provided in subdivision 16 of section 67 of the multiple dwelling law and section 120 of the multiple dwelling law, dwelling units within (i) a class A multiple dwelling as defined in section 27-2004 of the administrative code, (ii) occupancy group J-2 as described in section 27-265 of the administrative code or (iii) occupancy group R-2 as described in section [310.1.2] 310.4 of the New York city building code shall be used only for permanent residence purposes as required pursuant to subparagraph a of paragraph eight of subdivision a of section 27-2004 of the administrative code. It shall be unlawful for any person or entity who owns or occupies a multiple dwelling or dwelling unit classified for permanent residence purposes to use or occupy, offer or permit the use or occupancy or to convert for use or occupancy such multiple dwelling or dwelling unit for other than permanent residence purposes. For the purposes of this section a conversion in use of a dwelling unit may occur irrespective of whether [any] physical changes have been made to such dwelling unit. The provisions of this section shall not be construed to prohibit lawful accessory uses permitted pursuant to the zoning resolution or the lawful conversion of dwellings in accordance with applicable law.

§28-210.3.1 Reporting on illegal conversions of dwelling units from permanent residences. By no later than September 1 of each year, the department shall, with the cooperation of the mayor’s office of special enforcement and all other relevant city agencies, submit a report to the council including, but not limited to, the following information for the previous year, disaggregated by council district:

1.	The number of complaints received by the department alleging the conversion of dwelling units for other than permanent residence purposes;

2.	The number of inspections conducted by the city in response to suspected conversions of dwelling units for other than permanent residence purposes;

3.	The number of notices of violation issued for conversions of dwelling units for other than permanent residence purposes;

4.	The amount of civil penalties imposed for such violations and the amount of such penalties collected;

5.	For each inspection resulting in the issuance of a notice of violation:

5.1.	The name of the owner and the address of the building to which such notice of violation was issued; and

5.2.	The number and type of violations issued, disaggregated by whether such violations are upheld, pending or dismissed;

6.	For each inspection resulting in the issuance of a notice of violation pursuant to section 28-210.3:

6.1.	Whether each such notice of violation was classified as immediately hazardous pursuant to item 16 of section 28-201.2.1;

6.2.	For each such immediately hazardous violation, whether the notice of violation was for the illegal conversion of more than one dwelling unit or for a second or subsequent offense; and

6.3.	The number of notices of violation issued pursuant to section 28-210.3 to the building in the five years preceding the submission date of the report.

§28-210.4 Unlawful advertisement for certain occupancies.  It shall be unlawful to advertise occupancy or use of dwelling units in a class A multiple dwelling for occupancy that would violate subdivision eight of section four of the multiple dwelling law defining a "class A" multiple dwelling as a multiple dwelling that is occupied for permanent residence purposes.

§28-210.4.1 Enforcement.  The provisions of section 28-210.4 shall be enforced by the mayor’s office of special enforcement.  Any person found to have violated the provisions of section 28-210.4 shall be liable for a civil penalty of not more than $1,000 for the first violation, $5,000 for the second violation and $7,500 for the third and subsequent violations.

§28-210.4.2 Definition.  For the purposes of this section, the term "advertise" shall mean any form of communication, promotion or solicitation, including but not limited to direct mail, newspapers, magazines, flyers, handbills, television commercials, radio, signage, electronic mail, websites, text messages or similar displays, intended or used to induce, encourage or persuade the public to enter into a contract for goods and/or services.

ARTICLE 211
FALSE STATEMENTS

§28-211.1 False statements in certificates, forms, written statements, applications, reports, or certificates of correction. It shall be unlawful for any person to knowingly or negligently make or allow to be made a material false statement in any certificate, professional certification, form, signed statement, application, report or certification of the correction of a violation that is either submitted directly to the department or that is generated with the intent that the department rely on its assertions.

§28-211.1.1 Rebuttable presumption. In any proceeding that relates to a false statement in a certification of correction of a violation filed in compliance with section 28-204.2 if an inspection made within six months after the filing of the certification finds a condition constituting a violation that is the same as the condition described in the notice of violation with respect to which such certification was filed, there shall be a rebuttable presumption that the condition described in such notice of violation continued and is the same condition found in the inspection.

§28-211.1.2 Additional penalty for false statements. In addition to any other penalty provided by law, the commissioner may refuse to accept an application or other document submitted pursuant to or in satisfaction of a requirement of this code or of a rule of any agency promulgated there under that bears the signature of a person who has been found, after a hearing at the office of administrative trials and hearings pursuant to the department’s rules, to have knowingly or negligently made a false statement or to have knowingly or negligently falsified or allowed to be falsified any certificate, form, signed statement, application, report or certification of the correction of a violation required under the provisions of this code or of a rule of any agency promulgated there under.

§28-211.1.3 Notification to other government agencies. Where the department makes a determination that a person has violated section 28-211.1, the department shall send written notice to the council, the department of investigation, New York state division of housing and community renewal and the state tenant protection unit, and shall refer such finding to the district attorney of the county in which the property is located and the state attorney general.

§28-211.1.4 [.] Reporting. By no later than January 30 of each year, the department shall submit a report to the mayor and to the speaker of the council that indicates the actions it took in every instance in which it made a determination that a person had violated section 28-211.1.

§28-211.2 Falsely impersonating a department officer, inspector, or employee. It shall be unlawful for any person to falsely represent himself or herself as an officer, inspector or employee of the department, or as acting under the authority of the department, or without authority to use, wear or display a shield or other insignia or emblem such as is worn by such officer, inspector or employee.

§28-211.3 Identifying unlawful statements. The department, in coordination with the department of finance, shall collect information from the department of finance regarding occupied and rent regulated buildings to identify violations of section 28-211.1. The department shall also request information from the New York state division of housing and community renewal regarding occupied and rent regulated buildings to identify violations of section 28-211.1.

§28-211.3.1 Required audits. If the department determines that a person has violated section 28-211.1, or that the person has performed work in violation 28-105.1 in a building that is occupied as a dwelling, the department shall conduct an audit of filings for all buildings owned by such person and located in the city to determine if other violations of 28-211.1 have occurred with respect to other buildings owned by such person. If more than five amendments to approved construction documents have been submitted to the department within a six month period for a single building, and where such amendments indicate (i) a change in occupancy, (ii) a change in whether the building contains occupied housing accommodations subject to rent control or rent stabilization under chapters 3 and 4 of title 26 of the code or (iii) a change that would require the person to submit an application for a new permit to the department,  the department shall conduct an audit of all properties owned by such person and located in the city to determine if any statements were made that are unlawful pursuant to section 28-211.1. At least once per year, the department shall audit no less than 25 percent of buildings placed on the watch list established by article 3 of subchapter 4 of chapter 2 of title 27 for compliance with building permit requirements, including whether section 28-211.1 has been violated.

ARTICLE 212
ABATEMENT OF PUBLIC NUISANCE CAUSED BY CERTAIN ILLEGAL OCCUPANCIES

§28-212.1 Abatement of public nuisances caused by illegal commercial or manufacturing occupancy in residence districts and certain other zoning districts. Any building or part thereof or vacant land that is located in a residence zoning district and that is occupied for a use not permitted in such district in violation of the zoning resolution, without a certificate of occupancy [authorizing] or other authorization of such use, is hereby declared to be a public nuisance. Any building or part thereof or vacant land that is located in a C-1 or C-2 commercial zoning district and that is occupied for a commercial or manufacturing use indicated under use group 16, 17, or 18 as described in sections 32-25, 42-14, and 42-15 of the zoning resolution, in violation of the zoning resolution, without a certificate of occupancy authorizing such use is hereby declared to be a public nuisance.

§28-212.2 Order of closure. If a building or part thereof or vacant land in which such a nuisance occurs is not occupied primarily as a residence, the commissioner may, in addition to or as an alternative to any other remedy under any other provision of law, after notice and the opportunity for a hearing in accordance with this article, order the closing of such building or part thereof or such vacant land to the extent necessary to abate the nuisance.

§28-212.3 Notice of hearing. A notice of hearing with respect to an order of closure shall be served on the owner and mortgagee of record of such building or part thereof or such vacant land and on any person alleged to be occupying such building or part thereof or such vacant land at which the nuisance is located.

§28-212.4 Service of notice of hearing. Service may be made on the owner by delivering such notice to the owner or to an agent of the owner or to a person of suitable age and discretion at the residence or place of business of the owner or, if upon reasonable application such delivery cannot be completed, by affixing such notice in a conspicuous place at the owner’s place of business or residence or by placing it under the entrance door at either of such locations or by delivering such notice to a person employed by the owner to work at or to manage or maintain the premises at which the nuisance is located and, in all instances except personal delivery upon such owner by mailing the notice of hearing as follows:

§28-212.4.1 Mailing to owner’s registered address. To the person registered with the department of housing preservation and development as the owner or agent of the premises, at the address filed with such department in compliance with article two of subchapter four of chapter two of title twenty-seven of the administrative code;

§28-212.4.2 Mailing to billing address. To the person designated as owner of the building or designated to receive real property tax or water bills for the building at the address for such person contained in one of the files compiled by the department of finance for the purpose of the assessment or collection of real property taxes and water charges or in the file compiled by the department of finance from real property transfer forms filed with the city register upon the sale or transfer of real property; or

§28-212.4.3 Mailing to recorded address. To the person in whose name the real estate affected by the order of the commissioner is recorded in the office of the city register or the county clerk as the case may be at the address set forth on the recorded instrument.

§28-212.4.4 Service on corporate owner. Service may be made on an owner that is a corporation pursuant to section 306 of the business corporation law; however, service upon a corporation shall be deemed to have been completed 45 days following service upon the secretary of state.

§28-212.4.5 Service on mortgagees. Service may be made upon mortgagees of record by mailing such notice to the mortgagees at the address set forth on the recorded instrument.

§28-212.4.6 Service on occupants. Service may be made upon an occupant by delivering such notice to the occupant or to a person employed by the occupant to work at or to manage or maintain the premises at which the nuisance is located; or by affixing such notice to the premises at which the nuisance is located in a conspicuous place or by placing a copy under the entrance door of such premises and mailing a copy of such notice to the occupant at such premises; and in all instances except personal delivery upon such occupant, by mailing the notice of hearing to the occupant at the premises at which the nuisance is located.

§28-212.4.7 Proof of service. Proof of service pursuant to section 28-212.4.1 through 28-212.4.6 shall be filed with the commissioner.

§28-212.5 Conduct of hearing by office of administrative trials and hearings. The hearing shall be conducted by the office of administrative trials and hearings. The administrative law judge assigned to hear the matter shall submit his or her proposed findings of fact and recommended decision to the commissioner. If based on such recommended decision, proposed findings of fact, and the record of the hearing the commissioner determines that the building or part thereof or vacant land is a public nuisance, pursuant to this article, the commissioner may issue an order of closure. Such order shall not bar legally required ingress or egress for residential occupancy of parts of the building that are not subject to the order of closure.

§28-212.6 Lack of knowledge not a defense. At such hearing it shall not be a defense that the owner, occupant, lessor, lessee, mortgagee, or other person having an interest in the property lacked knowledge of or did not acquiesce or participate in the creation or continuation of the public nuisance.

§28-212.7 Closure not an act of possession. A closure ordered by the commissioner pursuant to this article shall not constitute an act of possession, ownership, or control by the city over the closed premises.

§28-212.8 Posting of order of closure. An order of closure shall be posted at the building or part thereof or vacant land that is the subject of such order, and shall be mailed to the record owner of such premises, and any record mortgagee at the address for such person set forth in the recorded instrument, and to the person designated as owner or agent of the building or designated to receive real property tax or water bills for the building at the address for such person contained in one of the files compiled by the department of finance for the purpose of the assessment or collection of real property taxes and water charges or in the file compiled by the department of finance from real property transfer forms filed with the city register upon the sale or transfer of real property. A copy shall also be filed with county clerk or register of the county in which such premises are located. Such filing shall be notice of the order to any subsequent owner and such owner shall be subject to such order.

§28-212.9 Enforcement of order of closure. On the tenth business day after the posting of such order and upon the written directive of the commissioner, police officers and authorized employees of the department shall act upon and enforce such order by sealing, padlocking, or otherwise preventing access to the premises in a manner that will not bar legally required ingress or egress for residential occupancy of parts of the building that are not subject to the closure order.

§28-212.10 Rescission of order of closure. If at any time after the issuance of such order, the owner, mortgagee, or other person having an interest in the property provides assurance, in a form satisfactory to the commissioner, that the illegal commercial or manufacturing use of the premises has been discontinued and will not reoccur, or such owner, mortgagee, or other person establishes that the premises may be lawfully occupied for such use, the commissioner shall rescind the closure order. If such order is rescinded, the commissioner shall, upon request of such owner, mortgagee, or other person, provide a copy of such rescission, which may be filed with the county clerk or register of the county in which such premises are located. No such re-occupancy shall be permitted without a certificate of occupancy or other department records authorizing such use.

§28-212.11 Violation of closure order. It shall be unlawful for any person to use or occupy or to permit any other person to use or occupy any building or part thereof or vacant land that has been sealed, padlocked, or otherwise closed pursuant to an order of the commissioner. It shall be unlawful to mutilate or remove a posted order of the commissioner. Intentional disobedience or violation of any provision of a closure order shall be punishable as an immediately hazardous violation.

ARTICLE 213
PENALTY FOR WORK WITHOUT A PERMIT

§28-213.1 Department penalty for work without a permit. In addition to any penalties otherwise authorized by law pursuant to article 202 and the rules of the department, whenever any work for which a permit is required pursuant to this code has been performed without a permit, a penalty shall be imposed by the department as provided in this article.

Exception: No such penalty shall be imposed for work performed without a permit to hang or attach upon or on the outside of any building a sign that is accessory to a use on the same zoning lot, as defined in section 12-10 of the zoning resolution that does not exceed one hundred fifty square feet in area, measured on one face only, or exceed one thousand two hundred pounds in weight. All such outstanding penalties imposed on or after December 28, 2017 shall be waived.

§28-213.1.1 Penalty for work without permit on one or two-family dwelling. Where work has been performed without a permit on a one-family or two-family dwelling the penalty shall equal six times the amount of the fee payable for the permit. Where only part of the work has been performed without a permit, the penalty shall be reduced proportionately according to the amount of work still to be performed at the time a permit is issued. Notwithstanding the foregoing, no such penalty shall be less than $600, nor more than $10,000.

§28-213.1.2 Penalty for work without permit on other than one or two-family dwelling. The penalty for work without a permit on buildings other than one or two-family dwellings shall be 21 times the amount of the fee payable for such permit. Where only part of the work has been performed without a permit, the penalty shall be reduced proportionately according to the amount of work still to be performed at the time a permit is issued. Notwithstanding the foregoing, no such penalty shall be less than $6,000, nor more than $15,000.

§28-213.2 Waiver. Such penalty and the permit fee shall be payable by the owner of the building on which the unpermitted work was performed. A waiver or reduction of such penalty shall be available to a subsequent bona fide purchaser of the premises pursuant to department rules.

§28-213.3 Payment of penalty required before issuance of permit. No permit shall be issued for work described in this article until the penalty assessed by the department pursuant to this article has been paid.

§28-213.4 Procedure. The department shall adopt a rule setting forth a procedure for assessment of penalties pursuant to this article.

§28-213.5 Watch list of contractors performing work without required permit. The department shall compile and maintain a watch list of contractors who have been found to have performed work without a required permit in the preceding two years.

§28-213.5.1 Increased oversight. At any site where a contractor that is included on the watch list created pursuant to section 28-213.5 performs work in an occupied building, the department shall perform one or more inspections in order to ensure compliance with applicable laws, rules, regulations and permitting requirements. The department may promulgate rules providing for additional oversight of such contractors where appropriate for the protection of the public.

§28-213.5.2 Exemption. Any work performed by a contractor that is wholly or partially exempt from a civil penalty for work performed without a permit pursuant to a rule of the department shall not be considered in determining whether the contractor is to be included on the watch list created pursuant to section 28-213.5.

§28-213.5.3 Removal from watch list. The department shall remove from the watch list created pursuant to section 28-213.5 any contractor who has not been found to have performed work without a permit in the two years after the latter of the following dates: (i) the date on which such contractor was originally placed on such watch list or (ii) the date on which such contractor most recently performed work without a required permit.

§28-213.6 Enhanced penalties for other violations. Where a penalty is imposed pursuant to this article for work that has been performed without a permit on a building (i) the civil penalty for each violation of this code issued for such building within one year after such imposition shall be two times the penalty that would otherwise apply for such violation or (ii) if such work without a permit was performed on only part of such building and the owner of such part is not the owner of such building, the civil penalty for each violation of this code issued for such part within one year after such imposition shall be two times the penalty that would otherwise apply for such violation.

§28-213.7 Inspection fees. Where a penalty is imposed pursuant to this article for work that has been performed without a permit on a building (i) the department may impose an inspection fee, in an amount to be established by rule, for each complaint-based inspection it conducts at such building within one year after imposition of such penalty where such inspection results in the issuance of a violation or (ii) if such work without a permit was performed on only part of such building and the owner of such part is not the owner of such building, the department may impose an inspection fee, in an amount to be established by rule, for each complaint-based inspection it conducts at only such part within one year after imposition of such penalty or until the date such part of such building changes

ARTICLE 214
ORDER TO SEAL, SECURE AND CLOSE

§28-214.1 Order to seal, secure and close. If the commissioner determines such action is necessary to the preservation of life and safety the commissioner may order a building subject to a vacate order to be sealed, secured and closed.

§28-214.1.1 Definition. For the purpose of this article, “sealed” and “sealed, secured and closed” shall mean the use of any means available to render the building, structure or part thereof inaccessible, including but not limited to the use of a padlock or cinder blocks.

§28-214.1.2 Hearing. Such order to seal, secure and close shall contain notice of the opportunity for a hearing with respect to such order to determine if the order was properly issued in accordance with the provisions of this article. Such hearing shall be conducted by the commissioner, or in the commissioner’s discretion, by the office of administrative trials and hearings or the environmental control board. If the matter is referred to such office or board, the hearing officer shall submit his or her findings of fact and a recommended decision to the commissioner. The hearing shall be held within three business days after the receipt of the written request of an owner, lessor, lessee, or mortgagee for such hearing. The commissioner shall render a decision within three business days after such hearing is concluded or findings of fact and a recommendation are submitted.

§28-214.1.3 Service of seal, secure and close order. Such order issued pursuant to this article shall be served as follows: It shall be mailed to the record owner of such premises; any record mortgagee of such premises at the address for such person as set forth in the recorded instrument; and if reasonably ascertainable, the person designated as owner’s agent of the building or designated to receive real property tax or water bills for the building at the address for such person contained in one of the files compiled by the department of finance for the purpose of the assessment or collection of real property taxes and water charges or in the file compiled by the department of finance from real property transfer forms filed with the city register upon the sale or transfer of real property. A copy shall also be filed with the county clerk of the county in which such premises is located. Such filing shall be notice of the order to any subsequent owner and such owner shall be subject to such order.

§28-214.1.4 Rescission of seal, secure and close order. An order issued pursuant to this article shall not be rescinded unless the owner, lessor, lessee or mortgagee seeking such rescission provides assurance, in a form satisfactory to the commissioner, that the conditions that caused the issuance of such order have been corrected and will not reoccur. If such order is rescinded, upon the request of the owner, lessor, lessee or mortgagee, the commissioner shall provide a certified copy of such rescission, which may be filed with the county clerk of the county in which such premises is located.

§28-214.1.5 Expenses of enforcing seal, secure and close orders. The expenses attending the execution of any and all orders duly made by the department shall respectively be a several and joint personal charge against each of the owners or part owners, and each of the lessees and occupants of the building, structure, enclosure, place or premises to which such order relates, and in respect to which such expenses were incurred; and also against every person or body who was by law or contract bound to do that in regard to such building, structure, enclosure, place or premises which such order requires. Such expenses shall also be a lien on all rent and compensation due, or to become due, for the use of any building, structure, place or premises, or any part thereof, to which such order relates, and in respect to which such expenses were incurred.

§28-214.1.6 Notice of seal, secure and close order to community. The commissioner shall give written notice of the closing of any building, structure, enclosure, place or premises pursuant to this article, and any subsequent actions taken with respect thereto, as soon as practicable, to the borough president of the borough within which the closing has occurred; the council member representing the district within which the closing has occurred; and the local community board. On January first of each year, the commissioner shall submit a report to the council, setting forth the number of closings made in the previous year, the locations of such closings, and the nature and use of the premises closed. The commissioner shall, in addition, as soon as practicable after a building, structure, enclosure, place or premises has been closed, make and publish a report of said closing in a manner calculated to quickly notify the local community in which such closing occurred. The commissioner shall also make and publish a report of any premises reopened pursuant to his or her permission under this article. Failure to comply with this section 28-214.1.6 shall not invalidate any action taken by the commissioner pursuant to this article.

§28-214.2 Access to sealed premises. The commissioner shall allow access to the premises sealed, secured and closed pursuant to this article to an owner, or a lessor, lessee or mortgagee upon the following conditions:

- The submission of a written affirmation, satisfactory to the commissioner, that such person or persons will commence or cause to be commenced without delay all work necessary to correct the conditions stated in the vacate order or otherwise to make the premises meet all applicable laws and rules and will complete such work within a period of time and in a manner to be approved by the commissioner;

- The submission of a written affirmation or other proof satisfactory to the commissioner describing the steps that have been taken and will be taken in the future to ensure that the premises will be used or operated in a lawful manner and specifying such lawful use;

- If a license, permit, certificate of operation or certificate of occupancy is necessary for such lawful use, the submission of a written affirmation or other proof, satisfactory to the commissioner, describing the steps that have been taken and will be taken in the future to ensure that such premises will be used or operated in compliance with any law requiring such license, permit, certificate of operation or certificate of occupancy; and

- If the premises are leased and the person making the affirmations described above in items 1, 2 and 3 is not such lessee, the commissioner may also require any authorized person seeking access to submit a written affirmation or other proof that proceedings to enable such person to take actions necessary to ensure compliance with the affirmations submitted by such authorized person pursuant to items 1, 2 and 3 have been commenced.

§28-214.3 Additional penalties for harm or injury from violation of order to seal, secure and close. Notwithstanding any other law, rule, or regulation, any person, corporation, partnership, association or any other legal entity who permits a building, structure, enclosure, place or premises, or any part thereof, to be unlawfully occupied or used in contravention of an order of the commissioner pursuant to this article, or who negligently fails to prevent or prohibit such unlawful occupancy or use, shall be liable for a civil penalty of not more than one million dollars, if any other person suffers serious physical injury, as defined in section ten of the penal law, or death in the building, structure, place or premises or any part thereof subject to such order as a result of such unlawful occupancy or use. If more than one person suffers serious physical injury or death, such penalty shall be recoverable for each person suffering serious physical injury or death. Such penalty shall be recovered in a civil action brought by the corporation counsel in the name of the city in any court of competent jurisdiction. In determining the amount of the civil penalty to be imposed the court shall consider:

- The extent and severity of injury to persons and property caused by the violation;

- The history of violations by the defendant at such premises, or any other premises, of laws or rules enforced by the department;

- The degree of willfulness, recklessness, or negligence displayed by the defendant in committing the subject violation;

- The defendant’s financial resources; and

- The defendant’s good faith efforts to cure the subject violation, including efforts to obtain entry to or possession of the premises in order to do so.

§28-214.3.1 Payment by city. In the event that the family of any person seriously injured or who has died as the result of any unlawful occupancy or use described in this section 28-214.3 is unable to collect a judgment recovered in a civil action for personal injury or wrongful death against a defendant who has violated this section 28-214.3 because of the insolvency of such defendant, the city may, in its discretion, pay to such injured person or the family of such deceased person an amount, as hereinafter provided, collected from such defendant in an action relating to the same injury or death commenced by the corporation counsel against such defendant pursuant to this section 28-214.3.1.

§28-214.3.2 Limitations. Payments pursuant to section 28-214.3.1 shall be made as a matter of grace and shall be in such amounts and in accordance with such standards and procedures as shall be established by the mayor, provided, however, that any payment made pursuant to section 28-214.3.1 shall be in an amount not exceeding out-of-pocket expenses, including indebtedness reasonably incurred for medical or other services necessary as a result of the injury upon which such action is based; loss of earnings or support resulting from such injury; burial expenses not exceeding two thousand five hundred dollars of a person who died as a result of such unlawful occupancy or use described in this section 28-214.3; and the unreimbursed cost of repair or replacement of articles of essential personal property lost, damaged or destroyed as a direct result of such unlawful occupancy or use. In no event shall the payment made to any person exceed the amount of such person’s uncollected judgment for personal injury or wrongful death and in no event shall the total amount paid to any number of persons with such uncollected judgments against a single defendant exceed the actual amount collected by the city from such defendant in an action under this subdivision.

ARTICLE 215
EMERGENCY POWERS OF THE COMMISSIONER

§28-215.1 Emergency work. Notwithstanding any other provisions of law, if the commissioner determines that a structure or premises or any part thereof poses an imminent danger of serious physical injury or death to the public or is in imminent danger of collapse and the exigency of the situation is such that any delay may cause further danger to the public safety, then the commissioner may direct the commissioner of housing preservation and development or the department of citywide administrative services, or other authorized agency to perform or arrange the performance of the emergency work on, or demolition of, such structure or premises or part thereof or such other work as deemed by the commissioner to make it safe.

§28-215.1.1 Lien for emergency work. The expenses of the city in performing emergency work on any structure or part of such structure pursuant to this article shall constitute a debt recoverable from the owner and a lien upon the land and any part of such structure that was not demolished. Every such lien shall have priority over all other liens and encumbrances on the premises except for the lien of taxes and assessments. Except as otherwise provided by rule of the affected agency, the agency incurring such expense shall be governed by the procedures set forth in article eight of subchapter five of the housing maintenance code with respect to the enforcement of such debt and lien against all types of structures, including those authorized to be occupied or otherwise occupied for residential, commercial, and manufacturing purposes.

§28-215.1.2 Interference prohibited. It shall be unlawful for any person to interfere, obstruct or hinder the commissioner or the commissioner of citywide administrative services, housing preservation and development, or other authorized agency, or any person who, acting under the authority conferred on such person by such commissioner, is performing the work authorized by section 28-215.1.

§28-215.1.3 Enforcement. The police commissioner shall enforce such orders or requirements when requested by the commissioner and shall likewise enforce same at the request of the commissioner of citywide administrative services, housing preservation and development, or other authorized agency, with respect to work performed by or under the direction of such commissioner pursuant to the provisions of section 28-215.1.

§28-215.2 Stopping work and securing structures. See section 28-207.2.

§28-215.3 Vacating structures. See section 28-207.4.

§28-215.4 Violations of protective measures during construction or demolition. During the construction or demolition of a structure, the commissioner shall notify the owner of the structure affected of any failure to comply with any of the provisions of this code that concern the protection of life, safety and property during construction or demolition. Unless the owner so notified proceeds immediately to comply with the orders of the commissioner, the commissioner shall have full power to correct the violation. All expenses incurred therefore shall become a lien on the property pursuant to section 28-112.9.

§28-215.5 Investigation of accidents or other emergency conditions. When necessary to conduct an investigation of any occurrence affecting building or construction safety, the commissioner may seize or impound equipment, building material, and portions of the affected building or premises for examination and testing. The police department or other authorized law enforcement agency shall cooperate with the commissioner upon request and shall provide a suitable place for the deposit of such items.

§28-215.6 Closing streets temporarily. The commissioner may, when necessary for the public safety, temporarily close the sidewalks, streets, structures or places adjacent to a structure or part thereof, and the police commissioner or commissioner of the department of transportation, any of his or her subordinates shall enforce all orders or requirements made by the commissioner, when so requested by the commissioner.

§28-215.7 Recovery of bodies from wrecked structures. Where any persons are known or believed to be buried under the ruins of any fallen structure or part thereof in the city, the commissioner shall cause an examination of the premises to be made for the recovery of the injured and bodies of the dead. Whenever, in making such examination, it shall be necessary to remove any debris from the premises, other city agencies shall cooperate with the commissioner in carrying out the purposes of this section 28-215.7, and shall provide suitable and convenient places for the deposit of such debris.

§28-215.8 Non-compliance with orders; execution of work by department. Upon the failure to comply with any order of the commissioner within the time limited thereby, and subject to the provisions of article 216, any work required to be executed by such order may be executed by the commissioner through the officers, agents or contractors of the department or other authorized agency; and the city shall be reimbursed promptly for all costs and expenses of such work. Such costs and expenses shall become a lien upon the premises involved and named in the commissioner’s order, which may be enforced in accordance with the provisions of section 28-112.9 of this code.

ARTICLE 216
UNSAFE BUILDINGS

§28-216.1 Conditions constituting an unsafe building or structure. Any building, structure or part thereof described in this article shall be deemed an unsafe building and shall be demolished or removed or made safe and secure as provided herein.

§28-216.1.1 Compromised structures. Any structure or premises or part of a structure or premises that from any cause may at any time become dangerous or unsafe, structurally or as a fire hazard, or dangerous or detrimental to human life, health or safety, shall be demolished and removed or made safe and secure.

§28-216.1.2 Vacant buildings. Any vacant building not continuously guarded or not sealed and kept secure against unauthorized entry shall have all openings sealed in a manner approved by the commissioner, and it shall be the duty of the owner thereof promptly to make any repairs that may be necessary for the purpose of keeping such building sealed and secure.

§28-216.2 Record and notice of unsafe building, structure or premises. The department shall cause a report to be filed on an unsafe building, structure or premises. The report shall describe the nature of the occupancy of the structure and the nature of the unsafe condition and be made a record of the department.

§28-216.3 Notice of survey and summons and order. The owner, executor, administrator, mortgagee, lessee or any other person who may have a recorded vested or recorded contingent interest in the unsafe building, structure or premises, shall be served with a notice of survey and summons containing a description of the unsafe building, structure or premises and an order requiring such building be sealed, secured, repaired, shored, or demolished and removed as may be deemed necessary by the commissioner.

§28-216.3.1 Content. Such notice of survey and summons shall require the person thus served immediately to certify to the commissioner his or her acceptance or rejection of the order. The notice of survey and summons shall further notify said person(s) that upon his or her refusal or neglect to comply with any of the requirements of this provision, a survey of the building or premises named in such notice will be made at a time and place therein named. The notice of survey and summons shall also state that if, pursuant to the survey, it is found that the building, structure, or premises referred to therein is unsafe or dangerous by the surveyors, their report of survey will be placed before the supreme court for trial at a time and place named in such notice.

§28-216.4 Method of service. The notice of survey and summons and order shall be served in accordance with the civil practice law and rules of the state of New York.

§28-216.5 Owner abatement of unsafe or dangerous conditions. If the person served with a notice and order pursuant to section 28-216.4 shall immediately certify his or her assent to the securing or removal of such unsafe building, structure or premises condition, such person shall be allowed a period of time as determined by the commissioner [, or his or her designee,] within which to commence and complete the abatement of the unsafe or dangerous condition. Such person shall employ sufficient labor and assistance to secure or remove such conditions as expeditiously as possible.

§28-216.6 Survey. A survey of the building or premises shall be conducted as follows:

§28-216.6.1 Identity of surveyors. The survey shall be made by three competent persons, of whom one shall be the commissioner [or his or her designee]; another shall be a registered design professional appointed by a recognized professional organization or by the commissioner; and the third shall be a registered design professional appointed by the person served with a notice pursuant to section 28-216.4. If the person served with such notice shall neglect or refuse to appoint such surveyor, the other two surveyors shall make the survey. In case they disagree, they shall appoint a third person to take part in such survey, who shall be a registered design professional of at least 10 years’ practice, whose decision shall be final.

§28-216.6.2 Posting report of survey. A copy of the report of the survey shall be posted on the structure that is the subject thereof by the persons holding the survey, immediately on their issuing such report.

§28-216.6.3 Compensation of surveyors. The registered design professional appointed by the respective professional organization or by the commissioner, as hereinbefore provided, who may act on any survey called in accordance with the provisions of this section 28-216.6, and the third surveyor who may have been called in the case of disagreement provided for in this section 28-216.6, shall each be paid a sum to be determined by rule to be promulgated by the department.

§28-216.6.4 Cost of survey. Any costs incurred by the city in connection with the survey shall become money due and owing to the city as part of the return of precept and judgment provided for in section 28-216.9, 28-216.10 and 28-216.11 of this code or pursuant to lien provided for in section 28-112.9 of this code.

§28-216.7 Court proceeding. Whenever the report of survey shall recite that the building, structure or premises surveyed is unsafe or dangerous, the corporation counsel or his or her designee shall, at the time specified in the notice, place such notice and report before a justice of the court named in the notice. The report of survey shall be in writing and constitute the issues to be placed before the court for trial. The purpose of the trial shall be to determine whether the unsafe building, structure, or premises shall be vacated and sealed, secured, shored, or demolished and removed.

§28-216.7.1 Precedence of proceeding. The unsafe building proceeding shall have precedence over every other business of such supreme court. The trial on the issues in the unsafe building proceeding shall be held without delay, at the time specified in the notice, and shall be held by a justice of the court or by a referee, whose decision or report in the matter shall be final.

§28-216.7.2 Precept to abate. If the justice or referee determines the building, structure or premises that is the subject of the report of survey is unsafe or dangerous, such justice or referee trying the case shall immediately issue a precept directed to the commissioner authorizing the commissioner forthwith to vacate pursuant to section 28-207.4, if necessary, and to seal, secure, shore, or demolish and remove the unsafe building, structure or premises named in such report. The precept shall be effective for a period of three years from the date of issuance.

§28-216.7.3 Notice of pendency. A notice of pendency shall be filed in accordance with the following procedure:

- The notice of pendency shall be filed in accordance with the Civil Practice Law and Rules of the State of New York and shall be filed in the office of the clerk of the county where the property affected by such action, suit or proceeding is located. Such notice of pendency may be filed at any time after the service of the notice described in section 28-216.3.

- Any notice of pendency filed pursuant to the provisions of this section 28-216.7.3 that has not expired may be vacated and cancelled of record upon an order of a justice of the court in which such suit or proceeding was instituted or is pending, or upon the consent in writing of the corporation counsel. The clerk of the county where the notice is filed is hereby directed and required to mark any such notice of pendency, and any record or docket thereof, as vacated and cancelled of record upon the presentation and filing of a certified copy of such order or consent.

§28-216.8 Execution of precept. A precept issued pursuant to section 28-216.7.2 shall be executed in accordance with the procedure set forth in sections 28-216.8.1 through 28-216.8.3.

§28-216.8.1 Work by the department. Upon receiving a precept under the provisions of section 28-216.7.2, the commissioner shall execute such precept, as therein directed, and may employ such labor and assistance and furnish such materials as may be necessary for that purpose. The commissioner [or his or her designee] shall direct the commissioner of citywide administrative services or the department of housing preservation and development or other authorized agency to perform work in accordance with the precept. Such work shall be performed by or under the direction of citywide administrative services in accordance with the provisions of section 4-204 of the administrative code, or the department of housing preservation and development, or such other authorized agency.

§28-216.8.2 Owner application to perform work. The owner of such unsafe building, structure, or premises, or any party interested therein, if such person applies to the commissioner immediately upon the issuing of such precept, shall be allowed to perform the requirements of such precept at his or her own cost and expense, if the performance shall be done immediately and in accordance with the requirements of such precept and other applicable laws and rules and such other requirements as the commissioner shall impose.

§28-216.8.3 Modification of precept. The commissioner [or his or her designee] shall have authority to modify the requirements of any precept when such commissioner [or designee] shall be satisfied that such change will secure the safety of such structure or premises equally well.

§28-216.8.3.1 Upon application. The commissioner shall also have authority to modify the requirements of any precept upon application to such commissioner in writing by the owner of the unsafe building, structure, or premises, or such owner’s authorized representative. In addition, upon application to modify the requirements of any precept to seal, shore or demolish the structure by the commissioner of housing preservation and development, citywide administrative services or such other authorized agency, the commissioner [or designee] shall have authority to modify such precept accordingly when the commissioner shall be satisfied that such change will secure the safety of such structure or premises equally well.

§28-216.8.3.2 Notice. After a determination to modify the precept is made by the commissioner, written notice of such determination shall be sent by regular mail to the owner and applicant for the modification if other than the owner, at his or her last known address.

§28-216.8.3.3 Failure of owner to perform work. If no action in accordance with the modified precept is undertaken by the owner or applicant for modification within the time period provided in the modification following the granting of such application, the commissioner may direct the department of housing preservation and development or the department of citywide administrative services or other authorized agency to execute the original precept, provided however that prior to such execution, notice shall be provided by regular mail to the owner of the unsafe building, structure or premises and applicant for the modification if other than the owner, at his or her last known address. The owner shall continue to have the right to request the commissioner to modify the requirements of the precept prior to the execution thereof.

§28-216.8.4 Interference prohibited. It shall be unlawful for any person to interfere, obstruct or hinder the commissioner or the commissioner of citywide administrative services, housing preservation and development, or other authorized agency, or any person who, acting under the authority conferred on such person by such commissioner, [in] is performing the work authorized by a precept issued out of any court or modified in accordance with section 28-216.8.3, or the work ordered by the commissioner in accordance with such precept under the provisions of section 28-216.8.3.3.

§28-216.8.5 Enforcement. The police commissioner shall enforce such orders or requirements when requested by the commissioner and shall likewise enforce same at the request of the commissioner of citywide administrative services, housing preservation and development, or other authorized agency, with respect to work performed by or under the direction of such commissioner pursuant to the provisions of section 28-216.8.3.3.

§28-216.9 Return of precept and reimbursement of city. Upon compliance with any precept issued to the commissioner in a proceeding under this article, the commissioner may make return thereof, with an endorsement of the action there under and the costs and expenses thereby incurred, to the justice of the court from which such precept issued. Such justice shall then tax and adjust the amount endorsed upon such precept, and shall adjust and allow the disbursements of the proceeding, including but not limited to the preliminary expenses of searches, service of the notice of survey and summons on interested parties, surveys thereof, and costs of executing the precept, which shall be inserted in the judgment in such proceeding. Such justice shall then render judgment for such amount and for the sale of the premises named in such notice, together with all the right, title and interest that the person named in such notice had in the lot, ground or land upon which such structure was placed, at the time of the filing of a notice of pendency in such proceedings, or at the time of the entry of judgment therein, to satisfy such judgment in foreclosure of mortgages. Nothing in this article shall preclude the city from recovering such costs and expenses in any other lawful manner, including pursuant to sections 28-112.9, 28-216.10 and 28-216.11 of this code.

§28-216.10 Judgment lien. Any judgment rendered in an action or proceeding instituted under this article shall be and become a lien upon the premises named in such action or proceeding, such lien to date from the time of filing a notice of pendency in the office of the clerk of the county wherein the property affected by such action or proceeding, is located. Every such lien shall have priority before any mortgage or other lien as may exist prior to such filing except tax and assessment liens.

§28-216.11 Tax lien. Any costs and expenses incurred by any agency of the city pursuant to this article, including but not limited to the preliminary expenses of searches, service of the notice of survey and summons on interested parties, surveys thereof, and costs of executing the precept, shall be a debt recoverable from the owner of the premises and a lien upon the land and buildings upon or in respect to which such costs and expenses were incurred. Every such lien shall have priority over all other liens and encumbrances on the premises except for the lien of taxes and assessments. Except as otherwise provided by rule of the affected agency, the agency incurring such expense shall be governed by the procedures set forth in article eight of subchapter five of the housing maintenance code with respect to the enforcement of such debt and lien.

ARTICLE 217
BUILDINGS AND STRUCTURES THAT ARE POTENTIALLY COMPROMISED

§28-217.1 Buildings and structures that are potentially structurally compromised. For purposes of this article, “potentially compromised” shall include a building or structure that: [has had an open roof for sixty days or longer, that has been shored and braced or otherwise temporarily safeguarded pursuant to an emergency declaration issued by the commissioner, that has been subject to a precept as a compromised structure under section 216.1.1 of this code or that may have suffered structural damage by fire or any other cause as determined by the commissioner.]

- Has had an open roof for sixty days or longer;

- Has been shored and braced or otherwise temporarily safeguarded pursuant to an emergency declaration issued by the commissioner, or due to concern for structural integrity as determined by a registered design professional;

- Has been subject to a precept as a compromised structure under section 28-216.1.1 of this code; or

- May have suffered structural damage by fire or any other cause as determined by the commissioner.

§28-217.1.1 Structural inspections of potentially compromised buildings or structures. When a building or structure has become potentially compromised, the owner [shall cause] is required to have a structural inspection [of such building or structure to be] performed. Such inspection shall be performed within 60 days of the opening of the roof, or within 60 days of the [shoring and bracing or other temporary safeguards pursuant to an emergency declaration, or within 60 days of damage by fire or a determination by the commissioner that the building has suffered structural damage by other cause] onset of any of the conditions listed in section 28-217.1. A report of such inspection shall be filed with the department within 30 days thereafter in such form and detail and with provision for periodic monitoring of the building or structure as the commissioner may require.

§28-217.1.2 Structural inspections shall only be performed by a registered design professional in good standing with the New York state department of education.

§28-217.1.3 If a violation of any applicable statute, law, rule or regulation or any unsafe condition that poses a threat to the structural integrity of the building or to the public is found during the course of such inspection, the registered design professional performing the inspection shall immediately notify the department and the owner of such violation or unsafe condition by calling 311 and in writing.

§28-217.1.4 An inspection of the buildings and structures subject to the inspection and filing requirements of section [28-216.12] 28-217.1 shall be performed every year [or, for a specified building or structure, within such other period as determined by the commissioner but not longer than two years, and shall continue] until such time as the registered design professional documents and certifies that the building or structure is no longer potentially compromised and such certification is accepted by the commissioner.

§28-217.1.5 The owner shall hire a registered design professional to perform a structural inspection of buildings and structures subject to section 28-217.1 prior to the issuance of a permit to alter, repair, demolish or enlarge such building or structure, except that the commissioner may waive such inspection if a structural inspection of the entire building or structure has been performed within the prior year.

[§28-217.16] §28-217.1.6 Any owner of a building or structure shall notify the department in writing that such building or structure has become potentially compromised immediately after such owner knows or should have known of the condition. Such notice shall contain the name and business address of the owner of record of such building or structure and shall identify the building or structure by street address and tax block and lot. The notices required by this subdivision shall be in such form and manner as established by the commissioner by rule.

§28-217.1.7 If an owner subject to the inspection and filing requirements of this section fails to file such report, the owner shall be liable for a civil penalty in an amount not less than two thousand dollars. In such a case, the department may cause a structural inspection to be conducted and a report filed.

ARTICLE 218
SAFETY COMPLIANCE OFFICER

§28-218.1 Definition. For purposes of this article, the terms "Safety Compliance Officer" and "SCO" shall mean a person whose presence is required by the commissioner pursuant to section 28-218.2 and who satisfies the qualifications of section 28-218.4.

§28-218.2 Safety [Compliance Officer] compliance officer. In addition to any other remedies or penalties authorized by law, the commissioner in his or her discretion may require the presence of a SCO at any permitted site that has received immediately hazardous violations that the commissioner determines adversely affect public safety and require the presence of a SCO to protect public safety. In any circumstance where a SCO is required, the commissioner [or designee] shall state in writing the circumstances necessitating the SCO, and the duration of the compliance monitoring and/or conditions that must be satisfied prior to the termination of the compliance monitoring.

§28-218.3 Appointment of a safety compliance officer. The owner or contractor shall employ, at the owner’s or contractor’s expense, an SCO approved by the department.

§28-218.4 Qualifications. Safety compliance officers shall have experience in supervising the type of construction operations being monitored. They shall be an architect or engineer who has experience supervising construction projects in New York city, a licensed site safety manager or coordinator or other licensee of the department, or a special inspector as provided for in article 115 of this title. Safety compliance officers shall carry insurance as required by the department.

[§28-218.3] §28-218.5 Compliance monitoring. The SCO shall monitor the operations related to the circumstances and conditions that the commissioner [or designee] has identified pursuant to section 28-218.2 until the areas of concern set forth by the commissioner [or designee] have been addressed as determined by the commissioner [or designee] , but in no case shall any monitoring period exceed ninety days. For such purpose, the SCO and his or her employees shall be designated as authorized representatives of the commissioner with authority pursuant to section 28-103.13 of this code to enter upon and examine and inspect at all reasonable times any site, building or structure. In the event that the conditions [set-out] set out in the commissioner’s [or designee’s] determination, pursuant to section [28-217.2] 28-218.2, to require a SCO have not been satisfied within the prescribed monitoring period, the commissioner [or designee] may order the general contractor to appoint another SCO subject to the approval of the department, who shall be a different SCO than the initial SCO, to monitor operations for an additional period not to exceed ninety days.

§28-218.5.1 Hazardous conditions.  In addition to any other requirements specified by the commissioner, the SCO shall immediately report to the commissioner all conditions that are hazardous to life, safety or health.

[§28-218.4 Qualifications. Safety Compliance Officers shall have experience in supervising the construction operations being monitored. They shall be an architect or engineer who has experience supervising construction projects in New York City, a licensed site safety manager or coordinator or other licensee of the department, or a special inspector as provided for in article 115 of this title. Safety Compliance Officers shall carry insurance as required by the department.]

[§28-218.5] §28-218.6 Cost of a [Safety Compliance Officer] safety compliance officer. The owner of the site where the services of the SCO have been required shall reimburse the department for all direct costs and any related administrative expenses incurred by the department in the operation of the SCO program provided for in this article. Reimbursement shall be made at such times as the department shall require, but in any event, before a temporary or permanent certificate of occupancy is issued for the building or structure that is being monitored. No permit shall be issued for the job site at which a SCO has been assigned if reimbursements for the cost of the monitor are outstanding for more than thirty days. The department shall adopt rules establishing a process for the resolution of disputes concerning the costs of the SCO.

[§28-218.6] §28-218.7 The SCO shall document with photographs or other means any violation of the code. The SCO shall submit [an interim report, to be submitted at the midpoint of the appointment period, and a final report] reports to the department in the frequency, manner and form prescribed by the commissioner [or designee]. The department will share the results of these reports with the general contractor and provide the general contractor an opportunity to comment.

[§28-218.7] §28-218.8 Records. The SCO shall keep and maintain records relating to the services performed on behalf of the department in such manner and for such period of time as shall be established by the commissioner [by rule or by direction of the commissioner].

ARTICLE 219

FAILURE TO CERTIFY CORRECTION OF CERTAIN IMMEDIATELY HAZARDOUS VIOLATIONS

§28-219.1 Department penalty for failure to certify correction. In addition to any penalties otherwise authorized by law pursuant to article 202 and the rules of the department, whenever any person fails to submit a certification of correction of an immediately hazardous violation that  poses a threat of imminent danger to public safety or property, as required by an order issued pursuant to section  28-204.2, a penalty shall be paid to the department by the owner of the property in the amount of not less than [one thousand five hundred dollars] $1,500 or more than [five thousand dollars] $5,000.  No permit or certificate of occupancy shall be issued and no stop work order may be rescinded at the property named in the order until such penalty is paid to the department. Failure to pay such penalty shall not prevent the issuance of a permit for work to be performed pursuant to articles 215 or 216 of this chapter. In addition, even if the immediately hazardous violation is subsequently corrected, no certificate of correction shall be accepted for the violation giving rise to this civil penalty until such penalty has been paid to the department.

§28-219.2 [Reinspection] Re-inspection.  Where an immediately hazardous condition has been identified as posing a threat of imminent danger to public safety or property and a violation has been issued, the commissioner shall re-inspect the condition that gave rise to the violation within 60 days of the date of the notice of a violation, unless:

1.	 [A] An acceptable certification of the correction of the condition has been filed in the manner and form prescribed by the department;

2.	The person to whom the violation has been directed has obtained an extension of time for filing the certificate of correction of the violation from the commissioner in accordance with section 28-204.4 and with any applicable rules of the department, and said extension of time to file has not yet expired; or

3.	The condition has been corrected in the presence of the commissioner.

§28-219.2.1 Continued noncompliance. If, upon re-inspection, the commissioner  determines the condition continues to pose a threat of imminent danger to public safety or property, and the person against whom the initial violation was directed is not in compliance with section 28-204.4, the commissioner shall issue an appropriate violation and shall issue a stop-work order, pursuant to section 28-207.2, where appropriate, or the commissioner shall, if the commissioner is unable to obtain access to the premises, request the corporation counsel to institute legal proceedings to compel correction of the violation and abate the condition or take such other action as is appropriate.

§28-219.2.2 Inspections by the commissioner. The commissioner shall continue to re-inspect any condition that has given rise to an immediately hazardous violation that poses a threat of imminent danger to public safety or property every 60 days, and shall follow the procedures described in items 1, 2 and 3 of section [219.2] 28-219.2 until the condition has been found by inspection or certification to be corrected or abated.

§28-219.3 False certifications of correction. It shall be unlawful to prepare, file or offer for filing a certification of correction of an immediately hazardous condition, knowing that such certification contains a false statement or false information. Any person who prepares such a certificate shall be subject to prosecution under section 175.05 or 175.10 of the penal law. Any person who files such a certificate or offers such a certificate for filing shall be subject to prosecution under section 175.30 or 175.35 of the penal law. Nothing in this section shall be construed to limit, alter or affect the authority conferred by any other provision of this chapter or other law to bring criminal, civil or administrative actions or proceedings or other remedies for the preparation, filing or offering for filing of a certification of correction of an immediately hazardous condition containing a false statement or false information.

§28-219.4 Notice to the department of housing preservation and development for certain elevator-related violations. If, upon [reinspection] re-inspection of an immediately hazardous violation relating to an elevator that services one or more dwelling units in a multiple dwelling, the department determines that such owner has failed to correct the condition constituting such violation, then the commissioner shall refer such violation, within one week of such [reinspection] re-inspection, to the commissioner of housing preservation and development for a determination as to whether such violation is dangerous to human life and safety or detrimental to health pursuant to section 27-2125 of the housing maintenance code. If the department knows or has reason to believe that any such unit is not served by another operable elevator, the department shall include such information and any other relevant information in such referral. The department may continue enforcement action against the owner of the multiple dwelling after referral of such violation to the commissioner of housing preservation and development. Where the owner begins to take corrective action, the department shall notify the commissioner of housing preservation and development of such efforts. The department shall notify an owner of the referral of any such violation to the commissioner of housing preservation and development for action under this section.

Exceptions:

- Elevators located in owner-occupied multiple dwellings that service only the owner-occupied dwelling unit [,] provided that such unit is not occupied by boarders, roomers, or lodgers.

- Elevators located within convents and rectories that are not open to non-occupants on a regular basis.

§ 3.  Chapter 3 of title 28 of the administrative code of the city of New York, as added by local law number 33 for the year 2007, the opening paragraph of section 28-302.2 as amended by local law number 38 for the year 2007, item 1 of section 28-302.5, Articles 303, 304 and 305 and section 28-306.1 as amended by, and sections 28-303.6, 28-303.8, 28-306.2, Article 314, sections 28-315.1, 28-315.2, 28-315.3, 28-315.4, 28-315.5, 28-315.6 and 28-315.7 as added by, local law number 141 for the year 2013, section 28-304.6.1 as amended by chapter 750 of the laws of 2019, Article 308 as added by local law number 87 for the year 2009, Article 309 as added by local law number 84 for the year 2009, sections 28-309.2, 28-309.8, 28-309.9 as amended by, and section 28-309.11 as added by, local law number 133 for the year 2016, section 28-309.12 as added by local law number 33 for the year 2018, section 28-309.13 as added by local law number 93 for the year 2020, sections 28-310.1, 28-311.1 and 28-311.4 as added by local law number 88 for the year 2009, sections 28-310.2, 28-310.3 and 28-315.3.1 as amended by local law number 134 for the year 2016, sections 28-311.2, 28-311.3, 28-311.5 and 28-315.3.2 as amended by local law number 132 for the year 2016, sections 28-312.1, 28-312.2, 28-312.3, 28-312.4 and 28-312.5 as amended by, and sections 28-312.6, 28-312.7 and 28-315.2.4 as added by, local law number 157 for the year 2016, section 28-312.8 as added by local law number 113 for the year 2018, sections 28-313.1 and 28-313.2 as added by local law number 47 for the year 2012, sections 28-313.3 and 28-315.6.3 as added by local law number 122 for the year 2019, section 28-315.2.3 as added by local law number 78 for the year 2015, sections 28-315.8 and 28-315.8.1 as added by local law number 110 for the year 2013, sections 28-315.8.2 and 28-315.8.3 as added by local law number 108 for the year 2013, section 28-315.9 as added by local law number 79 for the year 2016, section 28-315.10 as added by local law number 111 for the year 2018, section 28-315.11 as added by local law number 191 for the year 2018, section 28-316.1 as added by local law number 12 for the year 2014, Article 317 as added by local law number 77 for the year 2015, section 28-317.5 as amended by local law number 76 for the year 2019, Article 318 as added by local law number 152 for the year 2016, Article 319 as added by local law number 105 for the year 2018, sections 28-320.1 and 28-321.1 as amended by, and section 28-320.3.10.1 as added by, local law number 116 for the year 2020, sections 28-320.2, 28-320.3.1.1, 28-320.3.2, 28-320.3.6, 28-320.3.6.1, 28-320.3.6.2, 28-320.3.6.3, 28-320.3.9, 28-320.6.1, 28-320.6.1, items 1 and 2 of section 28-320.7, 28-320.8 and 28-320.9 as amended by, and Article 322 as renumbered by, local law number 147 for the year 2019, sections 28-320.3, 28-320.4, 28-320.5, 28-320.6, 28-320.7, 28-320.10, 28-320.11 and Article 321 as added by local law number 97 for the year 2019, item 6 of section 28-320.3.1.1 and section 28-320.3.2.1 as amended by local law number 95 for the year 2020, and section 28-320.3.7 as amended by and section 28-320.3.7.2 as added by local law number 117 for the year 2020, is amended to read as follows:

CHAPTER 3

MAINTENANCE OF BUILDINGS

ARTICLE 301
GENERAL

§28-301.1 Owner’s responsibilities. All buildings and all parts thereof and all other structures shall be maintained in a safe condition. All service equipment, means of egress, materials, devices, and safeguards that are required in a building by the provisions of this code, the 1968 building code or other applicable laws or rules, or that were required by law when the building was erected, altered, or repaired, shall be maintained in good working condition. Whenever persons engaged in building operations have reason to believe in the course of such operations that any building or other structure is dangerous or unsafe, such person shall forthwith report such belief in writing to the department. The owner shall be responsible at all times to maintain the building and its facilities and all other structures regulated by this code in a safe and code-compliant manner and shall comply with the inspection and maintenance requirements of this chapter.

§28-301.1.1 Parapets. A building’s parapet shall be maintained in a safe condition. A building owner must have an annual parapet observation performed as described in the rules of the department. This observation must be performed on all buildings, regardless of height.

Exception: The requirements of this section shall not apply to detached one- or two-family homes.

§28-301.2 Filing of reports in writing or electronically. Reports required to be filed under this chapter shall be filed in writing or electronically as the commissioner may require.

ARTICLE 302
MAINTENANCE OF EXTERIOR WALLS

§28-302.1 General. A building’s exterior walls and appurtenances thereof shall be maintained in a safe condition. All buildings greater than six stories shall comply with the maintenance requirement of this article.

Exception: The requirements imposed by this article shall not apply to any part of an exterior wall that is less than 12 inches (305 mm) from the exterior wall of an adjacent building.

§28-302.2 Inspection requirements. A critical examination of a building’s exterior walls and appurtenances thereof shall be conducted at periodic intervals as set forth by rule of the commissioner, but such examination shall be conducted at least once [every five years. No later than January 1, 2009 the commissioner shall by rule establish staggered inspection cycles for buildings required to comply with this section] during each five-year report filing cycle, as defined by rule of the department. The initial examination for a new building shall be conducted in the fifth year following the erection or installation of any exterior wall and/or appurtenances as evidenced by the issuance date of a temporary or final certificate of occupancy or as otherwise prescribed by rule.

1.	Such examination shall be conducted on behalf of the building owner by or under the direct supervision of a registered design professional with appropriate qualifications as prescribed by the department.

2.	Such examination shall include a complete review of the most recently prepared report and an inspection.

3.	Such examination shall be conducted in accordance with rules promulgated by the commissioner.

§28-302.3 Immediate notice of unsafe condition. Whenever a registered design professional learns of an unsafe condition through a critical examination of a building’s exterior walls and appurtenances thereof, such person shall notify the owner and the department immediately in writing of such condition.

§28-302.4 Report of critical examination. The registered design professional shall submit a written report to the commissioner within 60 days of completing the critical examination, [but not more than five years following submission of the preceding report of critical examination] at least once during each five-year report filing cycle, as defined by rule of the department certifying the results of such critical examination as either safe, unsafe or safe with a repair and maintenance program. The report shall clearly document the condition of the exterior walls and appurtenances thereof and shall include a record of all significant deterioration, unsafe conditions and movement observed as well as a statement concerning the watertightness of the exterior surfaces. Such report must be [professionally certified] signed and sealed by such registered design professional.

§28-302.5 Repair of exterior walls, unsafe condition. Upon the notification to the department of an unsafe condition, the owner, the owner’s agent or the person in charge shall immediately commence such repairs, reinforcements or other measures as may be required to secure public safety and to make the building’s exterior walls or appurtenances thereof conform to the provisions of this code.

1.	All unsafe conditions shall be corrected within 90 days of filing the critical examination report.

2.	The owner shall engage a registered design professional [shall] to reinspect the premises and file an amended report within two weeks after the repairs have been completed certifying that the unsafe conditions of the building have been corrected.

3.	The commissioner may grant an extension of time of up to 90 days to complete the repairs required to correct an unsafe condition upon receipt and review of an initial extension application submitted by the registered design professional together with such additional documentation as may be prescribed by rule.

4.	The commissioner may grant further extensions of time to complete the repairs required to remove an unsafe condition upon receipt and review of an application for a further extension submitted by the registered design professional together with such further documentation as may be prescribed by rule.

§28-302.6 Safe condition with a repair and maintenance program. The registered design professional shall not file a report of a safe condition with a repair and maintenance program for the same building for two consecutive filing periods unless the second such report is accompanied by his or her professional certification attesting to the correction of all conditions identified in the prior report as requiring repair.

ARTICLE 303
PERIODIC BOILER INSPECTIONS

§28-303.1 General. Periodic boiler inspections shall be performed in accordance with this article and the provisions of section 1011.3 of the New York city mechanical code.

§28-303.2 Annual inspections. Except as otherwise provided in this article, each owner of a boiler, as defined in section 204 of the New York state labor law, excepting those boilers listed in subdivision five of such section of such labor law, shall have such boiler inspected at least once a year in accordance with this article. All individuals who perform periodic inspections pursuant to this article shall be qualified under section 204 of the New York state labor law and the rules promulgated by the commissioner of labor or the commissioner of buildings.

§28-303.2.1 Internal inspection required. All high pressure boilers shall have an annual internal inspection performed in accordance with section 204 of New York state labor law and the rules of the department. Where construction of a low pressure boiler allows, an internal inspection shall be performed on a periodic schedule in accordance with section 204 of the New York state labor law and the rules of the department.

§28-303.2.2 External inspection required. All high and low pressure boilers shall have an annual external inspection performed in accordance with section 204 of New York state labor law and the rules of the department. Such inspection shall include chimney connectors.

§28-303.2.3 Electric high pressure boilers.  Electric boilers operating at pressures or temperatures classified as high pressure boilers, as defined in the New York city mechanical code, shall be annually inspected as high pressure boilers in accordance with this article.

§28-303.3 Qualifications of boiler inspectors. All individuals who perform periodic inspections pursuant to this article shall have the qualifications set forth in the rules of the department and in section 28-303.3.1 or section 28-303.3.2, as applicable.

§28-303.3.1 High-pressure boilers. Inspections required by section 28-303.2 of a high-pressure boiler must be performed, in accordance with the rules of the department, on behalf of the owner, by boiler inspectors in the employ of a duly authorized insurance company who are qualified in accordance with section 204 of the New York state labor law.

§28-303.3.2 Low-pressure boilers. Inspections required by Section 28-303.2 of a low-pressure boiler must be performed, in accordance with the rules of the department, on behalf of the owner, by boiler inspectors who are qualified in accordance with section 204 of the New York state labor law.

§28-303.4 Staggered inspection cycles. The commissioner may by rule establish staggered inspection cycles for buildings required to comply with this article.

§28-303.5 Repair of defects. The owner of each boiler that is subject to periodic inspection shall correct any defects identified in the annual boiler inspection.

§28-303.6 Reporting an unsafe or hazardous condition. If an inspection reveals that any boiler is unsafe or hazardous to life and safety, the device is to be immediately taken out of service by the approved boiler inspection agency performing the inspection and the building owner shall be notified. Such agency shall notify the department of the unsafe or hazardous condition of the boiler within 24 hours after the condition is discovered. Notification to the department may be made by telephone, electronically or in writing.

§28-303.7 Owner’s annual boiler inspection report. The owner of each boiler that is subject to inspection pursuant to section 28-303.2 shall file a signed annual report with the commissioner in accordance with the rules of the department within [45] 14 days after the required annual inspection of the boiler has been performed. Extensions of time to file such report may be granted in accordance with the rules of the department. The report shall include, but shall not be limited to:

1.	The location of the boiler.

2.	The name and address of the inspector, the qualification of the inspector to perform the inspection, the date of inspection and if the inspector is a qualified boiler inspector in the employ of a duly authorized insurance company, the policy number covering the boiler.

3.	A list of all defects found in the inspection for each device inspected.

§28-303.7.1 Affirmation of correction. [The owner must file an affirmation that all] All defects identified in the annual boiler inspection report [have been corrected. Such affirmation must be filed with the department] shall be corrected within [120] 90 days after the date of [filing of the report.] initial inspection. The department may grant an extension of 45 days upon submission of an application by the owner demonstrating a practical difficulty in complying within the 90 day timeframe. In no case shall a single extension request be granted for more than 45 days, and no more than two such extensions be granted for a specific defect. An affirmation of correction shall be filed within 14 days of the date of correction.

§28-303.8 Scope of inspection. During required inspection and testing, in addition to any other requirements prescribed by this code or the rules of the department, all parts of the equipment shall be inspected to determine that they are in safe operating condition and that parts subject to wear have not worn to such an extent as to affect the safe and reliable operation of the boiler.

§28-303.9 Removal or discontinuance notice. The owner of a boiler that is removed or discontinued from use shall file a written notice of such removal or discontinuance with the commissioner within 30 days of the date of removal or discontinuance.

§28-303.10 Additional inspections. In addition to the inspections required by this article, the commissioner may make such additional inspections as required to enforce the provisions of this code.

§28-303.11 Fees. The owner of each boiler subject to periodic inspection pursuant to this article shall pay to the department an annual fee for each boiler in the amount prescribed by this code to cover the city’s administrative and supervisory costs. The fee shall be payable at the time of the filing of the owner’s annual boiler inspection report. No fee shall be charged for additional inspections made by the department pursuant to section 28-303.10.

ARTICLE 304
ELEVATORS AND CONVEYING SYSTEMS

§28-304.1 General. Elevators and conveying systems shall be maintained in a safe condition and in accordance with ASME A17.1, as modified by appendix K of the New York [City] city building code. Every new and existing elevator or conveying system shall be inspected and tested in accordance with this article.

§28-304.2 Elevators, escalators, moving walkways, material lifts, man lifts and dumbwaiters. Elevators, escalators, moving walkways, material lifts, man lifts and dumbwaiters shall be inspected and tested in accordance with section 28-304.6, chapter 30 of the New York city building code, and the schedule set forth in Table N1 of ASME [17.1] A17.1 as [referenced in chapter 35 and as may be] modified [in chapter 30 and] by chapter K1 of appendix K of the New York [City] city building code [(“Table N1”)].

[Exception: Elevators located in one-family, two-family or multiple-family dwellings that service only a single owner-occupied dwelling unit which is not occupied by boarders, roomers or lodgers, and elevators located within convents and rectories that are not open to non-occupants on a regular basis are not subject to periodic inspection requirement of such reference standard. Inspections and tests shall be performed in accordance with Table N1.]

§28-304.3 [Chair] Platform lifts, stairway chair lifts and vertical reciprocating conveyors (VRCs). [Chair] Platform lifts, stairway chair [lifts] lifts and VRCs shall be inspected and tested at intervals not exceeding one year. Inspections and tests shall be performed in accordance with Table N1.

§28-304.4 Amusement devices. Amusement devices shall be inspected and tested in accordance with department rules.

§28-304.5 Frequency of inspection and testing. Elevators and other conveying systems may be subject to more frequent inspection and testing as the commissioner finds necessary to protect public safety.

§28-304.6 Inspection and testing process. All devices shall be inspected and tested in accordance with Table N1 of ASME A17.1 as modified by chapter K1 of appendix K of the New York city building code and, where applicable, department rules and with sections 28-304.6.1 through 28-304.6.6.

§28-304.6.1 Inspection and testing entities. [The required periodic inspections in Table N1 shall be made by the department.] The [other] required category tests and periodic inspections in Table N1 of ASME A17.1 as modified by chapter K1 of appendix K of the New York City building code shall be performed on behalf of the owner by an approved elevator agency in accordance with this code and department rules. Where indicated in Table N1, tests [and inspections] shall be witnessed by an approved elevator agency not affiliated with the agency performing the test, and not affiliated with the agency performing the elevator work. Where indicated in Table N1, inspections shall be performed by an approved elevator agency not affiliated with the agency performing the maintenance. Not affiliated, as used in this section, shall mean the approved elevator agency owners, directors and inspectors shall be independent of all relative approved elevator agencies, maintenance firms or other entities providing any associated services to the device owner. Such other tests and inspections shall comply with the timeframes established as follows:

1.	Category 1 [inspections and] tests shall be performed between January 1st and December 31st of each year at a minimal time interval of six months from the date of the previous Category 1 testing. Category 1 tests are required on new installations the calendar year following final acceptance test.

2.	Category 3 [inspections and] tests for water hydraulics shall be performed every three years on or before the anniversary month of the last Category 3 testing.

3.	Category 5 [inspections and] tests shall be performed every five years on or before the month of the final acceptance test for new elevators or the anniversary month of the last Category 5 testing.

4.	Periodic inspections shall be performed between January 1st and December 31st of each year at a minimum of three months from the date of any Category 1 testing or previous periodic inspection. Initial periodic inspections on new installations shall be performed in the calendar year following the final acceptance test. For private residence elevators, the periodic inspection and category testing may be performed on the same date.

§28-304.6.1.1 Department notification. The department shall be notified by the [performing agency] agency performing the test at least [seven] five days prior to the Category 1 testing of escalators, Category 3 testing of water hydraulic elevators and Category 5 testing of elevators, pursuant to the rules of the department.

§28-304.6.2 Scope. During periodic inspection and category testing, in addition to any other requirements prescribed by this code, all parts of the equipment shall be inspected to determine that they are in safe operating condition and that parts subject to wear have not worn to such an extent as to affect the safe and reliable operation of the installation.

§28-304.6.3 Reporting an unsafe or hazardous condition. If [an] a periodic inspection or category test reveals that any elevator or other conveying system is unsafe or hazardous to life and safety, the device is to be taken out of service immediately by the agency performing the inspection or test and the building owner notified immediately. The performing agency shall notify the department by telephone, electronically or in writing within 24 hours.

§28-304.6.4 [Field] Periodic inspection and category testing reports and notations on the inspection certificate. [Field] Periodic inspection and category testing reports and notations on the inspection certificate shall comply with the requirements of sections 28-304.6.4.1 and 28-304.6.4.2.

§28-304.6.4.1 [When no witnessing agency is required] Periodic inspections. [When no witnessing agency is required to witness] For the periodic inspections [and tests under] listed in Table N1 of ASME A17.1, as modified by chapter K1 of appendix K of the New York city building code, the performing inspector shall, on the day of each inspection [and test]: (i) complete the [field] periodic inspection [and test] report, documenting all violating conditions, if any, and affix his or her signature; (ii) provide a copy of such report to the owner or owner’s representative; and (iii) affix the [inspection] date and his or her signature over a stamp identifying his or her approved elevator agency and his or her approval number on the inspection certificate issued by the department attesting to completion of items (i) and (ii). No witnessing agency is required to witness the periodic inspections.

§28-304.6.4.2 [When] Category testing when a witnessing agency is required. When a witnessing agency is required to witness [inspections and] category tests [under] listed in Table N1 of ASME A17.1, as modified by chapter K1 of appendix K of the New York city building code, the performing inspector shall, on the day of each [inspection and] test complete the [field inspection and] category test report, documenting all violating conditions, if any, and affix his or her signature; and provide a copy of such report to the owner or owner’s representative with the witnessing agency inspector signature. The witnessing agency inspector shall, on the day of each [inspection and] test: (i) review and confirm the [field inspection] category test report and also affix his or her signature to it; (ii) [provide] confirm that a copy of such report was provided to the owner or owner’s representative; and (iii) affix the [inspection] date and his or her signature over a stamp identifying his or her approved elevator agency and his or her approval number on the inspection certificate issued by the department attesting to the completion of items (i) and (ii).

§28-304.6.4.3 Category testing when no witnessing agency is required. When no witnessing agency is required to witness the category tests listed in Table N1 of ASME A17.1, as modified by chapter K1 of appendix K of the New York city building code, the performing inspector shall, on the day of each test: (i) complete the category test report, documenting all violating conditions, if any, and affix his or her signature; (ii) provide a copy of such report to the owner or owner’s representative; and (iii) affix the date and his or her signature over a stamp identifying his or her approved elevator agency and his or her approval number on the inspection certificate issued by the department attesting to completion of items (i) and (ii).

§28-304.6.5 [Inspection and] Periodic inspection or category test reports submission. [Inspection and] Periodic inspection or category test reports shall be submitted to the department on such forms and in such manner as required by the commissioner. Such reports shall comply with the following and department rules[:].

§28-304.6.5.1 Periodic inspection reports. Reports of periodic inspections shall comply with the following:

1.	The reports shall contain the signatures of (i) the performing agency director, and (ii) the building owner.

2.	The reports, with all applicable signatures, shall be filed with the department within 14 days after the date of the inspection.

§28-304.6.5.2 Category test reports. Reports of category tests shall comply with the following:

1.	The [inspection and test] reports shall contain signatures of (i) the performing agency inspector and director, (ii) the witnessing agency [inspector and] director, if required under Table N1 of ASME A17.1 as modified by chapter K1 of appendix K of the New York city building code, and (iii) the building owner.

2.	The completed [inspection and test] reports, with all applicable signatures, shall be [delivered to the owner by the approved performing and/or witnessing agency within 30 days of the test listing all violating conditions for each device tested, and] filed with the department within [60] 21 days after the date of the test [by the owner or its authorized designee].

Exception: [Inspection and test reports] Reports are not required to be submitted to the department for private residence wheelchair lifts and private residence dumbwaiters devices. However, the owner shall maintain an inspection and test log to be available to the department upon request.

§28-304.6.6 [Repair.] Periodic inspection and category testing repair. All defects as found in periodic inspection and category testing reports shall be corrected in accordance with the requirements of sections 28-304.6.6.1 and 28-304.6.6.2, except all hazardous conditions, as well as defects related to firefighters’ Phase I emergency recall operations or Phase II emergency in-car operation as required by section 3003.2 of the New York city building code, shall be corrected immediately.

§28-304.6.6.1 Periodic inspection repair. All defects as found in such periodic inspection report shall be corrected within 90 days after the date of inspection. The department may grant an extension of 45 days upon submission of an application by the owner demonstrating a practical difficulty in complying within the 90 day timeframe. In no case shall more than two such extensions be granted for a specific defect. An affirmation of correction shall be filed within 14 days after the date of inspection.

§28-304.6.6.2 Category test repair. All defects as found in such [inspection and test reports] category test report shall be corrected within [120] 90 days after the date of [inspection and] test [, except all hazardous conditions shall be corrected immediately]. An affirmation of correction shall be filed within [60] 14  days of the date of correction.

§28-304.7 Required contract. The owner of all new and existing passenger elevators, freight elevators, and escalators shall have a contract with an approved elevator agency to perform elevator and escalator maintenance, repair and replacement work as defined by ASME A17.1 as modified by chapter K1 of appendix K of the New York [City] city building code. The name, address and telephone number of such agency shall be maintained at each premises, on the mainline disconnect switch and in a location readily accessible to employees of the department and to maintenance and custodial staff at the premises.

§28-304.8 Fees. Every owner of elevators and other devices shall pay to the department [an inspection fee and] a report filing fee for each elevator or device in the amount prescribed by [this code] the department’s rules.

§28-304.9 Additional inspections. The commissioner may make such additional inspections as required to enforce the provisions of this code. No fee shall be charged for such additional inspections.

§28-304.10 Occupant notification for elevator work. In occupancy groups R-1 and R-2, when an elevator is to be out of service, a notice identifying the type of work to be performed and the expected start and end dates for such outage shall be provided in English, Spanish, and such other languages as the department may provide by rule, in accordance with sections 28-304.10.1 and 28-304.10.2.

§28-304.10.1 Occupant notification for alteration work. When an elevator is to be out of service for alteration work, notice shall be given to the residential occupants no fewer than 10 business days before the start of the work, except in case of emergency repairs. This notification requirement does not apply to minor alterations and ordinary repairs.

§28-304.10.2 Occupant notification for other elevator service outages. When all elevators servicing a building or any section of a building are expected to be out of service for two or more hours, notice shall be posted at least twenty-four hours before the start of the work. When all elevators servicing a building or any section of a building are expected to be out of service for less than two hours, or are out of service as the result of emergency work, notice is not required to be posted, except that where such outage lasts for two or more hours, notice shall be posted as soon as practicable after the commencement of such service outage.

ARTICLE 305
RETAINING WALLS, PARTITION FENCES AND OTHER SITE STRUCTURES

§28-305.1 Retaining walls, partition fences and other site structures. In addition to the requirements set forth in chapter 33 of the New York [City] city building code, the responsibility for maintaining and repairing retaining walls, partition fences and other site structures shall be in accordance with sections 28-305.1.1, [305.1.2] 28-305.1.2, and [305.4] 28-305.4.

§28-305.1.1 Structures located on the lot line of adjacent properties and partially on both properties. The owners of adjacent properties shall be responsible jointly for the proper maintenance and repair of retaining walls, partition fences and other site structures, or portions thereof, that are located along the common lot line and on both their properties; and each such owner shall be responsible for one-half of the costs of maintaining and repairing such fences, retaining walls and other site structures, or such portions thereof. Where an owner elects to remove temporarily a retaining wall or partition fence that is required to support a grade differential between the two properties, or for any other reason is required by this code, such owner shall protect the adjacent property, shall not impair its safe use, and shall replace the retaining wall or partition fence at his or her own cost. Refer to chapter 33 of the New York [City] city building code for additional requirements during construction and demolition operations.

§28-305.1.2 Structures located entirely on one property. Where such retaining walls, partition fences or other site structures, or portions thereof, are located entirely on one property, the owner of such property shall be wholly responsible for the proper maintenance and repair of the retaining wall, partition fence or other site structure. If, however, the proper maintenance and/or repair of such retaining wall, partition fence or other site structures requires access to the adjoining property, the owner of such adjoining property shall allow such access. Refer to chapter 33 of the New York [City] city building code for additional requirements during construction and demolition operations.

§28-305.2 Retaining walls required. Hereafter, when an owner elects to set his or her grade either higher or lower than the grade of an adjoining property at the property line, such owner shall erect, maintain and repair a retaining wall of sufficient height, structure and foundation to support such grade differential, and with proper drainage, in accordance with this code, such that the adjacent property is not impacted, and shall do so at the sole expense of such owner and entirely on the property of such owner without access to the adjoining property.

§28-305.3 Special agreement. Nothing in this article shall be construed to prevent the owners of adjacent properties from making or enforcing by private action special agreements with respect to maintenance or repair of retaining walls, partition fences and other site structures or access to adjoining property for such purpose.

§28-305.4 Maintenance, inspection and repair of retaining walls. Maintenance, inspection and repair of retaining walls shall comply with sections 28-305.4.1 through 28-305.4.8.

§28-305.4.1 Definition. As used in this article, the following term shall have the following meaning:

RETAINING WALL. A wall that resists lateral pressures and limits lateral displacement caused by soil, rock, water or other materials, except that basement and vault walls that are part of a building, underground structures, including but not limited to utility vault structures, tunnels, transit stations and swimming pools, shall not be considered retaining walls.

§28-305.4.2 Owner’s responsibility. Owners of retaining walls with a height of ten feet or more and fronting a public right-of-way shall comply with the requirements of this section. For the purposes of this section, the height of a retaining wall shall be the distance from the top of the ground in front of the wall to the top of the wall stem, or wall step for stepped walls, including any parapets or fencing capable of retaining material.

§28-305.4.3 Condition assessment requirements. A condition assessment of a retaining wall shall be conducted at periodic intervals as set forth by rule of the commissioner, but such assessment shall be conducted at least once every 5 years. The commissioner may establish staggered assessment cycles for retaining walls required to comply with this section.

§28-305.4.3.1 Registered design professional. The condition assessment shall be conducted on behalf of the owner by or under the direct supervision of a registered design professional with appropriate qualifications as prescribed by the department.

§28-305.4.3.2 Department rules. The condition assessment shall be conducted in accordance with rules promulgated by the commissioner.

§28-305.4.4 Report of condition assessment. A report of condition assessment shall be submitted to the department in accordance with sections 28-305.4.4.1 and 28-305.4.4.2.

§28-305.4.4.1 Submission deadlines. Except as otherwise provided in section 28-305.4.6, the registered design professional shall submit a written report to the commissioner within 60 days of completing the assessment, but not more than 5 years following submission of the preceding report of assessment, certifying the results of the assessment.

§28-305.4.4.2 Contents. The report shall certify the results of the assessment as either safe, safe with minor repair or safe with repair and/or engineering monitoring, as prescribed by rules of the department. The report shall clearly document the condition of the retaining wall and shall include a record of all significant deterioration, potentially unsafe conditions of the wall or affecting the wall, and movement observed. The report must be certified by the registered design professional.

§28-305.4.5 Fees. Every owner of a retaining wall shall pay to the department a report filing fee for each report of condition assessment in the amount prescribed by this code.

§28-305.4.6 Immediate notice of unsafe condition. Whenever the registered design professional under whose supervision the inspection is performed learns of an unsafe condition through a condition assessment of a retaining wall, such person shall notify the owner and the department of such condition immediately by calling 311 and by written notification to the department.

§28-305.4.7 Repair of unsafe condition. Upon the notification to the department of an unsafe condition, the owner or the owner’s agent shall immediately commence such repairs, reinforcements or other measures as may be required to secure public safety.

§28-305.4.7.1 Permit. The owner or the owner’s agent shall obtain a permit within the time set forth in the rules of the department in order to correct the unsafe condition, after securing public safety as provided above.

§28-305.4.7.2 Monitoring. The owner or the owner’s agent shall monitor the protection of public safety until the unsafe condition is remedied.

§28-305.4.7.3 Reinspection. The owner or the owner’s agent shall reinspect the retaining wall and file an amended report within two weeks after the repairs have been completed certifying that the unsafe conditions of the retaining wall have been corrected.

§28-305.4.7.4 Extension. The commissioner may grant an extension of time of up to 90 days from the date of the application for an extension to complete the repairs required to correct an unsafe condition upon receipt and review of an initial extension application submitted by the registered design professional together with such additional documentation as may be prescribed by rule.

§28-305.4.7.5 Further extension. The commissioner may grant further extensions of time to complete the repairs required to remove an unsafe condition upon receipt and review of an application for a further extension submitted by the registered design professional together with such further documentation as may be prescribed by rule.

§28-305.4.8 Safe with repair and/or engineering monitoring. A retaining wall or any part thereof that may pose a potential danger to persons or property, but does not require immediate action shall be rated safe with repair and/or engineering monitoring. This condition requires further investigation and timely remedial action to prevent its deterioration into an unsafe condition. A registered design professional shall be responsible for appropriately monitoring the wall until the repair is completed.

§28-305.4.8.1 Safe with repair and/or engineering monitoring for two cycles. The registered design professional shall not file a report of safe with repair and/or engineering monitoring for the same retaining wall for 2 consecutive filing periods unless the second such report is accompanied by his or her professional certification attesting to the correction of all conditions identified in the prior report as requiring repair.

§28-305.5 Removal of retaining structures. Any retaining structure, standing partly on the land of each owner, may be removed by either owner when the original reason for the erection of such retaining structure ceases to exist. Notification shall be provided to the adjoining property owner.

ARTICLE 306
PARTY WALLS

§28-306.1 Responsibility for party walls. Repair and maintenance of the construction, design and fire-resistance rating of party walls shall be the joint responsibility of the owners of the adjoining properties, and any change by either owner must maintain the weather protection, structural, vertical fire division and other requirements of this code for party walls.

§28-306.2 Safeguards during construction or demolition. Refer to section [BC] 3309 of the New York [City] city building code for additional requirements for the maintenance of party walls during construction or demolition operations.

ARTICLE 307
WORKPLACE EXITS

§28-307.1 Obstruction of workplace exits prohibited. Except for the exemptions specified in subdivision j of section 27-371 of the administrative code or chapter 10 of the New York [City] city building code, as applicable, it shall be unlawful for an employer or the agent of an employer to lock the doors of a workplace or otherwise obstruct or prohibit exit from a workplace when such act may endanger the health or safety of any employee, independent contractor or other individual in such workplace in the event of a fire or other hazardous condition or event. The commissioner shall classify a violation of this section as an immediately hazardous violation. Notwithstanding any other provision of this code, upon criminal conviction or civil adjudication of liability for a violation of this section an additional fine or civil penalty of not less than five thousand dollars nor more than twenty thousand dollars shall be imposed for each employee, independent contractor or other individual endangered by a violation of this section.

§28-307.1.1 Notice. A sign shall be posted conspicuously at the workplace of a person convicted of or found liable for a violation of section 28-307.1. Such sign shall, in English, Spanish, Korean, Chinese or any other language directed by the fire commissioner, provide notice to employees of the acts prohibited by section 28-307.1 and of the remedies for employer retaliation as set forth in section 28-307.3. The sign shall be in a form and posted in a manner directed by the fire commissioner and may contain any other information deemed necessary by the fire commissioner or as recommended by the police commissioner or the commissioner. The fire commissioner may, in the interest of public safety, adopt a rule requiring the posting of such signs at other workplaces.

§28-307.2 Unannounced inspections of workplaces by fire department. In addition to any other inspections required by law or rule, the fire department shall conduct a minimum of fifty unannounced workplace inspections annually to ensure the identification and abatement of any hazardous conditions in violation of section 28-307.1. Such inspections shall include, but not be limited to, sites where there are known or suspected conditions affecting employee safety and health.

§28-307.3 Retaliation. It shall be unlawful for an employer or the agent of such employer to take a retaliatory action, as defined by section 740 of the labor law, against an employee because of the lawful acts of such employee in furtherance of a civil or criminal enforcement proceeding arising out of the failure of such employer or agent to comply with section 28-307.1 An employee who is the victim of such retaliatory action may commence an action in any court of competent jurisdiction for the relief provided for in this section and shall be entitled to all relief necessary to make such employee whole. Lawful acts of an employee shall include, but not be limited to, assisting in the investigation and initiation of an enforcement proceeding alleging a violation of section 28-307.1, providing testimony in any such proceeding or providing other assistance in connection therewith. The relief to which such employee shall be entitled shall include, but not be limited to, (i) an injunction to restrain any adverse or retaliatory action, (ii) reinstatement to the position such officer or employee would have had but for such action, or to an equivalent position, (iii) reinstatement of full benefits and seniority rights including payment of any missed back pay, plus interest and (iv) compensation for any special damages sustained as a result of such action, including litigation costs and reasonable attorneys’ fees.

ARTICLE 308
ENERGY AUDITS AND RETRO-COMMISSIONING OF BASE BUILDING SYSTEMS

§28-308.1 Definitions. As used in this article, the following terms shall have the following meanings:

BASE BUILDING SYSTEMS. The systems or subsystems of a building that use energy and/or impact energy consumption including:

1.	The building envelope.

2.	The HVAC (heating ventilating and air conditioning) systems.

3.	Conveying systems.

4.	Domestic hot water systems.

5.	Electrical and lighting systems.

Exception: The term "base building systems" shall not include:

1.	Systems or subsystems owned by tenants (other than a net lessee for a term of 49 years or more, inclusive of renewal options), condominium unit owners or cooperative unit shareholders, or a system or subsystems for which a tenant bears full maintenance responsibility and that is within the tenant’s leased space and/or exclusively serves such leased space.

2.	Industrial processes that occur within a covered building.

BUILDING MANAGEMENT SYSTEM. A computer-based system that monitors and controls a building’s mechanical and electrical equipment, such as HVAC, lighting, power, fire, and security systems, including, at a minimum, control of the heating equipment using interior temperature sensors.

CITY BUILDING. A covered building that is owned by the city and for which the city regularly pays all or part of the annual energy bills.

Exception: The term "city building" shall not include:

1.	Any building that participates in the tenant interim lease apartment purchase program.

2.	Any building that participates in a program administered by the department of housing preservation and development.

3.	Any building managed by the New York [City] city health and hospitals corporation.

4.	Any senior college in the City University of New York system.

5.	Any cultural institution that is in the Cultural Institutions Group as determined by the department of cultural affairs.

COOPERATIVE CORPORATION. A corporation governed by the requirements of the state cooperative corporation law or general business law that, among other things, grants persons the right to reside in a cooperative apartment, that right existing by such person’s ownership of certificates of stock, proprietary lease, or other evidence of ownership of an interest in such entity.

COVERED BUILDING. As it appears in the records of the department of finance: (i) a building that exceeds 50,000 gross square feet (4645 m2), (ii) two or more buildings on the same tax lot that together exceed 100,000 gross square feet (9290 m2), or (iii) two or more buildings held in the condominium form of ownership that are governed by the same board of managers and that together exceed 100,000 gross square feet (9290 m2).

Exception: The term "covered building" shall not include real property classified as class one pursuant to subdivision one of section eighteen hundred two of the real property tax law of the state of New York.

CURRENT FACILITY REQUIREMENTS. The owner’s current operational needs and requirements for a building, including temperature and humidity set points, operating hours, filtration, and any integrated requirements such as controls, warranty review, and service contract review.

ENERGY AUDIT OR AUDIT. A systematic process of identifying and developing modifications and improvements of the base building systems, including but not limited to alterations of such systems and the installation of new equipment, insulation or other generally recognized energy efficiency technologies to optimize energy performance of the building and achieve energy savings, provided that such process shall not be less stringent than the Level II Energy Survey and Engineering Analysis of the 2004 edition of Procedures for Commercial Building Energy Audits published by the American Society of Heating, Refrigerating and Air-conditioning Engineers Inc. (ASHRAE).

ENERGY AUDITOR. An approved agency authorized by the department to perform energy audits and to certify audit reports required by this article. Until such time as there is a national standard establishing qualifications for persons performing energy audits and such standard has been adopted by the department, an energy auditor shall be a registered design professional with such other certification or qualification as the department deems to be appropriate. After the establishment of such a national standard, the department may adopt the qualifications of the national standard with such modifications as the department deems to be appropriate.

ENERGY MANAGEMENT SYSTEM. A system incorporating interior temperature sensors and a central processing unit and controls, which are used to monitor and control gas, steam and oil usage, as is applicable, based on the need for heating.

ENERGY EFFICIENCY REPORT. The report required to be filed pursuant to section 28-308.4.

FINANCIAL HARDSHIP (OF A BUILDING). A building shall be considered to be subject to financial hardship if the building:

1.	Had arrears of property taxes or water or wastewater charges that resulted in the property’s inclusion, within two years prior to the due date of an energy efficiency report, on the department of finance’s annual New York City tax lien sale list;

2.	Is exempt from real property taxes pursuant to sections 420-a, 420-b, 446 or 462 of the real property tax law and applicable local law and the owner had negative revenue less expenses during the two tax years prior to the due date of an energy efficiency report as certified to the department by a certified public accountant;

3.	Had outstanding balances under the department of housing preservation and development’s emergency repair program that resulted in the property’s inclusion, within two years prior to the due date of an energy efficiency report, on the department of finance’s annual New York City tax lien sale list; or

4.	Has an active or effective commitment letter from a governmental agency that provides for the financing of the rehabilitation, within a period of 5 years or less, of such building by such government agency for the purposes of affordable housing for low or moderate income families.

OWNER. The owner of record of a covered building, except that in the case of a net lease of an entire building for a term of 49 years or more, inclusive of renewal options, the term owner shall refer to the net lessee and in the case of a covered building held in cooperative or condominium form of ownership, the term owner shall refer to the board of managers in the case of a condominium and the board of directors in the case of a cooperative apartment corporation.

RETRO-COMMISSIONING. A systematic process for optimizing the energy efficiency of existing base building systems through the identification and correction of deficiencies in such systems, including but not limited to repairs of defects, cleaning, adjustments of valves, sensors, controls or programmed settings, and/or changes in operational practices.

RETRO-COMMISSIONING AGENT. An individual, who shall not be a certified refrigerating system operating engineer or a licensed high pressure boiler operating engineer on the staff of the building being retro-commissioned, authorized by the department to certify retro-commissioning reports required by this article. Until such time as there is a national standard establishing qualifications for persons who perform retro-commissioning and such standard has been adopted by the department, a retro-commissioning agent shall be a registered design professional, a certified refrigerating system operating engineer, or a licensed high pressure boiler operating engineer, with such other qualification or certification as determined by the department. After the establishment of such a national standard, the department may adopt the qualifications of the national standard with such modifications as the department deems to be appropriate.

SIMPLE BUILDING. A covered building with neither a central chilled water system nor a central cooling system that covers more than 10 percent of the building’s gross area.

SIMPLE PAYBACK. The number of years for the projected annual energy savings to equal the amount invested in the energy conservation measure, as determined by dividing the investment by the annual energy savings.

SPACE. An area within a building enclosed by floor to ceiling walls, partitions, windows and doors.

SYSTEM OR SUBSYSTEM. Shall have the same definition as set forth in section two hundred two of the New York [City] city energy conservation code.

§28-308.2 Energy audits required. The owner shall ensure that an energy audit is performed on the base building systems of a covered building prior to filing an energy efficiency report as required by this article. Except as otherwise provided in section 28-308.7, an energy audit shall be performed by or under the supervision of an energy auditor and shall be performed in accordance with rules promulgated by the department. The audit process shall cover the base building systems and shall identify at a minimum:

1.	All reasonable measures, including capital improvements, that would, if implemented, reduce energy use and/or the cost of operating the building;

2.	For each measure, the associated annual energy savings, the cost to implement, and the simple payback, calculated by a method determined by the department;

3.	The building’s benchmarking output consistent with the United States Environmental Protection Agency Portfolio Manager tool or as otherwise established by the department;

4.	A break-down of energy usage by system and predicted energy savings by system after implementation of the proposed measures; and

5.	A general assessment of how the major energy consuming equipment and systems used within tenant spaces impact the energy consumption of the base building systems based on a representative sample of spaces.

Exceptions:

1.	No energy audit is required if the building complies with one of the following as certified by a registered design professional:

1.1.	The covered building has received an EPA Energy Star label for at least two of the three years preceding the filing of the building’s energy efficiency report.

1.2.	There is no EPA Energy Star rating for the building type and a registered design professional submits documentation, as specified in the rules of the department, that the building’s energy performance is 25 or more points better than the performance of an average building of its type over a two-year period within the three-year period prior to the filing of an energy efficiency report consistent with the methodology of the LEED 2009 rating system for Existing Buildings published by the United States Green Building Council or other rating system or methodology for existing buildings, as determined by the department.

1.3.	The covered building has received certification under the LEED 2009 rating system for Existing Buildings published by the United States Green Building Council or other rating system for existing buildings, as determined by the department, within four years prior to the filing of the building’s energy efficiency report.

2.	An energy audit shall not be required for the first energy efficiency report of a simple building that is in compliance with six out of seven of the following items as certified by a registered design professional:

2.1.	Individual heating controls. (i) Each dwelling unit in the building has one or more thermostatic controls controlling all the heating units within the dwelling unit and any heated space not within a dwelling unit has one or more thermostatic controls controlling all the heating units within the space, or (ii) the building has a central heating system controlled by an energy management system or a building management system that incorporates temperature sensors located in at least 10 percent of the dwelling units and 10 percent of the heated spaces, except that the total number of sensors required within the building shall not be less than 10 nor more than 30.

2.2.	Common area and exterior lighting. Common area (lighting outside of tenant 	spaces) and exterior lighting, at a minimum, are in compliance with the provisions of the New York [City] city energy conservation code as in effect for new systems installed on or after July 1, 2010.

2.3.	Low flow faucets and shower heads. All faucets and showerheads within the building, at a minimum, meet the standards of Table 604.4 of the New York [City] city plumbing code as in effect for new systems installed on or after July 1, 2010.

2.4.	Pipe insulation. All exposed pipes that are used to convey heat or hot water are insulated, at a minimum, in accordance with the standards of the New York [City] city energy conservation code as in effect for new systems installed on or after July 1, 2010.

2.5.	Domestic hot water. All domestic hot water tanks that do not have built-in insulation are insulated with a minimum insulation value of R-8.

2.6.	Washing machines. All common area clothes washing machines are front loading.

2.7.	Cool roof. The roof complies with section 1504.8 of the New York [City] city building code as in effect for new buildings constructed on or after July 1, 2010.

§28-308.2.1 Contents of audit report. The energy auditor shall prepare and certify a report of the energy audit. Except as otherwise provided in section 28-308.7, the audit report shall include such information relating to the audit as shall be specified in the rules of the department, including but not limited to (i) the date that the audit was completed, and (ii) the information specified in section 28-308.2.

§28-308.2.1.1 Compliance with landmarks laws. The cost estimates for covered buildings that are regulated by any city, state or federal law regulating landmarks and historic buildings shall include all additional costs necessary for the proposed work to comply with such law.

§28-308.2.2 Timing of energy audit. Except as otherwise provided in section 28-308.7, the energy audit shall be completed no earlier than four years prior to the date on which a covered building’s energy efficiency report is filed with the department pursuant to this article.

§28-308.3 Retro-commissioning required. The owner shall ensure that retro- commissioning is performed on the base building systems of a covered building prior to filing an energy efficiency report as required by this article. Except as otherwise provided in section 28-308.7, retro-commissioning shall be performed by or under the supervision of a retro-commissioning agent in accordance with rules promulgated by the department. Such rules, at a minimum, shall ensure that sufficient analysis, corrections and testing have been done so that the base building systems meet the following criteria demonstrating efficient operation:

1.	Operating protocols, calibration, and sequencing:

1.1.	HVAC temperature and humidity set points and setbacks are appropriate and operating schedules reflect major space occupancy patterns and the current facility requirements.

1.2.	HVAC sensors are properly calibrated.

1.3.	HVAC controls are functioning and control sequences are appropriate for the current facility requirements.

1.4.	Loads are distributed equally across equipment when appropriate (i.e. fans, boilers, pumps, etc. that run in parallel).

1.5.	Ventilation rates are appropriate for the current facility requirements.

1.6.	System automatic reset functions are functioning appropriately, if applicable.

1.7.	Adjustments have been made to compensate for oversized or undersized equipment so that it is functioning as efficiently as possible.

1.8.	Simultaneous heating and cooling does not occur unless intended.

1.9.	HVAC system economizer controls are properly functioning, if applicable.

1.10.	The HVAC distribution systems, both air and water side, are balanced.

1.11.	Light levels are appropriate to the task.

1.12.	Lighting sensors and controls are functioning properly according to occupancy, schedule, and/or available daylight, where applicable.

1.13.	Domestic hot water systems have been checked to ensure proper temperature settings.

1.14.	Water pumps are functioning as designed.

1.15.	System water leaks have been identified and repaired.

2.	Cleaning and repair:

2.1.	HVAC equipment (vents, ducts, coils, valves, soot bin, etc.) is clean.

2.2.	Filters are clean and protocols are in place to replace, as appropriate.

2.3.	Light fixtures are clean.

2.4.	Motors, fans, and pumps, including components such as belts, pulleys, and bearings, are in good operating condition.

2.5.	Steam traps have been replaced as required to maintain efficient operation, if applicable.

2.6.	Manual overrides on existing equipment have been remediated.

2.7.	Boilers have been tuned for optimal efficiency, if applicable.

2.8.	Exposed hot and chilled water and steam pipes 3 inches (76 mm) or greater in diameter with associated control valves are insulated in accordance with the standards of the New York [City] city energy conservation code as in effect for new systems installed on or after July 1, 2010.

2.9.	In all easily accessible locations, sealants and weather stripping are installed where appropriate and are in good condition.

3.	Training and documentation:

3.1.	Permits for all HVAC, electrical and plumbing equipment are in order.

3.2.	Critical operations and maintenance staff have received appropriate training, which may include labor/management training, on all major equipment and systems and general energy conservation techniques.

3.3.	Operational and maintenance record keeping procedures (log books, computer maintenance records, etc.) have been implemented.

3.4.	The following documentation is on site and accessible to the operators: the operations and maintenance manuals, if such manuals are still available from the manufacturer, the maintenance contracts, and the most recent retro-commissioning report.

Exception: No retro-commissioning is required if the covered building has received certification under the LEED 2009 rating system for Existing Buildings published by the United States Green Building Counsel or other rating system for existing buildings, as determined by the department, within two years prior to the filing of the building’s energy efficiency report and earned the LEED point for Existing Building Commissioning investigation and analysis and the LEED point for Existing Building Commissioning implementation.

§28-308.3.1 Contents of retro-commissioning report. The retro-commissioning agent shall prepare and certify a retro-commissioning report. The retro-commissioning report shall include such information relating to the retro-commissioning as shall be set forth in the rules of the department including, at a minimum:

1.	Project and team information:

1.1.	Building address.

1.2.	Experience and certification of person performing retro-commissioning and any staff involved in the project.

1.3.	Name, affiliation, and contact information for persons performing retro-commissioning and members of the retro-commissioning team, owner of building, and facility manager of building.

2.	Building information:

2.1.	List of all HVAC, domestic hot water, electrical equipment, lighting, and conveyance equipment types in the base building systems.

2.2.	Benchmarking output.

3.	Testing protocol:

3.1.	List of all equipment types tested.

3.2.	For each equipment type tested, a list of the sample rates (percent of each type of equipment tested), the testing methodology, including any diagnostic equipment used, and the test results.

3.3.	List of integrated system testing performed.

4.	Master list of findings, including for each, the name of the retro-commissioning measure and its assigned number, a brief description of the measure, recommended corrections, the benefits attained, estimated annual savings (energy and cost), the estimated implementation cost, and the simple payback.

5.	Deficiencies corrected:

5.1.	List of repairs completed during investigation.

5.2.	List of deficiencies corrected, including, for each deficiency, the date corrected, by whom the correction was made, the actual cost, and projected savings.

§28-308.3.2 Timing of retro-commissioning. Except as otherwise provided in section 28-308.7, the retro-commissioning shall be completed no earlier than four years prior to the date on which a covered building’s energy efficiency report is filed with the department pursuant to this article.

§28-308.3.3 Documentation of retro-commissioning. A copy of the latest up-to-date equipment manuals and the most recent retro-commissioning report shall be maintained at every covered building and shall be made available upon request for inspection by the department.

§28-308.4 Energy efficiency report required. Except as otherwise provided in section 28-308.7, the owner of a covered building shall file an energy efficiency report for such building between January first and December thirty-first of the calendar year in which such report is due pursuant to this section and between January first and December thirty-first of every tenth calendar year thereafter.

Exceptions:

1. 	An owner may apply for an extension of time to file an energy efficiency report if despite such owner’s good faith efforts, to be documented in such application, the owner is unable to complete the required energy audit and retro-commissioning prior to the scheduled due date for such report. The commissioner may grant no more than two such extensions of no more than one year each. Extensions granted pursuant to this provision shall not extend the scheduled due dates for subsequent energy efficiency reports.

2. 	An owner may receive annual extensions of time to file an energy efficiency report based on financial hardship of the building.

§28-308.4.1 Due dates. The first energy efficiency reports for covered buildings [in existence on the effective date of this article] and for new buildings shall be due [, beginning with calendar year 2013,] in the calendar year with a final digit that is the same as the last digit of the building’s tax block number, as illustrated in the following chart:

| Last digit of tax block number | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Year first EER is due | 2020 | 2021 | 2022 | [2013] 2023 | [2014] 2024 | [2015] 2025 | [2016] 2026 | [2017] 2027 | [2018] 2028 | [2019] 2029 |

Owners of covered buildings (i) that are less than 10 years old at the commencement of their first assigned calendar year or (ii) that have undergone substantial rehabilitation, as certified by a registered design professional, within the 10 year period prior to any calendar year in which an energy efficiency report is due, such that at the commencement of such calendar year all of the base building systems of such building are in compliance with the New York [City] city energy conservation code as in effect for new buildings constructed on and after July 1, 2010, or as in effect on the date of such substantial rehabilitation, whichever is later, may defer submitting an energy efficiency report for such building until the tenth calendar year after such assigned calendar year.

Exceptions:

- [The first due dates for city buildings shall be in accordance with a staggered schedule, commencing with calendar year 2013 and ending with calendar year 2022 for buildings in existence on the effective date of this article, to be submitted by the department of citywide administrative services to the department on or prior to December 31, 2011.] A city building constructed after [the effective date of this article] December 28, 2009 shall be added to such schedule within 10 years after the issuance of the first certificate of occupancy for such building. Copies of energy efficiency reports submitted to the department with respect to city buildings that are not submitted by the department of citywide administrative services shall also be submitted to the department of citywide administrative services.

2.	A cooperative corporation that owns multiple covered buildings located on different tax block numbers, that is required to file an energy efficiency report for more than one covered building in different calendar years, may consolidate all such energy efficiency reports into one report, disaggregated by covered building, due no later than the year in which the last energy efficiency report would be due, which shall be accepted by the department in satisfaction of the requirements of this section for each covered building included in such consolidated report.

§28-308.4.2 Combined audit and retro-commissioning. Nothing in this article shall prevent an owner from performing the audit and the retro-commissioning in a combined process, provided that all the requirements of sections 28-308.2 and 28-308.3 are met.

§28-308.5 Content of energy efficiency report. Except as otherwise provided in section 28-308.7, the energy efficiency report shall include, in a format prescribed by the department, (i) the energy audit report or documentation substantiating that an exception as set forth in section 28-308.2 applies to such building, and (ii) the retro-commissioning report or documentation substantiating that an exception as set forth in section 28-308.3 applies to such building.

§28-308.6 Notification by the department of finance. The department of finance shall notify the owner of the requirements of this article three years prior to the calendar year in which the covered building’s energy efficiency report is due and in the calendar year prior to the calendar year in which such report is due.

[§28-308.7 Early compliance. Notwithstanding any other provision of this article, an owner may submit an energy efficiency report, including both an energy audit report pursuant to section 28-308.7.1 and a retro-commissioning report pursuant to section 28-308.7.2, in the calendar year commencing January 1, 2013 and ending December 31, 2013 in order to achieve early compliance with this section. An energy efficiency report submitted for early compliance shall be deemed to satisfy the first required energy efficiency report for the building as assigned pursuant to section 28-308.4.1. The next required energy efficiency report for such building shall be due in the tenth calendar year after the first assigned due date for such report.]

[§28-308.7.1 Early compliance energy audit report. An energy audit report for a covered building shall be acceptable for early compliance if it is completed after January 1, 2006 and it includes:]

[1. 	The address of the building, completion date of the audit, signature and credentials of the person performing or supervising the performance of the audit and of the audit team; and]

[2. 	The information required in items 1 through 5 of section 28-308.2.]

[§28-308.7.1.1 Early compliance audit completed after January 1, 2006 and prior to the effective date of this article. An early compliance audit completed after January 1, 2006 and prior to the effective date of this article shall have met the following additional criteria:]

[1. 	The audit shall have met the requirements of the Level II Energy Survey and Analysis of the 2004 edition of Procedures for Commercial Building Energy Audits published by ASHRAE; or]

[2. 	The audit shall have been performed under a New York Power Authority or New York State Energy Research and Development Authority (NYSERDA) contract or by a NYSERDA Flex Tech contractor; and]

[3. 	The audit report shall be submitted along with certification by a registered design professional that the audit satisfies the criteria of this section.]

[4. 	A partial audit completed after January 1, 2006 and prior to the effective date of this article shall qualify for early compliance only if the base building systems that were not subject to such audit are audited, after the effective date of this article, in the manner set forth in section 28-308.7.1.2.]

[§28-308.7.1.2 Early compliance audit completed after the effective date of this article. An early compliance audit completed after the effective date of this article shall meet the following additional criteria:]

[1.	The audit shall be performed by or under the supervision of a registered design professional and shall meet the requirements of the Level II Energy Survey and Analysis of the 2004 edition of Procedures for Commercial Building Energy Audits published by ASHRAE;]

[2.	The auditing team shall include an individual who is one of the following:]

[2.1.	A NYSERDA approved Flex Tech contractor;]

[2.2.	A Certified Energy Manager (CEM) or Certified Energy Auditor (CEA), certified by the Association of Energy Engineers (AEE);]

[2.3.	A High-Performance Building Design Professional (HPBD) certified by ASHRAE; or]

[2.4.	For audits of multifamily residential buildings only, a Multi-family Building Analyst (MFBA), certified by the Building Performance Institute (BPI), or have such other qualification or certification as determined by the department;]

[3.	An individual with at least three years of professional experience performing energy audits on buildings larger than 50,000 gross square feet (4645 m2) shall be a member of the auditing team;]

[4.	The building’s operations and maintenance staff shall be consulted at the start of and during the audit process; and]

[5.	The registered design professional performing or supervising the audit shall certify that the audit satisfies the criteria of this section.]

[§28-308.7.2 Early compliance retro-commissioning. A retro-commissioning shall be acceptable for early compliance if it is completed after the effective date of this article and meets the following criteria:]

[1. 	The retro-commissioning shall be performed under a NYSERDA contract for base building retro-commissioning or certified by an individual who is not on the staff of the building and is (i) a registered design professional, (ii) a certified refrigerating system operating engineer, or (iii) a licensed high pressure boiler operating engineer;]

[2. 	The retro-commissioning team shall include an individual who is a Certified Commissioning Professional (CCP) certified by the Building Commissioning Association (BCA), a Certified Building Commissioning Professional (CBCP) certified by the AEE, a Commissioning Process Management Professional (CPMP) certified by ASHRAE, or an Accredited Commissioning Process Authority Professional (ACPAP) approved by the University of Wisconsin, or has such other certification as determined by the department;]

[3. 	The retro-commissioning team shall include an individual with at least one year of professional experience performing retro-commissioning on the mechanical systems of buildings larger than 50,000 gross square feet (4645 m2);]

[4. 	The building’s operations and maintenance staff shall be consulted at the start of and during the retro-commissioning process; and]

[5. 	The retro-commissioning report shall contain a certification that sufficient analysis and testing has been done and corrections have been performed so that the base building systems meet the criteria of section 28-308.3 and shall include the information specified in section 28-308.3.1.]

[6. 	Nothing in this section shall be construed to determine which individuals may perform the work to correct deficiencies identified during the retro- commissioning process, except as otherwise provided by applicable law.]

[§28-308.8 Optional compliance for energy efficiency reports due in the calendar year commencing January 1, 2013. Notwithstanding any other provision of this article, audits and retro-commissioning for energy efficiency reports scheduled to be due in the calendar year commencing January 1, 2013 shall be performed, at the option of the owner, in accordance with the provisions for early compliance as set forth in section 28-308.7 or in accordance with procedures set forth in the rules of the department, if such procedures are promulgated within one year prior to the due date of such report. If such procedures are not promulgated within one year prior to the due date of such report, audit and retro-commissioning for energy efficiency reports due in the calendar year commencing January 1, 2013 shall comply with the audit and retro-commissioning procedures for early compliance.]

[§28-308.9] §28-308.7 Rules. The department shall promulgate such rules as are necessary to carry out the provisions of this article in a timely manner, which may include separate fees for filing and review of applications and reports filed pursuant to this article.

ARTICLE 309
BENCHMARKING ENERGY AND WATER USE
AND DISCLOSURE OF ENERGY EFFICIENCY SCORES AND GRADES

§28-309.1 General. The energy and water use of city buildings and covered buildings shall be benchmarked in accordance with this article.

§28-309.2 Definitions. As used in this article, the following terms shall have the following meanings:

BENCHMARK. To input and submit to the benchmarking tool the total use of energy and water for a building for the previous calendar year and other descriptive information for such building as required by the benchmarking tool.

BENCHMARKING TOOL. The internet-based database system developed by the United States environmental protection agency, and any complementary interface designated by the office of long-term planning and sustainability, to track and assess the energy and water use of certain buildings relative to similar buildings.

CITY BUILDING. A building that is more than 10,000 gross square feet (929 m²), as it appears in the records of the department of finance, that is owned by the city or for which the city regularly directly pays all of the annual energy bills, provided that two or more buildings on the same tax lot shall be deemed to be one building.

Exception: The term "city building" shall not include:

1.	Any building owned by the city that participates in the tenant interim lease apartment purchase program; or

2.	Any building owned by the city that (i) is 25,000 gross square feet (2323 m²) or less, as it appears in the records of the department of finance, and (ii) participates in a program administered by the department of housing preservation and development.

COVERED BUILDING. As it appears in the records of the department of finance: (i) a building that exceeds 25,000 gross square feet (2323 m²), (ii) two or more buildings on the same tax lot that together exceed 100,000 gross square feet (9290 m²), (iii) two or more buildings held in the condominium form of ownership that are governed by the same board of managers and that together exceed 100,000 gross square feet (9290 m²), or (iv) a city building.

Exceptions: The term "covered building" shall not include:

1.	Any building owned by the city that participates in the tenant interim lease apartment purchase program.

2.	Real property classified as class one pursuant to subdivision one of section 1802 of the real property tax law.

3.	Real property, not more than three stories, consisting of a series of attached, detached or semi-detached dwellings, for which ownership and the responsibility for maintenance of the HVAC systems and hot water heating systems is held by each individual dwelling unit owner, and with no HVAC system or hot water heating system in the series serving more than two dwelling units, as certified by a registered design professional to the department.

DATA CENTER. A room or rooms used primarily to house [high density] high-density computing equipment, such as server racks, used for data storage and processing.

DWELLING UNIT. A single unit consisting of one or more habitable rooms, occupied or arranged to be occupied as a unit separate from all other units within a building, and used primarily for residential purposes and not primarily for professional or commercial purposes.

ENERGY. Electricity, natural gas, fuel oil and steam.

OWNER. The owner of record, provided that "owner" shall be deemed to include: (i) the net lessee in the case of a building subject to a net lease with a term of at least forty-nine years, inclusive of all renewal options, (ii) the board of managers in the case of a condominium, and (iii) the board of directors in the case of a cooperative apartment corporation.

TENANT. Any tenant, tenant-stockholder of a cooperative apartment corporation, condominium unit owner or other occupant.

§28-309.3 Benchmarking required for city buildings. [No later than May 1, 2010, and no] No later than every May first [thereafter] , any city building shall be benchmarked by the agency or entity primarily responsible for the management of such building, in coordination with the department of citywide administrative services with respect to energy use, and with the New York [City] city department of environmental protection with respect to water use. Benchmarking of water use shall not be required unless the building was equipped with automatic meter reading equipment by the New York [City] city department of environmental protection for the entirety of the previous calendar year. The city shall maintain such documents as the department determines are necessary for the purpose of carrying out the provisions of this article.

§28-309.4 Benchmarking required for covered buildings other than city buildings. The owner of a covered building, other than a city building, shall annually benchmark such covered building [no later than May 1, 2011, and] no later than every May [1 thereafter] first. Benchmarking of water use shall not be required unless the building was equipped with automatic meter reading equipment by the New York [City] city department of environmental protection for the entirety of the previous calendar year. The owner or the owner’s representative performing the benchmarking shall consult with the operating staff of the building, as appropriate. Information submitted to the benchmarking tool must be accurate and complete.

Exception: The first mandatory benchmarking for a covered building, other than a city building, that (i) does not exceed 50,000 gross square feet (4645 m2), (ii) is not one of two or more buildings on the same tax lot that together exceed 100,000 gross square feet (9290 m2) and (iii) is not one of two or more buildings held in the condominium form of ownership that are governed by the same board of managers and that together exceed 100,000 gross square feet (9290 m2), shall be completed on or before May [1] first of the first year that commences after the department determines and sets forth in a rule that the utility company providing energy to such buildings will, upon request of an owner, directly upload information necessary to benchmark such building.

§28-309.4.1 Obligation to report energy use for all utility accounts and addresses connected to the building. The owner shall submit information to the benchmarking tool for all utility accounts and addresses connected to the building, including those for separately metered tenant spaces. The owner shall obtain information for separately metered tenant spaces from the utility. If the utility does not have a program to provide such information, the owner shall make reasonable efforts to obtain such information from the tenant. Tenants shall have the obligation to provide such information.

§28-309.4.2 Preservation of documents, inspection, and audit. An owner of a covered building shall maintain such records as the department determines are necessary for carrying out the purposes of this article, including but not limited to energy and water bills and reports or forms received from utilities and tenants. Where energy use within separately metered tenant spaces is omitted, records shall be maintained documenting owner’s efforts to obtain such information. All records shall be preserved for a period of three years, provided that the commissioner may consent to their destruction within that period or may require that such records be preserved longer than such period. At the request of the department, such records shall be made available for inspection and audit by the department at the place of business of the owner or at the offices of the department during normal business hours.

§28-309.4.3 Violations. It shall be unlawful for the owner of a covered building to fail to benchmark pursuant to section 28-309.4. The commissioner shall classify such violation as a lesser violation. If, upon audit of a benchmarking report, the department finds that information submitted to the benchmarking tool was substantially inaccurate or incomplete, the department may reject the purported benchmarking and the owner shall be liable for a violation of section 28-309.4 as if no benchmarking had been performed.

Exception: Notwithstanding section 28-204.2, no civil penalty shall be imposed on the owner of a covered building for a violation of this section for such covered building if:

1.	Such covered building (i) does not exceed 50,000 gross square feet (4645 m2), (ii) is not two or more buildings on the same tax lot that together exceed 100,000 gross square feet (9290 m2), (iii) is not two or more buildings held in the condominium form of ownership that are governed by the same board of managers and that together exceed 100,000 gross square feet (9290 m2), and (iv) is not a city building;

2.	Such owner requested, from the department or another agency designated pursuant to section 28-309.11, benchmarking assistance in connection with such building, and such request was made at least 60 days before the due date of the benchmarking report for which such violation was issued; and

3.	Such owner corrects such violation within 60 days after the date of the notice of such violation.

§28-309.5 Direct upload. Information shall be directly uploaded to the benchmarking tool in accordance with the following:

§28-309.5.1 Direct upload by a utility company or other source. The office of long-term planning and sustainability shall encourage and facilitate any utility company or any other source authorized by the office of long-term planning and sustainability to upload directly to the benchmarking tool as soon as practicable, information necessary to benchmark a building.

§28-309.5.2 Direct upload by the New York [City] city department of environmental protection. The New York [City] city department of environmental protection shall upload directly to the benchmarking tool information on water use at all buildings that were equipped with automatic meter reading equipment by the New York [City] city department of environmental protection for the entirety of the previous calendar year and that are subject to the benchmarking requirements of this article.

§28-309.6 Suspension. The director of the office of long-term planning and sustainability may suspend all or part of the requirement to benchmark pursuant to this article upon a written finding that a technological deficiency in the benchmarking tool precludes compliance with this article. The director of the office of long-term planning and sustainability may lift all or part of any such suspension upon a written finding that such deficiency has been corrected. The office of long-term planning and sustainability shall notify the speaker of the city council, the department, the department of citywide administrative services, the [New York City] department of environmental protection and the department of finance promptly upon issuing a suspension or lifting a suspension pursuant to this section.

§28-309.7 Notification and transmission of information. The department of finance shall:

1.	Annually notify owners of covered buildings of their obligation to benchmark pursuant to section 28-309.4, provided that the failure of the department of finance to notify any such owner shall not affect the obligation of such owner to benchmark pursuant to such section.

2.	Notify owners of covered buildings of any suspension or lifting of a suspension pursuant to section 28-309.6.

3.	Make available to the department information regarding owners of covered buildings for which no benchmarking information was generated by the benchmarking tool.

§28-309.8 Disclosure. The department of finance shall make information generated by the benchmarking tool available to the public on the internet no later than September [1] first of the year in which the covered buildings are benchmarked. Such information shall include, but need not be limited to: (i) the energy use intensity, (ii) the water use per gross square foot, (iii) where available, a rating or score that compares the energy and water use of the building to that of similar buildings, and (iv) a comparison of data across calendar years for any years such building was benchmarked. [Information generated by the benchmarking tool for the 2009 calendar year for city buildings, for the 2010 calendar year for covered buildings, and for the 2011 calendar year for covered buildings whose primary use is residential, as determined by the department of finance, shall not be disclosed.]

Exception: Ratings or scores generated by the benchmarking tool for a covered building that contains a data center, television studio, and/or trading floor that together exceed ten percent of the gross square footage of any such building shall not be disclosed until the office of long-term planning and sustainability determines that the benchmarking tool can make adequate adjustments for such facilities. When the office of long-term planning and sustainability determines that the benchmarking tool can make such adjustments, it shall report such determination to the mayor and the speaker of the city council. Until such determination is made, the office of long-term planning and sustainability shall report biennially to the mayor and the speaker of the city council that the benchmarking tool is unable to make such adjustments.

§28-309.9 Report. No later than December 31 of each year, the office of long-term planning and sustainability shall prepare, submit to the mayor and the speaker of the city council, and post on the internet a report reviewing and evaluating the administration and enforcement of this article and analyzing data obtained from the benchmarking tool. Such report shall contain information regarding: (i) the energy and water efficiency of buildings in the city, (ii) the accuracy of benchmarked data and whether there is a need to train and/or certify individuals who benchmark, (iii) compliance with the requirements of this article, (iv) any administrative and legislative recommendations for strengthening the administration and enforcement of this article, (v) the effectiveness of the benchmarking tool in accounting for New York City conditions, including, but not limited to, high density occupancies, use of steam, large building size, and specific high-energy uses such as data centers, television studios, and trading floors, and (vi) such other information and analyses as the office of long-term planning and sustainability deems appropriate.

§28-309.10 Rules. The department, the department of finance and the office of long-term planning and sustainability may promulgate such rules as deemed necessary to carry out the provisions of this article.

§28-309.11 Benchmarking assistance. The department or another agency designated by the mayor shall establish a system to receive and respond to requests from owners for assistance with respect to fulfilling the benchmarking requirements of this section. Such assistance may include, but need not be limited to, trainings, the provision of reference guides, and a publicized telephone number and email address to receive direct questions. The annual notice required by section 28-309.7 shall notify covered building owners that such assistance is available and shall describe how such assistance can be obtained.

§28-309.12 Energy efficiency scores and energy efficiency grades. Energy efficiency scores and grades for buildings shall be obtained, assigned and disclosed in accordance with this section.

§28-309.12.1 Definitions. As used in section 28-309.12, the following terms shall have the following meanings:

ENERGY EFFICIENCY GRADE. The term “energy efficiency grade” means, for a covered building, a grade based on an energy efficiency score assigned through the benchmarking tool in accordance with this section as follows:

1.	If such score is equal to or greater than 85, the energy efficiency grade shall be A;

2.	If such score is equal to or greater than 70 but less than 85, the energy efficiency grade shall be B;

3.	If such score is equal to or greater than 55 but less than 70, the energy efficiency grade shall be C;

4.	If such score is less than 55, the energy efficiency grade shall be D;

5.	If the owner of such building has not complied with section 28-309.12.2, and such owner has had an opportunity to be heard with respect to such non-compliance, the energy efficiency grade shall be F; and

6.	If, in accordance with the rules of the department, it is not feasible to obtain an energy efficiency score for such building or if such building is subject to the exception in section 28-309.8, the energy efficiency grade shall be N.

ENERGY EFFICIENCY SCORE. The term "energy efficiency score" means, for a building, the Energy Star rating for such building or a score that assesses the energy use of such building relative to similar buildings that is assigned through the benchmarking tool.

ENERGY STAR RATING. The rating that a building earns using the United States Environmental Protection Agency ENERGY STAR portfolio manager to compare building energy performance to similar buildings in similar climates.

§28-309.12.2 Energy efficiency score and energy efficiency grade required. In 2020 and in each calendar year thereafter, an owner of a covered building shall use the benchmarking tool to provide an energy efficiency score for such building to the department in accordance with the rules of the department unless, in accordance with such rules, the building is a type of building for which it is not feasible to obtain an energy efficiency score. In each such year, the department shall issue an energy efficiency grade to the owner in accordance with such rules.

§28-309.12.3 Display of energy efficiency score and energy efficiency grade. Within 30 days after the owner of a covered building obtains an energy efficiency grade, such owner shall post such grade and the energy efficiency score upon which such grade was based in a conspicuous location near each public entrance to such building, in a form and manner established by the department.

Exception: This section 28-309.12.3 shall not apply to posting of the energy efficiency score of a building with an energy efficiency grade of N.

§28-309.12.4 Publication of energy efficiency grades and energy efficiency scores. For each building for which an energy efficiency grade or energy efficiency score is generated pursuant to this section, the department shall make information generated in connection with such grade and score publicly available online by no later than May 1 of the year following such generation.

Exception: This section 28-309.12.4 shall not apply to information generated with respect to a building with an energy efficiency grade of N.

§28-309.12.5 Audits. The department shall, from time to time, audit information submitted for buildings in connection with energy efficiency grades and energy efficiency scores. Such audits shall occur at least annually and shall involve appropriate sample size of buildings, as determined by the department.

§28-309.13 Outreach to building owners regarding making energy efficiency improvements. Each year, the department shall provide information regarding energy efficiency improvements to owners of buildings of all sizes, including buildings connected to gas lines. Such information shall also be posted on the department’s website. The information shall include but not be limited to making energy efficiency improvements including the use of fossil fuel alternatives, the benefits of energy efficiency improvements, compliance with the New York city energy conservation code, and compliance with other laws aimed at reducing building energy use and carbon emissions.

ARTICLE 310
REQUIRED UPGRADE OF LIGHTING SYSTEMS

§28-310.1 General. Lighting systems in covered buildings shall be upgraded as provided for in this article.

§28-310.2 Definitions. As used in this article, the following terms shall have the following meanings:

COVERED BUILDING. As it appears in the records of the department of finance: (i) a building that exceeds 25,000 gross square feet (2323 m2), (ii) two or more buildings on the same tax lot that together exceed 100,000 gross square feet (9290 m2) or (iii) two or more buildings held in the condominium form of ownership that are governed by the same board of managers and that together exceed 100,000 gross square feet (9290 m2).

Exceptions: The term "covered building" shall not include:

1.	Real property classified as class one pursuant to subdivision one of section eighteen hundred two of the real property tax law; or

2.	Real property, not more than three stories, consisting of a series of attached, detached or semi-detached dwellings, for which ownership and the responsibility for maintenance of the HVAC systems and hot water heating systems is held by each individual dwelling unit owner, and with no HVAC system or hot water heating system in the series serving more than two dwelling units, as certified by a registered design professional to the department.

§28-310.3 Upgrade of lighting systems of covered buildings required. No later than January 1, 2025, the lighting systems of covered buildings shall be in compliance with the standards for new systems set forth in the New York [City] city energy conservation code and/or applicable standards referenced in such energy code. The owner of a covered building shall ensure that the upgrade of the lighting system of the entire covered building is completed on or prior to such date and shall file a report with the department, in accordance with the rules of the department, prepared by a registered design professional or a licensed master or special electrician certifying that such upgrade has been completed and that the work is in compliance with the technical standards of the New York [City] city electrical code. The department may impose a fee for filing and review of such reports.

Exceptions:

1.	An element of a lighting system that is in compliance with the standards of the New York city energy conservation code and/or applicable standards referenced in such code as in effect for new systems installed on or after July 1, 2010.

2.	Lighting power densities in any space bounded by permanent floor-to-ceiling partitions and/or closable doors that are in compliance with the standards of the New York city energy conservation code and/or applicable standards referenced in such code as in effect for new systems installed on or after July 1, 2010.

[2] 3.	The lighting system within dwelling units classified in occupancy group R-2 or R-3.

[3] 4.	The lighting system within a space classified in occupancy group A-3 that is within a house of worship.

ARTICLE 311
INSTALLATION OF ELECTRICAL SUB-METERS IN TENANT SPACES

§28-311.1 General. Sub-meters shall be installed in covered buildings as provided in this article.

§28-311.2 Definitions. As used in this article, the following terms shall have the following meanings:

COVERED BUILDING. As it appears in the records of the department of finance: (i) a building that exceeds 25,000 gross square feet (2323 m2), (ii) two or more buildings on the same tax lot that together exceed 100,000 gross square feet (9290 m2), or (iii) two or more buildings held in the condominium form of ownership that are governed by the same board of managers and that together exceed 100,000 gross square feet (9290 m2).

Exceptions: The term "covered building" shall not include:

1.	Real property classified as class one pursuant to subdivision one of section eighteen hundred two of the real property tax law; or

2.	Real property, not more than three stories, consisting of a series of attached, detached or semi-detached dwellings, for which ownership and the responsibility for maintenance of the HVAC systems and hot water heating systems is held by each individual dwelling unit owner, and with no HVAC system or hot water heating system in the series serving more than two dwelling units, as certified by a registered design professional to the department.

COVERED TENANT SPACE. (i) A tenant space larger than 5,000 gross square feet (465 m2) on one or more floors of a covered building let or sublet to the same person, or (ii) a floor, of a covered building, larger than 5,000 gross square feet (465 m²) consisting of tenant spaces let or sublet to two or more different persons.

Exception: The term "covered tenant space" shall not include dwelling units classified in occupancy group R-2 or R-3.

METER. A device installed by an electrical utility company or corporation that measures the flow of electricity supplied to a building or to a defined space within a building and used by the utility to bill consumers for electrical service.

SUB-METER. A device meeting the standards of the department or, where applicable, the public service commission, installed within a building’s electrical distribution system that measures the flow of electricity within a defined space within the building and that may, but need not, be used for apportioning the cost of electricity among the building’s tenants or subtenants.

TENANT SPACE. Space within a covered building that is let or sublet to another person by the owner or a lessee of such space.

§28-311.3 Sub-meters required for covered tenant spaces. On and after January 1, 2025, the electrical consumption of each covered tenant space shall be measured by one or more sub-meters. Sub-meters shall be installed in existing covered tenant spaces by the owner or the lessor of such space on or before January 1, 2025 and thereafter as new covered tenant spaces are created within the building. If the covered tenant space is a floor with multiple tenancies, each tenancy that is 5,000 gross square feet (465 m2) or less shall (i) have a separate sub-meter, (ii) share a sub-meter with other tenant spaces on the floor, or (iii) share a sub-meter covering the entire floor.

Exception: Covered tenant space for which the electrical consumption within such space is measured by a meter dedicated exclusively to that space.

§28-311.4 Monthly statements. Each tenant or subtenant within a covered tenant space that has a sub-meter or sub-meters to measure electrical consumption shall be provided with a monthly statement showing the amount of electricity measured by the sub-meter for such tenant or subtenant during the month, and any amount charged to the tenant or subtenant for electricity. If the covered tenant space is a floor with multiple tenancies and the tenant’s sub-meter covers other tenant spaces, the statement for such tenant shall show the electrical consumption for the area covered by the sub-meter and the percentage of that area that is leased by the tenant.

§28-311.5 Reports. The owner of each covered building shall file a report in accordance with the rules of the department prepared by a registered design professional or a licensed master or special electrician certifying that sub-meters have been installed in all covered tenant spaces in such building as required by this article or that covered tenant spaces are subject to the exception set forth in section 28-311.3. The department may impose a fee for filing and processing such reports.

ARTICLE 312
CARBON MONOXIDE AND SMOKE ALARMS

§28-312.1 General. Required carbon monoxide and smoke alarms shall comply with the provisions of this article.

§28-312.2 Periodic replacement of carbon monoxide alarms. Carbon monoxide alarms required pursuant to section [908.7] 915.1 of the New York [City] city building code or sections 27-981.1, 27-981.2 and 27-981.3 of the 1968 building code shall be replaced when the time elapsed since the installation of such alarm exceeds the manufacturer’s suggested useful life of the alarm.

Exception: A carbon monoxide alarm installed [prior to the effective date of this article] before April 25, 2012 shall be replaced when the time elapsed since the installation of such alarm exceeds the manufacturer’s suggested useful life of the alarm [or within 6 months after the effective date of this article, whichever is later].

§28-312.3 Audible notification of expiration of useful life of carbon monoxide alarms. All carbon monoxide alarms installed after [the effective date of this article] April 25, 2012 shall comply with UL 2034 and be of a type that emits an audible notification at the expiration of the useful life of such alarm.

§28-312.4 Periodic replacement of smoke alarms. Smoke alarms required pursuant to section 907.2 of the New York [City] city building code or sections 27-978, 27-979, 27-980 and 27-981 of the 1968 building code shall be replaced when the time elapsed since the installation of such alarm exceeds the manufacturer’s suggested useful life of the alarm.

Exception: A smoke alarm installed [prior to the effective date of this section] before April 1, 2014 and whose end of useful life is not known shall be replaced with an alarm that complies with section 28-312.5 [within 7 years after the effective date of this section] by no later than April 1, 2021.

§28-312.5 Audible notification of expiration of useful life of smoke alarms. All smoke alarms installed after [the effective date of this section] April 1, 2014 shall comply with UL 217, shall employ a non-removable, non-replaceable battery that powers the alarm for a minimum of 10 years, and shall be of the type that emits an audible notification at the expiration of the useful life of the alarm.

§28-312.8 Location of smoke alarms and smoke detectors. On or after January 1, 2021, smoke alarms and smoke detectors installed or replaced in group R occupancies shall be installed in accordance with section [907.2.11.5] 907.2.11.6 of the New York city building code.

ARTICLE 313
ACCESSIBILITY

§28-313.1 Retroactive requirement for directional signage at building entrances. The provisions of section [1110.2] 1111.2 of the New York [City] city building code requiring directional signage to be posted at inaccessible building entrances indicating the route to the nearest accessible entrance shall apply retroactively to all buildings that have such accessible entrances. [Buildings in existence on the effective date of this section shall post such directional signage on or before August 1, 2013.] Such directional signage shall be maintained in good condition.

Exception: Directional signage posted at building entrances in compliance with the americans with disabilities act of 1990 shall be deemed to be in compliance with section [1110.2] 1111.2 of the New York [City] city building code.

§28-313.2 Retroactive requirement for accessible building entrances. The provisions of item [5] 4 of section [1110.1] 1111.1 of the New York [City] city building code requiring signage to be posted at accessible entrances where an inaccessible building entrance exists shall apply retroactively to all buildings that have such accessible entrances. [Buildings in existence on the effective date of this section shall post such signage on or before August 1, 2013. Such signage shall be maintained in good condition.]

Exception: Accessible entrance signs that are posted at building entrances in compliance with the americans with disabilities act of 1990 shall be deemed to be in compliance with section [1110.1] 1111.1 of the New York [City] city building code subject to the inclusion on or adjacent to such signage of a contact telephone number or instructions to gain access if an otherwise accessible building entrance is subject to locking.

§28-313.3 Retroactive requirement for signage and safety requirements for portable ramps at inaccessible building entrances where such ramps are permissible. The provisions of item 7 of section [1110.3] 1111.3 of the New York city building code requiring that signage stating a portable ramp is available, if provided by the building, and the phone number to request such ramp, be posted at inaccessible building entrances shall apply retroactively to all prior code buildings that have such portable ramps where use of such a ramp is permissible. The use of a portable ramp by any building must comply with all applicable laws, and must comply with Section 405 (Ramps) of ICC A117.1 except to the extent the commissioner has waived a requirement pursuant to section 28-313.3.1. All signage posted pursuant to this section shall comply with Section [1110] 1111 of the New York city building code and be maintained in good condition. Nothing in this section shall be construed to authorize the provision of a portable ramp where such provision would not otherwise be lawful.

§28-313.3.1 Waiver of requirements related to portable ramps at inaccessible building entrances where such ramps are permissible. The commissioner may waive the requirement of section 28-313.3 that all portable ramps used by prior code buildings must comply with Section 405 (Ramps) of ICC A117.1, provided, however, that such waiver would not significantly adversely affect safety and that equally safe and proper alternatives are prescribed and, further, that such waiver is based upon a specific finding by the commissioner that strict compliance with the requirement:

1.	Would create an undue economic burden;

2.	Would not achieve its intended objective;

3.	Would be physically or legally impossible;

4.	Would be unnecessary in light of alternatives which ensure the achievement of the intended objective or which, without a loss in the level of safety, achieve the intended objective more efficiently, effectively or economically; or

5.	Would entail a change so slight as to produce a negligible additional benefit.

§28-313.3.2 Waiver application process. Each application for a waiver under section 28-313.3.1 shall be made to the commissioner in writing, setting forth each requirement of Section 405 (Ramps) of ICC A117.1 sought to be waived and the specific reason or reasons therefore. The commissioner shall determine, under all of the circumstances presented by such application, which of such requirements may appropriately be waived. The commissioner shall render such determination in a writing, which shall set forth in detail the commissioner’s findings and conclusions with respect to each requirement sought to be waived. A copy of such written determination shall be forwarded to the applicant. Such written determination shall be filed with the department and shall be available for public inspection.

§28-313.3.3 Waiver recommendation. The mayor’s office for people with disabilities, or its successor agency shall be consulted by and shall advise the commissioner concerning each application for a waiver under section 28-313.3.1.

ARTICLE 314
 [PERIODIC WASTEWATER RECYCLING SYSTEM INSPECTION 
AND TESTING] 
RESERVED

[§28-314.1 General. Wastewater recycling systems installed in accordance with section C102 of appendix C of the New York City plumbing code shall be periodically inspected and tested in accordance with this article. This article shall not apply to rainwater recycling systems installed in accordance with section C103 of appendix C of the New York City plumbing code.]

[§28-314.2 Frequency of inspection and testing. The owner shall test and inspect wastewater recycling systems on a monthly basis. The commissioner may require additional testing and inspections of wastewater recycling systems as necessary to protect public safety.]

[§28-314.3 Inspection and testing process. Wastewater recycling systems shall be inspected and tested in accordance with sections 28-314.3.1 through 28-314.3.6.]

[§28-314.3.1 Inspection and testing entities. Required tests performed on behalf of the owner shall be performed by an approved agency with qualifications as set forth in department rules.]

[§28-314.3.2 Scope. At each test and inspection, in addition to the requirements prescribed by this article, all wastewater treatment equipment provided for operation of wastewater recycling systems shall be inspected to determine that they are in safe operating condition and parts have not worn to such an extent as to affect the safe and reliable operation of the installation. At each test and inspection, treated effluent from the wastewater recycling system shall be sampled and tested, the results of which shall comply with section C102.1 of the New York City plumbing code.]

[§28-314.3.3 Notation of inspection or test. After each test and inspection, the inspector shall affix the inspection date and his or her signature over a stamp identifying his or her approved agency and his or her approval number on the inspection certificate issued by the department.]

[§28-314.3.4 Inspection and test reports submission. Inspection and test reports shall be submitted on forms in such manner as required by the commissioner. Each inspection and test report shall include a listing of all violations for each device inspected and tested associated with the wastewater recycling system. A copy of the report, signed by the inspector performing the inspection and tests shall be delivered to the owner within 30 days of the site visit. All reports shall be kept on file by the approved agency and the owner for a period of at least 6 years.]

[§28-314.3.5 Reporting an unsafe or hazardous condition. The operation of the system shall immediately cease if any test sample does not meet the minimum water quality standards of Table C102.1 of the New York City plumbing code. The wastewater recycling system shall be placed into start-up mode and testing shall commence for at least five consecutive days demonstrating full compliance. If further inspection and testing reveals that the wastewater recycling system test samples do not meet the minimum water quality standards in table C102.1 of the New York City plumbing code, the system shall be taken out of service immediately by the agency performing the inspection. The building owner shall be notified immediately by the agency performing the inspection. The department shall be notified by the agency that the system has been taken out of service within 24 hours by telephone, electronically, in writing or as otherwise directed by the commissioner.]

[§28-314.3.6 Repair. All defects and violations identified during the inspection and testing process shall be corrected immediately prior to continuing the operation of the wastewater recycling system.]

ARTICLE 315
RETROACTIVE REQUIREMENTS

§28-315.1 General. Buildings must be in compliance with the retroactive requirements of the provisions of this code. Such requirements are listed in this article along with the dates by which compliance must be achieved. The retroactive requirements of the 1968 building code continue in effect under this code in accordance with section 28-102.4.1 of this code. The dates for compliance with the retroactive requirements of the 1968 building code are as set forth in the applicable provisions of such 1968 building code. Failure to comply with a retroactive requirement of this code or of the 1968 building code by the date specified for such compliance is a violation of this code.

§28-315.2 Fire protection systems. The work specified in this section to enhance the fire protection systems of buildings shall be completed by the dates specified herein.

§28-315.2.1 Painting of certain exposed portions of sprinkler systems. The painting of exposed risers, cross connections and handles of valves of sprinkler systems in accordance with the retroactive requirements of section 903.6.3 of the New York [City] city building code shall be completed by June 2, 2010 and certification of such painting shall be maintained in accordance with section 903.6.5 of such code.

§28-315.2.2 Painting of certain exposed portions of standpipe systems. The painting of exposed portions of standpipe systems and handles of valves serving such systems in accordance with the retroactive requirements of section 905.11.3 of the New York [City] city building code shall be completed by June 2, 2010 and certification of such painting shall be maintained in accordance with section 905.11.6 of such code.

§28-315.2.3 Animal service facilities. By December 31, 2016, animal service facilities shall comply with the retroactive requirements of section 903.2.2.2 of the New York city building code and owners of such facilities shall file with the department a report certifying either that sprinklers have been installed or that the facility is in compliance with one of the exceptions set forth in such section.

§28-315.3 Sustainability. The work specified in this section to enhance the sustainability of buildings must be completed by the dates specified herein.

§28-315.3.1 Lighting systems. By January 1, 2025, the lighting systems of certain buildings shall be in compliance with article 310 of this chapter and the owners of such buildings shall file a report in accordance with the rules of the department, prepared by a registered design professional or a licensed master or special electrician, certifying compliance with such section and compliance with the technical standards of the New York city electrical code. The department may impose a fee for filing and reviewing such reports.

§28-315.3.2 Electrical sub-meters. By January 1, 2025, the installation of electrical sub-meters in tenant spaces in certain buildings in accordance with article 311 of this chapter shall be completed and the owners of such buildings shall file a report in accordance with the rules of the department, prepared by a registered design professional or a licensed master or special electrician, certifying compliance with such section. The department may impose a fee for filing and reviewing such reports.

§28-315.4 Elevator safety. The work specified in this section to improve the safety of existing elevators shall be completed by the dates specified herein.

§28-315.4.1 Compliance with ASME A17.3 of [2002] 2015. Existing elevators and escalators shall, at a minimum, comply with ASME A17.3 of [2002] 2015, as modified by chapter K3 of appendix K of the New York [City] city building code. [All work to achieve compliance with such requirements shall be completed by December 14, 2009.]

Exceptions:

1.	Spaces below hoistways. Spaces below hoistways shall be protected in accordance with section 2.5 of chapter K3 of such appendix by December 14, 2010.

2.	Car doors and gates. Car doors and gates shall be in compliance with section 3.4.2 of chapter K3 of such appendix by December 14, 2012.

3.	Car illumination. Car illumination shall be in compliance with section 3.4.5 of chapter K3 of such appendix by December 14, 2010.

4.	Traction elevators. Traction elevators with single plunger brakes shall be in compliance with section 3.8.4.1 of chapter K3 of such appendix by January 1, 2027.

5.	Electrical protective devices. Electrical protective devices shall be in compliance with section 3.10.4 of chapter K3 of such appendix by December 14, 2010.

6.	Automatic passenger and freight elevators. Automatic passenger and freight elevators shall be in compliance with section 3.10.12 of chapter K3 of such appendix by January 1, 2020.

7.	Hydraulic elevators. Hydraulic elevators shall be in compliance with section 4.3.3 of chapter K3 of such appendix by December 14, 2014.

8.	Escalator skirt obstruction devices. Escalator skirt obstruction devices shall be in compliance with Section 5.3.7 of Chapter K3 of such appendix by January 1, 2014.

§28-315.5 Fuel gas systems. The work specified in this section to enhance the safety of fuel gas systems shall be completed by the dates specified herein.

§28-315.5.1 Outside gas shut-off. Existing gas services shall be provided with an outside emergency shutoff device acceptable to the commissioner and the fire commissioner in accordance with the retroactive requirements of item 1 of section [E6] E.6 of appendix E of the New York [City] city fuel gas code. Installation of such a device shall be completed no later than January 1, 2010.

Exception: For R-3 occupancies, the installation of such a device shall be completed no later than January 1, 2020.

§28-315.6 Accessibility. The work specified in this section to enhance the accessibility of buildings shall be completed by the dates specified herein.

§28-315.6.1 Directional signage at inaccessible building entrances. The posting of directional signage at inaccessible building entrances in accordance with the retroactive requirements of section 28-313.1 of this code shall be completed on or before August 1, 2013.

§28-315.6.2 Signage at accessible building entrances. The posting of signage at accessible building entrances in accordance with the retroactive requirements of section 28-313.2 of this code shall be completed on or before August 1, 2013.

§28-315.6.3 Signage for portable ramps at inaccessible building entrances where such ramps are permissible. The posting of signage for portable ramps at inaccessible building entrances where such a ramp is permissible in accordance with the requirements of item 7 of [1110.3] 1111.3 of the New York city building code shall be completed on or before March 1, 2020.

§28-315.7 Building security. The work specified in this section to enhance building security shall be completed by the dates specified herein.

§28-315.7.1 Security grilles on buildings in occupancy groups B or M. Security grilles abutting sidewalks on buildings in occupancy groups B or M shall comply with the retroactive requirements of item 4 of section [1008.1.4.5] 1010.1.4.4 of the New York [City] city building code. On and after July 1, 2026, such grilles when closed shall permit visibility from the sidewalk of at least 70 percent of the area covered by such grille.

§28-315.8Resiliency. The work specified in this section to enhance building resiliency shall be completed by the dates specified herein.

§28-315.8.1 Emergency source of water for residential occupancies. [Within 8 years after the effective date of this section,] As of December 31, 2022, existing buildings greater than five stories in occupancy groups I-1, R-1, R-2, and R-3 that supply potable water from the public water main to occupants with the assistance of pumps, other than pumps connected to an emergency or a standby power system that complies with the requirements of chapter 27 of the New York [City] city building code, shall be equipped with additional fixtures capable of supplying potable water to occupants utilizing only the available pressure from the public water main in compliance with section 614 of the New York [City] city plumbing code.

§28-315.8.2 Connections for temporary external generators. For the following buildings, the provision of connections for temporary external generators in accordance with the retroactive requirements of section [G311.2] G312.2 of appendix G of the New York [City] city building code shall be completed by January 1, 2033, and a report detailing compliance with such requirements shall be filed with the department in accordance with section [G311.2.2] G312.2.2 by such date:

1.	Buildings whose main use or dominant occupancy is group I-1 and that are located in [an area of] a special flood hazard area, as such term is defined in appendix G of the New York [City] city building code;

2.	Buildings whose main use or dominant occupancy is an adult home, enriched housing, community residence or intermediate care facility classified as occupancy group R pursuant to an exception to section [308.2.1] 308.3.1 or [308.2.2] 308.3.2 of the New York [City] city building code and that are located in [an area of] a special flood hazard area, as such term is defined in appendix G of the New York [City] city building code;

3.	Buildings whose main use or dominant occupancy is group I-2 hospital and that are located in [an area of] a special flood hazard area or shaded X-Zone, as such terms are defined in appendix G of the New York [City] city building code;

4.	Buildings whose main use or dominant occupancy is group I-2 nursing home and that are located in [an area of] a special flood hazard area, as such term is defined in appendix G of the New York [City] city building code; and

5.	Buildings whose main use or dominant occupancy is group I-2, other than hospitals and nursing homes, and that are located in [an area of] a special flood hazard area, as such term is defined in appendix G of the New York [City] city building code.

§28-315.8.2.1 Modification to the [area of special] flood hazard [or shaded X-Zone] area. Where the [area of] special flood hazard area or shaded X-Zone, as established in appendix G of the New York [City] city building code, is modified on or after the effective date of this section, any building identified in section 28-315.8.2 and newly identified as being within such modified [area of] special flood hazard area or shaded X-Zone shall, no later than 20 years following the adoption of such modification, comply with the retroactive requirements of section [G311.2] G312.2 of appendix G of the New York [City] city building code. The owner of such building shall, no later than 20 years following the adoption of such modification, file with the department a report detailing compliance with such requirements in accordance with section [G311.2.2] G312.2.2.

§28-315.8.3 Connections for temporary external boilers and chillers. For buildings whose main use or dominant occupancy is group I-2 hospital and that are located in [an area of special] a flood hazard [or shaded X-Zone] area, as such [terms are] term is defined in appendix G of the New York [City] city building code, the provision of connections for temporary external boilers and chillers in accordance with the retroactive requirements of section [G311.3] G312.3 of appendix G of the New York [City] city building code shall be completed by January 1, 2033, and a report detailing compliance with such requirements shall be filed with the department in accordance with section [G311.3.2] G312.3.2 by such date.

§28-315.8.3.1 Modification to the [area of special] flood hazard [or shaded X-Zone] area. Where the [area of] special flood hazard area or shaded X-Zone, as established in appendix G of the New York [City] city building code, is modified on or after the effective date of this section, any building whose main use or dominant occupancy is group I-2 hospital and that is newly identified as being within such modified [area of] special flood hazard area or shaded X-Zone shall, no later than 20 years following the adoption of such modification, comply with the retroactive requirements of section [G311.3] G312.3 of appendix G of the New York [City] city building code. The owner of such building shall, no later than 20 years following the adoption of such modification, file with the department a report detailing compliance with such requirements in accordance with section [G311.3.2] G312.3.2.

§28-315.9 Single-occupant toilet rooms. Notwithstanding any other provision of law or rule requiring separate facilities for each sex, on and after January 1, 2017, all single-occupant toilet rooms shall be made available for use by persons of any sex in accordance with section [403.2.1] 403.2.2 of the New York city plumbing code. Nothing in this section shall be construed to require physical alteration of a single-occupant toilet room except for the posting and maintenance of appropriate signage in accordance with section 403.4 of the New York city plumbing code.

§28-315.10 Self-closing doors. All doors providing access to interior corridors or stairs in occupancy groups R-1 and R-2 shall be self-closing or equipped with a device that will ensure closing after having been opened by July 31, 2021.

§28-315.11 Buildings that are equipped with a fire alarm system and that contain Group A-1, A-2, A-3, Group B or Group M occupancies. By January 1, 2021, existing buildings equipped with a fire alarm system and that contain group A-1, A-2 or A-3, Group B or Group M occupancies shall comply with the retroactive requirements of section [908.7.3.1] 915.1.2.1 of the New York city building code.

ARTICLE 316
INSULATION OF CONCEALED PIPES EXPOSED DURING ALTERATION OR REPAIR

§28-316.1 Required insulation of certain concealed piping exposed during alteration or repair. Where concealed existing piping is exposed in the course of the alteration or repair of a building, the owner of the building shall provide for the insulation of the exposed piping. The exposed piping shall be insulated to the extent required by the New York [City] city energy conservation code for newly installed pipe of the same specifications and serving the same function as the exposed pipe. The entire exposed length of the piping shall be insulated as well as any further length of concealed pipe that can be directly accessed through openings made in the course of such alteration or repair.

Exceptions:

- Exposed pipe with one-inch (25-mm) thick continuous coverage of existing insulation in good condition.

- Where the length of concealed pipe which may be directly accessed through openings made in the course of such alteration or repair is less than three feet (914 mm).

- Where there is not sufficient space to insulate pipes to the extent required by the New York [City] city energy conservation code due to conflicts with existing construction, pipes shall be insulated to the extent that space allows.

ARTICLE 317
COOLING TOWERS

§28-317.1 General. All owners of cooling towers shall comply with this article and the rules of the department.

§28-317.2 Definitions. As used in this article, the following terms shall have the following meanings:

COOLING TOWER. The term "cooling tower" means a cooling tower, evaporative condenser or fluid cooler that is part of a recirculated water system incorporated into a building’s cooling, industrial process, refrigeration, or energy production system.

§28-317.3 Registration. All owners of cooling towers shall register such towers with the department prior to initial operation in a form and manner as required by the commissioner and shall include, at a minimum, the following information:

1.	Address of the building at which the cooling tower is located;

2.	Intended use of cooling tower;

3.	Name, address, telephone number and email address of owner;

4.	Manufacturer of the cooling tower;

5.	Model number of the cooling tower;

6.	Specific unit serial number of the cooling tower;

7.	Cooling capacity (tonnage) of the cooling tower;

8.	Basin capacity of the cooling tower; and

9.	Commissioning date of the cooling tower.

[Exception: Owners of existing cooling towers shall register such towers within 30 days after the effective date of this section.]

§28-317.3.1 Discontinued use. The owner or operator of a cooling tower shall notify the department within 30 days after removing or permanently discontinuing use of a cooling tower. Such notice shall include a statement that such cooling tower has been drained and sanitized in compliance with the requirements of the department of health and mental hygiene for discontinuance of a cooling tower.

§28-317.4 Inspecting, cleaning, disinfecting and testing. All cooling towers shall be inspected, tested, cleaned and disinfected in accordance with section 17-194.1 of the administrative code and the rules of the department of health and mental hygiene.

§28-317.5 Annual certification. The owner or operator of a cooling tower shall file an annual certification that such cooling tower was inspected, tested, cleaned and disinfected in compliance with section 17-194.1 of the administrative code and the rules of the department of health and mental hygiene, and that a maintenance program and plan has been developed and implemented as required by such section. Such certification shall be submitted [by November 1, 2016 and] by November [1] first of each year [thereafter] , or by a date otherwise specified in the rules of the department. Consecutive annual certifications shall be submitted at least 90 days apart. The department of health and mental hygiene shall send an electronic reminder to each owner or operator of a cooling tower at least 30 days before such certification submission deadline. Such electronic reminder shall include a link to the website where such certification may be submitted.

§28-317.6 Fees. The department may charge filing fees for registration, discontinuing of use and annual certification as set forth in the rules of the department.

§28-317.7 Enforcement. Failure to register a cooling tower or submit a certification or statement required by this article shall be classified as a major violation.

ARTICLE 318
PERIODIC INSPECTION OF GAS PIPING SYSTEMS

§28-318.1 General. [Commencing January 1, 2019, building] Building gas piping systems, other than gas piping systems of buildings classified in occupancy group R-3, shall be periodically inspected in accordance with this article.

Exception: A building that contains no gas piping and for which the owner of such building has submitted to the commissioner, in a form and manner determined by the commissioner, a certificate of a registered design professional, or a person satisfying other qualifications that the commissioner may establish, that such building contains no gas piping.

§28-318.2 Frequency of inspection. An inspection of a building’s gas piping system shall be conducted at periodic intervals as set forth by rule of the commissioner, but such inspection shall be conducted at least once every five years.

Exceptions:

1.	If the New York state public service commission adopts a rule or other requirement for periodic inspections of service lines, as defined in section 255.3 of title 16 of the New York codes, rules and regulations, with a frequency other than five years, the commissioner may, by rule, require that the periodic inspections required by this article be conducted with such frequency.

2.	The initial inspection for a new building shall be conducted in the tenth year after the earlier of (i) the issuance by the department of a letter of completion or, if applicable, a temporary or final certificate of occupancy for such building or (ii) the date such building was completed as determined by department rule.

§28-318.3 Inspection process. Gas piping systems shall be inspected and tested in accordance with sections 28-318.3.1 through 28-318.3.4.

§28-318.3.1 Inspection entity. Inspections of gas piping systems shall be conducted on behalf of the building owner by a licensed master plumber or by an individual under the direct and continuing supervision of a licensed master plumber, with appropriate qualifications as prescribed by department rule.

§28-318.3.2 Scope. At each inspection, in addition to the requirements prescribed by this article or by the commissioner, all exposed gas lines from point of entry of gas piping into a building, including building service meters, up to individual tenant spaces shall be inspected for evidence of excessive atmospheric corrosion or piping deterioration that has resulted in a dangerous condition, illegal connections, and non-code compliant installations. The inspection entity shall also test public spaces, hallways, corridors, and mechanical and boiler rooms with a portable combustible gas detector to determine if there is any gas leak, provided that such testing need only include public spaces, hallways and corridors on floors that contain gas piping or gas utilization equipment.

§28-318.3.3 Report and certificate of inspection. The inspection entity conducting an inspection of a building pursuant to this article and the owner of such building shall comply with the following requirements:

1.	No later than 30 days after such inspection, such inspection entity shall submit to such owner (i) a report of such inspection, on a form and in a manner determined by the department, and (ii) a certification of the licensed master plumber who performed or exercised direct and continuing supervision over such inspection that an inspection pursuant to this article has been completed for such building. Such report shall be certified by such licensed master plumber and, where applicable, by any individual who performed such inspections under the direct and continuing supervision of such licensed master plumber, and shall include, for each gas piping system inspected, a list of conditions including instances where a part or parts of such system  is worn to such an extent that the safe and reliable operation of such system may be affected, gas leaks, any observed non-code compliant installations or illegal connections, any conditions described in section 28-318.3.4 and any additional information required by the department.

2.	No later than the due date for such inspection, in accordance with department rules, and no earlier than 60 days before such due date, such owner shall submit a certification from a licensed master plumber that an inspection pursuant to this article has been completed by such licensed master plumber for such building, provided that the department may by rule establish an alternative timeframe for such submissions.

3.	No later than 90 days after the due date for such inspection, in accordance with department rules, such owner shall electronically submit, or cause to be submitted by such inspection entity, such report to the utility company providing gas service to such building. Such submission shall only be required if, before the date that such submission would be required, the department has determined and set forth in a rule that such utility company will accept such electronic submission at no cost to such owner.

4.	No later than 120 days after the due date for such inspection, in accordance with department rules, such owner shall submit to the department, in a form and manner determined by the department, (i) a certification from a licensed master plumber that all conditions that were identified in the inspection report for which a certification was submitted pursuant to item 2 of this section have been corrected, except that such certification may note that correction of one or more conditions identified in such report, other than conditions referred to in section 28-318.3.4, will reasonably take additional time to complete and (ii) a certification from such owner that such owner is in compliance with item 3 of this section. If such certification notes that one or more conditions will take additional time to complete, such owner shall, no later than 180 days after the due date for such inspection, submit to the department, in a form and manner determined by the department, a certification from a licensed master plumber that all conditions identified in such report have been corrected.

5.	All reports and certifications required by this section shall be kept on file by the inspection entity and the building owner for at least eight years after the date of inspection and made available to the department at the department’s request.

§28-318.3.4 Reporting and correction of unsafe or hazardous condition. If an inspection reveals any of the following conditions, the inspection entity shall notify the building owner, the utility and the department immediately and the building owner shall immediately take action to correct such condition in compliance with the New York city construction codes:

1.	A gas leak;

2.	Evidence of illegal connections or non-code compliant installations; or

3.	Any other condition which (i) if verified by a utility company or utility corporation, would constitute a class A condition as described in part 261 of title 16 of the New York codes, rules and regulations or (ii) constitutes an imminently dangerous condition.

§28-318.4 Fees. The department may charge filing fees for the certifications required by section 28-318.3.3, as set forth in the rules of the department.

§28-318.5 Enforcement. Failure to submit a certification required by this article shall be classified as a major violation.

ARTICLE 319
MAINTENANCE AND REMOVAL OF SMALL WIND TURBINES

§28-319.1 Maintenance. The owner of a small wind turbine or small wind turbine tower, as such terms are defined in [section 3113.2] chapter 2 of the New York city building code, shall maintain such turbine and tower in accordance with department rules.

§28-319.2 Removal. The owner of a small wind turbine, as such term is defined in [section 3113.2] chapter 2 of the New York city building code, shall remove such turbine when (i) the time elapsed since installation exceeds the manufacturer’s suggested useful life of such turbine or (ii) such turbine has been continuously inoperable for 12 months or more, whichever occurs sooner, provided that the commissioner shall by rule establish a timeframe for removing small wind turbines that do not have manufacturer’s suggested useful lives.

ARTICLE 320
 [Building ENERGY AND emissions limits] 
BUILDING ENERGY AND EMISSIONS LIMITS

§28-320.1 Definitions. As used in this article, the following terms shall have the following meanings:

BUILDING EMISSIONS. The term “building emissions” means greenhouse gas emissions as expressed in metric tons of carbon dioxide equivalent emitted as a result of operating a covered building and calculated in accordance with rules promulgated by the department in consultation with the mayor’s office of long term planning and sustainability. The term “building emissions” shall not include greenhouse gas emissions emitted during a local state of emergency declared by the mayor pursuant to section 24 of the executive law or a state of emergency declared by the governor pursuant to sections 28 of the executive law, where such local or state emergency has an impact on building emissions.

BUILDING EMISSIONS INTENSITY. The term “building emissions intensity” means, for a covered building, the number obtained by dividing the building emissions by the gross floor area for such building, expressed in metric tons of carbon dioxide equivalent per square foot per year.

[Carbon dioxide equivalent] CARBON DIOXIDE EQUIVALENT. The term “carbon dioxide equivalent” means the metric used to compare the emissions of various greenhouse gases based upon their global warming potential as defined in the Intergovernmental Panel on Climate Change Fifth Assessment Report (2014).

CAPACITY RESOURCE. The term “capacity resource” means a facility that has the capability to generate and transmit electrical power and sell capacity (i) by bilateral contracts, (ii) in the wholesale capacity market, or (iii) by indirect sales of capacity in the wholesale market in accordance with the schedules of rates and charges of a utility in effect pursuant to section 66 of the public service law.

CITY BUILDING. The term “city building” means a building that is owned by the city or for which the city regularly pays all of the annual energy bills, or a cultural institution that is in the Cultural Institutions Group as determined by the department of cultural affairs for which the city regularly pays all or part of the annual energy bills.

Exception: The term “city building” shall not include any senior college in the city university of New York system.

CLEAN DISTRIBUTED ENERGY RESOURCE. The term “clean distributed energy resource” means a distributed energy resource that (i) uses any of the following sources to generate electricity: hydropower, solar photovoltaics, geothermal wells or loops, tidal action, waves or water currents, or wind; or (ii) is designed and operated to store energy, including but not limited to batteries, thermal systems, mechanical systems, compressed air, and superconducting equipment.

COVERED BUILDING. The term “covered building” means, as it appears in the records of the department of finance, (i) a building that exceeds 25,000 gross square feet (2322.5 m2) or (ii) two or more buildings on the same tax lot that together exceed 50,000 gross square feet (4645 m2), or (iii) two or more buildings held in the condominium form of ownership that are governed by the same board of managers and that together exceed 50,000 gross square feet (4645 m2).

Exceptions:

1.	An industrial facility primarily used for the generation of electric power or steam.

2.	Real property, not more than three stories, consisting of a series of attached, detached or semi-detached dwellings, for which ownership and the responsibility for maintenance of the HVAC systems and hot water heating systems is held by each individual dwelling unit owner, and with no HVAC system or hot water heating system in the series serving more than 25,000 gross square feet (2322.5 m2), as certified by a registered design professional to the department.

3.	A city building.

4.	A housing development or building on land owned by the New York city housing authority

5.	A rent regulated accommodation.

6.	A building whose main use or dominant occupancy is classified as occupancy group A-3 religious house of worship.

7.	Real property owned by a housing development fund company organized pursuant to the business corporation law and article eleven of the private housing finance law.

8.	A building that participates in a project-based federal housing program.

DISTRIBUTED ENERGY RESOURCE. The term “distributed energy resource” means a resource comprised of one or multiple units capable of generating or storing electricity, all at a single location that is directly or indirectly connected to an electric utility transmission and distribution system.  The resource may serve all or part of the electric load of one or more customers at the same location, and it may simultaneously or alternatively transmit all or part of the electricity it generates or stores onto the electric transmission and distribution system for sale to or use by other customers at other locations.

[Greenhouse gas] GREENHOUSE GAS. The term “greenhouse gas” means a unit of greenhouse gas, including carbon dioxide (CO2), methane (CH4), nitrous oxide (N2O), hydrofluorocarbons (HFCs), perfluorocarbons (PFCs), sulfur hexafluoride (SF6), and nitrogen trifluoride (NF3).

GREENHOUSE GAS OFFSET. The term “greenhouse gas offset” means a credit representing one metric ton of carbon dioxide equivalent emissions reduced, avoided, or sequestered by a project from a measured baseline of emissions and which has been verified by an independent, qualified third party in accordance with offset standards referenced by rules of the department.

FINANCIAL HARDSHIP (OF A BUILDING). The term “financial hardship (of a building)” means a building that for the combined two years prior to the application for an adjustment to annual building emissions limit pursuant to section 28-320.7:

1.	Had arrears of property taxes or water or wastewater charges that resulted in the property’s inclusion on the department of finance’s annual New York city tax lien sale list;

2.	Had been exempt from real property taxes pursuant to sections 420-a, 420-b, 446 or 462 of the real property tax law and applicable local law and the owner had negative revenue less expenses as certified to the department by a certified public accountant, or by affidavit under penalties of perjury; or

3.	Had outstanding balances under the department of housing preservation and development’s emergency repair program that resulted in the property’s inclusion on the department of finance’s annual New York city tax lien sale list.

METRIC TONS OF CARBON DIOXIDE EQUIVALENT. The term “metric tons of carbon dioxide equivalent” means the global standard unit in carbon accounting to quantify greenhouse gas emissions, also expressed as tCO2e.

RENEWABLE ENERGY CREDIT. The term “renewable energy credit” means a certificate representing the environmental, social and other non-power attributes of one megawatt-hour of electricity generated from a renewable energy resource, which certificate is recognized and tradable or transferable within national renewable energy markets or the New York generation attribute tracking system. This term also means the environmental, social, and other non-power attributes of one megawatt-hour of electricity generated from a hydropower resource that does not trade or transfer renewable energy certificates for those hydropower resources in any renewable energy market or via the New York generation attribute tracking system, provided that the hydropower resource owner certifies the amount of energy produced in each reporting year and that it has not sold the non-power attributes equal to its energy production more than once.

RENT REGULATED ACCOMMODATION. The term “rent regulated accommodation” means a building in which more than 35% of dwelling units are required by law or by an agreement with a governmental entity to be regulated in accordance with the emergency tenant protection act of 1974, the rent stabilization law of 1969, or the local emergency housing rent control act of 1962.

§28-320.2 Advisory board. There shall be an advisory board convened by the office of building energy and emissions performance upon the effective date of this article, in January of 2029 and in January of 2039, to provide advice and recommendations to the commissioner and to the mayor’s office of long term planning and sustainability relating to effectively reducing greenhouse gas emissions from buildings. Such recommendations shall include, but not be limited to:

1.	A report and recommendations to be delivered to the mayor and the speaker of the city council no later than January 1, 2023 for additional or improved approaches to assessing building energy performance. Such report shall include, but not be limited to:

1.1.	An approach for buildings to submit energy use or greenhouse gas emissions and other information for the purpose of assessing energy performance of covered buildings;

1.2.	A methodology that includes the metric of measure, adjustments to the metric, the approach to comparing the output to a benchmark, alternative compliance paths, credit for beneficial electrification and distributed energy resources, and an approach for a trading mechanism as described in section 28-320.11;

1.3.	Recommendations for addressing tenant-controlled energy usage;

1.4.	Recommendations for amendments to the audit required under section 28-308.2 of the administrative code, including consideration of whether such audit should be replaced by a capital plan;

1.5.	Recommendations for reducing building emissions from rent regulated accommodations;

1.6.	Recommendations for allowing additional time to comply with the emissions limits for buildings converting to a new occupancy group or use with lower emissions limits or some other change in status that would affect applicability of the provisions of this article;

1.7.	An evaluation of the extent to which the mayor’s 80x50 energy infrastructure pathways study is incorporated and addressed within the recommendations made pursuant to items 1.1 through 1.6 of this section; and

1.8.	A reference guide to delineate the responsibilities of the building designer and owners to comply with emissions limits.

2.	A report to be delivered to the mayor and the speaker of the city council no later than January 1, 2023, providing an analysis of, and any recommendations for improving, energy and emissions performance requirements for covered buildings. Such recommendations shall be targeted to achieve at least a 40 percent reduction in aggregate greenhouse gas emissions from covered buildings by calendar year 2030 relative to such emissions for the calendar year 2005. Such report shall include, but not be limited to assessments of:

2.1.	Incentives for reduction of peak energy demand;

2.2.	Methods to allow for staggered reporting cycles for compliance with energy and emissions performance improvements;

2.3.	Methods for calculating penalties for non-compliance;

2.4.	Estimated emissions reductions associated with any recommended energy performance requirements;

2.5.	The economic impact, including benefits, of achieving the energy and emissions performance requirements;

2.6.	Methods for achieving earlier or larger reductions from city buildings;

2.7.	Separate improvement targets for base building energy systems and tenant-controlled energy systems;

2.8.	Methods for achieving emissions reductions from manufacturing and industrial processes; and

2.9.	Methods for achieving emissions reductions from hospitals while maintaining critical care for human health and safety.

§28-320.2.1 Advisory board composition. Such advisory board shall be staffed with registered design professionals and be composed of 19 members as follows: the chairperson, the speaker of the council or the speaker’s designee, the mayor or the mayor’s designee, eight members appointed by the mayor, and eight members appointed by the speaker of the council. The mayor shall appoint one architect, one engineer, one building owner or manager, one public utility industry representative, one environmental justice representative, one business sector representative, one residential tenant representative, and one environmental advocacy organization representative. The speaker shall appoint one architect, one stationary engineer, one construction trades representative, one green energy industry representative, one residential tenant representative, one environmental justice organization representative, one environmental advocacy representative and one not for profit organization representative. The director of such office, or the designee of such director, shall serve as chairperson of the advisory board. The advisory board may convene in working groups. Such working groups may include individuals not on such advisory board to address the recommendations required by this article. The mayor shall invite the appropriate federal, state and local agencies and authorities to participate, including but not limited to the New York state energy research and development authority. Such advisory board shall convene a working group on hospitals that shall be composed of engineers, architects, and hospital industry representatives.

§28-320.3 Building emissions limits. Except as otherwise provided in this article, or otherwise provided by rule, on and after January 1, 2024, a covered building shall not have annual building emissions higher than the annual building emissions limit for such building as determined in accordance with this section based on the occupancy group of the building.

§28-320.3.1 Annual building emissions limits 2024-2029. For calendar years 2024 through 2029, the annual building emissions limits for covered buildings shall be calculated pursuant to items 1 through 10 of this section. For the purposes of such calculation the department shall provide a method for converting categories of uses under the United States environmental protection agency Portfolio Manager tool to the equivalent uses and occupancy groups set forth in this section. For a covered building with spaces classified in more than one occupancy group, the annual building emissions limit shall be the sum of the calculated values from items 1 through 10 of this paragraph, as applicable for each space.

1.	For spaces classified as occupancy group A: multiply the building emissions intensity limit of 0.01074 tCO2e/sf by the corresponding gross floor area (sf);

2.	For spaces classified as occupancy group B other than as described in item 6: multiply the building emissions intensity limit of 0.00846 tCO2e/sf by the corresponding gross floor area (sf);

3.	For spaces classified as occupancy groups E and I-4: multiply the building emissions intensity limit of 0.00758 tCO2e/sf by the corresponding gross floor area (sf);

4.	For spaces classified as occupancy group I-1: multiply the building emissions intensity limit of 0.01138 tCO2e /sf by the corresponding gross floor area (sf);

5.	For spaces classified as occupancy group F: multiply the building emissions intensity limit of 0.00574 tCO2e/sf by the corresponding gross floor area (sf);

6.	For spaces classified as occupancy groups B civic administrative facility for emergency response services, B non-production laboratory, Group B ambulatory health care facility, H, I-2 and I-3: multiply the building emissions intensity limit of 0.02381 tCO2e/sf by the corresponding gross floor area (sf);

7.	For spaces classified as occupancy group M: multiply the building emissions intensity limit of 0.01181 tCO2e/sf by the corresponding gross floor area (sf);

8.	For spaces classified as occupancy group R-1: multiply the building emissions intensity limit of 0.00987 tCO2e/sf by the corresponding gross floor area (sf);

9.	For spaces classified as occupancy group R-2: multiply the building emissions intensity limit of 0.00675 tCO2e/sf by the corresponding gross floor area (sf);

10.	For spaces classified as occupancy groups S and U: multiply the building emissions intensity limit of 0.00426 tCO2e/sf by the corresponding gross floor area (sf).

§28-320.3.1.1 Greenhouse gas coefficient of energy consumption for calendar years 2024 through 2029. The annual building emissions of a covered building in accordance with this section, greenhouse gas emissions shall be calculated as follows for calendar years 2024 through 2029:

1.	Utility electricity consumed on the premises of a covered building that is delivered to the building via the electric grid shall be calculated as generating 0.000288962 tCO2e per kilowatt hour or, at the owner’s option, shall be calculated based on time of use in accordance with referenced emissions factors promulgated by rules of the department. The department, in consultation with the office of long term planning and sustainability, shall promulgate rules governing the calculation of greenhouse gas emissions for campus-style electric systems that share on-site generation but make use of the utility distribution system and for buildings that are not connected to the utility distribution system.

2.	Natural gas combusted on the premises of a covered building shall be calculated as generating 0.00005311 tCO2e per kbtu.

3.	#2 fuel oil combusted on the premises of a covered building shall be calculated as generating 0.00007421 tCO2e per kbtu.

4.	#4 fuel oil combusted on the premises of a covered building shall be calculated as generating 0.00007529 tCO2e per kbtu.

5.	District steam consumed on the premises of a covered building shall be calculated as generating 0.00004493 tCO2e per kbtu.

6.	The amount of greenhouse gas emissions attributable to natural gas powered fuel cells shall be credited compared to the electricity grid marginal emissions factor that will be determined by the commissioner and promgulated into rules of the department.

Exception: Natural gas powered fuel cells that commence operation prior to the later of January 1, 2023 or the promulgation of such rules, shall be credited compared to the electricity grid marginal emissions factor published in the most recent New York state energy research and development authority renewable energy standard program impact evaluation and clean energy standard triennial review, or a successor to such report issued by the New York state energy research and development authority.

7.	The amount of greenhouse gas emissions attributable to other energy sources, including but not limited to distributed energy resources, shall be determined by the commissioner and promulgated into rules of the department.

§28-320.3.2 Building emissions limits for calendar years 2030 through 2034. For calendar years 2030 through 2034, the annual building emissions limits for covered buildings shall be calculated pursuant to items 1 through 10 of this section. For the purposes of such calculation, the department shall provide a method for converting categories of uses under the United States environmental protection agency Portfolio Manager tool to the equivalent uses and occupancy groups set forth in this section. For a covered building with spaces classified in more than one occupancy group, the annual building emissions limit shall be the sum of the calculated values from items 1 through 10 of this paragraph, as applicable for each space. The department may establish different limits, including a different metric or method of calculation, set forth in the rules of the department, where the department determines that different limits are feasible and in the public interest. Where such limits are set by rule, the average emission limits for all covered buildings shall not be less restrictive than the average emissions impact of the building emissions limits outlined in items 1 through 10 of this section. The advisory board and the office of long term planning and sustainability shall provide advice and recommendation regarding such limits.

1.	For spaces classified as occupancy group A: multiply the building emissions intensity limit of 0.00420 tCO2e/sf by the corresponding gross floor area (sf);

2.	For spaces classified as occupancy group B other than as described in item 6: multiply the building emissions intensity limit of 0.00453 tCO2e/sf by the corresponding gross floor area (sf);

3.	For spaces classified as occupancy groups E and I-4: multiply the building emissions intensity limit of 0.00344 tCO2e/sf by the corresponding gross floor area (sf);

4.	For spaces classified as occupancy group I-1: multiply the building emissions intensity limit of 0.00598 tCO2e/sf by the corresponding gross floor area (sf);

5.	For spaces classified as occupancy group F: multiply the building emissions intensity limit of 0.00167 tCO2e/sf by the corresponding gross floor area (sf);

6.	For spaces classified as occupancy groups B civic administrative facility for emergency response services, B non-production laboratory, Group B ambulatory health care facility, H, I-2 or I-3: multiply the building emissions intensity limit of 0.01330 tCO2e/sf by the corresponding gross floor area (sf);

7.	For spaces classified as occupancy group M: multiply the building emissions intensity limit of 0.00403 tCO2e/sf by the corresponding gross floor area (sf);

8.	For spaces classified as occupancy group R-1: multiply the building emissions intensity limit of 0.00526 tCO2e/sf by the corresponding gross floor area (sf);

9.	For spaces classified as occupancy groups R-2: multiply the building emissions intensity limit of 0.00407 tCO2e/sf by the corresponding gross floor area (sf);

10.	For spaces classified as occupancy groups S and U: multiply the building emissions intensity limit of 0.00110 tCO2e/sf by the corresponding gross floor area (sf).

§28-320.3.2.1 Greenhouse gas coefficients of energy consumption for calendar years 2030 through 2034. For the purposes of calculating the annual building emissions of a covered building in accordance with this section, the amount of greenhouse gas emissions attributed to particular energy sources shall be determined by the commissioner and promulgated into rules of the department by no later than January 1, 2023. The commissioner shall consult with the advisory board required by this article to develop such greenhouse gas coefficients for utility electricity consumption. When developing such coefficients, the commissioner shall consider factors, including but not limited to the best available New York state energy research and development authority and State Energy Plan marginal forecasts for Zone J for the end of the compliance period and beneficial electrification.

§28-320.3.4 Building emissions limits for calendar years 2035 through 2050. No later than January 1, 2023, the commissioner shall establish by rule annual building emissions limits and building emissions intensity limits applicable for calendar years 2035 through 2039 and building emissions limits and building emissions intensity limits applicable for calendar years 2040 through 2049. Such limits shall be set to achieve an average building emissions intensity for all covered buildings of no more than 0.0014 tCO2e /sf/yr by 2050.

§28-320.3.5 Building emissions limits on and after calendar year 2050. No later than January 1, 2023, the commissioner shall establish by rule annual building emissions limits and building emissions intensity limits applicable for calendar years commencing on and after January 1, 2050. Such limits shall achieve an average building emissions intensity for all covered buildings of no more than 0.0014 tCO2e /sf/yr.

§28-320.3.6 Deductions from reported annual building emissions. The department may authorize a deduction from the annual building emissions required to be reported by an owner pursuant to section 28-320.3 where the owner demonstrates the purchase of greenhouse gas offsets or renewable energy credits, or the use of clean distributed energy resources, in accordance with this section. For such sections that limit the dates of applicability of such deductions, the department shall promulgate rules to extend such deductions for each future compliance date.

§28-320.3.6.1 Deductions from reported annual building emissions for renewable energy credits. A deduction from the reported annual building emissions shall be authorized equal to the number of renewable energy credits purchased by or on behalf of a building owner, provided (i) the renewable energy resource that is the source of the renewable energy credits is considered by the New York independent system operator to be a capacity resource located in, or whose output directly sinks into, the zone J load zone for the reporting calendar year; (ii) the renewable energy credits are solely owned and retired by, or on behalf of, the building owner; (iii) the renewable energy credits are from the same year as the reporting year; and (iv) the building that hosts the system producing the energy does not receive a deduction under section 28-320.3.6.3.  Covered buildings claiming deductions for renewable energy credits under this section must provide the department with the geographic location of the renewable energy resource that created the renewable energy credits. The department, in consultation with the mayor’s office of long term planning and sustainability, shall promulgate rules to implement this deduction.

§28-320.3.6.2 Deductions from reported annual building emissions for purchased greenhouse gas offsets. For calendar years 2024 through 2029, a deduction shall be authorized for up to 10 percent of the annual building emissions limit. Such a deduction shall be authorized only where within the reporting calendar year, greenhouse gas offsets equivalent to the size of the deduction as measured in metric tons of carbon dioxide equivalent  and generated within the reporting calendar year have been (i) purchased by or on behalf of the owner in accordance with an offset standard referenced by rules of the department, (ii) publicly registered in accordance with such offset standard, and (iii) retired or designated to the department for retirement. Such greenhouse gas offsets must exhibit environmental integrity principles, including additionality, in accordance with rules promulgated by the department in consultation with the office of long term planning and sustainability. For the purposes of this section, additionality means a requirement that an offset project is not already required by local, national or international regulations. Prior to the department promulgation of rules pursuant to this section, the department shall consult the advisory board on environmental justice as established by section 3-1006 of the administrative code.

§28-320.3.6.3 Deductions from reported annual building emissions for clean distributed energy resources. A deduction from the reported annual building emissions shall be authorized based upon the calculated output of a clean distributed energy resource located at the building subject to the report. The department shall promulgate rules to set forth how such deduction shall be calculated, in accordance with the following:

1.	For a clean distributed energy resource that generates electricity, the department shall establish separate calculations for each type of commercially available clean distributed energy resource, which shall not be revised more frequently than once every three years.

2.	For a clean distributed energy resource that stores electricity, the deduction shall be based on the size of the resource and its ability to reduce greenhouse gas emissions during designated peak periods.

§28-320.3.7 Reports required to be filed by owner. By May 1, 2025, and by May [1] first of every year thereafter, the owner of a covered building shall file with the department a report, certified by a registered design professional, prepared in a form and manner and containing such information as specified in rules of the department, that for the previous calendar year such building is either:

1.	In compliance with the applicable building emissions limit established pursuant to section 28-320.3; or

2.	Not in compliance with such applicable building emissions limit, along with the amount by which such building exceeds such limit.

For a report filed on or after May 1, 2026, where a report required to be submitted by May 1 in the prior year indicated that the covered building was not in compliance with the applicable building emissions limit established pursuant to section 28-320.3 in the calendar year covered by such report, but such building is in compliance for the calendar year covered by the report required to be submitted by May 1 in the current year, such report shall describe the methods used to achieve compliance.

§28-320.3.7.1 Extension of time to file report. An owner may apply for an extension of time to file an annual report required by section 28-320.3.7 in accordance with this section and the rules of the department.  An extension may be granted where the owner is unable to file the certified report by the scheduled due date despite such owner’s good faith efforts, as documented in such application. An extension granted pursuant to this section shall not modify the owner’s obligation to comply with the applicable emission limits for such calendar year.

§28-320.3.7.2 Reporting on compliance by the department. By January 1, 2026, and January 1 of every year thereafter, the office of building energy and emissions performance shall submit to the mayor and speaker of the council a report relating to compliance with this section. Such report shall include, but not be limited to:

1.	Beginning with the report due January 1, 2027, the methods used by covered buildings to comply with the building emissions limits established pursuant to section 28-320.3 where such buildings were not in compliance for the report submitted in the previous year, including, as applicable, any retrofitting improvements and purchasing of clean energy, disaggregated by method and by number of buildings; and

2.	The total number of buildings in each occupancy group, and the number of buildings in compliance with emissions limits, disaggregated by occupancy group.

§28-320.3.8 Continuing requirements. In 2055, the office of building energy and emissions performance shall prepare and submit to the mayor and the speaker of the council recommendations whether to repeal or amend any of the requirements of this article.

§28-320.3.9 Extension for certain income-restricted housing. This section is applicable to covered buildings:

1.	That are owned by a limited-profit housing company organized under article 2 of the private housing finance law, and

2.	That contain one or more dwelling units for which occupancy or initial occupancy is restricted based upon the income of the occupant or prospective occupant thereof as a condition of a loan, grant, tax exemption, tax abatement, or conveyance of property from any state or local governmental agency or instrumentality pursuant to the private housing finance law, the general municipal law, or section 420-c of the real property tax law.

Such covered buildings are exempted from the annual building emissions limits set forth in section 28-320.3.1 and 28-320.3.2 and from any applicable reporting requirements. Commencing January 1, 2035, such covered buildings shall be subject to the annual building emissions limits established pursuant to sections 28-320.3.4 and 28-320.3.5 and any applicable reporting requirements.

§28-320.3.10 Changes in building status. The department may establish by rule procedures for a building to apply for additional time to comply with the emissions limits when such building converts to a new occupancy group or use with lower emissions limits, or undergoes a change affecting the applicability of this article to such building.

§28-320.3.10.1 Additional time for certain covered buildings. A covered building where at least one dwelling unit is required by law or by an agreement with a governmental entity to be regulated in accordance with the emergency tenant protection act of 1974, the rent stabilization law of 1969, or the local emergency housing rent control act of 1962, but that is not a rent regulated accommodation pursuant to this article, may delay compliance with annual building emissions limits until January 1, 2026, and submission of the first report required by section 28-320.3.7 until May 1, 2027.

§28-320.4 Assistance. The office of building energy and emissions performance shall establish and maintain a program for assisting owners of covered buildings in complying with this article, as well as expand existing programs established to assist owners in making energy efficiency and renewable energy improvements. These programs shall be made available to assist building owners without adequate financial resources or technical expertise.

§28-320.5 Outreach and education. The office of building energy and emissions performance shall establish and engage in outreach and education efforts to inform building owners about building emissions limits, building emissions intensity limits and compliance with this article. The materials developed for such outreach and education shall be made available on the office’s website. Such outreach shall include a list of city, state, federal, private and utility incentive programs related to energy reduction or renewable energy for which buildings reasonably could be eligible. The office of building energy and emissions performance shall also provide outreach, education, and training opportunities for buildings’ maintenance and operations staff.

§28-320.5.1. Reporting on outreach and education. By June 1, 2021, and by June 1 in every year thereafter, the office of building energy and emissions performance shall submit a report to the mayor and the speaker of the council, detailing the outreach and education efforts made pursuant to section 28-320.5, including, but not limited to information provided about incentive programs and other sources of funding. Such report shall also include the number of staff members working at the office of building energy and emissions performance.

§28-320.6 Penalties. An owner of a covered building who has submitted a report pursuant to section 28-320.3.7 [which] that indicates that such building has exceeded its annual building emissions limit shall be liable for a civil penalty of not more than an amount equal to the difference between the building emissions limit for such year and the reported building emissions for such year, multiplied by $268.

§28-320.6.1 Determination of penalty. In considering the amount of the civil penalty to be imposed pursuant to this article, a court or administrative tribunal shall give due regard to aggravating or mitigating factors including:

1.	The respondent’s good faith efforts to comply with the requirements of this article, including investments in energy efficiency and greenhouse gas emissions reductions before the effective date of this article;

2.	The respondent’s history of compliance with this article;

3.	The respondent’s compliance with the conditions of any adjustment to the applicable building emissions limit, issued by the department pursuant to section 28-320.7;

4.	Whether the non-compliance was directly related to unexpected and unforeseeable events or conditions during the calendar year outside the control of the respondent;

5.	The respondent’s access to financial resources, where the court or administrative tribunal may consider the financial hardship of a building owned by such respondent as evidence of such respondent’s access to such financial resources; and

6.	Whether payment of such penalty would impact the operations of facilities critical to human life or safety.

§28-320.6.2 Civil penalty for failure to file report. It shall be unlawful for the owner of a covered building to fail to submit an annual report as required by section 28-320.3.7 on or before the applicable due date. An owner of a covered building subject to a violation for failure to file a report shall be liable for a penalty of not more than an amount equal to the gross floor area of such covered building, multiplied by $0.50, for each month that the violation is not corrected within the 12 months following the reporting deadline; provided, however, that an owner shall not be liable for a penalty for a report demonstrating compliance with the requirements of this article if such report is filed within 60 days of the date such report is due.

§28-320.6.3 False statement. It shall be unlawful to knowingly make a material false statement in a report or other submission filed with the department, pursuant to this article. A violation of this section shall be a misdemeanor and subject to a fine of not more than $500,000 or imprisonment of not more than 30 days or both such fine and imprisonment. A person who violates this section shall also be liable for a civil penalty of not more than $500,000.

§28-320.6.4 Penalty recovery. Civil penalties provided for by this article may be recovered in a proceeding before an administrative tribunal within the jurisdiction of the office of administrative trials and hearings. Administrative summonses returnable to such tribunal for violations of this article may be issued by the department or by an agency designated by the department. Civil penalties provided for by this article may also be recovered in an action by the corporation counsel in any court of competent jurisdiction.

§28-320.7. Adjustment to applicable annual building emissions limit. The department, in consultation with the mayor’s office of long term planning and sustainability or any other agency designated by the mayor, may grant an adjustment of the annual building emissions limit applicable to a covered building in existence on the effective date of this article or for which a permit for the construction of such building was issued prior to such effective date, provided that the owner is complying with the requirements of this article to the maximum extent practicable.

1.	Such an adjustment may be granted upon a specific determination that all of the following conditions in items 1.1 through 1.3 are met:

1.1.	Capital improvements are necessary for strict compliance with the limit set forth in section 28-320.3 and it is not reasonably possible to make such improvements due to (i) a constraint imposed by another provision of law, including but not limited to designation as a landmark, landmark site, interior landmark, or within a historic district pursuant to chapter 3 of title 25 of the administrative code, or (ii)  a physical condition of the building or building site including but not limited to lack of access to energy infrastructure, space constraints, or lack of access to a space within a building covered by a lease in existence on the effective date of this section;

1.2.	The owner has made a good faith effort to purchase greenhouse gas offsets to comply with section 28-320.3 but a sufficient quantity is not available at a reasonable cost; and

1.3.	The owner has availed itself of all available city, state, federal, private and utility incentive programs related to energy reduction or renewable energy for which it reasonably could participate.

2.	Such an adjustment may be granted upon a specific determination that all of the following conditions in items 2.1 through 2.4 are met:

2.1.	The cost of financing capital improvements necessary for strict compliance with the limit set forth in section 28-320.3 would prevent the owner of a building from earning a reasonable financial return on the use of such building or the building is subject to financial hardship as defined in this article. In evaluating the ability of an owner to earn a reasonable financial return, the department may consider future savings expected from such capital improvements;

2.2.	The owner is not eligible for any program funded by the city or enabled by a local law that provides financing for the purpose of energy reduction or sustainability measures. Proof of ineligibility for financing must be demonstrated by rejection from any such program funded by the city or enabled by a local law or an affidavit explanation why such owner could not reasonably participate in such programs;

2.3.	The owner has made a good faith effort to purchase greenhouse gas offsets or renewable energy credits to comply with section 28-320.3 but a sufficient quantity is not available at a reasonable cost; and

2.4.	The owner has availed itself of all available city, state, federal, private and utility incentive programs related to energy reduction or renewable energy for which it reasonably could participate.

§28-320.7.1 Effective period. An adjustment granted pursuant to item 1 of section 28-320.7 may be effective for a period of not more than three calendar years. An adjustment granted pursuant to item 2 of such section may be effective for a period of not more than one calendar year.

§28-320.7.2 Application. An application for such an adjustment shall be made in the form and manner determined by the department and certified by a registered design professional.

§28-320.8 Adjustment to applicable annual building emissions limit for calendar years 2024-2029. The department may grant an adjustment of the annual building emissions limit for calendar years 2024 through 2029 applicable to a covered building in existence on the effective date of this article where such covered building emissions in calendar year 2018 exceeds the building emissions limit as prescribed by section 28-320.3.1 by more than 40 percent, as reported to the department by a registered design professional. The adjustment shall result in a required building emissions limit that is 70 percent of the calendar year 2018 building emissions for the covered building. Such adjustment may be granted where all of the following conditions in items 1 through 3 are met:

1.	The owner of the covered building demonstrates that the building emissions in excess of the building emissions limit is attributable to special circumstances related to the use of the building, including but not limited to 24 hour operations, operations critical to human health and safety, high density occupancy, energy intensive communications technologies or operations, and energy-intensive industrial processes;

2.	The owner of the covered building demonstrates that the energy performance of the covered building is equivalent to a building in compliance with the New York city energy conservation code in effect on January 1, 2015; and

3.	The owner of the covered building has submitted a plan to the department setting forth a schedule of alterations to the covered building or changes to the operations and management of the covered building sufficient to ensure that the covered building will be in compliance with the annual building emissions limits for calendar years 2030 through 2034, as required by section 28-320.3.2.

§28-320.8.1 Effective period. An adjustment granted pursuant to section 28-320.8 may be effective for the reporting years 2025 through 2030, as prescribed by section 28-320.3.7, provided that the certificate of occupancy has not been amended after December 31, 2018.

§28-320.8.1.1 Extension of effective period. The commissioner may also grant an extension of the effective period of the adjustment to applicable annual building emissions limit for calendar years 2030-2035, as prescribed by section 28-320.3.8. Such extension may be granted upon submission of a schedule of alterations to the covered building or changes to the operations and management of the covered building in accordance with section 28-320.8 sufficient to ensure that by 2035 the covered building will comply with a required building emissions limit that is 50 percent of the reported 2018 building emissions for the covered building.

§28-320.8.2 Application. An application for an adjustment shall be submitted to the department before July 1, 2021 in the form and manner determined by the department and certified by a registered design professional.

§28-320.9 Adjustment to applicable annual building emissions limit for not-for-profit hospitals and healthcare facilities. The department shall grant an adjustment of the annual building emissions limits for calendar years 2024-2029 and 2030-34 where all of the following conditions in items 1 and 2 are met:

1.	The building is classified as a not-for-profit hospital, not-for-profit health center, or not-for-profit HIP center, in existence on the effective date of this article; and

2.	By no later than July 21, 2021, the owner of the covered building submits an application to the department for such adjustment in a form and manner prescribed by the department.

For calendar years 2024 through 2029, the adjustment shall result in the covered building being subject to an emissions limit that is 85 percent of the calendar 2018 building emissions for such covered building. For calendar years 2030 through 2034, the adjustment shall result in the covered building being subject to an emissions limit that is 70 percent of the calendar 2018 building emissions for such covered building.

§28-320.10 Fee schedule. The department may establish by rule a schedule of fees that shall be paid upon the filing of a report or an application for an adjustment to the applicable building emissions limit pursuant to this article. Such schedule may include a fee for the late filing of a report.

§28-320.11 Carbon trading study. The office of long term planning and sustainability shall conduct a study on the feasibility of a citywide trading scheme for greenhouse gas emissions from buildings and submit a report and implementation plan with the findings of such study to the mayor and the speaker of the council no later than January 1, 2021. Such study shall include methods to ensure equitable investment in environmental justice communities that preserve a minimum level of benefits for all covered buildings and do not result in any localized increases in pollution.  Such study shall also include an approach to a marketplace for credit trading, pricing mechanisms, credit verification, and mechanisms for regular improvement of the scheme. Such study should also consider the reports and recommendations of the advisory board.

ARTICLE 321
ENERGY CONSERVATION MEASURE REQUIREMENTS FOR [Certain Buildings] CERTAIN BUILDINGS

§28-321.1 Definitions. As used in this article, the following terms shall have the following meanings:

COVERED BUILDING. The term “covered building” means a building that is (i) a rent regulated accommodation, (ii) a building whose main use or dominant occupancy is classified as occupancy group A-3 religious house of worship, (iii) owned by a housing development fund company organized pursuant to the business corporation law and article 11 of the private housing finance law, or (iv) a building that participates in a project-based federal housing program and, as it appears in the records of the department of finance, such building exceeds 25,000 (2322.5 m2) gross square feet, or (ii) is one of two or more buildings on the same tax lot that together exceed 50,000 gross square feet (4645 m2), or (iii) is one of two or more buildings held in the condominium form of ownership that are governed by the same board of managers and that together exceed 50,000 gross square feet (4645 m2).

Exceptions:

1.	Real property, not more than three stories, consisting of a series of attached, detached or semi-detached dwellings, for which ownership and the responsibility for maintenance of the HVAC systems and hot water heating systems is held by each individual dwelling unit owner, and with no HVAC system or hot water heating system in the series serving more than 25,000 (2322.5 m2) gross square feet, as certified by a registered design professional to the department.

2.	An industrial facility primarily used for the generation of electric power or steam.

RENT REGULATED ACCOMODATION. The term “rent regulated accommodation” means a building in which more than 35% of dwelling units are required by law or by an agreement with a governmental entity to be regulated in accordance with the emergency tenant protection act of 1974, the rent stabilization law of 1969, or the local emergency housing rent control act of 1962.

§28-321.2 Required energy conservation measures for certain buildings. A covered building must comply with either section 28-321.2.1 or section 28-321.2.2.

§28-321.2.1 Energy compliant buildings. The owner of a covered building shall demonstrate that, for calendar year 2024, the annual building emissions of such covered building did not exceed what the applicable annual building emissions limit would be pursuant to section 28-320.3.2 if such building were a covered building as defined in article 320 of this chapter.

§28-321.2.2 Prescriptive energy conservation measures. By December 31, 2024, the owner of a covered building shall ensure that the following energy conservation measures have been implemented where applicable:

1.	Adjusting temperature set points for heat and hot water to reflect appropriate space occupancy and facility requirements;

2.	Repairing all heating system leaks;

3.	Maintaining the heating system, including but not limited to ensuring that system component parts are clean and in good operating condition;

4.	Installing individual temperature controls or insulated radiator enclosures with temperature controls on all radiators;

5.	Insulating all pipes for heating and/or hot water;

6.	Insulating the steam system condensate tank or water tank;

7.	Installing indoor and outdoor heating system sensors and boiler controls to allow for proper set-points;

8.	Replacing or repairing all steam traps such that all are in working order;

9.	Installing or upgrading steam system master venting at the ends of mains, large horizontal pipes, and tops of risers, vertical pipes branching off a main;

10.	Upgrading lighting to comply with the standards for new systems set forth in section 805 of the New York city energy conservation code and/or applicable standards referenced in such energy code on or prior to December 31, 2024. This provision is subject to exception 1 in section 28-310.3, provided that July 1, 2010 is replaced by January 1, 2020 for the purposes of this section;

11.	Weatherizing and air sealing where appropriate, including windows and ductwork, with focus on whole-building insulation;

12.	Installing timers on exhaust fans; and

13.	Installing radiant barriers behind all radiators.

§28-321.3 Reports. By May 1, 2025, an owner of a covered building shall submit a report to the department to demonstrate compliance with this section in accordance with section 28-321.3.1 or section 28-321.3.2.

§28-321.3.1 Energy compliant buildings reports. The owner of a covered building shall file with the department a report, certified by a registered design professional, prepared in a form and manner and containing such information as specified in rules of the department, that for calendar year 2024 such building was in compliance with the applicable building emissions limit established pursuant to section 28-320.3.2.

§28-321.3.2 Prescriptive energy conservation measures reports. A retro-commissioning agent, as defined in article 308, shall prepare and certify a report in a form and manner determined by the department. The report shall include such information relating to the completion of the prescriptive energy conservation measures as shall be set forth in the rules of the department including, at a minimum:

1.	Project and team information:

1.1.	Building address.

1.2.	Experience and certification of persons performing the prescriptive energy conservation measures and any staff involved in the project.

1.3.	Name, affiliation, and contact information for persons performing the prescriptive energy conservation measures, owner of building, and facility manager of building.

2.	Building information:

2.1.	List of all HVAC, domestic hot water, electrical equipment, lighting, and conveyance equipment types serving the covered building.

ARTICLE 322
MAINTENANCE AND REMOVAL OF [large] LARGE WIND TURBINES

§28-322.1 Maintenance. The owner of a large wind turbine or large wind turbine tower, as such terms are defined in section 3114.2 of the New York city building code, shall maintain such turbine and tower in accordance with department rules.

§28-322.2 Removal. The owner of a large wind turbine, as such term is defined in section 3114.2 of the New York city building code, shall remove such turbine when (i) the time elapsed since the installation of such turbine exceeds the manufacturer’s suggested useful life of such turbine or (ii) such turbine has been continuously inoperable for 12 months or more, whichever occurs sooner, provided that the commissioner shall by rule establish a timeframe for removing large wind turbines that do not have manufacturer’s suggested useful lives.

§28-322.3 Locking before hurricane or strong wind conditions. If a hurricane or strong wind conditions are expected, the commissioner may order that large turbines equipped with passive locks be stopped and locked.

§28-322.4 Lighting. A large wind turbine shall not be artificially lighted.

Exception: Lighting that is required by this code or other applicable laws or rules, provided that such lighting is shielded in accordance with rules promulgated by the commissioner.

ARTICLE 323
PERIODIC INSPECTION OF PARKING STRUCTURES

§28-323.1 General. Parking structures shall be maintained in a safe condition. The owner  shall be responsible for the proper inspection, repair, and maintenance of the parking structure in accordance with the requirements set forth in this article.

Exceptions: The requirements imposed by this article shall not apply to:

1.	Unenclosed, unattached outdoor parking lots.

2.	Private garages serving one- and two-family homes as defined in chapter 2 of the New York city building code.

§28-323.2 Definitions. As used in this article, the following terms shall have the following meanings:

ANNUAL OBSERVATION CHECKLIST. A document developed by the approved agency during initial condition assessment containing baseline items to be inspected between condition assessments, annually or at more frequent intervals as prescribed by the approved agency, by or on behalf of the parking structure owner .

CONDITION ASSESSMENT. An on-site inspection and evaluation of a parking structure by an approved agency for evidence of deterioration of any structural element or building component of such parking structure, evidence of the existence of any unsafe structural condition in such parking structure, or evidence indicating that such parking structure is so damaged, decayed, dilapidated, or structurally unsafe, or is of such faulty construction or unstable foundation, that partial or complete collapse is possible.

INITIAL CONDITION ASSESSMENT. The first condition assessment conducted by an approved agency of a parking structure as outlined in the rules of the department.

PARKING STRUCTURE. A building or space used for the parking or storage of motor vehicles, other than an automotive service station, automotive repair shop, or private garage as defined in chapter 2 of the New York city building code.

§28-323.3 Condition assessment. A condition assessment of a parking structure shall be conducted at periodic intervals as set forth by rule of the commissioner, provided that such condition assessment shall be conducted at least once every six years and after each notification of an unsafe condition. All condition assessments shall be conducted on behalf of the building owner by an approved agency.

§28-323.3.1 Initial condition assessment. The initial condition assessment for a new parking structure shall be conducted in the second year following the completion of a parking structure or as otherwise prescribed by rule as evidenced by the issuance date of a temporary or final certificate of occupancy. Existing parking structures shall have an initial condition assessment performed by an approved agency as required herein and by rule. During the initial condition assessment, the approved agency shall develop and provide to the parking structure owner or owner’s authorized agent an annual observation checklist containing minimum requirements and elements to be inspected as part of the required annual observation.

§28-323.3.2 Subsequent condition assessments. Condition assessments shall be conducted at intervals specified in the rules of the department. Condition assessments shall include a complete review of the most recently prepared condition assessment report, owner’s annual inspection checklists since the last condition assessment, inspection of structural elements, and a structural assessment conducted in accordance with rules promulgated by the commissioner.

§28-323.4 Annual parking structure observation. An annual observation shall be performed by the parking structure owner or owner’s authorized agent at intervals specified in the annual observation checklist, but not less than once a year after the owner receives the most recent condition assessment report. The observation shall include, at a minimum, observation of the items included on the annual observation checklist provided or verified by the approved agency during the most recent condition assessment. Copies of all annual observation checklists completed since the last condition assessment shall be maintained at the parking structure.

§28-323.5 Report of condition assessment. A report shall be issued by the approved agency following each condition assessment in accordance with sections 28-323.5.1 and 28-323.5.2.

§28-323.5.1 Contents. The report shall indicate the results of the condition assessment as safe, safe with repair and/or engineering monitoring, or unsafe, as prescribed by the rules of the department. It shall include a record of all potentially unsafe conditions of the structure and the condition of structural framing members, any visible reinforcement, connections, and conditions of slabs and slab joints. The report must also contain the annual observation checklist to be used for subsequent annual parking structure observations. Such report must be signed and sealed by a professional engineer, who must file the report.

§28-323.5.2 Submission deadlines. Except as otherwise provided in section 28-323.7, the approved agency shall submit a written report to the commissioner within 60 days of completing the condition assessment, but not more than six years from the submission of the preceding report of condition assessment, certifying the results of the assessment as described in section 28-323.5.1.

§28-323.6 Fees. Every owner of a parking structure subject to condition assessments shall pay to the department a report filing fee for each report of condition assessment in the amount set forth in the rules of the department.

§28-323.7 Immediate notice of unsafe condition. The department must be notified of an unsafe condition immediately. A compliance report shall be filed after each unsafe notification.

1.	Whenever a representative of an approved agency learns of an unsafe condition through a condition assessment of a parking structure, such representative shall notify the owner and the department immediately.

2.	Whenever an owner or an owner’s authorized agent observes an unsafe condition during annual observations, or at any other time in between assessments, the owner shall notify the department immediately and undertake repairs in accordance with section 28-323.8.

§28-323.8 Repair of parking structure, unsafe condition. Upon the notification to the department of an unsafe condition, the owner or the owner’s authorized agent shall immediately secure public safety by removing the unsafe condition or safeguarding the area. The owner shall then engage an approved agency to conduct a condition assessment and file a compliance report.

1.	The owner shall commence repairs, reinforcements or other measures to make the structural elements of the parking structure conform to the provisions of this code.

2.	All unsafe conditions shall be corrected within 90 days of filing of the condition assessment report.

3.	The approved agency shall reinspect the premises and file an amended report within two weeks after the repairs have been completed certifying that the unsafe conditions of the building have been corrected.

4.	The commissioner may grant an extension of time of up to 90 days to complete the repairs required to correct an unsafe condition upon receipt and review of an initial extension application submitted by the approved agency together with such additional documentation as may be prescribed by rule.

5.	The commissioner may grant further extensions of time to complete the repairs required to remove an unsafe condition upon receipt and review of an application for a further extension submitted by the approved agency together with such further documentation as may be prescribed by rule.

§28-323.9 Safe with repair and/or engineering monitoring. A parking structure or any part thereof that may pose a potential danger to persons or property, but does not require immediate action shall be rated safe with repair and/or engineering monitoring. This condition requires further investigation and timely remedial action to prevent its deterioration into an unsafe condition. A registered design professional shall be responsible for appropriately monitoring the structure until the repair is completed.

§28-323.9.1 Safe with repair and/or engineering monitoring assessment requirements. When the results of an initial assessment indicate a parking structure is safe with repair and/or engineering monitoring, the parking structure shall be subsequently assessed no more than three years from the date of the initial assessment and an amended report filed with the department.

§28-323.9.2 Safe with repair and/or engineering monitoring for two cycles. The approved agency shall not file a report of a safe condition with repair and/or engineering monitoring program for the same parking structure for two consecutive filing periods unless the second such report is accompanied by his or her professional certification attesting to the correction of all conditions identified in the prior report as requiring repair.

ARTICLE 324
PERIODIC INSPECTIONS OF DRY FLOODPROOFING

28-324.1 General. This article shall apply to covered buildings and structures as described in 28-324.1.1 permitted on or after the effective date of the local law that added this article that are required to comply with the dry floodproofing requirements of appendix G of the New York city building code and that require human intervention to activate or implement the dry floodproofing systems prior to a flood event.

§28-324.1.1 Covered buildings and structures. Such buildings or structures include:

1.	new construction;

2.	substantial improvements;

3.	such portions of buildings or structures that are horizontal enlargements.

§28-324.1.2 Covered dry floodproofing systems. Covered dry floodproofing systems include any dry floodproofing system where human intervention is required to implement any measure, including the installation of shields, equipment, temporary stairs and platforms, hardware, signage, fixed flood-resistant glazing systems or similar components necessary to activate and implement the dry floodproofing system.

§28-324.2 Annual inspection of covered dry floodproofing system. An annual inspection of the covered dry floodproofing system shall be conducted by a person designated by the building owner.

§28-324.2.1 Scope of annual inspection. The annual inspection shall include, at a minimum, visual confirmation that all covered systems are in their stored locations and ready for deployment, and that any gaskets do not appear damaged or brittle.

§28-324.2.2 Records. Such inspection shall be documented and such documentation shall be maintained on the premises and provided to the department upon request.

§28-324.3 Triennial full-scale deployment inspection. A full-scale deployment inspection initiated by the owner shall be conducted every three years in the presence of a special inspection agency that is qualified to perform flood zone compliance special inspections.

§28-324.3.1 Scope of inspection. The special inspector shall observe, inspect and document the components in their deployed state. Any defects shall be noted. The special inspector shall also review all annual inspection documentation for the preceding three years to confirm its completeness.

§28-324.3.2 Notification. Prior to the triennial full-scale deployment inspection, the owner shall notify the department and the New York city fire department in accordance with procedures established by the department. Such notification shall not relieve the applicant, owner, engineer, architect or contractor of the obligation to comply with any notification or permitting requirement of the New York city department of transportation or the New York state department of transportation.

§28-324.3.3 Reports. The owner shall submit a written report prepared and certified by the special inspection agency that witnessed the deployment required by section 28-324.3 to the commissioner within 60 days of completing such deployment. The report shall clearly document the condition of the dry floodproofing system and related egress components and appurtenances thereof and shall include a record of all defects, including any significant deterioration, unsafe conditions and missing or defective components and outline any corrective action necessary to address such defects. Such report shall be submitted to the department on such forms and in such manner as required by the commissioner.

§28-324.3.4 Repair. All defects as found in such inspection shall be documented, noted in inspection reports, and corrected. Where missing or incomplete annual inspection records are the defect in question the owner shall provide a narrative of steps taken to ensure future records will be compliant. An affirmation of correction shall be filed by the owner  within 60 days of the date of correction.

§28-324.3.5 Fees. A report filing fee shall be paid to the department in the amount prescribed by rule.

ARTICLE 325
ANNUAL INSPECTIONS TO PREVENT CONTAMINATION OF MECHANICAL SYSTEMS

§28-325.1 General. This article shall apply to buildings with exhaust ducts under positive pressure, chimneys, and vents that extend into or pass through ducts or plenums.

§28-325.1.1 Covered buildings and structures. Such buildings or structures include:

1.	Buildings constructed after the effective date of this article;

2.	Alterations to existing buildings performed after the effective date of this article resulting in a plenum penetration by a chimney or vent serving an appliance with a heat input not greater than 350,000 Btu/hr.

§28-325.2 Annual inspection of covered buildings. An annual inspection of the covered building mechanical systems shall be conducted to ensure no contamination exists.  Such inspection shall be conducted by a person designated by the building owner who meets the qualifications established by the commissioner.

§28-325.2.1 Scope of annual inspection. The annual inspection shall include, at a minimum, visual confirmation that joints, seams and connections of covered mechanical systems are securely fastened and sealed with welds, gaskets, mastics (adhesives), mastic-plus-embedded-fabric systems, liquid sealants or tapes.

§28-325.2.2 Records. Such inspection shall be documented and such documentation shall be maintained on the premises for at least six years and provided to the department upon request.

§ 4.  Chapter 4 of title 28 of the administrative code of the city of New York, as added by local law number 33 for the year 2007, articles 404, 405, 412, 413, 414, 415 and 416 as amended by and articles 421 and 422 as added by local law number 141 for the year 2013 and amended by chapter 750 for the year 2019;  the definitions of “direct and continuing supervision” and “seal” in section 28-401.3 as amended by local law number 141 for the year 2013,  the definition of “elevator agency” as added by chapter 750 for the year 2019, the definitions of “elevator agency helper” and “elevator work” as added by chapter 750 for the year 2019 and amended by subpart O of chapter 55 for the year 2020, the definition of “general contractor” in such section as added by local law number 8 for the year 2008 and the definition of “safety registration recipient” in such section as added by local law number 8 for the year 2009; section 28-401.4, 28-401.6, 28-401.7, 28-401.8 28-401.9, 28-401.13, 28-401.15, 28-401.17, 28-401.19, 28-402.2, 28-403.2, 28-406.3, 28-407.3, 28-408.3,  28-408.4, 28-408.6, 28-410.4, 28-410.5, 28-410.6, 28-410.8, 28-417.1, 28-418.2, as amended by and 28-401.22 as added by local law number 141 for the year 2013;  section 28-418.4, 28-418.5 and articles 419 and 420 as added by local law number 8 for the year 2008, article 423 as added by local law number 150 for the year 2016,  article 424 as added by local law number 14 for the year 2018, and article 425 as added by chapter 750 for the year 2019 and amended by subpart O of chapter 55 for the year 2020 , article 426 as added by chapter 750 for the year 2019, and article 427 as added by chapter 750 for the year 2019 and amended by subpart O of chapter 55 for the year 2020, is amended to read as follows:

CHAPTER 4

LICENSING AND REGISTRATION OF BUSINESSES, TRADES AND OCCUPATIONS ENGAGED IN BUILDING WORK

ARTICLE 401
GENERAL

§28-401.1 Application. This chapter shall apply to the licensing and registration of businesses, trades and occupations engaged in building work regulated by this code.

§28-401.2 General requirements for all licenses. The provisions of this article shall apply to all licenses issued by the department pursuant to this chapter. All applicants and licensees shall comply with the provisions of this article as well as the specific requirements applicable to the particular license as set forth in other articles of this chapter and department rules.

§28-401.3 Definitions. As used in this chapter, the following terms shall have the following meanings unless the context or subject matter requires otherwise.

BOILER, HIGH-PRESSURE. An appliance for supplying steam or hot water that, for a steam boiler, operates at a pressure of more than 15 psig (103 kPa gauge), and for a hot water boiler, operates at a pressure exceeding 160 psig (1103 kPa gauge) or at a temperature exceeding 250°F (121°C).

CERTIFICATE OF COMPETENCE. A certificate issued by the department to an individual representing that such individual has completed all requirements for the master plumber or master fire suppression piping contractor license but has not obtained a seal [or plate] and that such certificate of competence has been renewed as required and is currently in effect. The certificate of competence shall bear the name of the holder and the certificate number. The holder of a certificate of competence is not a licensed master plumber or licensed master fire suppression piping contractor and may practice the trade for which the certificate is issued only under the direct and continuing supervision of a licensed master plumber or licensed master fire suppression piping contractor or, with respect to a city employee under the direct and continuing supervision of a supervising licensed master plumber or licensed master fire suppression piping contractor.

CITY AGENCY. A city, county, borough, or other office, position, administration, department, division, bureau, board or commission, or a corporation, institution or agency of government, the expenses of which are paid, in whole or in part, from the city treasury.

COMBINED STANDPIPE SYSTEM. A standpipe to which a sprinkler system is connected or is being connected.

DIRECT AND CONTINUING SUPERVISION. Responsible control exercised by a licensed individual, either personally or through one or more, but no more than three, levels of competent supervision over individuals performing the actual work of the [licensees] licensee’s trade who are (i) in the direct employ of an individual who is a licensee, or (ii) in the direct employ of the city agency employing the licensee or (iii) in the direct employ of a business employing the licensee, as allowed by the department, or (iv) where the licensee uses his or her license on behalf of a business, in the direct employ of such business provided that such business is disclosed to the department pursuant to this chapter. Such control shall be evidenced by such licensee’s signature, and seal where applicable, upon any required statements, applications and/or permits and by demonstrating involvement of the licensee in the operations of the business, including hiring of employees, responsibility for financial matters, and oversight of work performance. Direct and continuing supervision includes field inspection, supervision of job sites, and the maintenance of records of such supervision and such other requirements as the commissioner may prescribe by rule for a particular license type.

DIRECT EMPLOY. An individual is in the direct employ of a licensee or business or a city agency when such individual is on the payroll of such licensee or business or city agency and under the usual common law rules applicable in determining the employer-employee relationship has the status of an employee. The work performed by such employee shall not exceed the class of license held by the licensee. Direct employment shall be evidenced by payroll records, such as social security payments, income tax withholding or the disbursement of other funds as required by law for the benefit of such employee, timekeeping records, such as time cards and sign-in sheets, work orders, and assignment or route logs.

DIRECT SUPERVISION.  Responsible control exercised by a licensed individual over individuals performing the actual work of the licensee’s trade. Such control shall be evidenced by such licensee’s signature, and seal where applicable, upon any required statements, applications and/or permits. Direct supervision includes field inspection, supervision of job sites, and the maintenance of records of such supervision and such other requirements as the commissioner may prescribe by rule for a particular license type. All work shall be performed under the guidance and direction of the licensed individual, or, for gas work, a person who holds a gas work qualification pursuant to article 423, who shall be present at all times such trade work is conducted.

ELEVATOR AGENCY. An approved agency authorized by the commissioner to perform elevator work and to inspect and test elevators, escalators and other conveying equipment regulated by this code.

ELEVATOR AGENCY HELPER. An individual having required qualifications to perform elevator work, as defined in this chapter, under the direct and continuing supervision of an elevator agency director.

ELEVATOR WORK.   Alteration, assembly, installation, maintenance, repair, replacement and modernization work, as defined by ASME A17.1 as modified by appendix K of the New York city building code, performed on conveyances regulated by this code or other applicable laws or rules. Elevator work does not include material hoists, platform lifts, stair chair lifts, or personnel hoists. Outfitting, removal, refinishing, or replacement of interior finishes, including wall panels, drop ceilings, handrails and flooring, removal or replacement of interior lighting, recladding of doors, transoms and front return panels, finishing or ornamental work on elevator car operating panels shall not be considered elevator work. Operation of an elevator by any person employed as an operator of such elevator, including operation of an elevator operating under a temporary certificate of occupancy as issued by the department of buildings or such other issuing agency shall not be considered elevator work.

FIRE SUPPRESSION PIPING SYSTEM. Any system including any and all equipment and materials in connection therewith, [with the exception of any electrical components that must be installed by a licensed electrician pursuant to the New York city electrical code,] the purpose of which is to control, contain, suppress or extinguish fire and shall include:

1.	The systems, materials and equipment described or referred to in this code [(with the exception of any electrical components that must be installed by a licensed electrician pursuant to the New York city electrical code)] which [systems, materials or equipment] shall include any standpipe system to which a sprinkler system is or is now being connected; [provided, however, that such systems, materials or equipment shall not include any systems, materials or equipment constituting plumbing work, with the exception of up to thirty sprinkler heads off the domestic water in any one building;] or

2.	Up to thirty sprinkler heads off the domestic water in any one building; or

3.	Any dry, liquid or gaseous chemical fire containment, suppression, control or extinguishing system or any other device or means of control, suppression, containment or extinguishing of fire [(with the exception of any electrical components that must be installed by a licensed electrician pursuant to the New York city electrical code) but not including portable fire extinguishers].

Fire suppression piping systems shall not include:

1.	Any electrical components that must be installed by a licensed electrician pursuant to the New York city electrical code; or

2.	Portable fire extinguishers; or

3.	Connection to domestic water being used for sprinklers.

FIRE SUPPRESSION PIPING WORK. The installation, maintenance, repair, modification, extension, or alteration or testing of a fire suppression piping system in any building in the city of New York. Fire suppression piping work shall not include plumbing work.

GENERAL CONTRACTOR. An individual, corporation, partnership or other business entity that applies for a permit pursuant to this code to construct a new residential structure containing no more than three dwelling units. The term “general contractor” shall not be construed to include an individual, corporation, partnership or other business entity that holds a license pursuant to this code or subchapter twenty-two of chapter two of title twenty of the administrative code, and enters into a contract to perform work exclusively within the scope of such license, nor shall it include an individual who constructs a residential structure containing no more than three dwelling units for his or her own occupancy, or any subcontractors working for the general contractor.

GOVERNMENT AGENCY. Any office, position, administration, department, division, bureau, board, commission, corporation, institution or agency under the control of any city, county, state or the federal government of the United States of America.

LICENSE. A license, registration, certification or other evidence, issued by the department pursuant to this chapter, representing that an individual, a sole proprietorship, partnership, corporation, business association or other person meets the qualifications and requirements as set out in this chapter and in the rules of the department and is authorized to engage in the particular trade, occupation or business as indicated on the license and representing that such license, with associated [plate and/or] seal, where applicable, has been renewed as required and is currently in effect. The license shall bear the holder’s full name, the type of license, the license class, where applicable, the license number and any restrictions relating to the use of such license. Such term shall not include a certificate of competence.

[LICENSE BOARD OR BOARD. A panel of trade practitioners and others appointed by the commissioner as provided herein and in rules promulgated by the commissioner with the purpose of advising the commissioner regarding the character and fitness of applicants for a license or certificate of competence, allegations of illegal practices by persons licensed, or other matters as the commissioner may see fit.]

LICENSED MASTER FIRE SUPPRESSION PIPING CONTRACTOR, MASTER FIRE SUPPRESSION PIPING CONTRACTOR. An individual who has satisfied the requirements of this chapter for the master fire suppression piping contractor license, who has been issued a license [, plate] and [/or] seal, and who is authorized under the provisions of this chapter to perform fire suppression piping work in the city of New York, according to the classification of license held. A master fire suppression piping contractor licensee shall practice his or her trade in association with a master fire suppression piping contractor business or as an employee of a city agency.

LICENSED MASTER PLUMBER, MASTER PLUMBER. An individual who has satisfied the requirements of this chapter for the master plumber license, who has been issued a license [, plate] and [/or] seal, and who is authorized under the provisions of this chapter to perform plumbing work in the city of New York. A master plumber licensee shall practice his or her trade in association with a master plumber business or as an employee of a city agency.

[PLATE. A plaque issued by the department to a master plumber or a master fire suppression piping contractor setting forth the licensee’s name and number, the class of license and the master plumber business or master fire suppression piping contractor business operating pursuant to the plate, and displayed prominently and conspicuously on view to the public at the place of business registered with the department. The plate is the property of the department and is not transferable by the licensee.]

PLUMBING WORK. The installation, maintenance, repair, modification, extension or alteration of plumbing, standpipe where a sprinkler is not connected or is not now being connected, domestic water, connections to the domestic water, combination domestic water and reserve standpipe supply tank up to and including the roof tank check valve, gas piping or any piping system referred to in the New York city plumbing code, and/or up to thirty sprinkler heads off the domestic water in any building in the city of New York.

PRIVATE ELEVATOR INSPECTION AGENCY. An approved agency authorized by the commissioner to operate as an independent contractor for the purpose of inspecting and testing elevators, escalators and other conveying equipment regulated by this code and shall include but shall not be limited to an insurance company, elevator maintenance company, elevator manufacturer or elevator inspection company.

SAFETY REGISTRATION RECIPIENT. An individual, corporation, partnership or other business entity that applies for a permit to perform or performs, or supervises any work that requires the filing under this code of an application for (i) a new building permit; (ii) an alteration permit for work that involves a vertical or horizontal enlargement in excess of twenty-five percent of the floor area of an existing building; (iii) an alteration permit for work that involves the addition of three or more stories to an existing building; (iv) an alteration permit for work that involves alteration or demolition of more than fifty percent of the floor area of an existing building; (v) an alteration permit where the work will result in the removal of one or more floors of an existing structure; (vi) a demolition permit; or (vii) an individual, corporation, partnership or other business entity that places concrete in a building or building site in connection with excavations, foundations or superstructures, including but not limited to the placement of concrete in steel structures, where the concrete portion of the project involves the pouring of a minimum of two thousand cubic yards of concrete or such other amount as determined by rule.

SEAL. Emblem issued by the department to a licensee that allows the licensee to stamp documents required by this code to be signed and sealed. The seal shall bear the full name of the licensee, the license type, the license class, where applicable, and the license number. The seal is the property of the department and is not transferable by the licensee. For applications and other documents submitted electronically, the digital signature and imprint of the seal may be submitted in a manner authorized by the commissioner.

SIGN. A sign as defined in section 12-10 of the zoning resolution.

[TOTAL BOOM. A boom including jibs and other extensions.]

§28-401.4 Requirement of license. It shall be unlawful for any person to engage in or carry on in the city any business, trade or occupation regulated by this chapter or to hold himself or herself out as authorized to engage in or carry on such activity, without having first obtained a license from the commissioner and, if applicable, the proper endorsement for such license in accordance with and subject to the provisions of this chapter and the rules of the department. [A license issued by the department for any such business, trade or occupation prior to July 1, 2008 shall remain in full force and effect until the expiration or termination thereof in accordance with the terms thereof, unless sooner revoked or suspended for cause as hereinafter provided. Any renewal of such license shall be in accordance with the provisions of this code.]

§28-401.5 Application and conditions. Every application for a license or certificate of competence shall be made in such form and shall be accompanied by such information as the commissioner may prescribe, and by the required fee. Failure to provide all requested documents in a timely manner will constitute an incomplete application and will result in denial of the license. It is a condition of the license or certificate of competence that information in the application be kept correct and current. Any change in required information shall be reported to the department within fourteen days after any change prior to issuance of the license or certificate of competence or within thirty days after any change following issuance.

§28-401.6 Qualifications of applicant. All applicants for a license or certificate of competence shall be at least 18 years of age, shall be able to read and write the English language, shall be of good moral character, shall be fit to perform work authorized by the particular license or certificate of competence, and shall meet additional qualifications that may be prescribed for the particular license or certificate of competence. The department may refuse to qualify an applicant if it has found that the applicant violated any law, rule, or regulation of the department resulting in the suspension [or] , revocation or non-renewal of a department-issued license.

§28-401.7 Examination of applicant. Except as otherwise specified for the particular license type, applicants for a license shall be required to take an examination in accordance with the rules of the department. [Every applicant shall commence the license application process with the department within one year of passing the examination for licensure and shall furnish to the department a completed license application within one year of submission of the first filing. Failure to provide all requested documents in a timely manner will constitute an incomplete application and will result in denial of the license.]

§28-401.8 Investigation of applicant. Every applicant for a license or certificate of competence issued pursuant to this chapter shall submit to investigation as directed by a governmental entity in order to determine the applicant’s character and fitness and in accordance with the rules of the department. The applicant shall furnish the department with payment for the actual cost of conducting the background investigation. Failure to provide all requested and completed documents or any other information necessary for completion of the investigation in a timely fashion will constitute an incomplete application and will result in a denial of the license or certificate of competence.

§28-401.8.1 Fingerprinting. Applicants for licenses issued pursuant to this chapter shall be fingerprinted for the purpose of securing criminal history records from the state division of criminal justice services.

1.	The applicant shall pay a processing fee as required and in a form and manner as prescribed by the state division of criminal justice services. Fingerprints shall be taken of the individual seeking licensure in the form and manner as prescribed by the division of criminal justice services; the owner, if the applicant is a sole proprietorship; the general partners, if the applicant is a partnership; and the officers, principals, directors, and stockholders owning more than ten percent of the outstanding stock of the corporation, if the applicant is a corporation.

2.	Any person required to be fingerprinted hereunder shall furnish to the department three current passport-sized photographs of such person.

3.	Notwithstanding paragraph (1) above, an applicant may submit, in lieu of such fingerprints, copies of submissions to any federal, state or local regulatory entity containing information comparable to that required by the department, provided that the department may require fingerprinting and disclosure pursuant to such paragraph where it finds that it has not received sufficient information or information that is comparable to department requirements.

4.	Any person authorized by the department to request a check of criminal history information shall comply with the provisions of article 23a of the New York state correction law and all other applicable laws. If an applicant has been convicted of a crime, any decision regarding such applicant’s fitness for a license or certificate of competence issued pursuant to this chapter must be made upon consideration of New York state correction law sections 701-703-b (article 23) and sections 751-753 (article 23-a).

5.	The department shall authorize the director of the licensing backgrounds unit and a licensing unit attorney to review the criminal history record information disseminated by the division.

§28-401.9 Insurance. Except as noted otherwise for a particular license, or exempted by the commissioner pursuant to rule, prior to the issuance of a license, or during the renewal thereof, the applicant shall file with the department satisfactory evidence of a commercial general liability insurance policy in the amount of one million dollars or such other amount as the commissioner may require, together with satisfactory evidence of compliance with the workers’ compensation law and the disability benefits law. Required insurance shall be maintained for the duration of the license and any changes in coverage, insurance renewals, or policy status shall be provided to the department in accordance with department rules.

§28-401.10 Issuance of license [, plate] and [/or] seal, where applicable, or certificate of competence. The commissioner shall issue a license or certificate of competence to each applicant who shall have submitted satisfactory evidence of his or her qualifications, and shall have satisfactorily passed all required examinations and investigations, provided that no license or certificate of competence shall be issued unless and until the applicant shall have paid the required fee and complied with such other and further requirements for the particular license or certificate of competence as may be set forth in this chapter and in rules promulgated by the department. All licenses or certificates of competence issued by the commissioner shall have his or her signature affixed thereto; but the commissioner may authorize any subordinate to affix such signature. For licenses that require [a plate and/or] the application of a seal, the [plate and/or] seal shall be issued with the license except as provided otherwise in this chapter. The license [, plate] and seal are the property of the department and are not transferable by the licensee. No licensee shall make or cause to be made duplicates of a department-issued license [, plate] or seal. The loss or theft of a license [, plate] or seal must be reported to the department within five calendar days.

§28-401.11 Term of license. [All] Except as otherwise provided in this code or by rule, all licenses issued by the commissioner [for which an examination is required] shall expire three (3) years from the date of issuance thereof, and may be renewed every three (3) years thereafter without examination. The commissioner shall have authority to stagger the issuance of licenses for three-year terms. [All licenses not requiring examination shall expire one year from the date of issuance thereof, and may be renewed each year thereafter except as otherwise noted for a specific license.] The term of an elevator agency technician license issued in accordance with the provisions of article 425 of this chapter shall be two (2) years.

§28-401.12 Renewal of license or certificate of competence. Applications for renewal of a license or certificate of competence shall be accompanied by the renewal fee and such additional information as the commissioner may require, and shall be made at least 30 [calendar] days but not more than 60 [calendar] days prior to the expiration date of same. Applications for renewal of a license or certificate of competence submitted within 30 days prior to the license expiration date shall be considered late and subject to applicable late renewal fees. Applicants shall provide evidence satisfactory to the department that he or she is fit to perform the work authorized by the particular license as provided by department rule. Applications for renewal are subject to investigation by the department. The failure of an individual to renew his or her license or certificate of competence shall have the effect of cancellation of the license or certificate of competence upon expiration, and the holder of a [plate and/or] seal issued by the department shall immediately surrender such [plate and/or] seal to the department. A person who fails to renew a license or certificate of competence within the time period set forth in this section 28-401.12 may apply for late renewal [or reinstatement] of such license pursuant to section 28-401.13. The department may, following notice and an opportunity to be heard, refuse to renew a license or certificate of competence on any grounds on the basis of which it could deny, suspend or revoke such license.

§28-401.13 Late renewal [and reinstatement]. If a license or certificate of competence expires, the individual may apply for late renewal of the license or certificate of competence [,] within one (1) year of the date of its expiration without examination but subject to applicable late renewal fee. [Thereafter, and up to five years after the date of expiration, the commissioner may reinstate the license or certificate of competence without examination upon the applicant’s demonstration to the commissioner’s satisfaction of continued competence in the respective trade and satisfaction of any applicable continuing education requirements but subject to applicable late renewal and reinstatement fees. Applicants for late renewal and reinstatement shall provide evidence satisfactory to the department that he or she is fit to perform the work authorized by the particular license as provided by department rule. A license or certificate of competence shall not be reinstated after five years from date of expiration. The department may refuse to reinstate a license or certificate of competence on any grounds on the basis of which it could deny, suspend or revoke such license.]

§28-401.14 Continuing education. The commissioner may promulgate rules to require applicants for the renewal of licenses or certificate of competence to complete a prescribed number of hours of continuing education courses approved by the department within the term preceding the application for renewal and to provide proof of same in a form acceptable to the department. Such proof, when required, shall be submitted with the application for renewal.

§28-401.15 Schedule of fees.

| LICENSE TYPE | INITIAL FEE | RENEWAL FEE | ADDITIONAL FEES |
| --- | --- | --- | --- |
| Master rigger license. | $200 | $150 triennially | Late-renewal fee: $50 Reissuance fee: $50 |
| Special rigger license. | $100 | $75 triennially | Late-renewal fee: $50 Reissuance fee: $50 |
| Basic hoisting machine operator license (Class A). | $150 | $150 triennially | Late-renewal fee: $50 Reissuance fee: $50 |
| Basic hoisting machine operator license with endorsement to operate hoisting machinery without limitation or restriction (Class B). | $200 | $150 triennially | Late-renewal fee: $50 Reissuance fee: $50 |
| Special hoisting machine operator license (Class C). | $100 | $75 triennially | Late-renewal fee: $50 Reissuance fee: $50 |
| Lift director registration | As provided by dept rules. | As provided by dept rules. | As provided by dept rules. |
| Concrete testing laboratory license. | $100 | $75 annually | Late-renewal fee: $50 Reissuance fee: $50 |
| Welder license. | $50 | $45 triennially | Late-renewal fee: $50 Reissuance fee: $50 |
| Master plumber license (certificate of competence). | $200 | $150 triennially | Late-renewal fees: Up to 30 days late, $50; From 31 days to five years late, $100 for each year or part thereof. Reissuance fee: $50 |
| [Master plumber license plate.] | [$75] | [$100 triennially] | [Replacement fee upon loss of plate, w/affidavit: $100] |
| Master plumber license seal. | $50 | $75 triennially | Replacement fee upon loss of seal, w/affidavit: $75 |
| Journeyman plumber registration. | $50 |  | No renewal [, no reissuance]. Reissuance fee: $50 |
| Master fire suppression piping contractor (class A, B or C) license (certificate of competence). | $200 | $150 triennially | Late-renewal fees: Up to 30 days late, $50; From 31 days to five years late, $100 for each year or part thereof. Reissuance fee: $50 |
| [Master fire suppression piping contractor (class A, B or C) license plate.] | [$75] | [$100 triennially] | [Replacement fee upon loss of plate, w/affidavit: $100] |
| Master fire suppression piping contractor (class A, B or C) license seal. | $50 | $75 triennially | Replacement fee upon loss of seal, w/affidavit: $75 |
| Journeyman fire suppression piping installer registration. | $50 |  | No renewal [, no reissuance]. Reissuance fee: $50 |
| Oil-burning equipment installer. License [(class A or B)]. | $100 | $75 triennially | Late-renewal fee: $50 Reissuance fee: $50 |
| Oil-burning equipment installer seal. | $100 | $75 triennially | Replacement fee upon loss of seal, w/affidavit: $75 |
| High-pressure boiler operating engineer license. | $50 | $45 triennially | Late-renewal fee: $50 Reissuance fee: $50 |
| Portable high-pressure boiler operating engineer license. | $50 | $45 triennially | Renewal fee includes renewal fee for a hoisting machine operator license. Late-renewal fee: $50 Reissuance fee: $50 |
| Master sign hanger license. | $100 | $75 triennially | Late-renewal fee: $50 Reissuance fee: $50 |
| Special sign hanger license. | $100 | $75 triennially | Late-renewal fee $50 Reissuance fee: $50 |
| Outdoor advertising company registration. | As provided by dept rules. | As provided by dept rules. | As provided by dept rules. |
| Filing representative registration. | As provided by dept rules. | As provided by dept rules. | As provided by dept rules. |
| [Reinstatement of expired license, certificate of competence or certification without examination, if approved by commissioner, in addition to applicable renewal fees.] | [Same as initial license.] |  | [$100 for each year or part thereof from date of expiration] |
| Site safety coordinator certificate. | $100 | $50 | Late-renewal fee $50 Reissuance fee: $50 |
| Site safety manager certificate. | $300 | $150 | Late-renewal fee $50 Reissuance fee: $50 |
| General contractor registration. | $300 | $240 triennially | Late-renewal fee $50 Reissuance fee: $50 |
| Tower crane rigger license. | $150 | $50 triennially | Late-renewal fee $50 Reissuance fee: $50 |
| Safety registration [number (concrete contractor, demolition contractor, general contractor)] endorsement | $80 each | $80 triennially | Late-renewal fee: $50 Reissuance fee: $50 |
| Lift director registration | As provided by dept rules. | As provided by dept rules. | As provided by dept rules. |

§28-401.15.1 Additional fees. Additional fees for licensing shall be set forth in the rules of the department. Additional fees include, but are not limited to, reissuance, deactivation, reactivation, and late renewal.

§28-401.16 Restrictions on use [of license]. No holder of a license issued under this chapter shall authorize, consent to or permit the use of his or her license by or on behalf of any other person, and no person who has not qualified and obtained or renewed a license or qualification under this chapter shall hold himself or herself out to the public as qualified, licensed, certified, registered or as the holder of a license issued under this chapter, either directly or indirectly, by means of signs, sign cards, [plates,] stationery, or in any other manner whatsoever.

§28-401.17 Use on behalf of a business. Except for such additional requirements as may be set forth for a particular license, nothing in this chapter shall be construed to prohibit the use of a license by the holder thereof for or on behalf of a partnership, corporation or other business association, provided that such business entity is disclosed to the department in a manner required by the department and where:

1.	At least one member of the partnership or at least one officer of the corporation is licensed for the same business, trade or occupation, and that all work performed by such partnership or corporation is performed by or under the direct and continuing supervision of such license holder or holders; or

2.	Such partnership, corporation or other business association is itself authorized to engage in such business as prescribed herein.

§28-401.17.1 Use on behalf of a city agency. Nothing in this chapter shall be construed to prohibit the holder of a license who is an employee of a city agency from using such license to practice the trade for which such license is issued for or on behalf of such city agency in the course of such employment except as otherwise limited pursuant to articles 408 and 410 of this chapter for licensed master plumber and licensed master fire suppression piping contractor licensees.

§28-401.17.2 Change of business. A license holder who is required to register his or her business or apply for permits with the department may change his or her registered business provided that such change is disclosed to the department in a manner required by the department and where:

1.	All business documentation required by the department, including new insurance certificates, for the new business is submitted; and

2.	All open applications filed by the license holder under the previous business are closed or transferred; and

3.	All fines, penalties or fees owed to the city or department related to the work performed by the previous registered business during the period the license holder was registered at that business are paid.

§28-401.18 New York city location required. Except as otherwise noted for a particular license, the holder of a license, other than an employee of a city agency, shall have or be employed by a business entity that has an established place [of] dedicated to the licensee’s business with an address within the city of New York at which such person can be contacted by the public and the department by mail, telephone, email or other modes of communication during usual business hours. A post office box or virtual office is not [an] acceptable [address].

§28-401.18.1 Notification required. Licensees shall promptly notify the department in writing of any address, telephone number and/or e-mail change within thirty days of the change. Licensees shall notify the department in writing of any criminal conviction within ten days of the occurrence.

§28-401.18.2 Posting. Licensees with established places of business shall post a photocopy of such license in a conspicuous place near the entrance of the licensee’s place of business.

§28-401.19 Suspension or revocation of license or certificate of competence. The commissioner shall have the power to suspend or revoke a license or certificate of competence and/or to impose a fine not to exceed twenty-five thousand dollars for each finding of violation, and/or to order any holder thereof to repair damage resulting from any act or omission as set forth in this chapter or in rules, for any of the following:

1.	Fraud or deceit in obtaining or renewing a license [, plate] or seal, certificate of competence, certification, registration, or permit;

2.	The making of a material false or misleading statement on any form or report filed with the department or other governmental entity;

3.	The failure to file a statement, report or form required by law to be filed;

4.	Willfully impeding or obstructing the filing of a statement, report or form of another required by law to be filed;

5.	Fraudulent dealings;

6.	Negligence, incompetence, lack of knowledge or fitness, or disregard of this code and related laws and rules;

7.	Failure to comply with this code or any order, rule, or requirement lawfully made by the commissioner including failure to cooperate with investigations related to the trade for which the individual is licensed conducted by the commissioner or other government entity;

8.	Failure to comply with any order, rule, regulation or requirement lawfully made by the commissioner of environmental protection or commissioner of transportation pertaining to water services, house connections, street openings, street/lane closures or sidewalk closures that relate to requirements of this code;

9.	A practice or pattern of failing timely to perform or complete contracts relating to home improvements as defined by section 20-386 of the administrative code or a practice of abandoning contracts on residential buildings containing four dwelling units or less;

10.	Failure to provide documents, including payroll records, workers compensation or other insurance documents, employee timekeeping records and corporate tax returns, required by the commissioner;

11.	Engaging or assisting in any act that endangers the public safety and welfare;

12.	Conviction of a criminal offense where the underlying act arises out of the individual’s professional dealings with the city or any other governmental entity;

13.	Poor moral character that adversely reflects on his or her fitness to conduct work regulated by this code; [or]

14.	Failure to pay outstanding fines, penalties, or fees related to the individual’s professional dealings with the city or any other governmental entity [.];

15.	The unauthorized removal of documents from the department;

16.	Repeated failure to be prepared for and/or attend scheduled meetings with the department as provided by rule; or

17.	Failure to notify the department in accordance with section 28-401.18.1.

[15.] 18. With respect to general contractor registration, upon a finding that the applicant or registrant or a business entity in which one of the applicant’s or registrant’s principals, officers or directors is a principal, officer or director has engaged in any of the acts set forth in items 1 through [14] 17or any of the following:

[15.1.] 18.1.	Fraud, misrepresentation or bribery in securing a sign-off of work or a temporary or permanent certificate of occupancy.

[15.2.] 18.2.	A practice on the part of the registrant of failure to timely perform or complete its contracts for the construction of new residential structures containing no more than three dwelling units, or the manipulation of assets or accounts, or fraud or bad faith.

[15.3.] 18.3.	Approval or knowledge on the part of the registrant of an act of omission, fraud, or misrepresentation committed by one or more agents or employees of the registrant, and failure to report such act to the department.

[15.4.] 18.4.	The applicant or registrant, or any of its principals, officers or directors, or any of its stockholders owning more than ten percent of the outstanding stock of the corporation has been convicted of a crime which, in accordance with article twenty-three-a of the correction law, is determined to have a direct relationship to such person’s fitness or ability to perform any of the activities for which a registration is required under this article.

[15.5.] 18.5.	The applicant or registrant, or any of its principals, officers or directors has been or is a principal, officer or director of a registered general contractor whose registration has been revoked.

§28-401.19.1 Notice and hearing. The commissioner shall not revoke or suspend a license or certificate of competence for any cause or impose any other sanction on a licensee unless and until the holder has been given at least five calendar days prior written notice and an opportunity to be heard at the office of administrative trials and hearings (OATH) or its successor agency. However, when the public safety may be imminently jeopardized, the commissioner shall have the power, pending a hearing and determination of charges, to forthwith suspend any license for a period not exceeding 15 days.

§28-401.19.2 Resolution of proceedings. Resolution of proceedings shall comply with the following:

1.	Surrender of [plate or] seal. Upon surrender, suspension or revocation of a license for which the department has also issued a [plate or] seal, the license and [such plate and/or] seal shall be immediately surrendered to the department.

2.	Posting of resolution of proceedings. The names of all licensees whose licenses were suspended or revoked or upon whom penalties have been imposed after a hearing and a department determination [following an office of administrative trials and hearings (OATH), or its successor agency, as applicable, report and recommendation] shall be posted on the department’s website. The department shall post the names of the licensees who have entered into stipulations with the department, unless the stipulation agreed to by the parties provides otherwise.

[§28-401.19.3 Reinstatement fees. The fees required for the reinstatement of a certificate of competence or license, plate or seal after suspension shall be the same as those required to obtain an original document. If reinstatement of the certificate of competence, license, plate or seal is not requested within 30 days of the lifting of the suspension, then late fees shall be imposed in accordance with article 119 of chapter 1 of this title.]

[§28-401.19.4] §28-401.19.3 Mandatory suspension or revocation. The commissioner shall immediately suspend or revoke a license issued pursuant to this code as set forth below. Nothing in the following sections shall be construed to limit the commissioner’s power to revoke or suspend licenses in other circumstances.

[§28-401.19.4.1] §28-401.19.3.1 Rigger license. Any licensed rigger who has been found guilty after proceedings before the environmental control board or other adjudicative proceedings of violating section 28-404.1 or 28-401.9 of the administrative code or sections 3314.1.1 and 3314.4.3.1 of the New York city building code, or of failing to insure that workers have certificates of fitness required pursuant to this code or applicable rule three times within any six-month period, shall be subject to immediate suspension of his or her license pending a hearing and determination in accordance with the provisions of this code.

[§28-401.19.4.2] §28-401.19.3.2 General contractor registration. Any registered general contractor who has defaulted at or been found liable after proceedings before the environmental control board or in an adjudication in criminal court of violations of any provisions of this code relating to a stop work order, public health or safety, structural integrity, building in compliance with approved construction documents or fire safety three times within any twenty-four-month period shall be subject to immediate suspension of his or her registration, pending a hearing and determination at office of administrative trials and hearings (OATH) or its successor agency, as applicable.

§28-401.19.4 Restriction on disciplined licensees. A person who previously held a license that was surrendered subsequent to commencement of a Department disciplinary action, or had their license revoked or was denied renewal, may be prohibited from serving as an officer, director, partner, manager, or licensed individual of a licensed business, whether or not the individual had knowledge of or participated in the prohibited acts or omissions for which the license was surrendered, revoked or denied renewal. The election or appointment of that person by another licensee shall constitute grounds for disciplinary action.

§28-401.20 Cooperation required. Any person, including any corporation, partnership, business or other entity, issued a license or certificate of competence by the department shall, pursuant to a request or order of the commissioner or any other city agency or office, cooperate fully and completely with respect to any department or city agency or office investigation. Evidence of cooperation shall include, but is not limited to, appearing before the department or other city agency or office, answering questions completely and accurately, and providing any and all requested documents. Failure to comply with such request or order may subject such person to disciplinary measures authorized by law, including but not limited to suspension or revocation of the license or certificate of competence.

§28-401.20.1 Service of request or order. Such request or order by the commissioner or other city agency or office shall be mailed by regular mail to the person named therein to his or her last known business or home address at least ten days before such appearance and shall contain the name of the person, date, time and place of such appearance and, if known or applicable, a description of any requested documents. If the appearance or information is required immediately, the request or order may be transmitted via facsimile or delivered to the person’s last known business or home address prior to the date and time specified therein.

§28-401.21 Judicial review of determinations. Notwithstanding any other provision of law to the contrary, decisions, orders and interpretations of the commissioner made pursuant to this chapter shall not be subject to review by the board of standards and appeals. Final decisions and orders of the commissioner made pursuant to this chapter shall be subject to review pursuant to article 78 of the civil practice law and rules.

§28-401.22 Deactivation of license. In the event that the holder of a license is no longer actively engaged as a licensee in a trade or business licensed by the department, the licensee may submit his or her license for deactivation pursuant to department rules. During the period of deactivation, the licensee must continue to pay the license renewal fee required under this chapter for each year of the deactivation period. The holder of a deactivated license may not practice in the trade or business as a licensee or hold himself or herself out as a licensee during the period of deactivation. Application for reactivation of a deactivated license without reexamination shall be made within a time period prescribed by rule and subject to a demonstration of work experience in the trade satisfactory to the commissioner during the time that the license was deactivated.

ARTICLE 402
SITE SAFETY MANAGER CERTIFICATE

§28-402.1 Certificate required. It shall be unlawful to perform the duties and responsibilities of a site safety manager, as specified in chapter 33 of the New York city building code, unless such work is performed by a person certified as a site safety manager under the provisions of this article and department rules.

§28-402.2 Qualifications. All applicants for a site safety manager certificate shall submit satisfactory proof establishing that the applicant:

1.	[Is a registered design professional and has three years of experience supervising construction or demolition of major buildings as the term major building is defined in chapter 33 of the New York city building code, and within one year prior to application has satisfactorily completed a 40-hour course approved by the department;] Has, within one (1) year prior to application, satisfactorily completed a course that is at least forty (40) hours in length and approved by the department in construction and demolition site safety;

2.	[Has a Certified Safety Professional (“CSP”) designation from the Board of Certified Safety Professionals (“BCSP”) and has three years of experience supervising construction or demolition of major buildings as the term major building is defined in chapter 33 of the New York city building, and within one year prior to application has satisfactorily completed a 40-hour course approved by the department;] Possesses a valid Site Safety Training (SST) Supervisor Card; and

3.	[Has eight years of construction supervision experience within the 10 years prior to application, including five years supervising construction or demolition of major buildings as the term major building is defined in chapter 33 of the New York city building code, and within one year prior to application has satisfactorily completed a 40-hour course approved by the department;] Meets one of the following experience criteria:

3.1.	Is a registered design professional and has at least three (3) years of field experience, within the five (5) years prior to application, either (i) serving in a supervisory role with responsibility over workers engaged in construction or demolition work at major buildings in the city of New York, or (ii) providing site safety oversight during the construction or demolition of major buildings in the city of New York, including but not limited to conducting site safety risk assessments, developing or implementing site safety hazard control measures, managing site safety operations, or performing inspections to verify compliance with requirements imposed by chapter 33 of the New York city building code and related rules;

3.2.	Holds a Certified Safety Professional (“CSP”) certification from the Board of Certified Safety Professionals (“BCSP”) and has at least three (3) years of field experience, within the five (5) years prior to application, either (i) serving in a supervisory role with responsibility over workers engaged in construction or demolition work at major buildings in the city of New York, or (ii) providing site safety oversight during the construction or demolition of major buildings in the city of New York, including but not limited to conducting site safety risk assessments, developing or implementing site safety hazard control measures, managing site safety operations, or performing inspections to verify compliance with safety requirements imposed by law;

3.3.	Is a New York city certified site safety coordinator and has at least three (3) years of experience, within the five (5) years prior to application, serving as a designated site safety coordinator during the construction or demolition of major buildings in New York city;

3.4.	Is a New York city registered concrete safety manager and has at least four (4) years of experience, within the seven (7) years prior to application, serving as a designated concrete safety manager during the construction or demolition of major buildings in the city of New York;

3.5.	Holds a Construction Health and Safety Technician (“CHST”) certification from the Board of Certified Safety Professionals (“BCSP”) and has at least four (4) years of field experience, within the eight (8) years prior to application, either (i) serving in a supervisory role with responsibility over workers engaged in construction or demolition work at major buildings in the city of New York, or (ii) providing site safety oversight during the construction or demolition of major buildings in the city of New York, including but not limited to conducting site safety risk assessments, developing or implementing site safety hazard control measures, managing site safety operations, or performing inspections to verify compliance with safety requirements imposed by law;

3.6.	Has at least five (5) years of experience, within the eight (8) years prior to application, serving in a supervisory role with full-time responsibility over workers engaged in construction or demolition work at major buildings in the city of New York;

3.7.	Has eight (8) years of experience, within the ten (10) years prior to application, as a New York city buildings department enforcement official, as determined by the commissioner. At least four (4) years of the experience must have been in the inspection of major buildings under construction or demolition for compliance with the provisions of chapter 33 of the New York city building code and related rules;

3.8.	Has completed an 18-month on-the-job site safety manager training program conducted under the direct supervision of a certified site safety manager during the construction or demolition of major buildings in the city of New York. Such on-the-job training program shall conform to rules promulgated by the department. During the on-the-job training program, the applicant shall only serve as a site safety manager in training, and shall serve in such role on a full-time basis.  The supervising site safety manager shall register the trainee with the department prior to the commencement of the training program and shall certify the trainee’s satisfactory completion of the training program at the conclusion of the program; or

3.9.	Has successfully completed a site safety manager apprenticeship program approved by the New York State Department of Labor.

[4.	Has completed an 18 month on-the-job training program working on major buildings as that term is defined in chapter 33 under the direct and continuing supervision of a certified site safety manager. Such on-the-job training program shall conform to rules promulgated by the department. The supervising site safety manager shall certify the trainee’s satisfactory completion of the training program. In addition, the applicant shall provide proof that, within one year prior to the date of application, he or she has satisfactorily completed a 40-hour course approved by the department;]

[5.	Has equivalent education and construction experience as determined by the department and within one year prior to application has satisfactorily completed a 40-hour course approved by the department; or]

[6.	Has three years of experience as a certified site safety coordinator and within one year prior to application has satisfactorily completed a 40-hour course approved by the department.]

§28-402.3 Fitness to perform work. As a condition of certificate renewal, a certified site safety manager shall provide evidence satisfactory to the department that he or she is fit to perform the work.

ARTICLE 403
SITE SAFETY COORDINATOR CERTIFICATE

§28-403.1 Certificate required. It shall be unlawful to perform the duties and responsibilities of a site safety coordinator, as specified in chapter 33 of the New York city building code, unless such work is performed by a person certified as a site safety coordinator under the provisions of this article and department rules.

§28-403.2 Qualifications. All applicants for a site safety coordinator certificate shall submit satisfactory proof establishing that the applicant:

1.	[Is a registered design professional and has two years of experience supervising construction or demolition of major buildings as the term major building is defined in chapter 33 of the New York city building code, and within one year prior to application has satisfactorily completed an 8-hour course approved by the department;] Has, within one (1) year prior to application, satisfactorily completed a course that is at least forty (40) hours in length and approved by the department in construction and demolition site safety;

2.	[Has a Construction Health and Safety Technician (“CHST”) designation from the Board of Certified Safety Professionals (“BCSP”) and has two years of experience supervising construction or demolition of major buildings as the term major buildings is defined in chapter 33 of the New York city building code, and within one year prior to application has satisfactorily completed an 8-hour course approved by the department;] Possesses a valid Site Safety Training (SST) Supervisor Card; and

3.	[Has five years of construction supervision or construction safety experience within the 10 years prior to application, including three years supervising construction or demolition of major buildings as the term major building is defined in chapter 33 of the New York city building code, and within one year prior to application has satisfactorily completed an 8-hour course approved by the department; or] Meets one of the following experience criteria:

3.1.	Is a registered design professional and has at least two (2) years of field experience, within the five (5) years prior to application, either (i) serving in a supervisory role with responsibility over workers engaged in construction or demolition work at major buildings in the city of New York, or (ii) providing site safety oversight during the construction or demolition of major buildings in the city of New York, including but not limited to conducting site safety risk assessments, developing or implementing site safety hazard control measures, managing site safety operations, or performing inspections to verify compliance with requirements imposed by chapter 33 of the New York city building code and related rules;

3.2.	Holds a Certified Safety Professional (“CSP”) certification from the Board of Certified Safety Professionals (“BCSP”) and has at least two (2) years of field experience, within the five (5) years prior to application, either (i) serving in a supervisory role with responsibility over workers engaged in construction or demolition work at major buildings in the city of New York, or (ii) providing site safety oversight during the construction or demolition of major buildings in the city of New York, including but not limited to conducting site safety risk assessments, developing or implementing site safety hazard control measures, managing site safety operations, or performing inspections to verify compliance with safety requirements imposed by law;

3.3.	Is a New York city registered concrete safety manager and has at least three (3) years of experience, within the seven (7) years prior to application, serving as a designated concrete safety manager during the construction or demolition of major buildings in the city of New York;

3.4.	Holds a Construction Health and Safety Technician (“CHST”) certification from the Board of Certified Safety Professionals (“BCSP”) and has at least three (3) years of field experience, within the seven (7) years prior to application, either (i) serving in a supervisory role with responsibility over workers engaged in construction or demolition work at major buildings in the city of New York, or (ii) providing site safety oversight during the construction or demolition of major buildings in the city of New York, including but not limited to conducting site safety risk assessments, developing or implementing site safety hazard control measures, managing site safety operations, or performing inspections to verify compliance with safety requirements imposed by law;

3.5.	Has at least four (4) years of experience, within the seven (7) years prior to application, serving in a supervisory role with full-time responsibility over workers engaged in construction or demolition work at major buildings in the city of New York; or

3.6.	Has five (5) years of experience, within the eight (8) years prior to application, as a New York city buildings department enforcement official, as determined by the commissioner.  At least two and a half (2.5) years of the experience must have been in the inspection of major buildings under construction or demolition for compliance with the provisions of chapter 33 of the New York city building code and related rules.

§28-403.3 Fitness to perform work. As a condition of certificate renewal, a certified site safety coordinator shall provide evidence satisfactory to the department that he or she is fit to perform the work.

ARTICLE 404
RIGGER LICENSE

§28-404.1 Rigger license required. It shall be unlawful to hoist or lower any suspended article, including but not limited to suspended scaffolds, on the outside of any building [in the city] unless such work is performed by or under the direct and continuing supervision of a person licensed as a rigger under the provisions of this article. The provisions of this article shall also apply to the erection or dismantling of a tower crane [or a climber crane on a building and to the use of a derrick in their removal, except that such erection or dismantling may be performed by or under the direct and continuing supervision of a licensed climber or tower crane rigger in accordance with rules promulgated by the department].

[Exception] Exceptions: The provisions of this article shall not apply to:

1.	The hoisting or lowering of signs if the person so doing possesses a license as a sign hanger, as provided in this chapter;

2.	The loading or unloading of a material delivery truck if the material loaded or unloaded is not raised more than 12 feet (3658 mm) above the bed of the truck during the loading or unloading process; [or]

3.	The hoisting or lowering of articles on the outside of a building [in the city] where chapter 33 of the New York city building code authorizes such articles to be hoisted or lowered by or under the supervision of a qualified and/or competent person [.]; or

4.	The assembly or disassembly of a self-erecting tower crane, provided such operation is supervised by an assembly/disassembly director in accordance with rules promulgated by the commissioner.

§28-404.2 Classification. Rigger licenses shall be classified as follows:

1.	Master rigger license. Authorizes the holder thereof to install or use a suspended scaffold, or to hoist or lower any suspended article [with a hoisting machine] , irrespective of weight, on the outside of any building.

2.	Special rigger license. Authorizes the holder thereof to:

2.1.	Install or use a suspended scaffold; and

2.2.	Hoist or lower any suspended article not exceeding 2,000 pounds (907 kg) in weight on the outside of any building with [a] hoisting [machine] equipment, provided the manufacturer rated capacity of such hoisting [machine] equipment does not exceed 2,000 pounds (907 kg).

3.	[Climber or tower] Tower crane rigger license. Authorizes the holder thereof to assemble, jump or disassemble a tower crane [or a climber crane] , or to supervise such work, and to install or use a derrick(s) in conjunction with such work and supervise such installation or use of the derrick.

§28-404.3 [Additional qualifications] Qualifications. [Applicants] All applicants for a rigger license shall [have the additional qualifications as set forth in sections 28-404.3.1 through 28-404.3.3] submit satisfactory proof establishing that the applicant meets the qualifications, as set forth below, for the type of license sought.

§28-404.3.1 Master rigger license qualifications. All applicants for a master rigger license shall submit satisfactory proof establishing that the applicant:

1.	[Has at least five years of practical experience in the hoisting and rigging business within the seven years prior to application] Possesses valid certifications for both rigging supervision and lift direction.  The certifications must be acceptable to the commissioner and be issued by a rigging supervision and lift direction certification program that is accredited by the National Commission for Certifying Agencies (NCCA) or the American National Standards Institute (ANSI).  The certifications shall cover areas including, but not limited to, the inspection and use of rigging hardware, rigging techniques, signaling, hazards associated with rigging, and calculations and problem solving with respect to rigging;

2.	[Has knowledge of and is able to explain the risks incident to such business and precautions to be taken in connection therewith, safe loads and computation thereof, types of rigging, size and strength of ropes, cables, blocks, poles, derricks, shear legs and other tools used in connection with such business; and] Has, within the one (1) year prior to application, satisfactorily completed a department-approved training course for lift directing that is at least 32 hours in length and in accordance with the requirements of section 28-424.3;

3.	[Has satisfactorily completed a department-approved training course of not less than thirty hours. Any person who, within the three years prior to the date of the application, has successfully completed at least a thirty-hour training course need not take a second thirty-hour course, provided such person can provide to the department a dated certificate as set forth in this section. Such person shall, however, take a department-approved eight-hour re-certification course within three years of the initial course and every three years thereafter. Successful completion of the training or re-certification course shall be evidenced by a dated certificate issued by the provider of the training or re-certification course. The certificate shall include such information as specified by the department by rule. The certificate, or a valid wallet card version thereof, shall be readily available to the commissioner upon request. Such training or recertification course shall be conducted (i) pursuant to a registered New York state department of labor training program, or (ii) by a provider approved by the department.] Has, within the one (1) year prior to application, satisfactorily completed a department-approved training course for rigging supervision that is at least 32 hours in length and in accordance with the requirements of section 3316.9.2 of the New York city building code; and

4.	Meets one of the following experience criteria:

4.1.	Has at least five (5) years of experience, within the seven (7) years prior to application, working as a designated master rigging foreman in the city of New York under the direct and continuing supervision of a licensed master rigger;

4.2.	Is a licensed professional engineer and, within the five (5) years prior to application, has developed and provided onsite verification of the critical pick plan in accordance with section 3316.9.1 of the New York city building code for at least twenty-five (25) separate New York city certificates of on-site inspections; or

4.3.	Has at least five (5) years of experience, within the seven (7) years prior to application, working as a licensed lift director in the city of New York.

§28-404.3.2 Special rigger license qualifications. All applicants for a special rigger license shall submit satisfactory proof establishing that the applicant:

1.	[Has at least one year of practical experience in the hoisting and rigging business within the three years prior to application] Has, within the one (1) year prior to application, satisfactorily completed a department-approved training course for special riggers that is at least 16 hours in length;

2.	[Has knowledge of and is able to explain the risks incident to such business and precautions to be taken in connection therewith] Has, within the one (1) year prior to application, satisfactorily completed a department-approved training course for suspended scaffold supervision that is at least 32 hours in length and in accordance with the requirements of section 3314.4.5.3 of the New York city building code; and

3.	[Has satisfactorily completed a department-approved training course of not less than thirty hours. Any person who, within the three years prior to the date of the application, has successfully completed at least a thirty-hour training course need not take a second thirty-hour course, provided such person can provide to the department a dated certificate as set forth in this section. Such person shall, however, take a department-approved eight-hour re-certification course within three years of the initial course and every three years thereafter. Successful completion of the training or re-certification course shall be evidenced by a dated certificate issued by the provider of the training or re-certification course. The certificate shall include such information as specified by the department by rule. The certificate, or valid wallet card version thereof, shall be readily available to the commissioner upon request. Such training or recertification course shall be conducted (i) pursuant to a registered New York state department of labor training program, or (ii) by a provider approved by the department.] Meets one of the following experience criteria:

3.1.	Has at least two (2) years of experience, within the three (3) years prior to application, working as a designated special rigging foreman in the city of New York under the direct and continuing supervision of a licensed special rigger; or

3.2.	Has at least three (3) years of experience, within the five (5) years prior to application, supervising the installation or use of suspended scaffolds in the city of New York in accordance with section 3314.4 of the New York city building code.

§28-404.3.3 [Climber or tower] Tower crane rigger license qualifications. All applicants for a [climber or] tower crane rigger license shall submit satisfactory proof establishing that the applicant:

1.	[Has at least five years of practical experience in the climber or tower crane rigging business within the seven years prior to application;] Has, within the one (1) year prior to application, satisfactorily completed a department-approved training course for tower crane rigging that is at least 30 hours in length and in accordance with the requirements of section 3319.10.1 of the New York city building code; and

2.	[Has knowledge of and is able to explain the risks incident to such business and precautions to be taken in connection therewith, including connecting pins, cables, anchorage, platform or pad, plumb of mast, torque of bolts, supervision of rigging and hoisting of loads, placement of components, and coordination of sequencing; and] Has at least five (5) years of practical experience in the tower crane rigging business in the city of New York within the seven (7) years prior to application.

[3.	Has satisfactorily completed a department-approved training course of not less than thirty hours. Any person who, within the three years prior to the date of the application, has successfully completed at least a thirty-hour training course need not take a second thirty-hour course, provided such person can provide to the department a dated certificate as set forth in this section. Such person shall, however, take a department-approved eight-hour re-certification course within three years of the initial course and every three years thereafter. Successful completion of the training or re-certification course shall be evidenced by a dated certificate issued by the provider of the training or re-certification course. The certificate shall include such information as specified by the department by rule. The certificate, or a valid wallet card version thereof, shall be readily available to the commissioner upon request. Such training or recertification course shall be conducted (i) pursuant to a registered New York state department of labor training program, or (ii) by a provider approved by the department.]

§28-404.4 Additional requirements. The additional requirements set forth in sections 28-404.4.1 through 28-404.4.3 shall apply to licensed riggers:

§28-404.4.1 Danger warning. Every licensed [master and special] rigger shall, while rigging operations are in progress at a job site, place, conspicuously, at such job site two plates or signs not less than 18 inches (457 mm) by 24 inches (610 mm) in size (i) displaying the word “danger” in letters not less than 6 inches (152 mm) high, and (ii) disclosing the rigger’s name, business address, type of rigger license and license number.

§28-404.4.2 Rigger place of business. Every licensed master and special rigger shall have a place of business located within the city and shall display prominently at such place of business a plate or sign marked with the words “master rigger” or “special rigger,” respectively, and his or her license number immediately [there under] thereunder. A master, special and tower [or climber] rigger shall be a sole proprietor, a partner in the partnership or an officer of the corporation and shall be allowed to associate his or her license with only one other rigger business. Such businesses shall be located at the same place of business.

§28-404.4.3 Fitness to perform work. As a condition of license renewal [or reinstatement,] , a licensed master or special rigger shall provide evidence satisfactory to the department that he or she is fit to perform the work.

ARTICLE 405
HOISTING MACHINE OPERATOR LICENSE

§28-405.1 Hoisting machine operator license required. It shall be unlawful for any persons to take charge of or operate any power-operated hoisting machine used for hoisting purposes or cableways under the jurisdiction of the department, unless such person is licensed under the provisions of this article [or is a holder of a certificate of qualification as a hoisting machine operator issued prior to December 6, 1968 and not allowed to lapse].

Exceptions:

1.	Operators of machinery that is exempted from the requirements of section 3319.1 of the New York city building code.

2.	Operators of mobile cranes of a limited size and capacity, or operators of mobile cranes performing a limited use, and exempted from the requirements of this article [under chapter 33 of the New York city building code, or exempted] in accordance with rules promulgated by the commissioner.

[2.] 3.	 [Hoisting] Operators of hoisting machines with a manufacturer’s rated capacity of one ton or less.

[3.] 4.	 [Power-operated] Operators of power-operated scaffolds and window-washing machines.

5.	Learners supervised in accordance with the rules of the department by a licensed hoisting machine operator.

§28-405.2 Classification. Hoisting machine operator licenses shall be classified as follows:

1.	Class A license: [Basic license] License to operate cranes with a [total] boom [less than] , including jibs and any other extensions to the boom, not exceeding 200 feet (60 960 mm) in length, derricks, and [cableways, excluding truck-mounted tower cranes that exceed 200 feet (60 960 mm) in height] other hoisting machines. This license shall not authorize the operation of a truck-mounted tower crane or a self-erecting tower crane when such crane exceeds 200 feet (60 960 mm) in height. This license further shall not authorize the operation of a cableway.

2.	Class B license: [Endorsement on basic license to include the operation of] License to operate any hoisting machinery, except that to operate hoisting machinery with a boom, including jibs and other extensions, exceeding 300 feet (91 440 mm) in length, or a truck-mounted or self-erecting tower crane that exceeds 300 feet (91 440 mm) in height, the licensee must hold a rating, issued by the department, for the specific make and model of hoisting machine.

3.	Class C license: [Special hoisting machine operator license to operate a specified class of hoisting machine of limited size and capacity as follows:]

[Class C1:] License to operate wheel mounted cranes with telescoping, hydraulic, articulating, or folding booms, including jibs and any other extensions to the boom, not exceeding 200 feet (60 960 mm) in length [(60 960 mm)] with a manufacturer’s rated capacity of 50 tons ( [51] 45.36 t) or less [;] , as well as to operate any hoisting machine within the scope of a limited license.

4.	Limited licenses: Limited hoisting machine operator licenses shall be classified as follows:

4.1.	Limited license for articulating boom cranes. Limited license to operate boom trucks with an articulating boom, including jibs and any other extensions to the boom, not exceeding 200 feet (60 960 mm) in length with a manufacturer’s rated capacity of 50 tons (45.36 t) or less.

4.2.	 [Class C2: License] Limited license for boom trucks. Limited license to operate boom trucks with telescoping, hydraulic, articulating, or folding booms, including jibs and any other extensions to the boom, not exceeding 200 feet (60 960mm) in length with a manufacturer’s rated capacity of 50 tons ( [51] 45.36 t) or less [;]. This license shall also authorize the operation of any hoisting machine within the scope of a limited license for mini cranes.

4.3.	Limited license for mini cranes. Limited license to operate mobile cranes, other than boom trucks, with a telescoping, hydraulic, articulating, or folding boom, including jibs and any other extensions to the boom, not exceeding 50 feet (15 240 mm) in length with a manufacturer’s rated capacity of 3 tons (2.72 t) or less.

4.4.	 [Class C3: License] Limited license for sign hanging cranes. Limited license to operate boom trucks with telescoping, hydraulic, articulating, or folding booms, including jibs and any other extensions to the boom, not exceeding 135 feet (41 148 mm) in length with a manufacturer’s rated capacity of [three] 3 tons (2.72 t) or less, used exclusively for the erection, maintenance, or removal of signs.

4.5.	Additional limited licenses via rule. The commissioner may, via rule, establish additional limited hoisting machine operator licenses. Such additional licenses must be limited as to the type, size, and capacity of hoisting machinery authorized to be operated by a holder of the license.

§28-405.3 [Additional] Experience qualifications. Applicants for a hoisting machine operator license shall [have] meet the following [additional] experience qualifications.

§28-405.3.1 Class A license. An applicant for a class A [basic] hoisting machine operator license shall have at least three (3) years of experience, within the five (5) years prior to application, operating hoisting machines in the city of New York in the presence of and under the direct [and continuing] supervision of a licensed class A or class B hoisting machine operator. Such experience shall have been obtained operating hoisting machines of a size, type, and capacity as specified in rules promulgated by the commissioner.

§28-405.3.2 Class B license. An applicant for a class B hoisting machine operator license shall have the following qualifications.

§28-405.3.2.1 Licensing [Endorsement] qualifications. An applicant for a class B hoisting machine operator license shall: (i) have a class A [basic] hoisting machine operator license [, and shall have at least two years of experience prior to application under the direct and continuing supervision of a class B licensed hoisting machine operator operating the equipment for which he or she is applying for endorsement and shall satisfactorily demonstrate by operation that he or she is competent to operate a crane with a boom, including jibs and other extensions, exceeding 200 feet (60 960 mm) in length or truck-mounted tower crane exceeding 200 feet (60 960 mm) in height, or as otherwise provided in rules of the department.] and have held such class A license for at least five (5) years prior to application; (ii) have at least three (3) years of experience, within the eight (8) years prior to application, operating, in the city of New York as a class A licensed hoisting machine operator, mobile cranes with a manufacturer’s rated capacity in excess of 50 tons (45.36 t) or tower cranes; and (iii) separately, while holding the class A license, have at least one (1) year of experience, within the five (5) years prior to application, operating cranes in the city of New York with a boom, including jibs and any other extensions to the boom, greater than 200 feet (60 960 mm) in length as a learner in the presence of and under the direct supervision of a licensed class B hoisting machine operator.

§28-405.3.2.2 Licensing ratings qualifications. An applicant for a class B hoisting machine operator licensing rating shall have a class B hoisting machine operator license and shall satisfactorily demonstrate that he or she is competent to operate a hoisting machine with a boom, including jibs and any other extensions to the boom, exceeding 300 feet (91 440 mm) in length or a truck-mounted tower crane exceeding 300 feet (91 440 mm) in height. Unless otherwise provided in rules of the department, such [competence] competency shall be demonstrated by operation, practical examination, or completion of simulator training and shall be specific to the make and model of the hoisting machine for which the rating [shall] is to be issued. In addition to holding a rating, such hoisting machine operator must complete any orientation required by the department.

§28-405.3.3 Class C license. An applicant for a class C [special] hoisting machine operator license shall have at least two (2) years of experience, within the three (3) years prior to application, operating hoisting machines in the presence of and under the direct [and continuing] supervision of a licensed hoisting machine operator [and have satisfactorily passed a practical examination in the operation of equipment for which such license is to be issued]. Such experience shall have been obtained operating hoisting machines of a size, type, and capacity as specified in rules promulgated by the commissioner.

§28-405.3.4 Limited licenses. An applicant for a limited hoisting machine operator license shall have at least two (2) years of experience, within the three (3) years prior to application, in the presence of and under the direct supervision of a licensed hoisting machine operator.  Such experience shall have been obtained operating hoisting machines of a size, type, and capacity as specified in rules promulgated by the commissioner.

Exception: The commissioner may, by rule, establish alternative pathways for individuals who, on or before the date that is two years after the effective date of this provision, apply for a limited license for articulating boom cranes or a limited license for mini cranes.

§28-405.4 Fitness to perform work. As a condition of license issuance and renewal, [and reinstatement,] a [licensed] hoisting machine operator shall provide evidence satisfactory to the department that he or she is fit to perform the work.

§28-405.5 Insurance exemption. Unless otherwise required by rule, licensed hoisting machine operators are exempt from the insurance requirements of section 28-401.9.

§28-405.6 Certification required. The commissioner shall, by rule, require hoisting machine operators to possess one or more certifications for the operation of hoisting machinery.  Such certifications shall be based on the passage of a written and a practical examination for the type of hoisting machinery authorized to be operated by the certification.

ARTICLE 406
CONCRETE TESTING LABORATORY LICENSE

§28-406.1 Concrete testing laboratory license required. Testing of concrete required by this code or other applicable laws or rules shall be conducted by a concrete testing laboratory licensed in accordance with this article.

§28-406.1.1 Term of license. The term of a concrete testing laboratory license shall be one (1) year and may be renewed every year thereafter.

§28-406.2 Qualifications. All applicants for a concrete testing laboratory license shall maintain a laboratory within 50 miles (80 467 m) of the city and shall submit satisfactory proof establishing that the business is conducted by qualified personnel in accordance with procedures, safety requirements and professional standards as set forth in rules of the department. The department shall inspect an applicant’s place of business and equipment and conduct an investigation of applicant’s personnel in a manner to be set forth in department rules prior to the issuance or renewal of a license.

§28-406.3 Additional requirements. The following additional requirements shall apply to concrete testing laboratories:

§28-406.3.1 Director. Each laboratory shall have in responsible charge a director who shall be a full-time employee of the laboratory and shall not serve as the director of more than one licensed laboratory at a time. The director shall be a registered design professional, comply with additional qualification requirements as set forth in department rules, and shall personally supervise all technical functions of the laboratory relating to testing of concrete and concrete materials as required in this code and in rules of the department.

§28-406.3.2 Certification of reports by director. The director shall certify the truth and accuracy of all reports filed by the laboratory under the provisions of this code or other applicable laws and rules.

§28-406.4 No examination required. An examination shall not be required for a concrete testing laboratory license.

ARTICLE 407
WELDER LICENSE

§28-407.1 Welder license required. It shall be unlawful to perform manual welding work on any structural member of any building [in the city] unless such work is performed by a person licensed as a welder under the provisions of this article.

§28-407.2 Qualifications. All applicants for a welder license shall submit satisfactory proof of the applicant’s fitness to make structural welds, including his or her ability to pass operator qualification tests as determined by the commissioner.

§28-407.3 Fitness to perform work. As a condition of license renewal [and reinstatement] , a licensed welder shall provide evidence satisfactory to the department that such licensee is fit to perform the work.

§28-407.4 Insurance exemption. Unless otherwise required by rule, licensed welders are exempt from the insurance requirements of section 28-401.9.

ARTICLE 408
MASTER PLUMBER LICENSE

§28-408.1 Master plumber license required. It shall be unlawful for any person:

1.	To perform plumbing work unless such person is a licensed master plumber or working under the direct and continuing supervision of a licensed master plumber, except that a city employee who holds a master plumber license may only perform [replacement, maintenance and repair] plumbing work on existing buildings in the course of his or her employment.

2.	To use the title licensed master plumber, master plumber or any other title in such manner as to convey the impression that such person is a licensed master plumber, unless such person is licensed as such in accordance with the provisions of this article.

§28-408.2 Seal. All documents that are required to be filed with any department or agency of the city of New York shall bear the stamp of the seal as well as the signature of the licensee. The licensed master plumber performing the work and services shall personally sign and seal all applications and other documents required to be filed pursuant to this code.

§28-408.3 Additional qualifications. Applicants for a master plumber license shall have the following additional qualifications:

§28-408.3.1 Experience. All applicants for a master plumber license shall submit satisfactory proof establishing that the applicant:

1.	Has at least seven (7) years total experience, within the ten (10) years prior to application, in the installation of plumbing systems and the planning or design [, and installation,] of plumbing systems under the direct and continuing supervision of a licensed master plumber in the United States, with at least two (2) years of such experience as a registered journeyman plumber in accordance with the provisions of article 409 [, except that during the three years immediately following July 1, 2008, there shall be no requirement for such registered journeyman plumber experience];

2.	Has received a bachelor’s degree in mechanical engineering or appropriate engineering technology from an accredited college or university and has at least five (5) years total experience, within the seven (7) years prior to application, in the installation of plumbing systems and the planning or design [and installation] of plumbing systems under the direct and continuing supervision of a licensed master plumber in the United States, where at least two (2) years of such experience were in New York city;

3.	Is an architect or engineer with at least three (3) years of experience, within the five (5) years prior to application, in the installation of plumbing systems and the planning or design [, and installation,] of plumbing systems. All required experience must be under the direct and continuing supervision of a licensed master plumber in the United States, [where] and at least one (1) year of such experience [was] must be in New York city;

4.	Has at least seven (7) years total experience, within the ten (10) years prior to application, with at least two (2) years of such experience working [in the] with installation of plumbing systems and in the planning or design [, and installation,] of plumbing systems under the direct and continuing supervision of a licensed master plumber in the United States. The balance of such required experience may be obtained by performing maintenance, replacement and repair plumbing work on existing buildings while in the employ of a city agency under the direct and continuing supervision of a licensed master plumber supervisor employed by the city agency. [Three years after July 1, 2008 the] The two (2) years’ experience in the installation of plumbing systems and in the planning or design [, and installation,] of plumbing systems set forth above may only be satisfied by working as a registered journeyman plumber; or

5.	Has experience as an employee of a government agency, or a private inspection agency or other entity [, acceptable to the commissioner] as specified in department rules, whose duties primarily involve the inspection of plumbing work for compliance with the New York city plumbing code and/or other laws relating to the installation, alteration or repair of plumbing systems [which] that shall be credited for fifty percent (50%) of the number of years that he or she has been satisfactorily employed in such duties within the ten (10) year period prior to application, which, however, in no event, shall exceed two and one-half (2.5) years credit of satisfactory experience. The balance of the required seven (7) years must have been obtained by working with installation of plumbing systems and in the planning or design [, and installation,] of plumbing systems under the direct and continuing supervision of a licensed master plumber in the United States, except that the requirement of paragraph 1 of this section 28-408.3.1 that an applicant’s working experience must have been within the ten (10) year period prior to application shall not apply to such balance of the work experience required pursuant to this paragraph.

§28-408.3.2 Armed services. Applicants who were engaged in plumbing work as above provided prior to entering the armed services of the United States shall be permitted to credit their time in the service as experience in the plumbing business, as above provided; but such service credit shall not exceed one-third of the time required for experience.

§28-408.4 Certificate of competence, [and] license [, plate] and [/or] seal. The commissioner shall issue a certificate of competence, license [, plate,] and [/or] seal, in accordance with the following:

§28-408.4.1 Certificate of competence. A certificate of competence shall be issued by the commissioner to an applicant who satisfactorily complies with the experience and examination requirements of this chapter for a license, upon payment of the fee. Such certificate shall contain the full name of the individual and a certificate number, the date of issuance, and shall be signed by the commissioner.

§28-408.4.2 Effect of issuance. The issuance of a certificate of competence shall constitute evidence that the person named therein is qualified, upon payment of applicable fees, to obtain a [plate and] seal while the certificate is valid [except that a city employee while in the employ of the city shall only be entitled to obtain a seal].

§28-408.4.3 [Plate and/or seal] Seal required. The holder of a certificate shall not be entitled to perform work or hold himself or herself out to perform work as a licensed master plumber until such [plate and/or] seal [have] has been obtained. Further, no holder of a certificate of competence shall enter into any contractual agreement to install or alter any plumbing, gas piping, or any piping system, other than an employment agreement with a master plumber business or a city agency.

§28-408.4.4 [Effect of failure] Failure to obtain [plate and/or] seal. If a holder of a certificate of competence has held the certificate for five (5) years without a [plate and/or] seal, then the commissioner may require said person to submit an affidavit and supporting documentation satisfactory to the department stating that over the five (5) year period the individual has been engaged in the installation of plumbing systems and the planning or the design [, and installation,] of plumbing systems in the United States under the direct and continuing supervision of a licensed master plumber. If the holder’s qualifications are not satisfactory to the commissioner, the commissioner may require such person to submit to reexamination or to provide evidence of retained proficiency. [In addition, additional] Additional fees will be due, as set forth in this chapter.

§28-408.4.5 Requirement for obtaining a license [, plate] and [/or] seal. A holder of a certificate of competence or an applicant who has satisfied all requirements for a master plumber license shall obtain:

1.	A license [, plate] and [/or] seal issued upon establishing a master plumbing business conforming to the requirements of this article and rules promulgated by the department; or

2	A license and seal issued upon demonstrating employment with a city agency. The license shall clearly state: “The bearer of this master plumber license is a government employee and as such is not authorized to engage in plumbing contract work outside of his/her government employment and within such government employment shall only engage in [maintenance, replacement and repair] plumbing work on existing buildings.” [No plate shall be issued to a licensed master plumber employed by a city agency.]

§28-408.4.6 Issuance. A certificate of competence or a license [, plate,] and [/or] seal as a master plumber shall be issued only to an individual.

§28-408.4.7 Duplication prohibited. Not more than one license [, plate] and [/or] seal shall be issued to an individual and no individual shall make or cause to be made a duplicate of such license [, plate or] and seal.

§28-408.5 Surrender of license [, plate] or seal. Upon the death or the retirement of a licensed master plumber, or upon the surrender, revocation or suspension of his or her license, his or her license, [plate] and [/or] seal shall immediately be surrendered to the commissioner. Nothing contained herein shall be construed to prevent the legal representative of a deceased licensee, with the consent of the commissioner, from retaining such [plate and] seal for the purpose of completing all unfinished work of the deceased licensee for which plans have been approved and a permit issued, provided such work is performed by or under the direct and continuing supervision of a licensed master plumber and is completed within one (1) year from the date of the death of the original licensee. Retired licensees and the legal representatives of deceased licensees shall schedule for inspection, withdraw or have another licensee re-file any open application filed under such license in accordance with department procedures.

§28-408.6 Master plumber business required. No individual, corporation, partnership or other business association shall conduct a plumbing [contracting] contractor business in the city of New York, or employ the name “plumber” or “plumbing” in its business name unless such business is a master plumber business as follows:

1.	No less than 51 percent of the control and voting capital stock of such plumbing [contracting] contractor business is owned by one or more individuals who are licensed master plumbers [who cannot be terminated from the public contracting business by any person or entity] , except as otherwise provided;

2.	All plumbing or gas piping work performed by such entity is performed by or under the direct and continuing supervision of such licensed master plumber;

3.	The person in charge of such work is such licensed master plumber; and

4.	The persons actually performing such work are in the direct employ of such master plumber business as authorized by the code.

Exception: A company, corporation, partnership or other business association or its predecessor that was engaged in plumbing work prior to January 25, 1990 may continue to do so in any one or more of such business forms without complying with the foregoing, if (i) application was made to the department prior to July 25, 1990, and (ii) necessary evidence was furnished on or prior to January 25, 1991, that such company, corporation, partnership or other business association or its predecessor had employed an average of ten or more journeymen plumbers doing plumbing work for at least five days a week for a period of ten (10) years or more out of the twenty (20) years preceding July 25, 1990, provided, that such plumbing business continues to have all plumbing work conducted under the management and direct and continuing supervision of a licensed master plumber in the direct employ of such plumbing business and that such licensed master plumber is not otherwise interested in, associated with or employed by any other plumbing business operating in this city except as a joint venture in which such master plumber’s employer is one of the joint venturers.

§28-408.6.1 Use. Nothing herein contained shall be construed to prohibit the use of a master plumber license by the holder thereof for or on behalf of a partnership, corporation or other business association, provided that such partnership, corporation or other business is a master plumber business.

§28-408.6.2 Identification. All business vehicles, advertising, websites and stationery used in connection with a master plumber business shall display prominently the full name of the licensee, the words “N.Y.C. licensed plumber,” the licensee’s number and the licensee’s business address. If the business is conducted under a trade name, or by a partnership or corporation, the trade name, partnership or corporate name shall be placed immediately above the full name or names of the licensed master plumber or licensed master plumbers [to whom the plates were issued]. Prior to using, the trade name, partnership or corporate name must have been disclosed to the department in a form and manner required by the department.

§28-408.6.3 Withdrawal of license. If a licensed master plumber withdraws from a master plumbing business operating pursuant to such individual’s license, the right of the business to perform plumbing work shall lapse if the provisions of this [section 28-408.6] article are no longer satisfied. If a licensed master plumber’s license is revoked or suspended, such licensee will be deemed withdrawn from such business.

§28-408.6.4 Ownership limitations. An individual who is a licensed master plumber whose interest or ownership in a master plumber business constitutes any portion of the 51 percent interest or control required by this section 28-408.6 shall be allowed to possess an interest or ownership in only one other master plumber business, where such interest or ownership would constitute any portion of the 51 percent interest or control required by this section 28-408.6. Both master plumber businesses in which the licensed master plumber has an interest shall be located at the same place of business. For the purposes of this section 28-408.6, where two or more individuals who are licensed master plumbers possess an interest or ownership in any master plumber business [which] that together represents more than 51 percent of the interest or control of such entity, all of such licensees shall be deemed to possess a portion of the 51 percent interest or control required by this section 28-408.6.

§28-408.6.5 Joint ventures. Nothing contained in this section 28-408.6 shall be construed to prevent a master plumber business from entering into a joint venture of limited duration for a particular project with another master plumber business. The terms of a joint venture must be in writing, and documentation of the joint venture must be submitted to the department for approval prior to the initiation of work under such venture.

§28-408.6.6 Supervision. The master plumber shall conduct his or her business to provide direct and continuing supervision in accordance with the provisions of this code.

Exception: The provisions of this section 28-408.6.6 shall not apply to minor alterations or ordinary repairs, as defined in this code, or to the installation or alteration of gas service piping and gas meter piping, including meters, valves, regulators or related equipment, when such work is to be performed, serviced and maintained by utility corporations subject to the jurisdiction of the New York state public service commission.

§28-408.7 Fitness to perform work. As a condition of license renewal, a licensed master plumber shall provide evidence satisfactory to the department that such licensee is fit to perform the work.

ARTICLE 409
JOURNEYMAN PLUMBER REGISTRATION

§28-409.1 Journeyman plumber registration [; additional] qualifications. [Upon satisfactory completion of a New York State-recognized training program or affirmation of an applicant’s qualifications by an employer licensed master plumber or, in the case of a city agency, a supervising licensed master plumber and upon written stipulation of same by the applicant, the] The commissioner shall register an applicant as a journeyman plumber [. Such] who has qualifications [shall reflect] reflecting a progressive understanding, proficiency and competence in the plumbing trade, including:

1.	A working familiarity with the plumbing code and technical standards and the ability to apply the code requirements correctly;

2.	The application of basic plumbing theory and the utilization of trade skills on the job site;

3.	A working knowledge of the tools of the trade and the ability to utilize them properly; and

4.	An ability to draft simple diagrams and interpret from drawings for the purpose of the plumbing work in which the applicant is engaged.

§28-409.2 Experience. The applicant for journeyman plumber registration [shall have a] must demonstrate that he or she has a progressive understanding, proficiency and competence in the plumbing trade by having:

1.	A minimum of five (5) years of full-time experience in the performance of plumbing work under the direct and continuing supervision of a licensed master plumber or equivalent, where at least one (1) year of such experience shall have been in New York city [.]; or

2.	Satisfactorily completed a New York State recognized training program in plumbing.

§28-409.3 Registration need not be renewed. The registration for journeyman plumber shall have no expiration and shall not require renewal or [re-issuance] reissuance.

§28-409.4 Registration card. The registration card shall clearly state: “This registration is NOT A LICENSE, and the holder is NOT AUTHORIZED TO PERFORM PLUMBING WORK in New York city except under the direct and continuing supervision of a licensed master plumber.”

ARTICLE 410
MASTER FIRE SUPPRESSION PIPING
CONTRACTOR LICENSE

§28-410.1 Master fire suppression piping contractor license required. It shall be unlawful for any person:

1.	To perform fire suppression piping work unless such person is a licensed master fire suppression piping contractor or working under the direct and continuing supervision of a licensed master fire suppression piping contractor, except that a city employee who holds a master fire suppression piping contractor license may only perform [replacement, maintenance and repair] fire suppression piping work on existing buildings in the course of his or her employment.

2.	To use the title licensed master fire suppression piping contractor, master fire suppression piping contractor or any other title in such manner as to convey the impression that such person is a licensed master fire suppression piping contractor, unless such person is licensed as such in accordance with the provisions of this article.

§28-410.2 Seal. All documents that are required to be filed with any department or agency of the city of New York shall bear the stamp of the seal as well as the signature of the licensee. The licensed master fire suppression piping contractor performing the work and services shall personally sign and seal all applications and other documents required to be filed pursuant to the code.

§28-410.3 Classification. There shall be three classes of licenses for master fire suppression piping contractor:

1.	Class A. The holder of a class A master fire suppression piping contractor license is authorized to perform any work in connection with any and all fire suppression piping systems as set forth in paragraphs 1 [and 2] -3 of the definition of fire suppression piping system in section 28-401.3.

2.	Class B. The holder of a class B master fire suppression piping contractor license is authorized to perform any work in connection with any and all fire suppression piping systems as set forth in paragraph 1 of the definition of fire suppression piping system in section 28-401.3.

3.	Class C. The holder of a class C master fire suppression piping contractor license is authorized to perform any work in connection with any and all fire suppression piping systems as set forth in paragraph [2] (3) of the definition of fire suppression piping system in section 28-401.3.

§28-410.4 Additional qualifications. Applicants for a master fire suppression piping contractor license shall have the following additional qualifications:

§28-410.4.1 Experience. All applicants for a master fire suppression piping contractor license shall submit satisfactory proof establishing that the applicant:

1.	Has at least seven (7) years total experience, within the ten (10) years prior to application, in the performance of fire suppression piping work, including the planning or design [, and installation,] of fire suppression piping systems under the direct and continuing supervision of a licensed master fire suppression piping contractor in the United States with the class of license for which application is made, with at least two (2) years of such experience as a registered journeyman fire suppression piping installer in accordance with the provisions of article 411 [, except that during the three years immediately following July 1, 2008, there shall be no requirement for such registered journeyman fire suppression piping installer experience];

2.	Has received a bachelor’s degree in mechanical engineering, fire protection engineering or appropriate engineering technology from an accredited college or university and has at least five (5) years total experience, within the seven (7) years prior to application, in the performance of fire suppression piping work, including the planning or design [, and installation,] of fire suppression piping systems under the direct and continuing supervision of a licensed master fire suppression piping contractor in the United States [for] with the class of license for which application is made, at least two (2) of which were in New York city;

3.	Is an architect or engineer with at least three (3) years of experience, within the five (5) years prior to application, in the performance of fire suppression piping work, including the planning or design [, and installation,] of fire suppression piping systems. All required experience must be under the direct and continuing supervision of a licensed master fire suppression piping contractor in the United States [for] with the class of license for which application is made, [where] and at least one (1) year of such experience [was] must be in New York city;

4.	Has at least seven (7) years total experience, within the ten (10) years prior to application, with at least two (2) years of such experience [working] in the performance of fire suppression piping work, including the planning or design [, and installation,] of fire suppression piping systems under the direct and continuing supervision of a licensed master fire suppression piping contractor in the United States with the class of license for which application is made. The balance of such required experience may be obtained by performing maintenance, replacement and repair of fire suppression piping work on existing buildings while in the employ of a city agency under the direct and continuing supervision of a licensed master fire suppression piping contractor supervisor employed by the city agency with the class of license for which application is made. [Three years after the effective date of this article the] The two (2) years of experience in the planning or design [, and installation,] of fire suppression piping systems set forth above may only be satisfied by working as a registered journeyman fire suppression piping installer; or

5.	Has experience as an employee of a government agency, or a private inspection agency or other entity, [acceptable to the commissioner] as specified in department rules, whose duties primarily involve the inspection of [plumbing work] fire suppression systems for compliance with [this] the New York city plumbing code and/or other laws relating to the installation, alteration or repair of fire suppression piping systems [which] that shall be credited for fifty percent (50%) of the number of years that he or she has been satisfactorily employed in such duties within the ten (10) year period prior to application, which, however, in no event, shall exceed two and one-half (2½) years credit of satisfactory experience. The balance of the required seven (7) years must have been obtained [by working] in the performance of fire suppression piping work and in the planning or design [, and installation,] of fire suppression piping systems under the direct and continuing supervision of a licensed fire suppression piping contractor in the United States with the class of license for which application is made except that the requirement of paragraph 1 of this section 28-410.4.1 that an applicant’s working experience must have been within the ten (10) year period prior to application shall not apply to such balance of the work experience required pursuant to this paragraph.

§28-410.4.1.1 Non-qualifying experience. Notwithstanding section 28-410.4.1, work on 30 or fewer sprinkler heads off the domestic water shall not be considered qualifying experience for a master fire suppression piping contractor license.

§28-410.4.2 Armed services. Applicants who were engaged in fire suppression piping work prior to entering the armed services of the United States shall be permitted to credit their time in the service as experience in the fire suppression piping business, as above provided; but such service credit shall not exceed one-third of the time required for experience.

§28-410.5 Certificate of competence, and license [, plate] and [/or] seal. The commissioner shall issue a certificate of competence, license [, plate] and [/or] seal in accordance with the following:

§28-410.5.1 Certificate of competence. A certificate of competence shall be issued by the commissioner to an applicant who satisfactorily complies with the experience and examination requirements of this article for a license, upon payment of the fee. Such certificate shall contain the full name of the individual and a certificate number, and shall be signed by the commissioner.

§28-410.5.2 Effect of issuance. The issuance of a certificate of competence shall constitute evidence that the person named therein is qualified, upon payment of applicable fees, to obtain a [plate and] seal while the certificate is valid [except that a city employee while in the employ of the city shall only be entitled to obtain a seal].

§28-410.5.3 [Plate and/or seal] Seal required. The holder of a certificate of competence shall not be entitled to perform work or hold himself or herself out to perform work as a licensed master fire suppression piping contractor until such [plate and/or] seal [have] has been obtained. Further, no holder of a certificate of competence shall enter into any contractual agreement to install or alter any fire suppression piping system other than an employment agreement with a master fire suppression piping business or a city agency.

§28-410.5.4 Failure to obtain [plate and/or] seal. If a holder of a certificate of competence has held the certificate for five (5) years without a [plate and/or] seal, then the commissioner may require said person to submit an affidavit and supporting documentation satisfactory to the department stating that over the five (5) year period the individual has been engaged in the performance of fire suppression piping work, including the planning or design [, and installation,] of fire suppression piping systems in the United States under the direct and continuing supervision of a licensed master fire suppression piping contractor. If the holder’s qualifications are not satisfactory to the commissioner, the commissioner may require such person to submit to reexamination or to provide evidence of retained proficiency. [In addition, additional] Additional fees will be due, as set forth in this chapter.

§28-410.5.5 [License plate and/or seal] Requirement for obtaining a license and seal. A holder of a certificate of competence or an applicant who has satisfied all requirements for a master fire suppression piping contractor license shall obtain:

1.	A license [, plate] and seal issued upon establishing a fire suppression piping contracting business conforming to the requirements of this article and any rules promulgated by the department; or

2.	A license and seal issued upon demonstrating employment with a city agency. The license shall clearly state: “The bearer of this master fire suppression piping contractor license is a government employee and as such is not authorized to engage in fire suppression piping contract work outside of his/her government employment and within such government employment shall only engage in [maintenance, replacement and repair] fire suppression piping work on existing buildings.” [No plate shall be issued to a licensed master fire suppression piping contractor employed by a city agency.]

§28-410.5.6 Issuance. A certificate of competence or a license [, plate and/] or seal as a master fire suppression piping contractor shall be issued only to an individual.

§28-410.5.7 Duplication prohibited. Not more than one license [, plate and/] or seal shall be issued to an individual, and no individual shall make or cause to be made a duplicate of such license [, plate] or seal.

[§28-410.6 Waiver of examinations. Any license issued without examination pursuant to an application filed prior to July 25, 1990 pursuant to the provisions of law in effect prior to July 1, 2008 that has not lapsed as of July 1, 2008, shall be renewable pursuant to the provisions of this code.]

[§28-410.7] §28-410.6 Surrender of license [, plate] and [/or] seal. Upon the death or the retirement of a licensed master fire suppression piping contractor, or upon the surrender, revocation or suspension of his or her license, his or her license [, plate] and seal shall immediately be surrendered to the commissioner. Nothing contained herein shall be construed to prevent the legal representative of a deceased licensee, with the consent of the commissioner, from retaining such [plate and] seal for the purpose of completing all unfinished work of such deceased licensee for which plans have been approved and a permit issued, provided such work is performed by or under the direct and continuing supervision of a licensed master fire suppression piping contractor and is completed within one (1) year from the date of the death of the original licensee. Retired licensees and the legal representatives of deceased licensees shall schedule for inspection, withdraw or have another licensee re-file any open application filed under such license in accordance with department procedures.

[§28-410.8] §28-410.7 Master fire suppression piping contractor business required. No individual, corporation, partnership or other business association shall conduct a fire suppression piping [contracting] contractor business in the city of New York, or employ the name “fire suppression piping” in its business name, unless the business is a master fire suppression business as follows:

1.	No less than 51 percent of the control and voting capital stock of such fire suppression piping [contracting] contractor business is owned by one or more individuals who are licensed master fire suppression piping contractors [who cannot be terminated from the fire suppression piping contracting business by any person or entity] , except as otherwise provided; [and]

2.	All fire suppression piping work performed by such entity is performed by or under the direct and continuing supervision of such licensed master fire suppression piping contractor;

3.	The person in charge of such work is such licensed master fire suppression piping contractor; and

4.	The persons actually performing such work are in the direct employ of such master fire suppression piping contractor business as authorized by the code.

Exception: A company, corporation, partnership or other business association or its predecessor that was engaged in fire suppression piping contractor work prior to January 25, 1990 may continue to do so in any one or more of such business forms without complying with the foregoing, if (i) application was made to the department prior to July 25, 1990, and (ii) necessary evidence was furnished on or prior to January 25, 1991, that such company, corporation, partnership or other business association or its predecessor had employed an average of 10 or more journeymen doing fire suppression piping contractor work for at least five days a week for a period of ten (10) years or more out of the twenty 20 years preceding July 25,1990, provided, that such business continues to have all fire suppression piping contractor work conducted under the management and direct and continuing supervision of a licensed master fire suppression contractor in the direct employ of such business and that such licensed master fire suppression contractor is not otherwise interested in, associated with or employed by any other licensed master fire suppression contracting business operating in this city except as a joint venture in which such licensed master fire suppression contractor’s employer is one of the joint venturers.

[§28-410.8.1] §28-410.7.1 Use. Nothing herein contained shall be construed to prohibit the use of a master fire suppression piping contractor license by the holder thereof for or on behalf of a partnership, corporation or other business association, provided that such partnership, corporation or other business is a master fire suppression piping contractor business.

[§28-410.8.2] §28-410.7.2  Identification. All business vehicles, advertising, websites and stationery used in connection with a master fire suppression piping contractor business shall display prominently the full name of the licensee, the words “N.Y.C. licensed fire suppression piping contractor – class A, B or C,” the licensee’s number and the licensee’s business address. If the business is conducted under a trade name, or by a partnership or corporation, the trade name, partnership or corporate name shall be placed immediately above the full name or names of the licensed master fire suppression piping contractor or licensed master fire suppression piping contractors [to whom the plates were issued]. Prior to using, the trade name, partnership or corporate name must have been disclosed to the department in a manner required by the department.

[§28-410.8.3] §28-410.7.3 Withdrawal of [licensee] license. If a licensed master fire suppression piping contractor withdraws from a master fire suppression piping contractor business operating pursuant to such individual’s license, the right of the business to perform fire suppression piping work shall lapse if the provisions of this article are no longer satisfied. If a licensed master fire suppression piping contractor’s license is revoked or suspended, such licensee will be deemed withdrawn from such business.

[§28-410.8.4] §28-410.7.4 Ownership limitations. An individual who is a licensed master fire suppression piping contractor whose interest or ownership in a master fire suppression piping contractor business constitutes any portion of the 51 percent interest or control required by this section [28-410.8] 28-410.7 shall be allowed to possess an interest or ownership in only one other fire suppression piping contractor business where such interest or ownership would constitute any portion of the 51 percent interest or control required by this section [28-410.8] 28-410.7. Both fire suppression piping contractor businesses in which the licensed master fire suppression piping contractor has an interest shall be located at the same place of business. For the purposes of this section [28-410.8] 28-410.7, where two or more individuals who are licensed master fire suppression piping contractors possess an interest or ownership in any master fire suppression piping contractor business [which] that together represents more than 51 percent of the interest or control of such entity, all of such licensees shall be deemed to possess a portion of the 51 percent interest or control required by this section [28-410.8] 28-410.7.

[§28-410.8.5] §28-410.7.5 Joint ventures. Nothing contained in this section [28-410.8] 28-410.7 shall be construed to prevent a master fire suppression piping contractor business from entering into a joint venture of limited duration for a particular project with another master fire suppression piping contractor business. The terms of a joint venture must be in writing, and documentation of the joint venture must be submitted to the department for approval prior to the initiation of work under such venture.

[§28-410.8.6] §28-410.7.6 Supervision. The master fire suppression piping contractor shall conduct his or her business to provide direct and continuing supervision in accordance with the provisions of this [article] code.

[Exception: The provisions of this section 28-410.8.6 shall not apply to minor alterations or ordinary repairs, as defined in this code, and/or to maintenance of a fire suppression piping system.]

[§28-410.9] §28-410.8 Fitness to perform work. As a condition of license renewal, a licensed master fire suppression piping contractor shall provide evidence satisfactory to the department that such licensee is fit to perform the work.

ARTICLE 411
JOURNEYMAN FIRE SUPPRESSION PIPING
INSTALLER REGISTRATION

§28-411.1 Journeyman fire suppression piping installer registration [; additional] qualifications. [Upon satisfactory completion of a New York state-recognized training program or affirmation of an applicant’s qualifications by an employer licensed master fire suppression piping contractor or, in the case of a city agency, a supervising licensed master fire suppression piping contractor and upon written stipulation of same by the applicant, the] The commissioner shall register an applicant as a journeyman fire suppression piping installer [. Such] who has such qualifications [shall reflect] reflecting a progressive understanding, proficiency and competence in the fire suppression piping trade, including:

1.	A working familiarity with the code and technical standards with regard to fire suppression piping, and the ability to apply the code requirements correctly;

2.	The application of basic fire suppression theory and the utilization of trade skills on the job site;

3.	A working knowledge of the tools of the trade and the ability to utilize them properly; and

4.	An ability to draft simple diagrams and interpret from drawings for the purpose of the fire suppression piping work in which the applicant is engaged.

§28-411.2 Experience. The applicant for journeyman fire suppression piping installer registration [shall have a] must demonstrate that he or she has a progressive understanding, proficiency and competence in the fire suppression trade by having:

1.	A minimum of five (5) years of full-time experience in the performance of fire suppression piping work under the direct and continuing supervision of a licensed master fire suppression piping contractor or equivalent, where at least one (1) year of such experience shall have been in the city of New York [.]; or

2.	Has satisfactorily completed a New York State recognized training program in fire suppression piping.

§28-411.3 [No required expiration, renewal or reissuance] Registration need not be renewed. The registration for journeyman fire suppression piping installer shall have no expiration and shall not require renewal or reissuance.

§28-411.4 [Required statement] Registration card. The registration shall clearly state: “This registration is NOT A LICENSE, and the holder is NOT AUTHORIZED TO PERFORM FIRE SUPPRESSION PIPING WORK in New York city except under the direct and continuing supervision of a Licensed Master Fire Suppression Piping Contractor.”

ARTICLE 412
OIL-BURNING EQUIPMENT INSTALLER LICENSE

§28-412.1 Oil-burning equipment installer license required. It shall be unlawful to install oil-burning equipment in the city unless such work is performed by or under the direct and continuing supervision of a person licensed as an oil-burning equipment installer under the provisions of this article.

§28-412.2 [Classifications. Oil-burning] Use. An oil-burning equipment installer [licenses shall be classified as follows:]

[1.	Class A oil-burning equipment installer license. Licenses the holder thereof] license permits the license holder to install any type of oil-burning equipment [, as an independent contractor with]. The license holder shall have full responsibility for the manner in which the work is done, and for the material and equipment used, and for the control and direct and continuing supervision of the persons employed on the work. Such equipment shall include, but not be limited to, burners, boilers and generators.

[2.	Class B oil-burning equipment installer license. Licenses the holder thereof to install oil-burning equipment for the use of domestic fuel oils from number one fuel oil to and including number four fuel oil, as an independent contractor with full responsibility for the manner in which the work is done, for the materials and equipment used, and for the control and direct and continuing supervision of the persons employed on the work.]

§28-412.3 Qualifications. Applicants for an oil-burning equipment installer license shall [have the qualifications set forth in sections 28-412.3.1 through 28-412.3.2.]

[§28-412.3.1 Experience for Class A license. All applicants for a class A oil-burning equipment installer license shall] submit satisfactory proof establishing that the applicant has had at least four (4) years of practical experience, within the seven (7) years prior to application, in the installation of oil-burning equipment under the direct and continuing supervision of a [Class A-] licensed oil-burning equipment installer in the city [, including at least one year experience in the installation of oil-burning equipment for the use of number five and number six fuel oils].

[§28-412.3.2 Experience for Class B license. All applicants for a class B oil-burning equipment installer license shall submit satisfactory proof establishing that the applicant has had at least three years practical experience within the five years prior to application in the installation of oil-burning equipment under the direct and continuing supervision of a licensed oil-burning equipment installer in the city.]

§28-412.4 Fitness to perform work. As a condition of license renewal [and reinstatement] , a licensed oil-burning equipment installer shall provide evidence satisfactory to the department that such licensee is fit to perform the work.

§28-412.5 Oil-burning equipment installer place of business. Every licensed oil-burning equipment installer shall have a place of business within the city. A licensed oil-burning equipment installer shall be a sole proprietor, a partner in the partnership or an officer of the corporation. A licensed oil-burning equipment installer shall be allowed to associate his or her license with only one other oil burning business. Such businesses shall be located at the same place of business.

§28-412.6 Seal. At the time of issuance of an oil burning equipment installer license and upon payment of the required fee, the commissioner shall issue to the licensee a seal containing the full name of the license holder and the words “licensed oil-burning equipment installer”. The license holder shall not be entitled to perform work or hold himself or herself out as a licensed oil-burning equipment installer until such seal has been obtained. The seal shall remain the property of the city of New York. Upon revocation of an oil-burning equipment installer’s license or death of the licensee or failure of a licensee to renew such license, the seal must be surrendered to the department. If the seal is lost or stolen, and an affidavit is submitted by the licensee establishing such fact, a new seal shall be issued upon application and payment of a fee.

§28-412.6.1 Use of seal. All documents that are required to be filed with any department or agency of the city of New York shall bear the stamp of the seal as well as the signature of the licensee. The licensed oil burner equipment installer performing the work and services shall personally sign and seal all applications and other documents required to be filed by the department.

ARTICLE 413
HIGH-PRESSURE BOILER
OPERATING ENGINEER LICENSE

§28-413.1 High-pressure boiler operating engineer license required. It shall be unlawful to operate any high-pressure boiler for any purpose whatsoever, in the city of New York or in connection with any vessel on the waters in and around the city not subject to the jurisdiction of the United States, unless such boiler is operated by or under the direct and continuing supervision and in the presence of a person having a high-pressure boiler operating engineer license under the provisions of this article.

Exceptions: A licensed high-pressure boiler operating engineer is not required to operate a high-pressure boiler that meets all of the following conditions:

1.	The boiler is a stand-alone boiler;

2.	If the boiler is a steam boiler, the boiler has less than 100 square feet (9.3 m2) of heating surface;

3.	If the boiler is a steam boiler, it is capable of generating less than 1750 pounds (794 kg) per hour of steam; or if the boiler is a hot water boiler, it is capable of generating less than 2 million btu/h of hot water;

4.	The boiler has a safety relief valve setting of 200 psig (1379 kPa) or less;

5.	The boiler room enclosure is in compliance with section 508 of the New York city building code; and

6.	There is a carbon monoxide detector in the boiler room interlocked with the boiler.

§28-413.2 Qualifications. Applicants for a high-pressure boiler operating engineer license shall present satisfactory proof that:

1.	Applicant [was employed as a fireman, oiler, general assistant, journeyman, boiler-maker or machinist] has practical experience in the operation, maintenance, replacement, modification, assembly, or repair of high pressure boilers under the direct and continuing supervision of a licensed high-pressure boiler operating engineer in the city for a period of not less than five (5) years within the seven (7) year period preceding the date of the application; [however, in lieu of the experience requirement contained in this paragraph, an applicant for a high-pressure boiler operating engineer license who is employed in a fossil fuel production plant located in the Rockaway Peninsula area of Queens county may submit satisfactory proof establishing that the applicant has obtained at least five years experience within the seven years preceding the date of the application which shall include at least two years of experience obtained during employment under the direct and continuing supervision of a licensed high-pressure boiler operating engineer in a steam generating plant located outside of the city of New York but within the state of New York that is owned and operated by a licensed public utility company, and shall also include a separate period of at least three years of experience obtained comparable position as approved by the commissioner, in such steam generating plant;]

2.	Applicant received a bachelor’s degree in mechanical engineering from an accredited school or college and had one (1) year of experience in the operation and maintenance of high-pressure boilers under the direct and continuing supervision of a licensed high-pressure boiler operating engineer [in the city] within the two (2) year period preceding the date of the application;

3.	Applicant has held, for a minimum of four (4) years, either a certificate as an engineer issued by a board of examining engineers duly established and qualified pursuant to the laws of the United States or any state or territory thereof, or a certificate as a marine engineer issued by the United States Coast Guard [, and a]. In addition, an applicant shall have a minimum of one (1) year of experience in the city in the operation and maintenance of stationary high-pressure boiler plants under the direct and continuing supervision of a licensed high-pressure boiler operating engineer within the seven (7) years preceding the date of the application [, provided that the applicant shall have filed with such application a signed statement that the applicant is the person named in said certificate together with the supporting signed statements by three licensed high-pressure boiler operating engineers employed in the city of New York at the time of making of such signed statements];

4.	Applicant exercised [direct and continuing] supervision, care, operation and maintenance over a steam generating plant of a governmental building [having boilers] for a minimum of five (5) years, within the seven (7) year period preceding the date of the application, with each boiler having a minimum of 150 or more horsepower [, for a minimum of five years and had a minimum of one]. One (1) year of such experience shall be on high-pressure boilers under the direct and continuing supervision of a licensed high-pressure boiler operating engineer in the city [within the seven year period preceding the date of the application];

5.	Applicant successfully completed a New York state approved apprenticeship training program of at least two (2) years, and after the completion of such program had at least three (3) years’ experience, within the seven (7) years preceding the date of the application, in the operation and maintenance of high-pressure boilers in the city under the direct and continuing supervision of a licensed high-pressure boiler operating engineer;

6.	Applicant has held a Commission from the National Board of Boiler and Pressure Vessel Inspectors for a period of seven (7) years, and has a minimum of five (5) years of high pressure boiler operation, maintenance, and/or inspection experience under such commission within the seven (7) year period preceding the application; or

[7.	Applicant has held a Qualifications of High Capacity Fossil Fuel Operator (QFO) operator certification from ASME, and has a minimum of five years of high pressure boiler operation, maintenance, and/or inspection experience under such QFO certification within the seven year period preceding the application; or]

[8.] 7.	Applicant has held a high pressure certification/high pressure license for a period of five (5) years from other jurisdictions acceptable to the commissioner, provided such jurisdiction follows the ASME Boiler and Pressure Vessel Code, and was employed under such certification and/or license for a period of not less than five (5) of the last seven (7) years in the operation, maintenance and/or inspection of high pressure boilers.

§28-413.3 Fitness to perform work. As a condition of license renewal [and reinstatement] , a licensed high-pressure boiler operating engineer shall provide evidence satisfactory to the department that such licensee is fit to perform the work.

[§28-413.4 Individuals holding portable high-pressure boiler operating engineer license on the effective date of this section. Notwithstanding section 28-413.2, upon application, individuals who hold a portable high-pressure boiler operating engineer license on the effective date of this section may be issued a high-pressure boiler operating engineer license without examination. Such application shall be deemed to be an application for renewal of a license pursuant to this chapter.]

ARTICLE 414
RESERVED

ARTICLE 415
SIGN HANGER LICENSE

§28-415.1 Sign hanger license required. It shall be unlawful to hoist or lower or to hang or attach any sign upon or on the outside of any building or structure in the city unless such work is performed by or under the direct and continuing supervision of a person licensed as a sign hanger under the provisions of this article.

§28-415.2 Exemptions. The provisions of this article shall not apply to the following:

1.	Signs not exceeding 75 square feet (7 m2) in area, measured on one face only, nor exceeding 25 pounds (11 kg) in weight;

2.	Signs supported directly on the ground; or

3.	Directional signs; or

4.	Temporary signs erected during the construction or alteration of a building and related to such work; or

5.	The erection or placing of any signs by employees of the city, any city department or other city agency.

§28-415.3 Classification. Such licenses shall be classified as follows:

1.	Master sign hanger license. Authorizes the holder thereof to hoist or lower or to hang or attach any sign, irrespective of weight, upon or on the outside of any building.

2.	Special sign hanger license. Authorizes the holder thereof to hoist or lower or to hang or attach any sign not exceeding one hundred fifty square feet in area, measured on one face only, nor exceeding one thousand two hundred pounds in weight, upon or on the outside of any building.

§28-415.4 Additional qualifications. Applicants for a sign hanger license shall have the additional qualifications set forth in sections 28-415.4.1 through 28-415.4.2.

§28-415.4.1 Master sign hanger qualifications. All applicants for a master sign hanger license shall submit satisfactory proof establishing that the applicant has at least five (5) years of practical experience in sign hanging as a designated master sign hanging foreman within the seven (7) years preceding the date of the license application under the direct and continuing supervision of a licensed master sign hanger [; and the]. The applicant shall also have [a] knowledge of and ability to read plans and specifications relating to sign construction and erection, including supporting framework and other supports, and [a] knowledge of the problems and practices of sign construction and hanging and be familiar with the equipment and tools used in sign hanging.

§28-415.4.2 Special sign hanger qualifications. All applicants for a special sign hanger license shall submit satisfactory proof establishing that the applicant has at least three (3) years of practical experience in sign hanging as a designated special sign hanging foreman within the five (5) years preceding the date of the license application under the direct and continuing supervision of a licensed sign hanger [; and the]. The applicant shall also have [a] knowledge and ability to read plans and specifications relating to sign construction and erection, including supporting framework and other supports, and [a] knowledge of the problems and practices of sign construction and hanging and be familiar with the equipment and tools used in sign hanging.

§28-415.5 Additional requirements. The additional requirements set forth in sections 28-415.5.1 through 28-415.5.2 shall apply to sign hangers:

§28-415.5.1 Danger warning. Every licensed sign hanger shall, while sign hanging operations are in progress at a job site, place conspicuously at such job site two plates or signs not less than 18 inches (457 mm) by 24 inches (610 mm) in size (i) displaying the word “danger” in letters not less than 6 inches (152 mm) high, and (ii) disclosing the sign hanger’s name, business address, type of license and license number.

§28-415.5.2 Sign hanger place of business. Every licensed sign hanger shall have a place of business within the city and shall display prominently at such place of business a plate or sign marked with the words “sign hanger” and the license number immediately thereunder. A licensed sign hanger shall be a sole proprietor, a partner in the partnership or an officer of the corporation and shall be allowed to associate his or her license with only one other sign hanger business. Such businesses shall be located at the same place of business.

§28-415.6 Fitness to perform work. As a condition of license renewal [or reinstatement] , a licensed sign hanger shall provide evidence satisfactory to the department that such licensee is fit to perform the work.

ARTICLE 416
FILING REPRESENTATIVE REGISTRATION

§28-416.1 Filing representative registration required. No person shall use the term “registered filing representative” or “filing representative” or any similar representation in such manner as to convey the impression that such person is a registered filing representative in accordance with the provisions of this article; nor shall any person present, submit, furnish or seek approval of applications or construction documents, or remove any documents from the possession of the department, without first having registered with the department such person’s name, address and company affiliation on a form to be furnished by the department.

§28-416.2 Exemptions. The following persons are exempt from the provisions of this article. Any person from whom the department may refuse to accept an application or other document pursuant to section 28-211.1 shall not be afforded this exemption.

1.	The owners of the premises for which the building applications are filed including, in the case of partnerships or corporations, the general partners or the principal officers of the corporation, where the principal officers of a corporation shall include the president, vice presidents, secretary and treasurer;

2.	The lessees of such premises authorized by the owner to file building applications;

3.	Condominium unit owners authorized by the condominium board of managers to file building applications;

4.	Cooperative shareholders authorized by the cooperative board of directors to file building applications;

5.	Architects;

6.	Engineers;

7.	Attorneys admitted to practice in New York state;

8.	Master plumbers licensed pursuant to this chapter;

9.	Master fire suppression piping contractors licensed pursuant to this chapter; and

10.	Master electricians licensed pursuant to subchapter one of chapter 3 of title 27 of the administrative code.

§28-416.3 Rules. The commissioner shall promulgate rules for the proper and efficient administration and enforcement of this article. Unless required by rule, a registered filing representative shall not be required to take an examination or to complete continuing education courses as a condition for renewal of the registration.

ARTICLE 417
 [BOARDS] RESERVED

[§28-417.1 Plumbing and fire suppression piping contractor license board. The commissioner shall appoint annually and may remove in his or her discretion each member of a plumbing and fire suppression piping contractor license board that shall have as its purpose the following:]

[1.	To advise the commissioner regarding the character and fitness of applicants for certificates of competence and licenses who have passed the required examination.]

[2.	To advise the commissioner regarding allegations of illegal practices on the part of licensed master plumbers, licensed master fire suppression piping contractors, master plumber businesses or master fire suppression piping businesses.]

[3.	To advise the commissioner regarding plumbing and fire suppression piping practices, code applications, regulations and legislation.]

[4.	To perform such other responsibilities as may be requested by the commissioner and as set forth in rules promulgated by the department.]

[§28-417.1.1 Removal. The commissioner may remove any member of the license board and shall fill any vacancy therein.]

[§28-417.1.2 Membership. Membership of the board shall consist of:]

[1.	Two officers or employees of the department;]

[2.	Five licensed master plumbers, three of whom shall be selected from nominees of the New York city contracting plumbing association whose members perform the largest dollar value of work within the city and one of whom shall be the holder of a class A or class B master fire suppression piping contractor license. The two remaining licensed master plumber board member positions shall be from the next largest plumbing association in the city of New York.]

[3.	Two licensed master fire suppression piping contractors, both of whom shall hold a class A license and shall be selected from nominees of the New York city sprinkler/fire suppression piping contractors association whose members perform the largest dollar value of work within the city;]

[4.	A registered journeyman plumber from the organization representing the largest number of registered journeyman plumbers;]

[5.	A registered journeyman fire suppression piping installer from the organization representing the largest number of registered journeyman fire suppression piping installers;]

[6.	An engineer having at least five years experience in the planning or design, and installation, of plumbing systems;]

[7.	An architect;]

[8.	An engineer who is a full member of the society of fire protection engineers;]

[9.	Two officers or employees of the fire department representing the fire commissioner; and]

[10.	A real estate owner or manager or representative thereof.]

[§28-417.1.3 Organization of the board. A member of the board who is an officer or employee of the department representing the commissioner shall serve as chairperson and all members shall serve without compensation. Nine members including the chairperson, who shall be entitled to vote, shall constitute a quorum of the board for the transaction of business. In the absence of a member or in the event of a vacancy, an alternate member of the board, may vote in the place and stead of the member for whom he or she is the alternate or on account of whom the vacancy exists. Alternate members shall be appointed and removed at the commissioner’s discretion. All actions shall be conducted by majority vote except as otherwise provided, and the board shall keep minutes of its proceedings and records of its investigations. Except as otherwise determined by the chairperson, the board shall meet at least once a month.]

[§28-417.1.4 Advisory and support personnel. The board may request the commissioner to appoint duly authorized representatives to conduct investigations and other activities incidental to the functions of the license board. Such appointees shall be non-voting members of the committee to which they are appointed, and may include personnel who are not department employees who shall serve without compensation. In addition the commissioner may designate such employees of the department as the commissioner deems necessary to the service and support of the license board.]

ARTICLE 418
GENERAL CONTRACTOR REGISTRATION

§28-418.1 Requirement of registration. [On and after November 1, 2008, it] It shall be unlawful for a person to conduct business as a general contractor unless such person holds a general contractor registration in accordance with the provisions of this article.

§28-418.1.1 Expiration of registration. A general contractor registration shall expire on the third anniversary of such registration or such other date as determined by the commissioner by rule so as to distribute the expiration dates of the registrations evenly over the course of a year.

§28-418.2 Unlawful use of general contractor title. [On and after November 1, 2008, it] It shall be unlawful to use or cause to be used the title registered general contractor or any other title in a manner as to convey the impression that an individual, corporation, partnership or other business entity, or any person it employs, is a registered general contractor, unless such individual, corporation, partnership or other business entity is registered in accordance with the provisions of this article.

§28-418.3 Application requirements.  An application for a general contractor registration or renewal shall be made in writing to the commissioner on a form provided by the department and shall be accompanied by following:

1.	If the applicant is an individual: the applicant’s full name, residence address, business address and business telephone number;

2.	If the applicant is a corporation:

2.1.	The corporate name, address and telephone number of the applicant’s principal office or place of business;

2.2.	The date and state of incorporation;

2.3.	The name, residence address and residence telephone number of all corporate officers and registered agents and any person owning an interest of ten percent or more in the corporation;

2.4.	Proof that the corporation is in good standing under the laws of the state of New York;

3.	If the applicant is a partnership:

3.1.	The name, address and telephone number of the applicant’s principal office or place of business;

3.2.	The name, residence address and residence telephone number of all partners;

4.	The registration fee;

5.	A verified statement that the applicant is financially solvent;

6.	The name and address of the principal location from which the applicant has engaged in the business of general contracting at any time within the last five (5) years;

7.	If the applicant is not a sole proprietor, proof that the applicant is authorized to do business in the state of New York;

8.	Proof of insurance as required by section 28-401.9;

9.	The name and address of the officer, principal or director of the applicant who is primarily responsible for the registrant’s compliance with the requirements of this code or any rule adopted [there under] thereunder;

10.	Any other information that the commissioner may require.

§28-418.3.1 Financial solvency. For the purposes of this article, financial solvency shall mean that the applicant’s operating capital shall exceed twenty-five thousand dollars.

§28-418.4 Warranties. A warranty shall be provided to the buyer of a new one-, two- or three-family structure that accords with the provisions of article thirty-six-B of the New York state general business law, including the following:

1.	One (1) year from and after the warranty date the home will be free from defects due to a failure to have been constructed in a skillful manner;

2.	Two (2) years from and after the warranty date the plumbing, electrical, heating, cooling and ventilation systems of the home will be free from defects due to a failure by the builder to have installed such systems in a skillful manner; and

3.	Six (6) years from and after the warranty date the home will be free from material defects, including, but not limited to, any construction that is not in compliance with the building code or the zoning resolution of the city of New York.

§28-418.4.1 Modification prohibited. Except as otherwise provided in section seven hundred seventy-seven-b of such article thirty-six-B, no such warranty shall be modified or excluded in any way.

§28-418.5 Duties and responsibilities. The general contractor shall comply with sections 28-418.5.1 through 28-418.5.3.

§28-418.5.1 Subcontractor information. The general contractor shall be responsible for providing information to the department about his or her subcontractors and the particular work they perform on jobs for which the department has issued permits to the general contractor. Such information shall be provided in a format and at the times specified in the rules of the department.

§28-418.5.2 Technical reports. The general contractor shall maintain at the work site such technical reports as specified in the rules of the department and shall make such reports available to department personnel on request.

§28-418.5.3 Notice of pending disciplinary actions. The general contractor shall notify all of its suppliers of any pending suspension or revocation actions against such general contractor and shall provide an affidavit to the department stating that this notification has been made.

ARTICLE 419
SEIZURE AND FORFEITURE

§28-419.1 General. [On and after November 1, 2008] The vehicles and tools used in connection with unlicensed or unregistered activity at the work site of a new residential structure containing no more than three dwelling units shall be subject to seizure and forfeiture.

§28-419.2 Definitions. For purposes of this article, the following terms shall have the following meanings.

1.	The term “owner” as applied to vehicles shall mean an owner as defined in section one hundred twenty-eight and in subdivision three of section three hundred eighty-eight of the vehicle and traffic law.

2.	The term “security interest” as applied to vehicles shall mean a security interest as defined in subdivision k of section two thousand one hundred one of the vehicle and traffic law.

3.	The term “unlicensed activity” shall mean the conduct of any activity at a  work site for the construction of a residential structure containing no more than three dwelling units without a license for which a license is required under any law, rule or regulation enforced by the commissioner of buildings, and the term “unregistered activity” shall mean the conduct of any activity at a work site for the construction of a residential structure containing no more than three dwelling units without a registration for which a registration is required under any law or regulation enforced by the commissioner of buildings.

§28-419.3 Seizure procedure. The following provisions shall govern seizure of vehicles and tools pursuant to this article.

§28-419.3.1 Seizure. Any police officer or authorized officer or authorized employee of the department may seize any vehicle and any tools contained therein that such police officer or authorized officer or authorized employee has reasonable cause to believe is being used in connection with unlicensed or unregistered activity, upon service on the owner or operator of the vehicle of a notice of violation for engaging in such activity. Any vehicle and tools seized pursuant to this section shall be delivered into the custody of the department or other appropriate agency.

§28-419.3.2 Written demand. The owner or operator of the vehicle and/or tools may make a written demand for a hearing for the return of the seized property. Notice of the right to a hearing shall be provided to the operator at the time of seizure of the vehicle and/or tools, and a copy of such notice shall be sent by mail to the registered and/or title owner of the vehicle, if other than the operator, and to the owner of the tools if other than the owner or operator of the vehicle and if reasonably ascertainable, within five business days of the seizure. The department shall schedule the hearing at the office of administrative trials and hearings (OATH) or its successor agency, as applicable, for a date within ten business days after receipt of the demand and shall notify the operator and the owner(s) of the opportunity to participate in the hearing and the date thereof.

§28-419.3.3 Claimant. A claimant seeking release of the vehicle and tools at the hearing may be either the person from whom the vehicle and tools were seized, if that person was in lawful possession of the vehicle and tools, or the owner if different from such person.

§28-419.3.4 Determination. The OATH judge shall issue a determination within five business days after the conclusion of the hearing.

§28-419.3.5 Return pending hearing. The department shall establish a procedure whereby an owner or operator who wishes to have the vehicle and/or tools returned pending the hearing shall post a bond in an amount determined by the department, but in no event less than an amount sufficient to cover any applicable removal and storage fees as well as fines and penalties.

§28-419.3.6 Return without hearing. The department shall establish a procedure whereby an owner or operator may request the return of the vehicle and/or tools without a hearing if such owner or operator:

1.	Establishes that the vehicle and/or tools were seized in error, or

2.	Immediately applies for licensure or registration pursuant to the applicable provisions of this code and pays an amount not to exceed removal and storage fees and any fines or penalties that could have been imposed under the provisions of this code.

Where the owner or operator establishes that the vehicle and/or tools were seized in error, the department shall expeditiously return such vehicle and/or tools.

§28-419.4 Abandoned property. Any vehicle and/or tools for which a written demand for return of the vehicle and/or tools or for a hearing pursuant to section 28-419.3.2 has not been made within thirty days of service of the notice of violation on the operator of the vehicle and/or tools or within thirty days of service of the notice of violation on the owner of the vehicle and/or tools if the owner is not the operator of the vehicle and/or tools shall be deemed abandoned and shall be disposed of by the department pursuant to applicable law.

§28-419.5 Combined hearings. The department may choose to have the underlying violation adjudicated before the office of administrative trials and hearings in accordance with sections 28-419.5.1 through 28-419.5.3.

§28-419.5.1 Combined hearing and determination. Upon notice to the respondent, the department may choose to have the violation underlying the seizure returnable to and heard at OATH and may combine the hearing on the underlying violation with the hearing for the return of the seized property. At such combined hearing, the OATH judge shall make a determination as to both and may impose any penalty that could be imposed in a proceeding before the environmental control board for the underlying violation. The OATH judge shall issue a determination within five business days after the conclusion of the hearing.

§28-419.5.2 Release following finding of no violation. If the OATH judge finds that the vehicle and/or tools were not used in connection with unlicensed or unregistered activity, the department shall promptly release such vehicle and/or tools.

§28-419.5.3 Release following finding of violation. If the OATH judge finds that the vehicle and/or tools were used in connection with unlicensed or unregistered activity, the department may release such vehicle and/or tools upon payment of all applicable fines and civil penalties and all reasonable costs of removal and storage, or may commence a forfeiture action within twenty business days after the date of the judge’s determination.

§28-419.6 Separate hearings. In the event that the adjudication of the violation underlying the seizure is not held at OATH, and a determination is made that the vehicle and tools were not used in connection with unlicensed or unregistered activity, the department shall promptly release such vehicle and/or tools.

§28-419.7 Forfeiture procedure. The following provisions shall govern forfeiture of vehicles and tools pursuant to this article.

§28-419.7.1 Commencement of forfeiture. A forfeiture action pursuant to this article shall be commenced by the filing of a summons with a notice or a summons and complaint in accordance with the civil practice law and rules. Such summons with notice or a summons and complaint shall be served in accordance with the civil practice law and rules on the vehicle operator, the owner of the tools, if different from the vehicle operator, and owner of the vehicle, and on all owners of the subject vehicle listed in the records maintained by the department of motor vehicles, or for vehicles not registered in the state of New York, in the records maintained by the state of registration. Except as otherwise provided in this article, a vehicle and/or tools that are the subject of such action shall remain in the custody of the department or other appropriate agency pending the final determination of the forfeiture action.

§28-419.7.2 Notice of forfeiture. Notice of the institution of the forfeiture action shall be given by certified mail to all persons holding a security interest in such vehicle or tools, if known, if such security interest in the vehicle has been filed with the department of motor vehicles pursuant to the provisions of title ten of the vehicle and traffic law, at the address set forth in the records of such department, or, for vehicles not registered in the state of New York, all persons holding a security interest in such vehicle if such security interest has been filed with the state of registration and which persons are made known by such state to the department, at the address provided by such state of registration.

§28-419.7.3 Security interest. Any person with a security interest in such vehicle or tools who receives notice of the institution of the forfeiture action who claims an interest in such vehicle or tools subject to forfeiture may assert a claim in such action for satisfaction of such person’s security interest in such vehicle or tools.

§28-419.7.4 Forfeiture subject to security interest. Forfeiture shall be made subject to the interest of a person who claims an interest in the vehicle or tools, where such person establishes that:

1.	The use of the vehicle or tools for the conduct that was the basis for the seizure of the vehicle and tools occurred without the knowledge of such person, or if such person had knowledge of such use, that such person did not consent to such use by doing all that could reasonably have been done to prevent such use, and that such person did not knowingly obtain such interest in the vehicle or tools in order to avoid the forfeiture of such vehicle or tools, or

2.	The conduct that was the basis for such seizure was committed by any person other than such person claiming an interest in the vehicle or tools, while such property was unlawfully in the possession of a person who acquired possession thereof in violation of the criminal laws of the United States or any state.

§28-419.7.5 Disposition. The department or agency having custody of the vehicle and tools, after judicial determination of forfeiture, shall, at its discretion, either (i) retain such vehicle and tools for the official use of the city; or (ii) by public notice of at least five days, sell such forfeited vehicle and tools at public sale. The net proceeds of any such sale shall be paid into the general fund of the city.

§28-419.7.6 Amount of award. In any forfeiture action commenced pursuant to this article, where the court awards a sum of money to one or more persons in satisfaction of such person’s interest in the forfeited vehicle and tools, the total amount awarded to satisfy such interest or interests shall not exceed the amount of the net proceeds of the sale of the forfeited vehicle and tools after deduction of the lawful expenses incurred by the city, including reasonable costs of removal and storage of the vehicle and tools between the time of seizure and the date of sale.

ARTICLE 420
REQUIREMENT OF SAFETY REGISTRATION NUMBER

§28-420.1 Requirement of application for safety registration number. [On and after October 1, 2009, no] No safety registration recipient shall conduct business for the purposes that would qualify the person as a safety registration recipient unless such person has received the required safety registration number from the department.

§28-420.2 Application requirements. An application for a safety registration number shall be made in writing to the commissioner on a form provided by the department and shall be accompanied by the following:

1.	If the applicant is an individual: the applicant’s full name, residence address, business address, and business telephone number, and an email address for the receipt of notifications;

2.	If the applicant is a corporation:

2.1.	The corporate name, address, telephone number and email address of the applicant’s principal office or place of business for the receipt of notifications;

2.2.	The date and state of incorporation;

2.3.	Proof that the corporation is in good standing under the laws of the state of New York;

3.	If the applicant is a partnership:

3.1.	The name, address, telephone number and email address of the applicant’s principal office or place of business for the receipt of notifications;

3.2.	The name and telephone number of all partners;

4.	The name, telephone number and e-mail address of all corporate officers and registered agents and any person owning or controlling an interest of ten percent or more in the applicant’s business;

5.	The name, address, and telephone number of any entity in which the applicant is an employee, participates in the management of, or in which the applicant has a controlling interest and which files for permits with the department [.];

6.	The name and address of the principal location from which the applicant has engaged in the business that would qualify it as a safety registration recipient at any time within the last five (5) years;

7.	If the applicant is not a sole proprietor, proof that the applicant is authorized to do business in the state of New York;

8.	Proof of insurance as required by Title 28 of this code and the rules of the department;

9.	The name, address and e-mail address of the officer, principal or director of the applicant who is designated to receive official notices from the department;

10.	The name, address and telephone number and e-mail address of the officer(s), principal(s) or director(s) of the applicant who should be contacted in the event of an emergency; and

11.	The commissioner shall waive the requirements of items one through seven of section 28-420.2 for any applicant who has submitted a Vendex questionnaire to the Mayor’s Office of Contract Services within the previous three (3) years provided that the questionnaire contains the information required by this article and who provides a copy of the Vendex questionnaire to the department with such proof of submission as the department may require.

§28-420.3 Duties and [Responsibilities] responsibilities. The recipient of a safety registration number shall comply with the following requirements:

1.	Subcontractor information. The recipient of a safety registration number shall maintain at each work site the names, business addresses and contact information of the superintendent(s) of the subcontractors who hold subcontracts with the prime contractor, as well as the particular work they perform, and shall make such information available to department personnel upon request;

2.	Special inspection reports. The recipient of a safety registration number shall maintain at the work site such special inspection reports as specified in the building code and shall make such reports available to department personnel on request.

§28-420.4 Submission of plan to reduce rate of immediately hazardous violations. The commissioner may require any safety registration recipient to provide the department with a plan to improve its rate of immediately hazardous violations. The plan must be approved by the [Department] department and may include such measures as employment of a safety compliance officer to ensure compliance with the approved plan.

§28-420.5 Submission of a report to the city council. Within six months of the date by which all safety registration recipients shall have been required by section 420.1 of this article to have a safety registration number, the commissioner shall, after consultation with representatives of affected industries, including but not limited to representatives and employers of building and construction industry labor organizations and real estate owners, submit to the mayor and the city council recommendations for the establishment of objective criteria on which the commissioner may base a determination to commence a proceeding to suspend, revoke, or refuse to renew a safety registration number as well as the data used in the analysis and formulation of such recommendations. Within three months of the submission, the council shall review and may amend this provision to incorporate standards for the revocation and non-renewal of a safety registration number.

§28-420.6 Expiration of safety registration number. A safety registration number shall expire on the third anniversary that such safety registration number was issued or such other date as determined by the commissioner by rule so as to evenly distribute the expiration dates of the safety registration numbers.

§28-420.7 Unlawful use of safety registration number. [On and after October 1, 2009, it] It shall be unlawful to represent or cause to be represented that a person who would qualify as a safety registration recipient has been issued a safety registration number by the department or to otherwise convey the impression that an individual, corporation, partnership or other business entity, or any person it employs, conducts business for the purposes that would qualify it as a safety registration recipient that has been issued a safety registration number, unless such individual, corporation, partnership or other business entity has received a safety registration number from the department in accordance with the provisions of this article.

ARTICLE 421
ELEVATOR AGENCY DIRECTOR LICENSE

§28-421.1 Elevator agency director license required. It shall be unlawful to perform elevator work as defined by this chapter or perform and/or witness inspections and tests or enter into contracts pursuant to article 304 of chapter 3 of this code unless licensed pursuant to this article. Each elevator agency shall designate one director in responsible charge who shall be licensed pursuant to this article. The designated director in responsible charge shall be in the direct employ of the agency and shall supervise all the operations of the agency. All elevator work shall be performed by individuals who are under the direct and continuing supervision of the elevator agency director as defined in section 28-401.3 of this chapter.  All elevator work performed by such agency pursuant to article 304 of chapter 3 of this code shall be performed by or under the direct and continuing supervision of the designated director in responsible charge.

§28-421.1.1 Additional directors. In addition to the designated director in responsible charge, the agency may have other individuals in its employ who may be issued elevator agency director licenses pursuant to this article.

§28-421.2 Qualifications. All applicants for an elevator agency director license shall submit satisfactory proof establishing that the applicant has satisfactorily completed, within two (2) years prior to the date of application, a course that is at least thirty (30) hours in length and approved by the United States  department  of  labor and  the occupational safety and health administration in general industry training; and also satisfies one of the following:

1.	Has at least ten (10) years of practical experience in the supervision of the assembly, installation, maintenance, repair, design or inspection of elevators within the fifteen (15) years prior to application; or

2.	Is an engineer or architect and has at least five (5) years of experience in the supervision of the assembly, installation, maintenance, repair, review and approval of design documents or inspection of elevators within the seven (7) years prior to application.

§28-421.3 Restriction. Each elevator agency director shall supervise and perform elevator work or inspections and tests pursuant to article 304 of chapter 3 of this code for only one (1) elevator agency, and shall not inspect and/or test elevators or perform elevator work on related devices as an inspector, director or elevator agency helper for any other elevator agency.

§28-421.4 Place of business. Every licensed elevator agency shall have a place of business within the city in conformance with department rules and regulations. A licensed private elevator inspection agency director shall be allowed to associate his or her license with only one other private elevator inspection agency. Such businesses shall be located at the same place of business.

ARTICLE 422
ELEVATOR AGENCY INSPECTOR LICENSE

§28-422.1 Elevator agency inspector license required. It shall be unlawful to witness and/or perform inspections and tests on behalf of an elevator agency pursuant to article 304 of chapter 3 of this code unless licensed pursuant to this article. Licensed inspectors shall perform such work under the direct and continuing supervision of a designated director in responsible charge licensed pursuant to article 421 of this chapter.

§28-422.2 Qualifications. All applicants for an elevator agency inspector license shall submit satisfactory proof establishing that the applicant has satisfactorily completed, within two (2) years  prior  to  the date of application, a course that is at least ten (10) hours in length and approved by the United States  department  of  labor and  the occupational safety and health administration in general industry standards; and also satisfies the following:

1.	Has at least seven (7) years of practical experience in the inspection of elevators, or as an elevator mechanic within the ten (10) years prior to application.

§28-422.3 Restriction. Each elevator agency shall perform work pursuant to article 304 of chapter 3 of this code for only one elevator agency, and shall not witness and/or perform inspections and/or test elevators or related devices as an inspector, technician or director for any other elevator agency.

ARTICLE 423
QUALIFICATION FOR GAS WORK

§28-423.1 Qualification required. For the purposes of this article, “gas work” means work covered by section 101.2 of the New York city fuel gas code, where such work is required by this code to be performed under the direct and continuing supervision of a licensed master plumber, provided that the term “gas work” shall not include periodic inspections required pursuant to article 318 of chapter 3 of title 28 of the administrative code. On and after January 1, 2020, it shall be unlawful to perform gas work unless such work is performed by:

1.	A licensed master plumber; or

2.	A person working under the direct and continuing supervision of a licensed master plumber if such person:

2.1.	Holds a gas work qualification pursuant to this article; or

2.2.	Holds a limited gas work qualification pursuant to this article and is performing such work under the [personal and immediate] direct supervision of (i) a person who holds a gas work qualification pursuant to this article or (ii) a licensed master plumber.

Exception: The provisions of this article shall not apply to gas work performed, serviced and maintained by utility corporations and subject to the jurisdiction of the New York state public service commission.

§28-423.2 Applications for gas work qualification. [The commissioner shall issue gas work qualifications in accordance with sections 28-423.2.1 and 28-423.2.2.]

[§28-423.2.1 Applications for gas work qualification submitted before January 1, 2019. The commissioner shall issue a gas work qualification to a person who before January 1, 2019, submits satisfactory proof establishing that such person is a registered journeyman plumber pursuant to article 409 of this chapter.]

[§28-423.2.2 Applications for gas work qualification submitted on or after January 1, 2019.] The commissioner shall issue a gas work qualification to a person who [on or after January 1, 2019,] submits satisfactory proof establishing that such person:

1.	Has demonstrated an understanding of and proficiency and competency with gas work, including (i) a working familiarity with the fuel gas code and the ability to apply the requirements of such code correctly, (ii) the application of skills relating to gas work on the job site, (iii) a working knowledge of the tools for gas work and the ability to utilize such tools properly and (iv) an ability to draft simple diagrams and interpret from drawings for the purpose of performing gas work, by satisfying a requirement that the commissioner shall establish by rule; and

2.	Satisfies one or more of the following:

2.1.	Such person is a registered journeyman plumber pursuant to article 409 of this chapter;

2.2.	Such person successfully completed an apprenticeship in plumbing through a program approved by the New York state department of labor and has at least one (1) year of full-time experience performing or supervising plumbing work under the direct and continuing supervision of a licensed master plumber; or

2.3.	Such person has at least five (5) years of full-time experience performing or supervising plumbing work under the direct and continuing supervision of a licensed master plumber, provided that at least one (1) year of such experience occurred in the city.

§[28-423.2.3] 28-423.2.1 Concurrent applications. The commissioner shall establish a procedure for concurrently applying for a journeyman plumber registration pursuant to article 409 of this chapter and a gas work qualification pursuant to this section. No application fee shall be charged to an applicant for a gas work qualification if such applicant (i) is, at the time such application is filed, a registered journeyman plumber pursuant to such article or (ii) is applying concurrently for a journeyman plumber registration pursuant to such article and a gas work qualification.

§28-423.3 Applications for limited gas work qualification. [The commissioner shall issue limited gas work qualifications in accordance with sections 28-423.3.1 and 28-423.3.2.]

[§28-423.3.1 Applications for limited gas work qualification submitted before January 1, 2019. The commissioner shall issue a limited gas work qualification to a person who before January 1, 2019, submits satisfactory proof that such person has at least six months of full-time experience performing plumbing work under the direct and continuing supervision of a licensed master plumber.]

[§28-423.3.2 Applications for limited gas work qualification submitted on or after January 1, 2019.] The commissioner shall issue a limited gas qualification to a person who [on or after January 1, 2019] submits satisfactory proof establishing that such person:

1.	Has at least six months of full-time experience performing plumbing work under the direct and continuing supervision of a licensed master plumber; and

2.	Satisfies one or more of the following:

2.1.	Such person has successfully completed a training program that (i) relates to gas work, (ii) is at least 16 hours and (iii) is approved by the commissioner;

2.2.	Such person is an apprentice in plumbing registered in an apprenticeship program approved by the New York state department of labor; or

2.3.	Such person satisfies such other requirement for demonstrating competence with gas work as the commissioner may establish by rule.

§28-423.4 Expiration. The gas work qualification shall have no expiration and need not be renewed or reissued. The limited gas work qualification shall expire five (5) years after issuance and may not be renewed.

ARTICLE 424
LIFT DIRECTOR REGISTRATION

§28-424.1 Lift director required. It shall be unlawful for a crane or derrick that requires or possesses a certificate of on-site inspection, or which, in accordance with rules promulgated by the commissioner, is subject to supervision by a licensed master rigger in lieu of a certificate of on-site inspection, to perform any of the following tasks unless a lift director is present at the site during all times when:

1.	The crane or derrick is picking a load;

2.	The crane is traveling at the site, including but not limited to being moved onto or off of cribbing or up or down a ramp;

3.	The crane or derrick is being placed into a parked condition or otherwise being taken out of service;

4.	The crane’s or derrick’s boom/jib is being laid down or jackknifed;

5.	The crane’s or derrick’s boom/jib is being raised from a laid down or jackknifed position; or

6.	Other special protective measures for wind are being installed or removed.

[Exception:] Exceptions: The requirement for a lift director does not apply to [the]:

1.	The assembly or disassembly of a crane or derrick, nor to the use of an assist crane or derrick during assembly/disassembly, provided an assembly/disassembly director is supervising the assembly/disassembly operation in accordance with rules promulgated by the commissioner.

2.	Dedicated pile drivers.

§28-424.2 Registration required. Eighteen months after the department has established the requirements for the department-approved training course for lift directors as set forth in item 1 of section 28-424.3, it shall be unlawful for any person to act as a lift director or to perform the duties of a lift director unless such person is registered as a lift director pursuant to this article, or is licensed as a master rigger pursuant to article 404 of this chapter, or is a master rigging foreman designated in accordance with rules promulgated by the commissioner and acting as a lift director under the direct and continuing supervision of the licensed master rigger.

§28-424.3 Qualifications. Applicants for a lift director registration shall submit satisfactory proof establishing that the applicant:

1.	Has successfully completed a department-approved training course for lift directing that is at least 32 hours in length. Such lift directing training course shall cover topics relating to mobile cranes, tower cranes, and derricks, including but not limited to roles and responsibilities of site personnel, operational planning, weather warnings, conducting on-site meetings, and log and reporting requirements. Successful completion of a lift directing training course shall be based upon passage of a written exam, and evidenced by the issuance of a certificate card that is in accordance with the provisions of item 2.5 of section 3316.9.2 of the New York city building code; and

2.	Meets one of the following:

2.1.	Possesses a valid certification as a lift director. The certification must be acceptable to the commissioner and be issued by a lift director certification program that is accredited by the National Commission for Certifying Agencies (NCCA) or the American National Standards Institute (ANSI);

2.2.	Has at least two (2) years’ experience, within the three (3) years prior to application, supervising rigging operations in New York city in accordance with section 3316.9.1 of the New York city building code;

2.3.	Has been licensed as a New York city class A, class B, or class C hoisting machine operator for at least three (3) years prior to application; or

[2.4.	Is a master rigging foreman designated in accordance with rules promulgated by the commissioner; or]

[2.5.] 2.4.	Such applicant has at least one (1) year of experience as a lift director in New York city in accordance with rules promulgated by the commissioner, prior to the date that registration as a lift director is required pursuant to section 28-424.2.

ARTICLE 425
ELEVATOR AGENCY TECHNICIAN LICENSE

§28-425.1 Elevator agency technician license required. It shall be unlawful to perform elevator work as defined in this chapter, unless that work is performed by or under the direction of an elevator agency technician and under the supervision of a designated director of an elevator agency licensed pursuant to article 421 of this chapter.

§28-425.2 Restricted elevator agency technician license. A restricted class of lift mechanic license shall be known as "accessibility technician". Such class of license shall be restricted to performing work involving platform lifts including those installed in private residences which are covered by the provisions of ASME [(American society of mechanical engineers) codes and standards] A18.1 [-2005]. An applicant for such restricted license [shall complete an application approved by the board and] shall have at least (3) three years of verified work experience in constructing, maintaining and repairing those lifts covered by ASME A18.1  [-2005] and shall provide to the commissioner a certificate of completion of an accessibility training program for lifts under the scope of A18.1 [-2005] such as the certified accessibility training provided by the national association of elevator contractors, or an equivalent program as [deemed] determined by the department.

§28-425.3 Qualifications. An applicant for an elevator agency technician license or a restricted elevator agency technician license must possess a valid elevator mechanic’s license issued by the New York state department of labor in accordance with the provisions of article thirty-three of the New York state labor law.  Such state license must remain valid during the term of the city license. The agency may, by rule, establish qualifications for elevator agency technicians, including, but not limited to, acceptable proof that an applicant has worked on elevator construction, maintenance or repair with direct and [immediate] continuing supervision in this state for a specified period of time prior to the effective date of this article; provided, however, that the provisions of this section and any rules adopted pursuant thereto shall not be inconsistent with the requirements for elevator mechanics contained in article thirty-three of the New York state labor law and nothing herein shall prevent the enactment by local law, ordinance, or rule of additional requirements.

§28-425.4 Exemptions. No elevator agency technician license shall be required for the outfitting, removal, refinishing, or replacement of interior finishes, including wall panels, drop ceilings, handrails and flooring, removal or replacement of interior lighting, recladding of doors, transoms and front return panels, finishing or ornamental work on car operating panels.

§28-425.5 Term of license. The term of an elevator agency technician license and a restricted elevator agency technician license shall be two (2) years.

ARTICLE 426
ELEVATOR AGENCY HELPER

§28-426.1 Qualifications. The agency may, by rule, establish qualifications for elevator agency helpers.

ARTICLE 427
PERMITS

§28-427.1 Applications and permits. All applications/permits issued to elevator contractors shall appear on the department of buildings website within forty-eight (48) hours of issuance. The information required to be published must include, at a minimum, the date of issuance, the work covered by the permit, the elevator contractor or contractors involved and location and type of work to be performed.  The department shall maintain and publish a registry of all licensed elevator agency helpers, technicians, and inspectors, which shall list and identify, all licensed elevator agency helpers, technicians, and inspectors, doing business in the city of New York. The department shall make the registry available on its website.

§28-427.2 Licensing and permitting exemptions. Whenever an emergency exists in this state due to a disaster or act of god, which imperils the health, safety or welfare of an individual or  individuals  and  placing such individual or individuals in imminent danger of injury or death and the number of persons in the state holding licenses granted by the New York state elevator safety and standards advisory board established by section nine hundred fifty-six of article 33 of the New York state labor law is insufficient to cope with such emergency, any person certified by a licensed elevator contractor to have an acceptable combination of  documented  experience and education to perform elevator work without direct and immediate supervision shall seek an  emergency  elevator  mechanic’s license from the commissioner within five (5) business days after commencing work  requiring a license. The commissioner shall issue emergency elevator mechanic’s licenses to address the emergency that exists.  The licensed elevator contractor shall furnish proof of competency as the commissioner may require. Each such license  shall recite that it is valid for a period of fifteen (15) days from the date thereof and for such particular elevators or geographical  areas as the commissioner may designate to address the emergency and otherwise shall entitle the licensee to the rights and privileges of an elevator mechanic’s license issued in this article. The commissioner shall renew an emergency elevator mechanic’s license during the existence of an emergency as needed.  No fee shall be charged for any emergency elevator mechanic’s license or renewal thereof.

§28-427.3 License renewal. The renewal of all licenses granted under the provisions of this section shall be conditioned upon the submission of a certificate of completion of a course designed to ensure the continuing education of licensees on new and existing national, state, and local conveyances codes and standards and on technology and technical education and workplace safety. Such course shall consist of not less than eight (8) hours annually and shall be completed preceding any such license renewal.  The commissioner shall establish requirements for continuing education and training programs, and shall approve such programs, as well as maintain a list of approved programs, which shall be made available to license applicants, permit applicants, renewal applicants and other interested parties upon request. The commissioner shall promulgate rules and regulations setting forth the criteria for approval of such programs, the procedures to be followed in applying for such approval, and other rules and regulations as the commissioner deems necessary and proper to effectuate the purposes of this section. The renewal of all licenses granted under the provisions of this section shall be conditioned upon the submission of a certificate of completion of a course designed to ensure the continuing education of licensees on new and existing regulations of the department. Such course shall consist of not less than eight (8) hours of instruction that shall be attended and completed annually prior to any such license renewal. The courses shall be taught through continuing education providers that may include, but shall not be limited to, association seminars, and labor training programs or programs that deliver an approved apprenticeship and are registered with the department or the New York state apprenticeship training council.  The commissioner shall approve the continuing education providers.

§28-427.4 Renewal fees. The commissioner shall assess a fee for each training program completion certificate and for each refresher training program completion certificate, provided, however, that in no event shall the cost of such certificates be assessed by the sponsor of such training program against the participants.

§28-427.5 Recordkeeping.  All instructors shall be exempt from the requirements of the preceding section with regard to their application for license renewal provided that such applicant was qualified as an instructor at any time during the one (1) year immediately preceding the scheduled date for such renewal. Approved training providers shall keep uniform records, for a period of six (6) years, of attendance of licensees following a format approved by the commissioner and such records shall be available for inspection by the commissioner at his or her request. Approved training providers shall be responsible for the security of all attendance records and certificates of completion; provided, however, that falsifying or knowingly allowing another to falsify such attendance records or certificates of completion shall constitute grounds for suspension or revocation of the approval required under this section.

ARTICLE 428
CONSTRUCTION SUPERINTENDENT LICENSE

§28-428.1 License required. It shall be unlawful to perform the duties and responsibilities of a construction superintendent, as specified in chapter 33 of the New York city building code, unless such work is performed by a person licensed as a construction superintendent under the provisions of this article and department rules.

§28-428.2 Qualifications. All applicants for a construction superintendent license shall submit satisfactory proof establishing that the applicant:

1.	Has, within one (1) year prior to application, satisfactorily completed a course that is at least forty-hours (40) in length and approved by the department in construction and demolition site safety;

2.	Possesses a valid Site Safety Training (SST) Supervisor Card; and

3.	Either:

3.1.	Has at least three (3) years of experience, within the five (5) years prior to application, serving as a full-time project supervisor with on-site responsibility over the construction or demolition of buildings in the city of New York; or

3.2.	Has at least five (5) years of experience, within the eight (8) years prior to application, serving as a full-time project supervisor with on-site responsibility over the construction or demolition of buildings in the United States.

§28-428.3 Previous registrants.  Individuals who, as of the effective date of this section, held a valid registration as a construction superintendent in accordance with rules promulgated by the commissioner shall be deemed to hold a license as a construction superintendent.

§28-428.4 Fitness to perform work. As a condition of license renewal, a licensed construction superintendent shall provide evidence satisfactory to the department that such licensee is fit to perform the work.

§ 5.  Item 1 of section 28-502.4 of the administrative code of the city of New York, as added by local law number 33 for the year 2007, is amended to read as follows:

1.	The list shall include all signs, sign structures and sign locations located (i) within a distance of 900 linear feet (274 m) from and within view of an arterial highway; or (ii) within a distance of 200 linear feet (60 960 mm) from and within view of a public park with an area of 1/2 acre [(5000 m)] (2023 m2) or more.

§ 6.  Section 28-504.1 of the administrative code of the city of New York, as amended by local law number 105 for the year 2016, is amended to read as follows:

§28-504.1 Bicycle access to certain office buildings. This section shall apply to buildings that satisfy each of the following conditions: (i)  the main occupancy of such building is offices that are classified as occupancy group B, (ii) such building was in existence on December 11, 2009, or a permit for such building has been issued on or before such date but such building has not yet been completed, (iii) such building has a freight elevator that either complies with [ASME 17.1] ASME A17.1 with regard to the carrying of passengers on freight elevators, as referenced in chapter 35 of the New York city building code, or is operated by a freight elevator operator, and (iv) is not subject to the bicycle parking provisions of sections 25-80, 36-70 and 44-60 of the zoning resolution. It shall be presumed that if a freight elevator is available for carrying freight, it is available for carrying bicycles.

§ 7.  Section 28-504.1.1 of the administrative code of the city of New York, as renumbered and amended by local law number 105 for the year 2016, is amended to read as follows:

§28-504.1.1 Request for bicycle access. The tenant or subtenant of a building to which this section is applicable may request in writing, on a form provided by the department of transportation, that the owner of such building complete a bicycle access plan in accordance with section [28-501.1.2] 28-504.1.2 and provide bicycle access in accordance with such plan. Such request shall include a certification by such tenant or subtenant that there is sufficient space within such tenant’s or subtenant’s premises to store the requested number of bicycles in a manner that does not violate the building or fire code or any other applicable law, rule or code, or which would impede ingress or egress to such premises or building. Such request shall be sent to such owner by certified mail, return receipt requested, and a copy of the request shall be filed with the department of transportation.

§ 8.  Section 28-504.1.2 of the administrative code of the city of New York, as renumbered and amended by local law number 105 for the year 2016, is amended to read as follows:

§28-504.1.2 Bicycle access plan. Bicycle access plans shall comply with sections 28-504.1.2.1 through [28-504.1.2.3] 28-504.1.2.4.

§ 9.  Items 1.2, 1.3 and 2 of section 28-504.1.2.2  of the administrative code of the city of New York, as renumbered and amended by local law number 105 for the year 2016, are amended to read as follows:

1.2.	Bicycles will be allowed to be transported to and from such elevator along each route that is used to transport freight to and from such elevator, to the extent practicable and where such routes do not present substantial safety risks; [and]

1.3.	No escort by building personnel will be required for a person transporting a bicycle to or from such elevator if no such escort is required when a person is transporting freight to or from such elevator; and

2.	Provisions allowing bicycles to be brought in or out of such building using one or more designated passenger elevators that the building owner may designate as temporary freight elevators at any time when no freight elevator satisfying the conditions of item [2.1] 1 is operational;

§ 10.  Section 28-504.6 of the administrative code of the city of New York, as added by local law number 106 for the year 2016, is amended to read as follows:

§28-504.6 Foldable bicycles on passenger elevators in residential buildings. In any building classified in occupancy group R, it shall be unlawful for an owner to bar a tenant or subtenant from transporting a foldable bicycle on a passenger elevator provided that such bicycle is fully folded. For purposes of this section, the term “foldable bicycle” means a bicycle designed to fold into a compact assembly not exceeding 20 inches (508 mm) by 36 inches (914 mm) by 32 inches (813 mm).

§ 11.  The definitions of “low income housing” and “owner” in section 28-505.2 of the administrative code of the city of New York, as added by local law number 1 for the year 2018, are amended to read as follows:

LOW INCOME HOUSING. The term “low income housing” has the same meaning as in section 27-2093.1 of the housing maintenance code [,].

OWNER. The term “owner” has the same meaning as in section 27-2004 of the housing maintenance code [,].

§ 12.  Section 28-505.6 of the administrative code of the city of New York, as added by local law number 1 for the year 2018, is amended to read as follows:

§28-505.6 Time period for approval or rejection of construction documents. The time period in which the commissioner is required to approve or reject an application for construction document approval or resubmission thereof pursuant to this code shall commence from the date that the commissioner receives the documents required pursuant to item 3 of section 28-505.4.

Part B (Chapter 6 of Title 28 - New York City Plumbing Code)

§ 1.  Item 8 of section 107.5 of the New York city plumbing code, as amended by local law number 14 for the year 2020, is amended to read as follows:

8.	In [special] flood hazard areas, construction documents shall comply with Appendix G of the New York City Building Code.

§ 2.  Section 107.9 of the New York city plumbing code, as renumbered by local law number 14 for the year 2020, is amended to read as follows:

107.9 Private stormwater or sewage disposal system. If a private stormwater or sewage disposal system is to be installed, a site and subsoil evaluation indicating that the site and subsoil conditions comply with the applicable laws and rules shall be submitted in accordance with the provisions of Section [1704.20.1] 1705.27 of the New York City Building Code.

§ 3.  Section 107.11 of the New York city plumbing code, as added by local law number 14 for the year 2020, is amended to read as follows:

107.11 Retention of construction and submittal documents. Refer to Section [28-104.11] 28-104.12 of the Administrative Code.

§ 4.  Section 201.3.1 of the New York city plumbing code, as added by local law number 14 for the year 2020, is amended by adding new definitions ENVIRONMENTAL CONTROL BOARD OR ECB and LIMITED ALTERATION APPLICATION, in alphabetical order, to read as follows:

ENVIRONMENTAL CONTROL BOARD OR ECB.

LIMITED ALTERATION APPLICATION.

§ 5.  Section 314.2.3 of the New York city plumbing code, as amended by local law number 14 for the year 2020, is amended to read as follows:

314.2.3 Auxiliary and secondary drain systems. In addition to the requirements of Section 314.2.1, where damage to any building components could occur as a result of overflow from the equipment primary condensate removal system, one of the following auxiliary protection methods shall be provided for each cooling coil or fuel-fired appliance that produces condensate:

[Exception: Fuel-fired] Exceptions:

1.	An auxiliary drain protection method shall not be required for fuel-fired appliances that automatically shut down operation in the event of a stoppage in the condensate drainage system.

2.	An auxiliary drain protection method shall not be required where a suitably sized and located floor drain is provided.

§ 6.  Section 1302.8.3 of the New York city plumbing code, as added by local law number 14 for the year 2020, is amended to read as follows:

1302.8.3 [Conyeance] Conveyance piping bypass valve. One full-size three-way diverter valve shall be installed on the conveyance piping system upstream and downstream of all treated storage tanks, as applicable, to divert treated on-site nonpotable reuse water to the sanitary sewer to allow system testing, commissioning and bypass conditions

§ 7.  Section 1501.2 of the New York city plumbing code, as added by local law number 14 for the year 2020, is amended to read as follows:

1501.2 Subsequent additions, modifications or deletions. Refer to the rules of the department for any subsequent additions, modifications or deletions that may have been made to [the referenced national] these standards [set forth herein] in accordance with [the exception contained in] Section 28-103.19 of the Administrative Code.

Part C (Chapter 7 of Title 28 - New York City Building Code)

§ 1.  Section 28-701.2 of the administrative code of the city of New York, as amended by local law number 141 for the year 2013, is amended to read as follows:

§28-701.2 Enactment of the New York city building code. The New York city building code based on the 2003 edition of the International Building Code published by the International Code Council, with changes that reflect the unique character of the city and amendments that bring it up to date with the [2009] 2015 edition of such International Building Code, is hereby adopted to read as follows:

§ 2. Chapter 1 of the New York city building code, as amended by local law number 141 for the year 2013, section 107.11 as amended by and section 107.11.3 as added by local law number 97 for the year 2017, section 110.3.7 as added by local law number 154 for the year 2017, and section 107.9.2 as amended by local law number 195 for the year 2018, is amended to read as follows:

CHAPTER 1
ADMINISTRATION

SECTION BC 101
GENERAL

101.1 Title. This code shall be known and may be cited as the “New York City Building Code,” “NYCBC” or “BC.” All section numbers in this code shall be deemed to be preceded by the designation “BC.”

101.2 Scope. The provisions of this code shall apply to the construction, alteration, movement, addition, replacement, repair, equipment, use and occupancy, location, maintenance, removal and demolition of every building or structure or any appurtenances connected or attached to such buildings or structures.

101.3 Intent. Refer to Chapter 1 of Title 28 of the Administrative Code.

101.4 Referenced codes. The other codes listed in Sections 101.4.1 through 101.4.6 and referenced elsewhere in this code shall be considered part of the requirements of this code to the prescribed extent of each such reference.

101.4.1 Electrical. The provisions of the New York City Electrical Code shall apply to the installation of electrical systems, including alterations, repairs, replacement, equipment, appliances, fixtures, fittings and appurtenances thereto.

101.4.2 Gas. The provisions of the New York City Fuel Gas Code shall apply to the installation of gas piping, gas appliances and related accessories as covered in this code. These requirements apply to gas piping systems extending to the inlet connections of appliances and the installation and operation of residential and commercial gas appliances and related accessories.

101.4.3 Mechanical. The provisions of the New York City Mechanical Code shall apply to the installation, alterations, repairs and replacement of mechanical systems, including equipment, appliances, fixtures, fittings and/or appurtenances, including ventilating, heating, cooling, air-conditioning and refrigeration systems, incinerators and other energy-related systems.

101.4.4 Plumbing.  The provisions of the New York City Plumbing Code shall apply to the alteration, repair and replacement of plumbing systems, including equipment, appliances, fixtures, fittings and appurtenances, and where connected to a water or sewage system and all aspects of a medical gas system.

101.4.5 Fire prevention. The provisions of the New York City Fire Code shall apply to:

- The manufacturing, storage, handling, use, sale and transportation of hazardous materials, except for the installation of storage tanks and auxiliary storage tanks for oil-burning equipment;

- The design, installation, operation and maintenance of devices, equipment and systems designed to prevent, mitigate, control and extinguish fire, explosions or other life safety hazards;

- Emergency preparedness and planning, including the orderly evacuation of occupants of a building, structure or premises in the event of fire, explosion, biological, chemical or hazardous material incident or release, natural disaster or other emergency, or the threat thereof;

- The prevention, mitigation and control of hazards to firefighters and emergency responders during emergency operations; and

- The operation and maintenance of any manual, automatic or other fire alarm or fire extinguishing device, equipment or system.

101.4.6 Energy. The provisions of the New York City Energy Conservation Code shall apply to all matters governing the design, construction and alteration of buildings for energy efficiency.

SECTION BC 102
APPLICABILITY

102.1 General. Where there is a conflict between a general requirement and a specific requirement, the specific requirement shall govern. Where, in any specific case, different sections of this code specify different materials, methods of construction or other requirements, the most restrictive shall govern.

102.2 Reserved.

102.3 Application of references. References to chapter or section numbers, or to provisions not specifically identified by number, shall be construed to refer to such chapter, section or provision of this code.

102.4 Referenced standards. The standards referenced in this code and in the rules of the department shall be considered part of the requirements of this code to the prescribed extent of each such reference. Where differences occur between provisions of this code and referenced standards, the provisions of this code shall apply. Refer to Article 103 of Chapter 1 of Title 28 of the Administrative Code for additional provisions relating to referenced standards.

102.4.1 Editions of referenced standards. References to standards in this code shall be to the editions of those standards provided for in Chapter 35 of this code, or as otherwise provided by rule.

102.5 Partial invalidity. In the event that any part or provision of this code is held to be illegal or void, this shall not have the effect of making void or illegal any of the other parts or provisions.

102.6 Existing structures. The legal occupancy of any structure lawfully in existence at the time of the adoption or a subsequent amendment of this code shall be permitted to continue without change, except as is otherwise specifically provided in this code or as is deemed necessary by the commissioner for the general safety and welfare of the occupants and the public. Refer to Chapter 1 of Title 28 of the Administrative Code for additional provisions relating to existing structures.

SECTION BC 103
DEPARTMENT OF BUILDINGS

103.1 General. Refer to the New York City Charter and Chapter 1 of Title 28 of the Administrative Code.

SECTION BC 104
DUTIES AND POWERS OF COMMISSIONER OF
BUILDINGS

104.1 General. The commissioner shall have the authority to render interpretations of this code, [and to] adopt rules, and establish policies and procedures in order to clarify and implement its provisions[]. Such interpretations, policies, procedures, and rules shall be in compliance with the intent and purpose of this code. See the New York City Charter and Chapter 1 of Title 28 of the Administrative Code for additional provisions relating to the authority of the Commissioner of Buildings.

SECTION BC 105
APPROVALS

105.1 Approvals. Refer to Chapter 1 of Title 28 of the Administrative Code.

SECTION BC [105] 106
PERMITS

[105.1] 106.1 General. Permits shall comply with this section, with Article 105 of Chapter 1 of Title 28 of the Administrative Code, and with requirements found elsewhere in this code.

[105.2] 106.2 Required. Any owner or authorized agent who intends to construct, add to, alter, repair, move, demolish, or change the occupancy of a building or structure, or to erect, install, add to, alter, repair, remove, convert or replace any gas, mechanical or plumbing system, the installation of which is regulated by this code, or to cause any such work to be done, shall first make application for construction document approval in accordance with Chapter 1 of Title 28 of the Administrative Code and this chapter and obtain the required permit.

[105.3] 106.3 Work exempt from permit. Exemptions from permit requirements of this code as authorized in Chapter 1 of Title 28 of the Administrative Code and the rules of the department shall not be deemed to grant authorization for any work to be done in any manner in violation of the provisions of this code or any other laws or rules.

[105.4] 106.4 Validity of permit. The issuance or granting of a permit shall not be construed to be a permit for, or an approval of, any violation of any of the provisions of this code or of any other law. Permits presuming to give authority to violate or cancel the provisions of this code or other law shall not be valid. The issuance of a permit based on construction documents and other data shall not prevent the commissioner from requiring the correction of errors in the construction documents and other data. The commissioner is also authorized to prevent occupancy or use of a structure where in violation of this code or of any other law.

[105.5] 106.5 Foundation and earthwork permits. In addition to the requirements of Chapter 1 of Title 28 of the Administrative Code and Chapter 33 of this code, applications for foundation and earthwork permits shall include:

- Notice to adjoining owners. Proof of notice to adjoining owners as required by Section 3304.3.2.

- Liens. Satisfactory evidence that the property is free from any lien for unpaid city taxes, assessments, water rates, bail bonds, or judgments obtained by the city, together with consent in writing of the mortgagee, if there is a mortgage upon the property, and the consent in writing of the surrogate’s court or supreme court, if the owner of the property is a minor or incompetent.

[105.5.1] 106.5.1 Notice to the department of commencement of foundation and earthwork. The foundation and earthwork permit shall be issued on the condition that the applicant will provide written notice to the department at least 24 but no more than 48 hours prior to the commencement of the foundation or earthwork as required by Section 3304.3.1.

[105.6] 106.6 Full demolition permits. In addition to the requirements of Chapter 1 of Title 28 of the Administrative Code and Chapter 33 of this code, applications for full demolition permits shall include:

- Utility certifications. Certifications by the respective utility companies or governmental agencies having jurisdiction that all gas, electric, water, steam and other service lines to the building have been disconnected as required by Section 3303.2.5.

- Notice to adjoining owners. Proof of notice to adjoining owners as required by Section 3306.3.2.

- Certification of rodent extermination. Certification in accordance with department rules that the building has been treated effectively for rodent extermination as required by Section 3306.9.13.

[105.6.1] 106.6.1 Notice to department of commencement of demolition work. The full demolition permit shall be issued on the condition that the applicant will provide written notice to the department at least 48 hours prior to the commencement of demolition work.

[105.7] 106.7 Sign permits. In addition to the requirements of Chapter 1 of Title 28 of the Administrative Code, permits for the erection, alteration or installation of signs shall be subject to the special provisions set forth in Sections [105.7.1] 106.7.1 through [105.7.5] 106.7.5.

[105.7.1] 106.7.1 Identification number. Every sign permit shall have an identification number.

[105.7.2] 106.7.2 Changing copy or structural change of sign or sign structure. The changing of copy on a sign not permitted for changeable copy or any structural change of the sign or sign structure shall require a new permit pursuant to this code.

[105.7.3] 106.7.3 Permit does not constitute authorization for illegal sign. The issuance of a permit for the erection, alteration or installation of a sign or sign structure issued pursuant to this code shall not be deemed to constitute permission or authorization to maintain a sign that would otherwise be illegal without a maintenance permit for an outdoor sign if required pursuant to this code and department rule or that is otherwise illegal pursuant to any other provision of law nor shall any permit issued hereunder constitute a defense in an action or proceeding with respect to such an unlawful sign.

[105.7.4] 106.7.4 Name and business address of licensed sign hanger. The application shall contain the name and business address of the licensed sign hanger who is to perform or supervise the proposed work.

[105.7.5] 106.7.5 Outdoor advertising company. If the sign or sign location is under the control of an outdoor advertising company, as defined in Chapter 5 of Title 28 of the Administrative Code, the application shall be accompanied by the name and, where provided by rule, the registration number of such outdoor advertising company.

[105.8] 106.8 Temporary construction [equipment] installation permits. In addition to the requirements of Chapter 1 of Title 28 of the Administrative Code, permits for the erection, installation and use of temporary construction [equipment] installations shall be subject to the special provisions set forth in Sections [105.8.1] 106.8.1 through [105.8.3] 106.8.3.

[105.8.1] 106.8.1 Application. The need for each specific item of temporary construction [equipment] installation shall be stated on the application.

[105.8.2] 106.8.2 Term of permit. Notwithstanding any other provision of this code, a temporary construction [equipment] installation permit shall expire 1 year from the date of issuance, or when the permit holder’s insurance or street obstruction bond expires, whichever is earlier. Such permit shall be renewable. Such permit must be in effect at all times during which the [equipment] temporary construction installation is at the work site.

[105.8.3] 106.8.3 Special provisions for renewal of permit for a sidewalk shed. An application for the renewal of a temporary construction [equipment] installation permit for a sidewalk shed used in connection with the alteration of a building shall be accompanied by a report, acceptable to the department, prepared by a registered design professional who has examined that part of the premises on which the work requiring the use of a sidewalk shed is being performed. Such report shall document the condition of the applicable part of the premises and the scope of work that has been performed thereon since the issuance of the permit and shall provide an estimate of the additional time needed to complete the work.

[105.9] 106.9 Mandatory sewer and catch basin work required by Section 24-526 of the Administrative Code. In addition to the requirements of Chapter 1 of Title 28, an applicant for a permit who is required pursuant to Section 24-526 of the Administrative Code to construct or repair defects in sewers or catch basins that lie outside the property shall submit certification from the Department of Environmental Protection that the applicant or owner has provided the Department of Environmental Protection with:

- A performance bond or other security satisfactory to the Department of Environmental Protection and approved as to form by the Law Department for the full cost, as estimated by the Department of Environmental Protection, of constructing the part of the storm water drainage system for such property which shall lay outside the property line and repairing defects in such construction, if and as required by Section 24-526 of the Administrative Code;

- Any license or other written instrument that the Department of Environmental Protection or the Law Department may reasonably request that gives the Department of Environmental Protection, its agents and contractors and the surety for a performance bond described in Item 1 above the legal right to enter private property to perform the work described in Item 1 above, pursuant to the terms of the performance bond or in accordance with the conditions of acceptance of other security described in Item 1 above, and the legal right to connect to, to extend or to discharge storm water into any private sewer authorized as a point of disposal pursuant to Section 24-526 of the Administrative Code, in the event that the owner of property fails to do so, if and as required pursuant to Section 24-526 of the Administrative Code;

- Insurance of a kind and in an amount that the Department of Environmental Protection and the Law Department deem satisfactory to insure the city fully for all risks of loss, damage to property or injury to or death of persons to whomever occurring, arising out of or in connection with the performance of all work described in this section.

106.10 Permits with respect to limited alteration applications. For permits with respect to limited alteration applications, refer to Sections 28-101.5 and 28-104.6, Exception 1, of the Administrative Code.

[SECTION BC 106]
[RESERVED]

SECTION BC 107
CONSTRUCTION DOCUMENTS

107.1 General. Construction documents shall comply with Chapter 1 of Title 28 of the Administrative Code, this section and other applicable provisions of this code and its referenced standards.

107.2 Required construction documents. In addition to the requirements of [Chapter 1] Article 104 of Title 28 of the Administrative Code, the applicant shall submit any and all of the documents specified in Sections 107.3 through [107.15] 107.16 as appropriate to the nature and extent of the work proposed.

107.2.1 Composite plans. Composite plans showing architectural, structural, and mechanical parts and related energy use systems of a building may be submitted provided that a clear understanding of each part and system is not impaired.

107.2.2 Multiple building developments. The same set of plans may be used for several buildings of the same construction, if such buildings are located on adjoining lots under the same ownership, and if applications for construction document approval for the lots are filed simultaneously.

107.3 Lot diagram. The lot diagram shall show compliance with the New York City Zoning Resolution, indicating the size, height, and location of the proposed construction including parking and curb cuts; all existing structures on the zoning lot and their distances from lot and street lines; the established grade and existing curb elevations; and the proposed final grade elevations of the site shown by contours or spot grades at reasonable intervals. The lot diagram shall be drawn in accordance with an accurate boundary survey to the city datum, made by a land surveyor, which shall be attached to and form part of the application. A complete zoning analysis shall accompany the lot diagram with citation to the relevant sections of the New York City Zoning Resolution.

107.4 Building classification statement. The statement shall identify:

- The occupancy group or groups that apply to parts of the building in accordance with Section 302;

- The occupancy group of the main use or dominant occupancy of the building;

- The construction [class] type of the building in accordance with Section 602;

- The structural occupancy/risk category in accordance with Table 1604.5;

- The height of the building as defined in Section 502.1;

- The applicable measurements to the highest and lowest level of Fire Department access;

- Whether the building is inside or outside of the fire districts; [and]

8.	Whether the building is inside or outside a flood hazard area; and

9.	For multiple dwellings, the multiple dwelling classification as established by the New York State Multiple Dwelling Law.

107.5 Means of egress plans. Floor and roof plans shall show compliance with the requirements of Chapter 10, with sufficient notations indicating egress features and complete egress analysis as required by this code.

107.6 Architectural plans. Construction documents for all buildings shall provide detailed drawings of all architectural elements of the building showing compliance with the code, including but not limited to doors, windows and interior finish schedules, details necessary to substantiate all required fire-protection characteristics, details demonstrating compliance with the New York City Energy Conservation Code and details demonstrating compliance with all accessibility requirements of this code. [Site safety features shall be shown where applicable.] Plans shall also provide details of the exterior wall envelope as required, including but not limited to flashing, insulation, vapor retarder, intersections with dissimilar materials, corners, end details, control joints, intersections at roof, eaves or parapets, means of drainage, water-resistive membrane and details around openings.

Exception: Where a curtain wall system is to be employed containing elements that are normally detailed on shop or working drawings, approval of construction documents shall be conditioned upon deferred submittal of such shop or working drawings showing the approval of the registered design professional who prepared the architectural construction documents, or of a signed statement by such registered design professional that such drawings were prepared to his or her satisfaction. In such cases, submittal of construction documents showing compliance with the New York City Energy Conservation Code related to such curtain wall may also be deferred. Such deferred submittal of construction documents must demonstrate that the estimated annual energy use for the envelope in the energy analysis submitted as part of the initial filing is not exceeded.

107.7 Structural plans. Structural plans shall include the data and information described in this section and in Chapter 16. Structural calculations shall be made available to the department upon request.

Exceptions:

- Where structural elements are normally detailed on shop or working drawings, approval of construction documents shall be conditioned upon deferred submittal of such shop or working drawings showing the approval of the registered design professional who prepared the structural construction documents, or of a signed statement by such registered design professional that such drawings were prepared to his or her satisfaction.

2.	In cases where the detailing of structural elements has been made on the basis of fire-resistance ratings, load tables, or similar data as given in manufacturer’s catalogues, approval of construction documents shall be conditional upon submission of a manufacturer’s designation attesting to the accuracy of the data and indicating that such data were derived in conformance with the provisions of this code. Where the detailing of structural elements has been made on the basis of data published in technical documents of recognized authority issued or accredited by the agency or association promulgating the applicable referenced standard, such manufacturer’s designation will not be required.

107.7.1 Foundation plans. Foundation plans shall show compliance with the requirements of Chapter 18 of this code regarding foundation design and shall show the plan locations, design loads, design elevations of the bottoms, and details as to sizes, reinforcements, and construction of all footings, piers, foundation walls, pile groups, and pile caps. The foundation systems shown on plans shall be of a type indicated in the geotechnical report required by Section 1803.6. The levels of footings of adjacent structures shall be indicated or, if the adjacent structures are pile supported, this shall be stated. Where applicable, the plans shall include underpinning details. In addition, there shall be a statement indicating the character and minimum class of the soil strata required for the support of the foundation; the allowable soil pressure used for the design of footings; and the character, class, and presumptive bearing capacity of the bearing stratum to which piling is required to penetrate. The types and design capacities of piling and the records of required borings or test pits shall also be shown. In addition, foundation plans shall include insulation details as required by the New York City Energy Conservation Code.

107.7.2 Floor plans. Floor plans and sections showing all structural requirements shall be provided for all levels.

107.7.3 Detailed drawings. Drawings shall show sizes, sections, and locations of members, and such other information as may be required to indicate clearly all structural elements and special structural engineering features.

107.7.4 Column schedules. Column schedules shall show the design load contributed by the framing at any level and the total accumulated design load at each level.

107.7.5 Truss forces. Where trusses are employed, a diagram or table shall indicate the loads or moments in the various members under the design loading conditions. The requirement for a diagram or table may be waived when the trusses consist of elements selected from load tables or similar data, subject to the requirements for verification described in this code.

107.7.6 Prestressing forces. Where pre-stressed members are employed, a schedule or table shall show the total prestressing forces and the method and sequence of application.

107.8 Earthwork plans. Where the application is sought solely for or includes earthwork, excavation or fill operations, including but not limited to site decontamination, soil remediation and grading, the applicant shall submit 1) a lot diagram showing the exact location of the lot and dimensions to the nearest corner; and 2) plans showing the exact location, extent, and depth or height of the proposed earthwork, excavation or fill operation and any existing utilities, foundations or other infrastructure potentially impacted by the earthwork, excavation or fill operation. For excavation operations, the plans shall also indicate the levels of footings of all adjacent structures or, if the adjacent structures are pile supported, this shall be stated. Where applicable, the plans shall also include underpinning details, soil information in accordance with Chapter 18, and a final grading plan representing the lot after all earthwork, excavation or fill operations have been completed.

107.9 Fire protection system plans. Construction documents for fire protection systems shall include a plot plan to scale indicating the location of the system in relation to the rest of the building and shall comply with Sections 107.9.1 through 107.9.4. Such plans shall not be required in connection with applications for limited standpipe alterations and limited sprinkler alterations.

107.9.1 Sprinkler systems. Sprinkler systems plans shall comply with Section 903.1.2.

107.9.2 Alternative automatic fire-extinguishing systems. Notwithstanding any other provision of this code, design and installation documents for the installation of alternative automatic fire-extinguishing systems shall be filed with and reviewed by the Fire Department for compliance with this code, the New York City Fire Code and other applicable laws and regulations in accordance with Section 105 of the New York City Fire Code.

107.9.3 Standpipe systems. Standpipe systems plans shall comply with Section 905.1.1.

107.9.4 Fire alarm and detection systems. Fire alarm and detection systems plans shall comply with Section 907.1.1.

107.10 Sign installation plans. Construction documents for sign applications shall comply with Section [H 105.2 in Appendix H] H105.2.

107.11 Discharge of sewage and discharge and/or management of stormwater runoff. Applications for construction document approval shall comply with Sections 107.11.1, 107.11.2 and 107.11.3.

107.11.1 Sewage. Applications for construction document approval shall include submittal documents relating to the availability and feasibility of a public sanitary or public combined sewer and/or other approved discharge for sewage in accordance with Sections 107.11.1.1 and 107.11.1.2 for the following types of applications:

- New buildings that include any fixtures that produce sewage;

- Alterations that require an increase in size to an existing sanitary or combined sewer connection; and/or

- Alterations requiring a new connection to a sanitary or combined sewer.

107.11.1.1 Connection feasible and available. Where a public sanitary or combined sewer is certified by the Department of Environmental Protection or certified by an applicant in accordance with rules of such department to be available and connection thereto feasible, the applicant shall submit:

- Department of Environmental Protection certification of availability and feasibility. A sewer certification issued by the Department of Environmental Protection that a public sanitary or combined sewer is available and connection thereto is feasible. Applications for such certification shall be made to the Department of Environmental Protection on forms specified by such department (Department of Environmental Protection “house/site connection proposal application” or other form as specified in the rules of such department) and shall be reviewed and approved by such department in accordance with the rules of such department. Such certification may be conditioned by such department on part or all of the sewage to be disposed of with an on-site disposal system or with the use of an alternative disposal system; or

- Applicant certification of availability and feasibility. A certification submitted by the applicant to the Department of Environmental Protection in accordance with the rules of such department that a public sanitary or combined sewer is available and connection thereto is feasible, in such cases where the availability and feasibility of connection to a public sanitary or combined sewer are allowed to be certified by the applicant pursuant to such rules. Such certification shall be on forms specified by such department (Department of Environmental Protection “house/site connection proposal application” or other form as specified in the rules of such department).

107.11.1.2 Connection not feasible or not available. Where a public sanitary or combined sewer is not available, or where connection thereto is not feasible, the applicant shall submit:

- Department of Environmental Protection or applicant certification of unavailability or non-feasibility. (i) A certification issued by the Department of Environmental Protection that a public sanitary or combined sewer is not available or that connection to an available sewer is not feasible. Such certification shall be on forms specified by such department (Department of Environmental Protection “house/site connection proposal application” or other form as specified in the rules of such department) or (ii) A certification submitted by the applicant to the Department of Environmental Protection that a public sanitary or combined sewer is not available or that connection thereto is not feasible, in such cases where the availability and feasibility of connection to a public sanitary or combined sewer are allowed to be certified by the applicant pursuant to the rules of such department. Such certification shall be on forms specified by such department (Department of Environmental Protection “house/site connection proposal application” or other form as specified in the rules of such department); and

- On-site disposal. A proposal for the design and construction of a system for the on-site disposal of sewage conforming to the provisions of this code and other applicable laws and rules including but not limited to minimum required distances from lot lines or structures and subsoil conditions. Construction documents for such system shall be subject to the approval of the department.

107.11.2 Stormwater. Applications for construction document approval shall include submittal documents relating to the availability and feasibility of a public combined or storm sewer or other approved method for stormwater discharge in accordance with Sections 107.11.2.1 and 107.11.2.2 for the following types of applications:

- New buildings;

- Alterations of buildings proposing horizontal building enlargement; and/or

- Alterations that increase impervious surfaces on the tax lot.

Exceptions:

- Applications for construction document approval for the alteration of an existing one- or two-family dwelling need not include such submittal documents, where the [area] footprint of a proposed horizontal building enlargement and any proposed increase in impervious surfaces combined is less than or equal to 200 square feet (19 m2). Construction documents shall include the amount of proposed increase in impervious area.

  - This exception shall not apply if the horizontal building enlargement and increase in impervious surface related to the current application for construction document approval and any other enlargement or increase in impervious surface made on the same tax lot after July 1, 2008 together exceed 200 square feet (19 m2).

- Applications for construction document approval for the alteration of a building need not include such submittal documents, where the [area of a] increase in area of the footprint resulting from a proposed horizontal building enlargement and any proposed increase in impervious surfaces on a lot combined is less than or equal to 1,000 square feet (93 m2), and on-site disposal of stormwater conforming to the provisions of the applicable laws and rules as determined by the department is proposed for such enlargement and/or increase in impervious surface. Construction documents shall include the amount of proposed increase in impervious area.

  - This exception shall not apply where on-site disposal cannot be designed to conform to the provisions of the applicable laws and rules including but not limited to minimum required distances from lot lines or structures or subsoil conditions as determined by the department.

  - This exception shall not apply if the horizontal building enlargement and increase in impervious surface related to the current application for construction document approval and all other enlargements or increases in impervious surface made on the same tax lot after July 1, 2008 together exceed 1000 square feet (93 m2).

107.11.2.1 Connection feasible and available. Where a public combined or storm sewer is certified by the Department of Environmental Protection or certified by an applicant in accordance with rules of such department to be available and connection thereto is feasible, applicants shall submit:

- Department of Environmental Protection certification of availability and feasibility. A sewer certification issued by the Department of Environmental Protection that a public storm or combined sewer is available and connection thereto is feasible. Applications for such certification shall be made to the Department of Environmental Protection on forms specified by such department (Department of Environmental Protection “house/site connection proposal application” or other form as specified in the rules of such department) and shall be reviewed and approved by such department in accordance with the rules of such department. Such certification may be conditioned by such department on part or all of the stormwater runoff to be disposed of through an on-site detention or retention system, or by use of alternative disposal methods including but not limited to ditches, swales or watercourses; or

- Applicant certification of availability and feasibility. A certification submitted by the applicant to the Department of Environmental Protection in accordance with the rules of such department that a public storm or combined sewer is available and connection thereto is feasible, in such cases where the availability and feasibility of connection to a public storm or combined sewer are allowed to be certified by the applicant pursuant to such rules. Such certification shall be on forms specified by such department (Department of Environmental Protection “house/site connection proposal application” or other form as specified in the rules of such department).

107.11.2.2 Connection not feasible or not available. Where a public combined or storm sewer is not available, or where connection thereto is not feasible, applicants shall submit:

- Department of Environmental Protection or applicant certification of unavailability or non-feasibility. (i) Certification issued by the Department of Environmental Protection that a public storm or combined sewer is not available or that connection thereto is not feasible. Such certification shall be on forms specified by such department (Department of Environmental Protection “house/site connection proposal application” or other form as specified in the rules of such department); or (ii) Certification submitted by the applicant to the Department of Environmental Protection that a public storm or combined sewer is not available or that connection thereto is not feasible, in such cases where the availability and feasibility of connection to a public storm or combined sewer are allowed to be certified by the applicant pursuant to rules of such department. Certification shall be on forms specified by such department (Department of Environmental Protection “house/site connection proposal application” or other form as specified in the rules of such department); and

- On-site disposal. A proposal for the design and construction of a system for the on-site disposal of stormwater conforming to the provisions of this code and other applicable laws and rules including but not limited to minimum required distances from lot lines or structures and subsoil conditions. Construction documents for such system shall be subject to the approval of the department.

107.11.3 Post-construction stormwater management facilities. A post-construction stormwater management facility that is constructed as part of a covered development project shall comply with the rules of the Department of Environmental Protection and with this code.

107.12 Predemolition photographs. In addition to the requirements of Section 3306.3, construction documents for full demolition shall comply with the following requirements for archival photographs:

- Number required. Applications shall contain two sets of photographs of the building or buildings to be demolished or removed. Both sets shall be received by the department on behalf of the New York City Landmarks Preservation Commission and the New York City Municipal Archives Division of the Department of Records and Information Services.

- Format. The photographs shall conform to the standards and specifications established by rules promulgated by the commissioner upon the advice of the commissioner of the Department of Records and Information Services and the chairperson of the Landmarks Preservation Commission.

Exception: Applications made on behalf of the New York City Department of Housing Preservation and Development or made pursuant to Article 215 of Chapter 2 of Title 28 of the Administrative Code are exempt from the requirements of this section.

107.13 Energy efficiency plans. Construction documents shall include compliance documentation as required by the New York City Energy Conservation Code.

107.14 Mechanical and fuel gas plans. Construction documents for gas piping, heating, ventilation, refrigeration and other mechanical work to be performed shall be submitted as per New York City Mechanical and Fuel Gas Codes.

107.15 Plumbing plans. Construction documents for plumbing work to be performed shall be submitted as per the New York City Plumbing Code.

107.16 Flood zone compliance plans. Flood zone compliance plans demonstrating compliance with Appendix G shall be submitted with applications for construction document approval for projects located within a flood hazard area, or where required by Appendix G.

107.17 Retention of construction and submittal documents. Refer to Section 28-104.12 of the Administrative Code.

107.18 Construction documents for extension or relocation of an existing chimney or vent. Where an owner of a new or altered taller building is required by Section 801 of the New York city Mechanical Code, Section 501 of the New York City Fuel Gas Code, or Section 2113 of this code, to extend, alter or relocate an existing chimney or vent on an affected building, the construction documents for the new or altered taller building shall comply with the requirements of Section 107.18.1.

107.18.1 Chimney and vent plan. At the time of initial filing for construction, a chimney and vent plan shall be included as part of the construction documents. Such chimney and vent plan shall include the following information for all chimneys and vents within 100 feet (30 480 mm) of construction:

1.	A drawing identifying the location of each existing chimney and vent.

2.	A chimney and vent schedule containing the following information for each chimney and vent:

2.1.	The cross-sectional area of the chimney or vent outlet.

2.2.	The horizontal distance measured from the adjacent construction to the outlet

2.3.	The elevation of the outlet.

2.4.	The appliance, mechanical system, or fireplace to which the chimney or vent is attached, including the flue gas temperature, or a notation that this information is not yet known.

2.5.	If extension, alteration, or relocation is required and describing the expected work.

3.	Calculations demonstrating which chimneys and vents require no alteration based on the termination requirements including but not limited to those found in Section 503.5.4 of the New York City Fuel Gas Code and Section 801.20 of the New York City Mechanical Code.

SECTION BC 108
TEMPORARY STRUCTURES AND USES

108.1 General. Refer to Chapter 1 of Title 28 of the Administrative Code.

SECTION BC 109
FEES

109.1 Payment of fees. Refer to Chapter 1 of Title 28 of the Administrative Code.

SECTION BC 110
INSPECTIONS

110.1 General. Except as otherwise specified, inspections required by this code or by the department during the progress of work may be performed on behalf of the owner by approved agencies or, if applicable, by special inspectors. However, in the interest of public safety, the commissioner may direct that any of such inspections be performed by the department. All inspections shall be performed at the sole cost and expense of the owner. Refer to Article 116 of Chapter 1 of Title 28 of the Administrative Code for additional provisions relating to inspections.

110.2 Preliminary inspection. Refer to Chapter 1 of Title 28 of the Administrative Code.

110.3 Required progress inspections. The inspections set forth in Sections 110.3.1 through [110.3.8] 110.3.7 shall be made during the progress of work to verify substantial compliance with the code and with approved construction documents.

110.3.1 Footing and foundation inspection. Footing and foundation inspections shall be made after excavations for footings are complete and any required reinforcing steel is in place. For concrete foundations, any required forms shall be in place prior to inspection. Materials for the foundation shall be on the job, except where concrete is ready mixed in accordance with ASTM C 94, the concrete need not be on the job.

110.3.2 Lowest floor elevation. In [areas of special] flood hazard areas, upon placement of the lowest floor, including the basement (for flood zone purposes), and prior to further vertical construction, the elevation inspection report required in Item 1 of Section [G105.3] G107.3 of Appendix G shall be submitted to the department.

110.3.3 Structural wood frame inspection. Inspections shall be performed for wood structural framing to determine compliance with the approved construction documents.

Exception: Prefabricated wood structural elements and assemblies subject to Section [1704.6.1] 1705.5.1 through [1704.6.3] 1705.5.3 shall not be subject to progress inspection.

110.3.4 Fire-resistance-rated construction inspection. Fire-resistance-rated construction shall be inspected to determine compliance with the approved construction documents, including inspection of the following work:

- Fire-resistance-rated partitions, floors, ceilings, shafts; and

- Fire shutters.

Exception: Where the scope of work affecting an existing fire-rated wall assembly is limited to through-penetration firestopping and, in the course of work, the cutting away or removal of any part of the existing fire-resistance-rated construction becomes necessary in the general area surrounding the penetration, not to exceed 4 square feet (0.37 m2) in any given area, the progress inspection for fire-resistance-rated construction shall not be required provided that the special inspection agency for the through-penetration firestopping special inspection verifies that the removed portion of fire-resistance-rated construction (i) is less than 4 square feet (0.37 m2), and (ii) has been restored to its original condition.

110.3.5 Energy code compliance inspections. Inspections shall be made to determine compliance with approved construction documents.

110.3.6 Other inspections. In addition to the inspections specified above, the commissioner is authorized to make or require other inspections of any construction work to ascertain compliance with the provisions of this code and other laws that are enforced by the department.

110.3.7 Tenant protection plan compliance inspections. For buildings undergoing work for which a tenant protection plan is required by Article 120 of Title 28 of the Administrative Code, inspections shall be made by the department to determine compliance with the tenant protection plan.

110.4 Special inspections. Special inspections required by this code or by the commissioner shall be performed by special inspection agencies.

110.5 Final inspection. Refer to Article 116 of Chapter 1 of Title 28 of the Administrative Code.

110.6 Issuance of certificate of compliance. Upon satisfactory inspection of service equipment and the satisfaction of all the requirements for sign-off, the department shall issue a certificate of compliance as applicable for the following service equipment:

- Elevators;

- Escalators;

- Moving walkways;

- Heating systems; and

- Dumbwaiters.

110.7 Approved inspection agencies. Refer to Articles 114 and 115 of Chapter 1 of Title 28 of the Administrative Code.

110.8 Inspection requests. Refer to Chapter 1 of Title 28 of the Administrative Code.

110.9 Satisfactory inspection report required. Portions of work requiring inspection may be sequenced or phased to allow continuing progress of that work provided that work shall not be done beyond the point indicated in each successive required inspection for that phase. The inspector shall either indicate the portion of the construction that is satisfactory as completed, or notify the permit holder or the superintendent of construction wherein the same fails to comply with this code. Any portions that do not comply shall be corrected and such portion shall not be covered or concealed until corrected. The person performing the inspection shall complete a report of satisfactory inspection. Refer to Chapter 1 of Title 28 of the Administrative Code.

SECTION BC 111
CERTIFICATE OF OCCUPANCY

111.1 General. Refer to Chapter 1 of Title 28 of the Administrative Code.

SECTION BC 112
SERVICE UTILITIES

112.1 General. Refer to Chapter 1 of Title 28 of the Administrative Code.

SECTION BC 113
RESERVED

SECTION BC 114
VIOLATIONS

114.1 General. Refer to Chapter 2 of Title 28 of the Administrative Code.

SECTION BC 115
STOP WORK ORDER

115.1 General. Refer to Chapter 2 of Title 28 of the Administrative Code.

SECTION BC 116
UNSAFE STRUCTURES AND EQUIPMENT

116.1 General. Refer to Chapters 2 and 3 of Title 28 of the Administrative Code.

§ 3. Chapter 2 of the New York city building code, is REPEALED and a new chapter 2 is added to read as follows:

CHAPTER 2
DEFINITIONS

SECTION BC 201
GENERAL

201.1 Scope. Unless otherwise expressly stated, the following words and terms shall, for the purposes of this code, have the meanings shown in this chapter.

201.2 Interchangeability. Words used in the present tense include the future; words stated in the masculine gender include the feminine and neuter; the singular number includes the plural and the plural, the singular.

201.3 Terms defined in other codes. Where terms are not defined in this code and are defined in the New York City Fuel Gas Code, New York City Fire Code, New York City Mechanical Code, New York City Electrical Code, New York City Plumbing Code, or the New York City Energy Conservation Code, such terms shall have the meanings ascribed to them as in those codes.

201.3.1 Terms defined in the general administrative provisions. The following terms are defined in Section 28-101.5 of the Administrative Code:

1968 BUILDING CODE.

1968 OR PRIOR CODE BUILDINGS OR STRUCTURES (PRIOR CODE BUILDINGS).

ACCEPTANCE OR ACCEPTED.

ADDITION.

ADMINISTRATIVE CODE.

ALTERATION.

APPROVAL OR APPROVED.

APPROVED AGENCY.

APPROVED FABRICATOR.

APPROVED INSPECTION AGENCY.

APPROVED TESTING AGENCY.

ARCHITECT.

BUILDING.

CHARTER.

CERTIFICATE OF COMPLIANCE.

CITY.

COMMISSIONER.

CONSTRUCTION DOCUMENTS.

DAY.

DEFERRED SUBMITTAL.

DEMOLITION.

DEMOLITION, FULL.

DEMOLITION, PARTIAL.

DEPARTMENT.

ENGINEER.

ENLARGEMENT.

ENVIRONMENTAL CONTROL BOARD or ECB.

EXISTING BUILDING OR STRUCTURE.

FABRICATED ITEM.

FIRE PROTECTION PLAN.

HEREAFTER.

HERETOFORE.

INSPECTION CERTIFICATE.

LABEL.

LABELED.

LAND SURVEYOR.

LANDSCAPE ARCHITECT.

LETTER OF COMPLETION.

LIMITED ALTERATION APPLICATION.

LIMITED OIL-BURNING APPLIANCE ALTERATIONS.

LIMITED PLUMBING ALTERATIONS.

LIMITED SPRINKLER ALTERATIONS.

LIMITED STANDPIPE ALTERATIONS. Category 2

LISTED.

MAIN USE OR DOMINANT OCCUPANCY (OF A BUILDING).

MANUFACTURER’S DESIGNATION.

MARK.

MATERIALS.

OCCUPANCY.

OWNER.

PARTY WALL.

PERMIT.

PERSON.

PREMISES.

PRIOR CODE BUILDING.

PROFESSIONAL CERTIFICATION.

PROGRESS INSPECTION.

PROJECT.

REGISTERED DESIGN PROFESSIONAL.

REGISTERED DESIGN PROFESSIONAL OF RECORD.

REQUIRED.

RETAINING WALL.

SERVICE EQUIPMENT.

SIGN-OFF.

SINGLE ROOM OCCUPANCY MULTIPLE DWELLING.

SPECIAL INSPECTION.

SPECIAL INSPECTION AGENCY.

SPECIAL INSPECTOR.

STRUCTURE.

SUBMITTAL DOCUMENTS.

SUPERINTENDENT OF CONSTRUCTION (CONSTRUCTION SUPERINTENDENT).

USE (USED).

UTILITY COMPANY OR PUBLIC UTILITY COMPANY.

UTILITY CORPORATION OR PUBLIC UTILITY CORPORATION.

WORK NOT CONSTITUTING MINOR ALTERATIONS OR ORDINARY REPAIRS.

WRITING (WRITTEN).

WRITTEN NOTICE.

ZONING RESOLUTION.

201.4 Terms not defined. Where terms are not defined through the methods authorized by this section, such terms shall have ordinarily accepted meanings such as the context implies.

SECTION BC 202
DEFINITIONS

24-HOUR BASIS. The actual time that a person is an occupant within a facility for the purpose of receiving care. It shall not include a facility that is open for 24 hours and is capable of providing care to someone visiting the facility during any segment of the 24 hours.

100-HOUR TRAINING PROGRAM. A program that (i) includes 100 or more hours of training in technical subjects relating to a construction trade, including an apprenticeship program registered with the New York State Department of Labor, (ii) is approved by OSHA, the United States Department of Labor, the New York State Department of Education or the New York State Department of Labor and (iii) provides training that the department determines is equivalent to or exceeds the training required to comply with Section 3321.

500-YEAR FLOOD ELEVATION. The elevation of the flood having a 0.2-percent chance of being equaled or exceeded in any given year, as specified on FEMA FIRM 360497 or FEMA FIS 360497.

AAC MASONRY. Masonry made of autoclaved aerated concrete (AAC) units, manufactured without internal reinforcement and bonded together using thin- or thick-bed mortar.

ACCESSIBLE. A site, building, facility or portion thereof that complies with Chapter 11.

ACCESSIBLE MEANS OF EGRESS. A continuous and unobstructed way of egress travel from any accessible point in a building or facility to a public way. Such way of egress travel may include an assisted rescue path.

ACCESSIBLE ROUTE. A continuous, unobstructed path that complies with Chapter 11.

ACCESSIBLE UNIT. A dwelling unit or sleeping unit that complies with this code and the provisions for Accessible units in ICC A117.1.

ACCREDITATION BODY. An approved, third-party organization that is independent of the grading and inspection agencies, and the lumber mills, and that initially accredits and subsequently monitors, on a continuing basis, the competency and performance of a grading or inspection agency related to carrying gout specific tasks.

ACTIVELY PROCTORED ONLINE TRAINING. Online training that satisfies each of the following conditions:

1.	The person responsible for conducting such training confirms the identification of the person taking such training in a manner established by the department.

2.	While such training is being conducted, the site of such training is actively observed by or on behalf of the person responsible for conducting such training.

3.	Such training complies with any other requirements the department establishes by rule.

ADHERED MASONRY VENEER. Veneer secured and supported through the adhesion of an approved bonding material applied to an approved backing.

ADJUSTMENT (SCAFFOLD). The calibration or modification of a scaffold, including any part or component, that does not meet the definition of installation, removal, repair, maintenance, or use, and does not constitute normal use or operation of the scaffold.

AEROSOL. A product that is dispensed from an aerosol container by a propellant, classified as follows:

Level 1. Aerosol products with a total chemical heat of combustion that is greater than 0 and less than or equal to 8,600 British thermal units per pound (Btu/lb) (20 kJ/g).

Level 2. Aerosol products with a total chemical heat of combustion that is greater than 8,600 Btu/lb (20 kJ/g), but less than or equal to 13,000 Btu/lb (30 kJ/g).

Level 3. Aerosol products with a total chemical heat combustion that is greater than 13,000 Btu/lb (30 kJ/g).

AGGREGATE. In roofing, crushed stone, crushed slag or water-worn gravel used for surfacing for roof coverings.

AIR-INFLATED STRUCTURE. A structure that uses air-pressurized membrane beams, arches or other elements to enclose space. Occupants of such a structure do not occupy the pressurized area used to support the structure.

AIR-SUPPORTED STRUCTURE. A building wherein the shape of the structure is attained and maintained by elevated air pressure and occupants of the structure are within the elevated pressure area. Air-supported structures are of two basic types:

Double skin. Similar to a single skin, but with an attached liner that is separated from the outer skin and provides an airspace which serves for insulation, acoustic, aesthetic or similar purposes.

Single skin. Where there is only the single outer skin and the air pressure is directly against that skin.

AISLE. An unenclosed exit access component that defines and provides a path of egress travel.

AISLE ACCESSWAY. That portion of an exit that leads to an aisle.

ALARM NOTIFICATION APPLIANCE. A fire alarm system component such as a bell, horn, speaker, light or text display that provides audible, tactile or visible outputs, or any combination thereof.

ALARM SIGNAL. A signal indicating an emergency requiring immediate action, such as a signal indicative of fire.

ALARM VERIFICATION FEATURE. A feature of automatic fire detection and alarm systems to reduce unwanted alarms wherein smoke detectors report alarm conditions for a minimum period of time, or confirm alarm conditions within a given time period, after being automatically reset, in order to be accepted as a valid alarm-initiation signal.

ALLOWABLE STRESS DESIGN. A method of proportioning structural members, such that elastically computed stresses produced in the members by nominal loads do not exceed specified allowable stresses (also called "working stress design").

ALTERNATE LOAD PATH. A secondary or redundant load path capable of transferring the load from one structural element to other structural elements.

ALTERNATE LOAD PATH METHOD. A design approach that accounts for an extreme event by providing alternate load paths for elements that are no longer able to carry load. In an alternate load path design, key elements are considered notionally removed, one at a time, and the structure is designed to transfer the loads from the removed element to other structural elements, as required by Section 1617.

ALTERNATING TREAD DEVICE. A device that has a series of steps between 50 and 70 degrees (0.87 and 1.22 rad) from horizontal, usually attached to a center support rail in an alternating manner so that the user does not have both feet on the same level at the same time.

AMBULATORY CARE FACILITY. Buildings or portions thereof used to provide medical, surgical, psychiatric, nursing or similar care on a less than 24-hour basis to individuals who are rendered incapable of self-preservation by the services provided.

ANCHOR BUILDING. An exterior perimeter building of a group other than H having direct access to a covered mall building but having required means of egress independent of the mall.

ANCHORED MASONRY VENEER. Veneer secured and supported through the adhesion of an approved bonding material applied to an approved backing.

ANIMAL SERVICE FACILITY. The following facilities where animals are sheltered on a 24-hour basis: animal hospitals, kennels, pounds, veterinary clinics and pet shops.

ANNULAR SPACE. The opening around the penetrating item.

ANNUNCIATOR. A unit containing one or more indicator lamps, alphanumeric displays or other equivalent means in which each indication provides status information about a circuit, condition or location.

APARTMENT. A dwelling unit providing permanent provisions for both sanitation and kitchen facilities, occupied or arranged to be occupied by not more than one family maintaining a common household.

APARTMENT, STUDENT. An apartment occupied or arranged to be occupied by students enrolled at a single accredited college or university and maintaining a common household pursuant to a lease, sublease, or occupancy agreement directly with such college or university.

ARCHITECTURAL TERRA COTTA. Plain or ornamental hard-burned modified clay units, larger in size than brick, with glazed or unglazed ceramic finish.

AREA.

Gross cross-sectional. The area delineated by the out-to-out specified dimensions of masonry in the plane under consideration.

Net cross-sectional. The area of masonry units, grout and mortar crossed by the plane under consideration based on out-to-out specified dimensions.

AREA, BUILDING. The area included within surrounding exterior walls (or exterior walls and firewalls) exclusive of vent shafts and courts. Areas of the building not provided with surrounding walls shall be included in the building area if such areas are included within the horizontal projection of the roof or floor above.

AREA OF RESCUE ASSISTANCE. An area where persons unable to use stairways can remain temporarily to await instructions or assistance during emergency evacuation.

AREA OF SPORT ACTIVITY. That portion of an indoor or outdoor space where the play or practice of a sport occurs.

AREAWAY. A space below grade adjacent to a building open to the outer air and enclosed by walls.

ARTICULATING BOOM CRANE. A crane whose boom consists of a series of folding, pin connected structural members, typically manipulated to extend or retract by power from hydraulic cylinders.

ASPECT RATIO. The height of any portion of a building divided by its least dimension at the elevation from which the height is being measured.

ASPHALT. A dark brown to black bitumen pitch that melts readily and which appears in nature in asphalt beds or is produced as a by-product of the petroleum industry.

ASPHALT CONCRETE or ASPHALT PAVING. A mixture of liquid asphalt and graded aggregate used as a paving material.

ASSEMBLY SPACE. Any part of a place of assembly, exclusive of the stage, that is occupied by numbers of persons during the major period of occupancy. Every tier of seating shall be considered a separate assembly space.

ASSISTED RESCUE PATH. A portion of the accessible means of egress which begins at the area of rescue assistance and terminates at the public way.

ATRIUM. An opening connecting two or more stories other than enclosed stairways, elevators, hoistways, escalators, plumbing, electrical, air-conditioning or any other vertical openings that are not required to be enclosed by other provisions of this code, which is closed at the top and not defined as a mall. Stories, as used in this definition, do not include balconies within assembly groups or mezzanines that comply with Section 505.

AUDIBLE ALARM NOTIFICATION APPLIANCE. A notification appliance that alerts by the sense of hearing.

AUGERED-CAST-IN-PLACE PILES. Augered-cast-in-place piles are constructed by pumping grout into an augered hole during the withdrawal of the auger. The pile is reinforced with a single reinforcing bar, a reinforcing steel cage or a structural steel section.

AUTOCLAVED AERATED CONCRETE (AAC). Low-density cementitious product of calcium silicate hydrates, whose material specifications are defined in ASTM C 1386.

AUTOMATIC. As applied to fire protection devices, a device or system providing an emergency function without the necessity for human intervention and activated as a result of a predetermined temperature rise, rate of temperature rise and/or the presence of combustion products.

AUTOMATIC FIRE-EXTINGUISHING SYSTEM. An approved system of devices and equipment that automatically detects a fire and discharges an approved fire-extinguishing agent onto or in the area of a fire.

AUTOMATIC SMOKE DETECTION SYSTEM. A fire alarm system that has initiation devices that utilize smoke detectors for protection of an area such as a room or space with detectors to provide early warning of fire.

AUTOMATIC SPRINKLER SYSTEM. A fire suppression or control device that operates automatically when its heat-activated element is heated to its thermal rating or above, allowing water to discharge over a specified area.

AUTOMATIC WATER MIST SYSTEM. A system consisting of a water supply, a pressure source, and a distribution piping system with attached nozzles, which, at or above a minimum operating pressure defined by its listing, discharges water in fine droplets meeting the requirements of NFPA 750 for the purpose of the control, suppression or extinguishment of a fire. Such systems include wet-pipe, dry-pipe and pre-action types. The systems are designed as engineered, pre-engineered, local-application or total flooding systems.

AVERAGE AMBIENT SOUND LEVEL. The root mean square, A-weighted sound pressure level measured over a 24-hour period, or the time any person is present, whichever time period is less.

AXIS OF ROTATION. The vertical axis around which the crane superstructure rotates.

AXLE. The shaft or spindle with which or about which a wheel rotates. On truck and wheel mounted cranes, it refers to a type of axle assembly including housing, gearing, differential, bearings, and mounting appurtenances.

A-ZONE. An area of special flood hazard without high-velocity wave action. When not shown on the FIRMs, the water surface elevation may be determined from available data by the registered design professional of record in accordance with Section G103.3. See also “Area of special flood hazard.”

BACKING. The wall or surface to which the veneer is secured.

BALCONY, EXTERIOR. An exterior floor projecting from and supported by a structure without additional independent supports.

BALED COTTON. A natural seed fiber wrapped in and secured with industry accepted materials, typically consisting of burlap, woven polypropylene, polyethylene or cotton or sheet polyethylene, secured with wire or bands. The term baled cotton includes lint removed from the cottonseed (linters) and residual materials from the ginning process (motes).

BALED COTTON, DENSELY PACKED. Baled cotton with a packing density of not less than 22 pounds per cubic foot (360 kg/m3). A bale of densely packed baled cotton typically measures 55 inches (1397 mm) in length, 21 inches (533.4 mm) in width, and 27.6 to 35.4 inches (701 to 899 mm) in height.

BALLAST. In roofing, ballast comes in the form of large stones or paver systems or light-weight interlocking paver systems and is used to provide uplift resistance to components of the roof assembly systems that are not adhered or mechanically attached to the roof deck.

BARRICADE. A structure or other artificial or natural barrier constructed in connection with the storage, handling and use of explosives that is designed to withstand the rapid release of energy in an explosion and provides a shield from the impact of such explosion. A straight line from the top of any sidewall of a building containing explosives to the eaveline of any magazine or other building or to a point 12 feet (3658 mm) above the center of a railway shall pass through such barrier.

Artificial barricade. An artificial mound or revetment, including a barrier constructed of sandbags, with a minimum thickness of 3 feet (914 mm).

Natural barricade. Terrain or other natural features of the ground.

BARRIER, TEMPORARY. An approved temporary fence, permanent fence, the wall of a permanent structure, any other structure, or any combination thereof that prevents access to the swimming pool by any person not engaged in the installation or construction of the swimming pool during its installation or construction.

BASE FLOOD. The flood having a 1-percent chance of being equaled or exceeded in any given year.

BASE FLOOD ELEVATION. The elevation of the base flood, including wave height, as specified on FEMA FIRMs 360497 or as determined in accordance with Section G103.3. In areas designated as ZONE AO, the base flood elevation shall be the elevation of the highest existing grade of the building’s perimeter plus the depth number (in feet) specified on the flood hazard map.

BASE (MOUNTING). The traveling base on which the rotating superstructure of a crawler crane is mounted.

BASEMENT. A story partly below the grade plane and having less than one-half its clear height (measured from finished floor to finished ceiling) below the grade plan (see "Story" and "Story above grade plane"). A basement shall be considered a story above grade plane.

BASEMENT (FOR FLOOD ZONE PURPOSES). The portion of a building having its floor subgrade (below ground level) on all sides. This definition of “Basement” is limited in application to the provisions of Appendix G.

BEARER (PUTLOG). A horizontal transverse scaffold member (which may be supported by legs or runners) upon which the scaffold platform rests and joins scaffold uprights, posts, poles, and similar members.

BED JOINT. The horizontal layer of mortar on which a masonry unit is laid.

BLEACHERS. Tiered seating supported on a dedicated structural system and two or more rows high and is not a building element (see "Grandstand").

BOARDER (ROOMER, LODGER). A person who pays a consideration for living within the household and does not occupy such space as an incident of employment.

BOILING POINT. The temperature at which the vapor pressure of a liquid equals the atmospheric pressure of 14.7 pounds per square inch (psia) (101 kPa) or 760 mm of mercury. Where an accurate boiling point is unavailable for the material in question, or for mixtures which do not have a constant boiling point, for the purposes of this classification, the 20-percent evaporated point of a distillation performed in accordance with ASTM D 86 shall be used as the boiling point of the liquid.

BOOM (CRANE OR DERRICK). A section or strut, of which the heel (lower end) is affixed to a base, carriage, or support, and whose upper end supports a cable and sheaves where the load is lifted by means of rope and a hook.

BOOM POINT. The outer extremity of the crane boom, containing the hoist sheave assembly.

BRACED WALL LINE. A straight line through the building plan that represents a location of the lateral resistance provided by wall bracing.

BRACED WALL PANEL. A full-height section of wall constructed to resist in-plane shear loads through interaction of framing members, sheathing material and anchors. The panel’s length meets the requirements of its particular bracing method and contributes toward the total amount of bracing required along its braced wall line.

BRAKE. A device used for retarding or stopping motion.

BREAKAWAY WALL. An open lattice wall subject to flooding that is not required to provide structural support to a building or other structure and that is designed and constructed such that, under base flood or lesser flood conditions, it will collapse under specific lateral-loading forces in such a way that (1) it allows the free passage of floodwaters, and (2) it does not damage the structure or the supporting foundation system.

BREAKOUT. For revolving doors, a process whereby wings or door panels can be pushed open manually for means of egress travel.

BRICK.

Calcium silicate (sand lime brick). A pressed and subsequently autoclaved unit that consists of sand and lime, with or without the inclusion of other materials.

Clay or shale. A solid or hollow masonry unit made of clay or shale, usually formed into a rectangular prism, then burned or fired in a kiln; brick is a ceramic product.

Concrete. A concrete masonry unit made from portland cement, water, and suitable aggregates, with or without the inclusion of other materials.

BUCKET HOIST. A power or manually operated bucket that (i) is temporarily installed at a construction or demolition site, (ii) moves vertically on guide members to raise or lower material, and (iii) is controlled from a point outside the conveyance.

BUILDING ELEMENT. A fundamental component of building construction, listed in Table 601, which may or may not be of fire-resistance-rated construction and is constructed of materials based on the building type of construction.

BUILDING, ENCLOSED. A building that does not comply with the requirements for open or partially enclosed buildings.

BUILDING, LOW-RISE. Enclosed or partially enclosed buildings that comply with the following conditions:

1.	Mean roof height, h, less than or equal to 60 feet (18 288 mm).

2.	Mean roof height, h, does not exceed least horizontal dimension.

BUILDING, OPEN. A building having each wall at least 80 percent open. This condition is expressed for each wall by the equation:

(Equation 2-1)

where:

Ao =	Total area of openings in a wall that receives positive external pressure, in square feet (m2).

Ag =	The gross area of that wall in which Ao is identified, in square feet (m2).

BUILDING, PARTIALLY ENCLOSED. A building that complies with both of the following conditions:

1.	The total area of openings in a wall that receives positive external pressure exceeds the sum of the areas of openings in the balance of the building envelope (walls and roof) by more than 10 percent; and

2.	The total area of openings in a wall that receives positive external pressure exceeds 4 square feet (0.37 m2) or 1 percent of the area of that wall, whichever is smaller, and the percentage of openings in the balance of the building envelope does not exceed 20 percent. These conditions are expressed by the following equations:

(Equation 2-2)

(Equation 2-3)

where:

,  are as defined for an open building.

The sum of the areas of openings in the building envelope (walls and roof) not including Ao, in square feet (m2).

The sum of the gross surface areas of the building envelope (walls and roof) not including Ag, in square feet (m2).

BUILDING, SIMPLE DIAPHRAGM. A building in which wind loads are transmitted through floor and roof diaphragms to the vertical lateral-force-resisting systems.

BUILDING-INTEGRATED PHOTOVOLTAIC (BIPV) PRODUCT. A building product that incorporates photovoltaic modules and functions as a component of the building envelope.

BUILDINGS AND OTHER STRUCTURES, FLEXIBLE. Buildings and other structures that have a fundamental natural frequency less than 1 Hz.

BUILT-UP ROOF COVERING. Two or more layers of felt cemented together and surfaced with a cap sheet, mineral aggregate, smooth coating or similar surfacing material.

BULKHEAD. An enclosed rooftop structure enclosing a shaft, stairway, tank or service equipment, or other space not designed or used for human occupancy.

CABLE-RESTRAINED, AIR-SUPPORTED STRUCTURE. A structure in which the uplift is resisted by cables or webbings that are anchored to either foundations or dead men. Reinforcing cable or webbing is attached by various methods to the membrane or is an integral part of the membrane. This is not a cable-supported structure.

CABLEWAY. A device used for hoisting, lowering, and transporting loads within a prescribed path, longitudinally and laterally. The load block (upper) travels on a rope catenary system having span ends that are supported on fixed or movable towers (masts) or other elevated supports.

CAISSON PILES. Steel cased piles constructed by advancing a steel shell seated into rock and drilling of an uncased socket within the rock. The shell and socket are filled with a steel core section or steel reinforcing, and concrete or grout.

CARBON DIOXIDE EXTINGUISHING SYSTEMS. A system supplying carbon dioxide (CO2) from a pressurized vessel through fixed pipes and nozzles. The system includes a manual- or automatic-actuating mechanism.

CARBON MONOXIDE ALARM. A listed single- or multiple-station alarm responsive to carbon monoxide.

CARBON MONOXIDE DETECTOR. A listed device that senses carbon monoxide.

CARBON MONOXIDE-PRODUCING EQUIPMENT. Any furnace, boiler, water heater, fireplace, cooking appliance, gas clothes dryer, apparatus, appliance or device that burns coal, kerosene, oil, wood, fuel gases and other petroleum products including, but not limited to, methane, natural gas, liquefied natural gas and manufactured fuel gases.

CARE SUITE. In Group I-2 occupancies, a group of treatment rooms, care recipient sleeping rooms and the support rooms or spaces and circulation space within the suite where staff are in attendance for supervision of all care recipients within the suite, and the suite is in compliance with the requirements of Section 407.4.4.

CARPORT. A structure or portion of a structure, accessory to a Group R-2 or R-3 occupancy, open on at least two sides and unenclosed for at least 50 percent of perimeter, used for the parking or storage of passenger motor vehicles. Such facility shall not exceed 650 square feet (60.45 m2) in area and one story in height.

CAST STONE. A building stone manufactured from portland cement concrete precast and used as a trim, veneer or facing on or in buildings or structures.

CEILING LIMIT. The maximum concentration of an air-borne contaminant to which one may be exposed. The ceiling limits utilized are those published in DOL 29 CFR Part 1910.1000. The ceiling Recommended Exposure Limit (REL-C) concentrations published by the U.S. National Institute for Occupational Safety and Health (NIOSH), Threshold Limit Value – Ceiling (TLV-C) concentrations published by the American Conference of Governmental Industrial Hygienists (ACGIH), Ceiling Workplace Environmental Exposure Level (WEEL-Ceiling) Guides published by the American Industrial Hygiene Association (AIHA), and other approved, consistent measures are allowed as surrogates for hazardous substances not listed in DOL 29 CFR Part 1910.1000.

CEILING RADIATION DAMPER. See Dampers, Types of.

CELL. See Section 408.1.1.

CELL. As used in Chapter 21, a void space having a gross cross-sectional area greater than 11/2 square inches (967 mm2).

CELL TIER. See Section 408.1.1.

CELLAR. That portion of a building that is partly or wholly underground, and having one-half or more of its clear height (measured from finished floor to finished ceiling) below the grade plane. Cellars shall not be counted as stories in measuring the height of the buildings.

CEMENT BOARD. A fiber reinforced cementitious panel most commonly used under flooring or as a tile backing board. Cement board shall include discrete nonasbestos fiber-cement interior substrate sheets or nonasbestos fiber-mat reinforced cement substrate sheets.

CEMENT PLASTER. A mixture of portland or blended cement, portland cement or blended cement and hydrated lime, masonry cement or plastic cement and aggregate and other approved materials as specified in this code.

CEMENTED SOIL. Soil in which the particles are held together by a chemical agent, such as calcium carbonate, such that a hand-size sample cannot be crushed into powder or individual soil particles by finger pressure.

CERAMIC FIBER BLANKET. A high-temperature mineral wool insulation material made of alumina-silica ceramic or calcium magnesium silicate soluble fibers and weighing 4 to 10 pounds per square cubic foot (pcf) (64 to 160 kg/m3).

CERTIFICATE OF APPROVAL. A certificate issued by the department upon review and approval of the engineering and testing of a specific make and model of hoisting equipment to ensure compliance with the applicable provisions of this code.

CERTIFICATE OF OPERATION. A certificate issued by the department upon satisfactory inspection of a specific piece of hoisting equipment to ensure that the equipment is in compliance with this code.

CERTIFICATE OF ON-SITE INSPECTION. A certificate issued by the department based on a site-specific inspection of the placement and founding of hoisting equipment.

CHILD CARE FACILITIES. See Section 308.2.1.

CHIMNEY. A primarily vertical structure containing one or more flues used to remove hot gases from burning fuel, refuse, or from industrial processes to the outdoor atmosphere.

Factory-built chimney. A listed and labeled chimney composed of factory-made components, assembled in the field in accordance with manufacturer’s instructions and the conditions of the listing.

Masonry chimney. A field-constructed chimney composed of solid masonry units, bricks, stones, or concrete.

Metal chimney. A field-constructed chimney of metal.

CHIMNEY TYPES.

High-heat appliance type. An approved chimney for removing the products of combustion from fuel-burning, high-heat appliances producing combustion gases in excess of 2,000°F (1093°C) measured at the appliance flue outlet (see Section 2113.11.3).

Low-heat appliance type. An approved chimney for removing the products of combustion from fuel-burning, low-heat appliances producing combustion gases not in excess of 1,000°F (538°C) under normal operating conditions, but capable of producing combustion gases of 1,400°F (760°C) during intermittent forces firing for periods up to 1 hour. Temperatures shall be measured at the appliance flue outlet.

Medium-heat appliance type. An approved chimney for removing the products of combustion from fuel-burning, medium-heat appliances producing combustion gases between 1,000°F (538°C) and 2,000°F (1093°C) measured at the appliance flue outlet (see Section 2113.11.2).

CIRCULATION PATH. An exterior or interior way of passage from one place to another for pedestrian travel, including that within accessible spaces.

CLAMSHELL. A shovel bucket with two jaws that clamp together by their own weight when it is lifted by a closing line.

CLEAN AGENT. Electrically nonconducting, volatile or gaseous fire extinguishant that does not leave a residue upon evaporation.

CLIMBER CRANE. A tower crane that can be raised to a new working height, either by adding tower sections to the top of the crane (top climbing), or by a system in which the entire crane is raised inside the structure (inside climbing).

CLINIC, OUTPATIENT. Buildings or portions thereof used to provide medical care on less than a 24-hour basis to persons who are not rendered incapable of self-preservation by the services provided.

CLOSED SYSTEM. The use of any compressed gas and the use of a solid or liquid hazardous material in equipment or a vessel or system that remains closed during normal operations, such that vapors emitted during the operation of such equipment, vessel or system are not liberated outside of the equipment, vessel or system and the gas or hazardous material is not exposed to the atmosphere during such operation. Examples of closed systems include hazardous materials conveyed through a piping system into closed equipment of a closed vessel or system.

CLOSED-CIRCUIT TELEPHONE. A telephone with a dedicated line such as a house phone, courtesy phone or phone that must be used to gain entrance to a facility.

COASTAL A-ZONE. An area within a special flood hazard area, shown on FEMA FIRMs 360497 as an area bounded by a “Limit of Moderate Wave Action,” landward of a V-Zone or landward of an open coast without mapped V-Zones. In a Coastal A-Zone, the principal source of flooding must be astronomical tides, storm surges, seiches, or tsunamis, and not riverine flooding. During the base flood conditions, the potential for breaking wave heights must be greater than or equal to 1 foot, 6 inches (457 mm). In no case shall an area of special flood hazard be deemed a coastal A-Zone unless and until it has been identified as such on the adopted FEMA FIRMs 360497.

COASTAL HIGH HAZARD AREA. Area within the area of special flood hazard extending from offshore to the inland limit of a primary dune along an open coast and any other area that is subject to high-velocity wave action from storms and shown on FEMA FIRMs 360497 as velocity Zone V, VO, VE or V1-30.

COHESIVE SOIL. Clay (fine grained soil), or soil with a high clay content, which has cohesive strength. Cohesive soil does not crumble, can be excavated with vertical side slopes, and is plastic when moist. Cohesive soil is hard to break up when dry, and exhibits significant cohesion when submerged. Cohesive soils include clayey silt, sandy clay, silty clay, clay and organic clay.

COLLAPSE (STRUCTURAL). Failure of a structural element to the extent that it can no longer support any load.

COLLAR JOINT. Vertical longitudinal space between wythes of masonry or between masonry wythe and backup construction that is permitted to be filled with mortar or grout.

COLLECTING SAFE AREA. See Section 1002.1.2.

COLLECTOR. A horizontal diaphragm element parallel and in line with the applied force that collects and transfers diaphragm shear forces to the vertical elements of the lateral-force-resisting system or distributes forces within the diaphragm or both.

COMBINATION FIRE/SMOKE DAMPER. See Dampers, Types of.

COMBINATION SIGN. A sign incorporating any combination of the features of pole, projecting and roof signs.

COMBINED HEAT AND POWER SYSTEMS. Equipment that simultaneously produces electricity and heat from a single fuel source.

COMBUSTIBLE DUST. Finely divided solid material that is 420 microns or less in diameter, will pass through a U.S. standard No. 40 sieve and, when dispersed in air in sufficient concentrations, can be ignited by a flame, spark or other source of ignition.

COMBUSTIBLE FIBERS. Readily ignitable and free-burning materials in fibrous or shredded form, such as cocoa fiber, cotton, excelsior, hay, hemp, henequen, istle, jute, kapok, oakum, sisal, Spanish moss, straw, tow, wastepaper or other natural or synthetic fibers that possess similar qualities, but excluding densely packed baled cotton.

Exception: Moss used for medicinal purposes.

COMBUSTIBLE LIQUID. For the purposes of transportation, a combustible liquid as defined in the regulations of the United States of Transportation, as set forth in 49 CFR 173.120. For all other purposes, a liquid, other than a compressed gas or cryogenic fluid, having a closed cup flash point at or above 100°F (38°C) classified as follows:

Class II. Liquids having a closed cup flash point at or above 100°F (38°C) and below 140°F (60°C).

Class IIIA. Liquids having a closed cup flash point at or above 140°F (60°C) and below 200°F (93°C).

Class IIIB. Liquids having a closed cup flash point at or above 200°F (93°C).

COMMERCIAL COOKING SYSTEM. A system consisting of commercial cooking equipment, exhaust hood, filters, exhaust duct system, fire suppression system and other related appurtenances designed to capture grease-laden cooking vapors and exhaust them safely to the outdoors.

COMMERCIAL MOTOR VEHICLE. A motor vehicle used to transport passengers or goods where the motor vehicle:

1.	Has a gross vehicle weight rating of 10,000 pounds (4540 kg) or more; or

2.	Is designed to transport 16 or more passengers, including the driver.

COMMERCIAL TRUCK MOUNTED CRANE (BOOM TRUCK). A mobile crane consisting of a rotating superstructure (center post or turntable), boom, operating machinery, and one or more operator’s stations mounted on a frame attached to a commercial truck chassis.

COMMON PATH OF EGRESS TRAVEL. That portion of exit access that the occupants are required to traverse before two separate and distinct paths of egress travel to two exits are available. Paths that merge are common paths of travel. Common paths of egress travel shall be included within the permitted travel distance.

COMMON USE. Interior or exterior circulation paths, rooms, spaces or elements that are made available for the shared use of two or more people but are not for public use.

COMPACTED CONCRETE PILES. Compacted concrete piles are constructed by filling a driven casing with low-strength concrete and compacting the concrete as the casing is withdrawn.

COMPETENT PERSON. One who is capable of identifying existing and predictable hazards in the surroundings or conditions that are unsanitary, hazardous or dangerous, and who has authorization to take prompt corrective measures to eliminate such hazards.

COMPLETED STEEL FLOOR. Any floor, in a building whose primary structural system consists of structural steel, where the structural floor system, including the final walkable structural surface, has been installed and has achieved its required strength for construction loading.

COMPONENTS AND CLADDING. Elements of the building envelope that do not qualify as part of the main wind force-resisting system.

COMPOSITE PILES. Composite piles consist of two or more approved pile types joined together.

COMPRESSED GAS. A material, or mixture of materials that:

1.	Is a gas at 68°F (20°C) or less at 14.7 psia (101 kPa) of pressure; and

2.	Has a boiling point of 68°F (20°C) or less at 14.7 psia (101 kPa) that is either liquefied, nonliquefied or in solution at that temperature and pressure, except those gases which have no other health- or physical-hazard properties are not considered to be compressed until the pressure in the packaging exceeds 41 psia (282 kPa) at 68°F (20°C).

The states of compressed gases are categorized as follows:

Nonliquefied compressed gases. Gases, other than those in solution, which are in packaging under the charged pressure and are entirely gaseous at a temperature of 68°F (20°C).

Liquefied compressed gases. Gases that, in a packaging under the charged pressure, are partially liquid at a temperature of 68°F (20°C).

Compressed gases in solution. Nonliquefied gases that are dissolved in a solvent.

Compressed gas mixtures. A mixture of two or more compressed gases contained in a single packaging, the hazard properties of which are represented by the properties of the mixture as a whole.

CONCEALED SPACES. Enclosed spaces within partitions, walls, floors, roofs, stairs, furring, pipe chases and column enclosures and other similar spaces.

CONCRETE.

Carbonate aggregate. Concrete made with aggregates consisting mainly of calcium or magnesium carbonate, such as limestone or dolomite, and containing 40 percent or less quartz, chert, or flint.

Cellular. A lightweight insulating concrete made by mixing a preformed foam with portland cement slurry and having a dry unit weight of approximately 30 pcf (480 kg/m3).

Lightweight aggregate. Concrete made with aggregates of expanded clay, shale, slag or slate or sintered fly ash or any natural lightweight aggregate meeting ASTM C 330 and possessing equivalent fire-resistance properties and weighing 85 to 115 pcf (1360 to 1840 kg/m3).

Perlite. A lightweight insulating concrete having a dry unit weight of approximately 30 pcf (480 kg/m3) made with perlite concrete aggregate. Perlite aggregate is produced from a volcanic rock that, when heated, expands to form a glass-like material of cellular structure.

Sand-lightweight. Concrete made with a combination of expanded clay, shale, slag, slate, sintered fly ash, or any natural lightweight aggregate meeting ASTM C 330 and possessing equivalent fire-resistance properties and natural sand. Its unit weight is generally between 105 and 120 pcf (1680 and 1920 kg/m3).

Siliceous aggregate. Concrete made with normal-weight aggregates consisting mainly of silica or compounds other than calcium or magnesium carbonate, which contains more than 40-percent quartz, chert, or flint.

Vermiculite. A lightweight insulating concrete made with vermiculite concrete aggregate that is laminated micaceous material produced by expanding the ore at high temperatures. When added to a portland cement slurry the resulting concrete has a dry unit weight of approximately 30 pcf (480 kg/m3).

CONCRETE-FILLED STEEL PIPE AND TUBE PILES. Concrete-filled steel pipe and tube piles are constructed by driving a steel pipe or tube section into the soil and filling the pipe or tube section with concrete. The steel pipe or tube section is left in place during and after the deposition of the concrete. For the purposes of this code, these piles shall be considered driven piles.

CONCRETE WASHOUT WATER. Wastewater from the rinsing of equipment used to mix, transport, convey, and/or place concrete. Such equipment shall include, but not be limited to, concrete buckets, concrete hose lines and pumps, boots, shovels, finishing tools, wheelbarrows, motorized concrete carts, concrete pour funnels and the chute of concrete mixer trucks.

Exceptions:

1. 	This term shall not include wastewater from the rinsing of equipment involved in the preparation, conveyance or application of concrete that is:

1.1. 	mixed on site if the total quantity of concrete is less than or equal to one and one half cubic yards (1.146m3), or

1.2. 	from bagged ready mix if the total quantity of concrete is less than or equal to sixty (60) eighty pound (36.287 kg) bags, or eighty (80) sixty pound (27.215 kg) bags, or the equivalent.

2. 	This term shall not include wastewater from the rinsing of the wheels, undercarriage or chassis of concrete mixer trucks.

CONGREGATE LIVING UNIT. A dwelling unit, comprised of one or more habitable rooms separated by nonrated partitions, occupied or arranged to be occupied by more than one family or by persons who are not maintaining a common household. Creation of or conversion to such unit shall be subject to Section 27-2077 of the New York City Housing Maintenance Code.

CONSTANTLY ATTENDED LOCATION. A designated location at a facility staffed by trained personnel on a continuous basis where alarm or supervisory signals are monitored and facilities are provided for notification of the Fire Department of other emergency services.

CONSTRUCTION. The excavation, erection, alteration, and repair of buildings or any component parts, including all operations incidental thereto.

CONTAINER GARDEN. A plant or plants maintained in a pot or planters located on a roof, terrace, or other horizontal exterior area.

CONTINUOUS GAS DETECTION SYSTEM. A gas detection system where the analytical instrument is maintained in continuous operation and sampling is performed without interruption. Analysis is allowed to be performed on a cyclical basis at intervals not to exceed 30 minutes.

CONTROL AREA. Spaces within a building where quantities of hazardous materials not exceeding the maximum allowable quantities per control area are stored, handled, or used, including any dispensing. See also definition of "Outdoor control area" in the New York City Fire Code.

CONVENTIONAL LIGHT-FRAME CONSTRUCTION. A type of construction whose primary structural elements are formed by a system of repetitive wood-framing members. See Section 2308 for conventional light-frame construction provisions.

CORNER SCAFFOLD (ANGLE SCAFFOLD). A suspended scaffold consisting of an assembly of two or more platforms connected nonlineraly and designed and manufactured to fit around a corner or a projecting part of a building.

CORRIDOR. An enclosed exit access component that defines and provides a path of egress travel to an exit. Corridors shall be either interior or public.

Corridor, interior. A corridor that serves only one tenant. In Group E occupancies, corridors serving only one institution shall be deemed as serving a single tenant.

Corridor, public. A corridor that serves more than one tenant.

CORROSIVE MATERIAL. A material that causes full thickness destruction of human skin at the site of contact within a specified period of time when tested by methods set forth in DOTn regulations 49 CFR 173.136 and 173.137, or a liquid that has a severe corrosion rate on steel or aluminum based on the criteria set forth in DOTn regulations 49 CFR 173.173(c)(2).

COUNTERWEIGHT. Weight used to supplement the weight of the machine in order to provide stability for lifting loads.

COVERED MALL BUILDING. A single building enclosing a number of tenants and occupants such as retail stores, drinking and dining establishments, entertainment and amusement facilities, passenger transportation terminals, offices, and other similar uses wherein two or more tenants have a main entrance into one or more malls. For the purpose of this chapter, anchor buildings shall not be considered as part of the covered mall building. The term "covered mall building" shall include open mall buildings as defined below.

Mall. A roofed or covered common pedestrian area within a covered mall building that serves as access for two or more tenants and not to exceed three levels that are open to each other. The term "mall" shall include open malls as defined below.

Open mall. An unroofed common pedestrian way serving a number of tenants not exceeding three levels. Circulation at levels above grade shall be permitted to include open exterior balconies leading to exits discharging at grade.

Open mall building. Several structures housing a number of tenants, such as retail stores, drinking and dining establishments, entertainment and amusement facilities, offices and other similar uses, wherein two or more tenants have a main entrance into one or more open malls. For the purposes of Chapter 4, anchor buildings are not considered as part of the open mall building.

CRANE. A power-operated machine for lifting or lowering a load and moving it horizontally which utilizes wire rope and in which the hoisting mechanism is an integral part of the machine. The definition of a crane shall also include articulating boom crane, regardless of whether it has a hoisting mechanism integral to the machine.

CRAWLER CRANE. A mobile crane consisting of a rotating superstructure with a power plant, operating machinery, and boom, mounted on a base and equipped with crawler treads for travel.

CRIPPLE WALL. A framed stud wall extending from the top of the foundation to the underside of floor framing for the lowest occupied floor level.

CRITICAL PICK. The attachment and detachment of loads from the hook of hoisting equipment used to hoist or lower loads on the outside of a building that involves one or more of the following:

1.	An article that is at or above 95 percent of approved rated capacity of the hoisting equipment or rigging equipment;

2.	An article that is asymmetrical and is not provided with lifting connections by the manufacturer or fabricator;

3.	An article that has a wind sail area exceeding 500 square feet (46 m2);

4.	A pick that may present an added risk because of clearance, drift, or other interference;

5.	An article that is fragile or of thin shell construction and is not provided with standard rigging ears;

6.	A pick that requires multiple power-operated hoisting equipment (tandem pick); or

7.	A pick that require out of the ordinary rigging equipment, methods, or setup.

CROSS AISLE. An unenclosed exit access component in a place of assembly usually parallel to rows of seats, connecting aisles or connecting an aisle and an exit. For the purposes of Chapter 10, a cross aisle is not an aisle.

CROSS-LAMINATED TIMBER (CLT). A prefabricated engineered wood product made of at least three orthogonal layers of graded sawn lumber or structural composite lumber (SCL) that are laminated by gluing with structural adhesives.

CRYOGENIC FLUID. A liquid having a boiling point lower than -130°F (-89.9°C) at 14.7 pounds per square inch absolute (psia) (an absolute pressure of 101.3 kPa).

CURB LEVEL. As defined in the New York City Zoning Resolution.

CURB LINE. The line coincident with the face of the street curb adjacent to the roadway.

CURTAIN WALL. A curtain wall or panel wall system is a nonload-bearing building wall, in skeleton frame construction, attached and supported to the structure at every floor or other periodic locations. Assemblies may include glass, metal, precast concrete or masonry elements arranged so as not to exert common action under load and to move independently of each other and the supporting structure.

CUSTODIAL CARE FACILITY. A building or part thereof occupied by persons, on less than a 24-hour basis and not overnight, who because of age, disability or other reasons, receive personal care services by individuals other than parents or guardians, relatives by blood, marriage, domestic partnership, or adoption, in a place other than the home of the person cared for.

DALLE GLASS. A decorative composite glazing material made of individual pieces of glass that are embedded in a cast matrix of concrete or epoxy.

DAMPERS, TYPES OF.

Ceiling radiation damper. A listed device, installed in a ceiling membrane of a fire-resistance-rated floor/ceiling or roof/ceiling assembly to limit automatically the radiative heat transfer through an air inlet/outlet opening. Ceiling radiation dampers include air terminal units, ceiling dampers and ceiling air diffusers.

Combination fire/smoke damper. A listed device, installed in ducts and air transfer openings designed to close automatically upon the detection of heat and resist the passage of flame and smoke. The device is installed to operate automatically controlled by a smoke detection system, and where required, is capable of being positioned from a fire command center.

Fire damper. A listed device, installed in ducts and air transfer openings designed to close automatically upon detection of heat and restrict the passage of flame. Fire dampers are classified for use in either static systems that will automatically shut down in the event of a fire, or in dynamic systems that continues to operate during a fire. A dynamic fire damper is tested and rated for closure under elevated temperature airflow.

Smoke damper. A listed device, installed in ducts and air transfer openings designed to resist the passage of air and smoke. The device is installed to operate automatically, controlled by a smoke detection system, and where required, is capable of being positioned from a fire command center.

DAMPPROOFING. Dampproofing is a protective measure applied to building foundation walls and slabs to prevent moisture from passing into interior spaces.

DAY BOX. A portable magazine designed to hold explosive materials constructed in accordance with the requirements for a Type 3 magazine as defined and classified in the New York City Fire Code.

DEAD END. A portion of a corridor in which the travel to an exit is in one direction only.

DEAD LOAD. The weight of materials of construction incorporated into the building, including but not limited to walls, floors, roofs, ceilings, stairways, built-in partitions, finishes, cladding and other similarly incorporated architectural and structural items, and the weight of fixed service equipment, such as cranes, pluming stacks and risers, electrical feeders, heating, ventilating and air-conditioning systems and automatic sprinkler systems.

DEBRIS. Rubbish, waste, discarded material, or the remains of something broken down, demolished, or destroyed.

DEBRIS NET or NETTING. A netting of a fine mesh of a size and strength sufficient to catch debris, such as falling tools and materials.

DECK. An exterior floor supported on at least two opposing sides by an adjacent structure and/or posts, piers, or other independent supports.

DECORATIVE GLASS. A carved, leaded or Dalle glass or glazing material whose purpose is decorative or artistic, not functional; whose coloring, texture or other design qualities or components cannot be removed without destroying the glazing material and whose surface, or assembly into which it is incorporated, is divided into segments.

DECORATIVE SHROUD. A listed partial combustible enclosure for aesthetic purposes that is installed at the termination of a venting system that surrounds or conceals the chimney or vent cap.

DEDICATED PILE DRIVER. A power operated machine that is designed primarily to drive, hammer, press, or vibrate piles into the earth ("pile drive"). These machines typically have the ability to both hoist the material that will be pile driven and to pile drive that material.

DEEP FOUNDATIONS. Deep foundations are comprised of concrete, grout, wood or steel structural elements either driven, drilled or jacked into the ground or cast in place. Deep foundations are relatively slender in comparison to their length, with lengths exceeding 12 times the least horizontal dimension. Deep foundations derive their load-carrying capacity through skin friction, end bearing, or a combination thereof.

DEFLAGRATION. An exothermic reaction, such as the extremely rapid oxidation of a flammable dust or vapor in air, in which the reaction progresses through the unburned material at a rate less than the velocity of sound. A deflagration can have an explosive effect.

DELUGE SPRINKLER SYSTEM. A sprinkler system employing open sprinklers attached to a piping system connected to a water supply through a valve that is opened by the operation of a detection system installed in the same areas as the sprinklers. When this valve opens, water flows into the piping system and discharges from all sprinklers attached thereto.

DEMOLITION. Full or partial demolition.

Full demolition. The dismantling, razing, or removal of all of a building or structure, including all operations incidental thereto.

Partial demolition. The dismantling, razing, or removal of structural members, floors, interior bearing walls, and/or exterior walls or portions thereof, including all operations incidental thereto.

DERRICK. An apparatus consisting of a mast or equivalent member held at the end by guys or braces, with or without a boom, for use with a hoisting mechanism and operating ropes, for lifting or lowering a load and moving it horizontally.

DESIGN EARTHQUAKE GROUND MOTION. The earthquake ground motion that buildings and structures are specifically proportioned to resist in Section 1613.

DESIGN FLOOD ELEVATION. The applicable elevation specified in ASCE 24, Tables 2-1, 4-1, 5-1, 6-1, or 7-1, depending on the flood design class designated in ASCE 24, Table 1-1.

DESIGN STRENGTH. The product of the nominal strength and a resistance factor (or strength reduction factor).

DETACHED BUILDING. A separate single-story building, without a basement or crawl space, used for the storage, handling or use of hazardous materials and located an approved distance from other buildings and structures.

DETECTABLE WARNING. A standardized surface feature built in or applied to walking surfaces or other elements to warn a person who is blind or has low vision of hazards on a circulation path.

DETECTOR, HEAT. A fire detector that senses heat – either abnormally high temperature or rate of rise, or both.

DETONATION. An exothermic reaction with explosive effect that utilizes shock compression as the principal heating mechanism and generates a shock wave in the material that establishes and maintains a reaction that progresses through the material at a rate greater than the velocity of sound.

DETOXIFICATION FACILITIES. See Section 308.2.1.

DEVELOPMENT. See Section G201.1.2.

DEWATERING. The removal of surface or ground water from a site by pumping or evaporation.

DIAPHRAGM. A horizontal or sloped system acting to transmit lateral forces to vertical elements of the lateral force-resisting system. When the term "diaphragm" is used, it shall include horizontal bracing systems.

Diaphragm, blocked. In light-frame construction, a diaphragm in which all sheathing edges not occurring on a framing member are supported on and fastened to blocking.

Diaphragm boundary. In light-frame construction, a location where shear is transferred into or out of the diaphragm sheathing. Transfer is either to a boundary element or to another force-resisting element.

Diaphragm chord. A diaphragm boundary element perpendicular to the applied load that is assumed to take axial stresses due to the diaphragm moment.

Diaphragm, unblocked. A diaphragm that has edge nailing at supporting members only. Blocking between supporting structural members at panel edges is not included. Diaphragm panels are field nailed to supporting members.

DIMENSIONS.

Nominal. The specified dimension plus an allowance for the joints with which the units are to be laid. Nominal dimensions are usually stated in whole numbers. Thickness is given first, followed by height and then length.

Specified. Dimensions specified for the manufacture or construction of a unit, joint or element.

DIRECT AND CONTINUING SUPERVISION. See Section 28-401.3 of the Administrative Code.

DIRECT EMPLOY. See Section 28-401.3 of the Administrative Code.

DISMANTLING. The final process of taking apart, piece by piece, in a specific sequence, the components of a tower crane. Dismantling shall include jumping.

DISPENSING. The pouring or transferring by other means of any material from a container, tank or similar vessel, which would release dusts, fumes, mists, vapors, or gases to the atmosphere, unless such release is prevented by a device, equipment or system designed for that purpose.

DISPLAY SIGN. The area made available by the sign structure for the purpose of displaying the advertising message.

DOOR, BALANCED. A door equipped with double-pivoted hardware so designed as to cause a semicounterbalanced swing action when opening.

DRAFT STOP. A material, device or construction installed to resist the movement of air within open spaces of concealed areas of building components such as crawl spaces, floor/ceiling assemblies, roof/ceiling assemblies and attics.

DRAG STRUT. See "Collector."

DRILLED DISPLACEMENT PILES. Rotary displacement piles installed by rotating a helical auger segment into the ground with both a vertical force and a torque. The soil is displaced laterally within the ground (with minimum spoil generated) and the void created is filled with grout or concrete.

DRIVEN UNCASED PILES. Driven uncased piles are constructed by driving a steel shell into the soil to shore an unexcavated hole that is later filled with concrete. The steel casing is lifted out of the hole during the deposition of the concrete. Driven uncased piles are not permitted under the provisions of this code.

DRUM. The cylindrical member around which a rope is wound for raising and lowering the load or boom.

DRY-CHEMICAL EXTINGUISHING AGENT. A powder composed of small particles, usually of sodium bicarbonate, potassium bicarbonate, urea-potassium-based bicarbonate, potassium chloride or monoammonium phosphate, with added particulate material supplemented by special treatment to provide resistance to packing, resistance to moisture absorption (caking) and the proper flow capabilities.

DRY (SOIL). Soil that does not exhibit visible signs of moisture content.

DWELLING. A building or structure that is occupied in whole or in part as the home, residence or sleeping place of one or more families.

DWELLING, MULTIPLE. A dwelling that is either rented, leased, let or hired out, to be occupied, or is occupied, as the residence or home of three or more families living independently of each other. A multiple dwelling does not include a building used for occupancies in Groups I-2, I-3 or I-4.

DWELLING, ONE-FAMILY. Any building or structure designed and occupied exclusively for residence purposes on a long-term basis for more than a month at a time by not more than one family. One-family dwelling shall also be deemed to include a dwelling located in a series of one-family dwellings each of which faces or is accessible to a legal street or public thoroughfare, provided that each such dwelling unit is equipped as a separate dwelling unit with all essential services, and also provided that each such unit is arranged so that is may be approved as a legal one-family dwelling.

DWELLING, TWO-FAMILY. Any building or structure designed and occupied exclusively for residence purposes on a long-term basis for more than a month at a time by not more than two families. Two-family dwellings shall also be deemed to include a dwelling located in a series of two-family dwellings each of which faces or is accessible to a legal street or public thoroughfare, provided that each such dwelling is equipped as a separate dwelling with all essential services, and also provided that each such dwelling is arranged so that it may be approved as a legal two-family dwelling.

DWELLING UNIT. A single unit consisting of one or more habitable rooms and occupied or arranged to be occupied as a unit separate from all other units within a dwelling.

DWELLING UNIT (ACCESSIBILITY). As used in Chapter 11 and Appendix E, a single unit providing complete, independent living facilities for one or more persons, including permanent provisions for living, sleeping, eating, cooking and sanitation.

DWELLING UNIT OR SLEEPING UNIT, MULTISTORY. See "Multistory unit".

DWELLING UNIT OR SLEEPING UNIT, TYPE B. See "Type B unit".

EAVE HEIGHT, h. The distance from the ground surface adjacent to the building to the roof eave line at the particular wall. If the distance of the eave varies along the wall, the average distance shall be used.

EFFECTIVE WIND AREA. See ASCE 7.

EGRESS, COURT. A court or yard that provides access to a public right of way for one or more exits.

ELECTRIC SIGN. A sign containing electrical wiring, but not including signs illuminated by an exterior light source.

ELECTRICAL CIRCUIT PROTECTIVE SYSTEM. A specific listed construction of devices, materials, or coatings installed as a fire-resistive barrier system applied to electrical system components, such as cable trays, conduits and other raceways, open run cables and conductors, cables, and conductors in accordance with UL 2196.

ELEMENT (STRUCTURAL). A structural member or structural assembly.

ELEVATOR LANDING. That portion of a floor, balcony, or platform used to receive and discharge passengers or freight adjacent to an elevator hoistway.

EMERGENCY ALARM SYSTEM. A system to provide indication and warning of an emergency condition involving a release of hazardous material or other hazardous material incident.

EMERGENCY CONTROL STATION. An approved location on the premises of a semiconductor fabrication facility staffed by trained personnel that monitor the operation of equipment and systems including alert and alarm signals.

EMERGENCY ESCAPE AND RESCUE OPENING. An operable window, door or other similar device that provides for a means of escape and access for rescue in the event of an emergency.

EMERGENCY VOICE/ALARM COMMUNICATIONS. Dedicated manual or automatic facilities for originating and distributing voice instructions, as well as alert and evacuation signals pertaining to a fire or other emergency, to the occupants of a building.

EMPLOYEE WORK AREA. All or any portion of a space used only by employees and only for work. Corridors, toilet rooms, kitchenettes and break rooms are not employee work areas.

ENGINEERED WOOD RIM BOARD. A full-depth structural composite lumber, wood structural panel, structural glued laminated timber or prefabricated wood I-joist member designed to transfer horizontal (shear) and vertical (compression) loads, provide attachment for diaphragm sheathing, siding and exterior deck ledgers, and provide lateral support at the ends of floor or roof joists or rafters.

ENLARGED BASE PILES. Enlarged base piles are cast-in-place concrete piles constructed with a base that is larger than the diameter of the remainder of the pile. The enlarged base is designed to increase the load-bearing area of the pile in end bearing. Enlarged base piles include piles installed by driving a precast concrete tip or by compacting concrete into the base of the pile to form an enlarged base.

EQUIPMENT. Tools, machinery, or other implements used to facilitate construction or demolition work.

EQUIPMENT PLATFORM. An unoccupied, elevated platform used exclusively for mechanical systems or industrial process equipment, including the associated elevated walkways, stairways, alternating tread devices and ladders necessary to access the platform (see Section 505.3).

ERECTION. The assembly and placement of tower crane sections and components into place, including all operations incidental thereto. Erection shall include jumping.

ESSENTIAL FACILITIES. Buildings and other structures that are intended to remain operational in the event of extreme environmental loading from flood, wind, snow or earthquakes.

EXCAVATION. The removal of earth from its natural position; except for any incidental removal that occurs during the course of auguring, drilling, vibrating, or driving.

EXHAUSTED ENCLOSURE. A device, typically consisting of a hood equipped with a fan, that serves to capture and exhaust fumes, mist, vapors and gases generated at a workstation or other local environment. An exhausted enclosure does not include a room provided with general ventilation.

EXISTING CONSTRUCTION (FOR FLOOD ZONE PURPOSES). See Section G201.1.2.

EXISTING STRUCTURE (FOR FLOOD ZONE PURPOSES). See Section G201.1.2.

EXIT. That portion of a means of egress system, which is separated from other interior spaces of a building or structure by fire-resistance-rated construction and opening protective as required to provide a protected path of egress travel between the exit access and the exit discharge. Exits include exterior exit doors at the level of exit discharge, interior exit stairways and ramps, exit passageways, exterior exit stairways, exterior exit ramps and horizontal exits, but do not include access stairs, aisles, exit access doors opening to corridors, or corridors.

EXIT ACCESS. That portion of a means of egress system that leads from any occupied portion of a building or structure to an exit.

EXIT ACCESS DOORWAY. A door or access point along the path of egress travel from an occupied room, area or space where the path of egress enters an intervening room, corridor, unenclosed exit access stair or unenclosed exit access ramp.

EXIT ACCESS RAMP. A ramp within the exit access portion of the means of egress system.

EXIT ACCESS STAIRWAY. A stairway within the exit access portion of the means of egress system.

EXIT DISCHARGE. That portion of a means of egress system between the termination of an exit and a public way.

EXIT DISCHARGE, LEVEL OF. The story at the point at which an exit terminates and an exit discharge begins.

EXIT, HORIZONTAL. An exit that provides a path of egress travel from one building to an area in another building on approximately the same level, or a path of egress travel through or around a wall or partition to an area on approximately the same level in the same building, or a bridge or tunnel between two buildings, which affords safety from fire and smoke from the area of incidence and areas communicating therewith.

EXIT PASSAGEWAY. An exit component that is separated from other interior spaces of a building or structure by fire-resistance-rated construction and opening protectives, and provides for a protected path of egress travel in a horizontal direction to an exit component or to the exit discharge.

EXPANDED VINYL WALL COVERING. Wall covering consisting of a woven textile backing, an expanded vinyl base coat layer and a non-expanded vinyl skin coat. The expanded base coat layer is a homogenous vinyl layer that contains a blowing agent. During processing, the blowing agent decomposes, causing this layer to expand by forming closed cells. The total thickness of the wall covering is approximately 0.055 inch to 0.070 inch (1.4 mm to 1.8 mm).

EXPLOSION. An effect produced by the sudden violent expansion of gases, whether or not accompanied by a shock wave or disruption, of enclosing materials, including the effects of the following sources of explosion:

1.	Chemical changes such as rapid oxidation, deflagration or detonation, decomposition of molecules and runaway polymerization (usually detonations).

2.	Physical changes such as pressure tank ruptures.

3.	Atomic changes (nuclear fission or fusion).

EXPLOSIVE. A chemical compound, mixture or device, the primary or common purpose of which is to function by explosion. The term includes, but is not limited to, dynamite, black powder, pellet powder, initiating explosives, detonators, safety fuses, squibs, detonating cord, igniter cord and igniters.

The term "explosive" includes any material determined to be within the scope of Chapter 40 of Title 18 of the United States Codes, and any material classified as an explosive by the hazardous materials regulations of the United States Department of Transportation, as set forth in 49 CFR Section 173.52, except fireworks. Explosives are classified in accordance with the following United States Department of Transportation classification and other terms in common usage:

UN/DOTn Class 1 explosives.

Division 1.1. Explosives that present a mass explosion hazard.

Division 1.2. Explosives that present a projection hazard but not a mass explosion hazard.

Division 1.3. Explosives that present a fire hazard and either a minor blast hazard or a minor projection hazard, or both, but not a mass explosion hazard.

Division 1.4. Explosives that present a minor explosion hazard. The explosive effects are largely confined to the package and no projection of fragments of appreciable size or range is to be expected. Such explosives are not subject to mass explosion when exposed to fire.

Division 1.5. Explosives that present a mass explosion hazard but which are so insensitive that there is very little probability of initiation or of transition from burning to detonation under normal conditions of transport.

Division 1.6. Explosives consisting of extremely insensitive articles that do not present a mass explosion hazard, and present a negligible probability of accidental initiation or propagation.

High explosive. Explosives, including dynamite, that, when detonated, are characterized by a high rate of reaction, high pressure development, and the presence of a detonation wave, and that can be caused to detonate by means of a No. 8 test blasting cap, when unconfined.

Low explosive. Explosives that will burn or deflagrate when ignited, and which are characterized by a rate of reaction that is less than the speed of sound, and low pressure development. Examples of low explosives include black powder, igniter cords, igniters, safety fuses, small arms ammunition and primers, and propellants, 1.3C.

Mass-detonating explosives. Division 1.1, 1.2 and 1.5 explosives that, whether individually or in combination, or loaded into ammunition or containers, explode virtually instantaneously when a small portion is subjected to fire, concussion, impact, the impulse of an initiating agent, or the effect of a considerable discharge of energy from without, with severe explosive effect, including the potential for structural damage to adjacent objects, and explosive propagation to other explosives stored in proximity, such that two or more quantities in proximity must be considered as one for quantity-distance purposes.

EXTERIOR EXIT RAMP. An exit component that serves to meet one or more means of egress design requirements, such as required number of exits or exit access travel distance, and is open to yards, courts or public ways.

EXTERIOR EXIT STAIRWAY. A stairway that is open on at least one side, except for required structural columns, beams, handrails and guards. The adjoining open areas shall be either yards, courts or public ways. The other sides of the exterior exit stairway need not be open.

EXTERIOR INSULATION AND FINISH SYSTEMS (EIFS). EIFS are nonstructural, nonload-bearing, exterior wall cladding systems that consist of an insulation board attached either adhesively or mechanically, or both, to the substrate, an integrally reinforced base coat and a textured protective finish coat.

EXTERIOR INSULATION AND FINISH SYSTEMS (EIFS) WITH DRAINAGE. An EIFS that incorporates a means of drainage applied over a water-resistive barrier.

EXTERIOR SURFACES. Weather-exposed surfaces.

EXTERIOR WALL. A wall, bearing or nonbearing, that is used as an enclosing wall for a building, other than a fire wall, and that has a slope of 60 degrees (1.05 rad) or greater with the horizontal plane.

EXTERIOR WALL COVERING. A material or assembly of materials applied on the exterior side of exterior walls for the purpose of providing a weather-resisting barrier, insulation or for aesthetics, including but not limited to, veneers, siding, exterior insulation and finish systems, architectural trim and embellishments such as cornices, soffits, facias, gutters and leaders.

EXTERIOR WALL ENVELOPE. A system or assembly of exterior wall components, including exterior wall finish materials, that provides protection of the building structural members, including framing and sheathing materials, and conditioned interior space, from the detrimental effects of the exterior environment.

F RATING. The time period that the through-penetration firestop system limits the spread of fire through the penetration when tested in accordance with ASTM E 814 or UL 1479.

FABRIC PARTITION. A partition consisting of a finished surface made of fabric, without a continuous rigid backing, that is directly attached to a framing system in which the vertical framing members are spaced greater than 4 feet (1219 mm) on center.

FABRICATION AREA. An area within a semiconductor fabrication facility in which processes using hazardous production materials are conducted.

FACILITY. All or any portion of buildings, structure, site improvements, elements and pedestrian or vehicular routes located on a site.

FACTORED LOAD. The product of a nominal load and a load factor.

FAMILY.

1.	A single person occupying a dwelling unit and maintaining a common household with not more than two boarders, roomers or lodgers;

2.	Two or more persons related by blood, adoption, legal guardianship, marriage or domestic partnership; occupying a dwelling unit and maintaining a common household with not more than two boarders, roomers or lodgers;

3.	Not more than three unrelated persons occupying a dwelling unit and maintaining a common household;

4.	Not more than three unrelated persons occupying a dwelling unit in a congregate housing or shared living arrangement and maintaining a common household;

5.	Members of a group home;

6.	Foster children placed in accordance with provisions of the New York State Social Services Law, their foster parent(s), and other persons related to the foster parents by blood, marriage or domestic partnership; where all residents occupy and maintain a common household with not more than two boarders, roomers or lodgers; or

7.	Up to seven unrelated students enrolled at a single accredited college or university occupying a student apartment and maintaining a common household pursuant to a lease, sublease, or occupancy agreement directly with such college or university, provided that:

7.1.	The entire structure in which the dwelling unit is located is fully sprinklered in accordance with Chapter 9;

7.2.	Such occupancy does not exceed the maximums contained in Section 27-2075(a) of the New York City Housing Maintenance Code;

7.3.	Prior to commencement of such occupancy, and on an annual basis thereafter such college or university has submitted a fire safety plan containing fire safety and evacuation procedures for such dwelling unit that is acceptable to the Fire Commissioner and in compliance with any rules promulgated by the Fire Commissioner; and

7.4.	The dwelling unit complies with additional occupancy and construction requirements as may be established by rule by the Housing Preservation and Development Commissioner.

A common household is deemed to exist if all household members have access to all parts of the dwelling unit. Lack of access to all parts of the dwelling unit establishes a rebuttable presumption that no common household exists.

FENESTRATION. Skylights, roof windows, vertical windows (fixed or moveable), opaque doors, glazed doors, glazed block and combination opaque/glazed doors. Fenestration includes products with glass and nonglass glazing materials.

FIBERBOARD. A fibrous, homogeneous panel made from lignocellulosic fibers (usually wood or cane) and having a density of less than 31 pounds per cubic foot (pcf) (497 kg/m3) but more than 10 pcf (160 kg/m3).

FIBER REINFORCED POLYMER. A polymeric composite material consisting of reinforcement fibers, such as glass, impregnated with a fiber-bonding polymer which is then molded and hardened. Fiber-reinforced polymers are permitted to contain cores laminated between fiber-reinforced polymer facings.

FIBER-CEMENT SIDING. A manufactured, fiber-reinforcing product made with an inorganic hydraulic or calcium silicate binder formed by chemical reaction and reinforced with discrete organic or inorganic nonasbestos fibers, or both. Additives that enhance manufacturing or product performance are permitted. Fiber cement siding products have either smooth or textured faces and are intended for exterior wall and related applications.

FILM SIGN. A flat section of a material that is extremely thin in comparison to its length and breadth and has a nominal maximum thickness of 0.01 inch (0.25 mm).

FIRE ALARM BOX, MANUAL. See "Manual Fire Alarm Box."

FIRE ALARM CONTROL UNIT. A system component that receives inputs from automatic and manual fire alarm devices and may be capable of supplying power to detection devices and transponders or off-premises transmitters. The control unit may be capable of providing a transfer of power to the notification appliances and transfer of condition to relays or devices.

FIRE ALARM SIGNAL. A signal initiated by a fire alarm-initiating device such as a manual fire alarm box, automatic fire detector, waterflow switch, or other device whose activation is indicative of the presence of a fire or fire signature.

FIRE ALARM SYSTEM. A system or portion of a combination system consisting of components and circuits arranged to monitor and annunciate the status of fire alarm or supervisory signal-initiating devices and to initiate the appropriate response to those signals.

FIRE AREA. The aggregate floor area enclosed and bounded by fire walls, fire barriers, exterior walls and/or horizontal assemblies of a building. Areas of the building not provided with surrounding walls shall be included in the fire area if such areas are included within the horizontal projection of the roof or floor next above.

FIRE BARRIER. A fire-resistance-rated wall assembly of materials complying with Section 707 designed to restrict the spread of fire in which continuity of the fire-resistance rating is maintained.

FIRE COMMAND CENTER. The principal attended or unattended location where the status of detection, alarm communications and control systems is displayed, and from which the systems can be manually controlled.

FIRE DAMPER. See Dampers, Types of.

FIRE DETECTOR, AUTOMATIC. A device designed to detect the presence of a fire signature and to initiate action.

FIRE DOOR. The door component of a fire door assembly.

FIRE DOOR ASSEMBLY. Any combination of a fire door, frame, hardware, and other accessories that together, as an opening protective, provide a specific degree of fire protection to the opening.

FIRE DOOR ASSEMBLY, FLOOR. See "Floor fire door assembly."

FIRE EXIT HARDWARE. Panic hardware that is listed for use on fire door assemblies.

FIRE LANE. A public or private road, roadway lane, parking lot lane or other surface designed to allow vehicular access, that has been specifically designated by means of signs or roadway markings as a priority thoroughfare for fire apparatus.

FIRE PARTITION. A vertical assembly of materials complying with Section 708, designed to restrict the spread of fire in which openings are protected.

FIRE PROTECTION RATING. The period of time that an opening protective assembly will maintain the ability to confine a fire as determined by tests prescribed in Section 716. Ratings are stated in hours or minutes.

FIRE PROTECTION SYSTEM. Approved devices, equipment and systems or combinations of systems used to detect a fire, activate an alarm, extinguish or control a fire, control or manage smoke and products of a fire or any combination thereof.

FIRE PUMP. A pump exclusively used to boost water supply pressures in a fire protection system.

FIRE PUMP, AUTOMATIC STANDPIPE. A fire pump located at or below street level or as required, at the design flood elevation, that supplies the lower 300 feet (91.4 m) of an automatic standpipe system or a combined standpipe and sprinkler system. This does not apply to manual wet standpipe systems which are combined with sprinkler systems.

FIRE PUMP, FOAM. A fire pump used to boost water supply pressures in a fire protection system where such system uses firefighting foam as an additive.

FIRE PUMP, LIMITED SERVICE. A fire pump with a motor rating not exceeding 30 hp and utilizing a limited service fire pump controller.

FIRE PUMP, SPECIAL SERVICE. A fire pump that is located above street level, and above flood level, and that receives its water supply from a gravity tank or suction tank.

FIRE PUMP, SPRINKLER BOOSTER PUMP. A fire pump that supplies sprinkler systems only.

FIRE PUMP, WATER MIST SYSTEM. A fire pump used to boost water supply pressures in a fire protection system where such system utilizes water misting technology.

FIRE RESISTANCE. That property of materials or their assemblies that prevents or retards the passage of excessive heat, hot gases or flames under conditions of use.

FIRE SAFETY FUNCTIONS. Building and fire control functions that are intended to increase the level of life safety for occupants or to control the spread of harmful effects of fire.

FIRE SEPARATION DISTANCE. The distance measured from the building face to one of the following:

1.	The closest interior tax lot line;

2.	To the centerline of a street, an alley or public space; or

3.	To an imaginary line between two buildings on the same tax lot.

The distance shall be measured at right angles from the face of the wall.

FIRE WALL. A fire-resistance-rated smoke-tight wall having protected openings, which restricts the spread of fire and extends continuously from the foundation to or through the roof, with sufficient structural stability under fire conditions to allow collapse of construction on either side without collapse of the wall.

FIRE WINDOW ASSEMBLY. A window, as an opening protective, constructed and glazed to give protection against the passage of fire, smoke and hot gases.

FIREBLOCKING. A building material or materials approved for use as fireblocking to resist the free passage of flame or hot gases to other areas of the building through concealed spaces.

FIRECUT. A sloping cut on the ends of wood beams, joists and rafters resting on masonry or concrete walls.

FIREPLACE. A hearth and fire chamber or similar prepared place in which a fire may be made and that is built in conjunction with a chimney.

FIREPLACE THROAT. The opening between the top of the firebox and the smoke chamber.

FIRE-RATED GLAZING. Glazing with either a fire protection rating or a fire-resistance rating.

FIRE-RESISTANCE RATING. The period of time a building element, component or assembly maintains the ability to withstand fire exposure, continues to perform a given structural function, or both, as determined by the tests, or the methods based on tests, prescribed in Section 703.

FIRE-RESISTANT JOINT SYSTEM. An assemblage of specific materials or products that are designed, tested, and fire-resistance rated in accordance with either ASTM E 1966 or UL 2079 to resist for a prescribed period of time the passage of fire through joints made in or between fire-resistance-rated assemblies.

FIRESTOPPING. A through-penetration firestop or a membrane penetration firestop.

FIREWORKS. Any article or device that does not present a mass explosion hazard, that is manufactured or used to produce a visible or audible effect for entertainment or other display purposes by combustion, deflagration or detonation that meets the definition of 1.4G fireworks or 1.3G fireworks as set forth herein.

Fireworks, 1.3G. Large firework devices, classified as UN0335 by the United States Department of Transportation regulations, intended for use in fireworks displays and designed to produce audible or visible effects by combustion, deflagration or detonation including firecrackers containing more than 130 milligrams (2 grains) of explosive composition, aerial shells containing more than 40 grams of pyrotechnic material, and other display pieces which exceeds the limits for classification as 1.4G fireworks.

Fireworks, 1.4G. Small firework devices, classified as UN 0336 by United States Department of Transportation regulations, containing restricted amounts of pyrotechnic materials designed primarily to produce visible or audible effects by combustion.

FISSURED (SOIL). A soil material that has a tendency to break along definite planes of fracture with little resistance, or a material that exhibits open cracks, such as tension cracks, in an exposed surface.

FIXED BASE OPERATOR (FBO). A commercial business granted the right by the airport sponsor to operate on an airport and provide aeronautical services, such as fueling, hangaring, tie-down and parking, aircraft rental, aircraft maintenance and flight instruction.

FIXED HEADED PILE (DEEP FOUNDATION). A pile connected to a pile cap in a manner that prevents rotation of the pile head.

FIXED SEATING. Furniture or fixture designed and installed for the use of sitting and secured in place including bench-type seats and seats with or without backs or arm rests.

FLAME SPREAD. The propagation of flame over a surface.

FLAME SPREAD INDEX. A comparative measure, expressed as a dimensionless number, derived from visual measurements of the spread of flame versus time for a material tested in accordance with ASTM E 84 or UL 723.

FLAMMABLE GAS. A material which has a boiling point and becomes a gas at 68°F (20°C) or less at 14.7 pounds per square inch absolute (psia) (101 kPa) of pressure which:

1.	Is ignitable at 14.7 psia (101 kPa) when in a mixture of 13 percent or less by volume with air, in accordance with testing procedures set forth in ASTM E 681; or

2.	Has a flammable range at 14.7 psia (101 kPa) with air of at least 12 percent, regardless of the lower explosive limit, in accordance with testing procedures set forth in ASTM E 681.

The limits specified shall be determined at 14.7 psia (101 kPa) of pressure and a temperature of 68°F (20°C) in accordance with ASTM E 681.

FLAMMABLE LIQUEFIED GAS. A liquefied gas that, under a charged pressure, is partially liquid at a temperature of 68°F (20°C) and which is flammable.

FLAMMABLE LIQUID. For the purposes of transportation, a flammable liquid as defined in the regulations of the United States Department of Transportation, as set forth in 49 CFR 173.120. For all other purposes, a liquid, other than a compressed gas or cryogenic fluid, having a closed cup flash point below 100°F (38°C) classified as follows:

Class IA. Liquids having a flash point below 73°F (23°C) and a boiling point below 100°F (38°C).

Class IB. Liquids having a flash point below 73°F (23°C) and a boiling point at or above 100°F (38°C).

Class IC. Liquids having a flash point at or above 73°F (23°C) and below 100°F (38°C).

FLAMMABLE MATERIAL. A material capable of being readily ignited from common sources of heat or at a temperature of 600°F (316°C) or less.

FLAMMABLE SOLID. A solid, other than a blasting agent or other explosive, whether in elemental or alloy form, that is capable of causing fire through friction, absorption or moisture, spontaneous chemical change, or heat retained from manufacturing or processing, or which has an ignition temperature below 212°F (100°C) or which burns so vigorously and persistently when ignited as to create a serious hazard. A chemical shall be considered a flammable solid if upon testing using the method prescribed in CPSC regulations, as set forth in 16 CFR 1500.44, if it ignites and burns with a self-sustained flame at a rate greater than 0.1 inch (2.5 mm) per second along its major axis.

FLAMMABLE VAPORS OR FUMES. The concentration of flammable constituents in air that exceed 25 percent of their lower flammable limit (LFL).

FLASH POINT. The minimum temperature in degrees Fahrenheit at which a liquid will give off sufficient vapors to form an ignitable mixture with air near the surface or in the container, but will not sustain combustion. The flash point of a liquid shall be determined by appropriate test procedure and apparatus as specified in ASTM D 56, ASTM D 93 or ASTM D 3278.

FLIGHT. A continuous run of rectangular treads, winders or combination thereof from one landing to another.

FLOOD or FLOODING. A general and temporary condition of partial or complete inundation of normally dry land from:

- The overflow of inland or tidal waters.

- The unusual and rapid accumulation or runoff of surface waters from any source.

FLOOD DESIGN CLASS. See Section G201.1.2.

FLOOD HAZARD AREA. The following two areas:

1.	The area within a flood plain subject to a 1-percent or greater chance of flooding in any year. Also defined as the “special flood hazard area”.

2.	Where buildings are classified as Flood Design Class 4, the area within a flood plain delineated as shaded X-Zones.

FLOOD INSURANCE RATE MAP (FIRM). An official map of a community on which the Federal Emergency Management Agency (FEMA) has delineated both the special flood hazard areas and the risk preminum zones applicable to the community.

FLOOD INSURANCE STUDY (FIS). The official report provided by the Federal Emergency Management Agency (FEMA) containing the Flood Insurance Rate Map (FIRM), the water surface elevation of the base flood and supporting technical data.

FLOOD-DAMAGE-RESISTANT MATERIALS. Any construction material, including finishes, capable of withstanding direct and prolonged contact with floodwaters without sustaining any damage that requires more than cosmetic repair.

FLOODPROOFING, DRY. For buildings and structures that are nonresidential (for flood zone purposes), a combination of design modifications that results in the building’s or structure’s being water tight to the design flood elevation, including the attendant utility and sanitary facilities, with walls substantially impermeable to the passage of water and with structural components having the capacity to resist loads as identified in ASCE 7.

FLOODPROOFING, WET. A floodproofing method designed to permit parts of the structure below the design flood elevation that are used for parking, storage, building access, or crawl space to intentionally flood, by equalizing hydrostatic pressures and by relying on the use of flood damage-resistant materials and construction techniques.

FLOODWAY. The channel of the river, creek or other watercourse and the adjacent land areas that must be reserved in order to discharge the base flood without cumulatively increasing the water surface elevation more than a designated height. Floodways are mapped only in the Boroughs of the Bronx and Staten Island.

FLOOR AREA, GROSS. The floor area within the inside perimeter of the exterior walls of the building under consideration, exclusive of courts, without deduction for corridors, stairways, closets, the thickness of interior walls, columns or other features. The floor area of a building, or portion thereof, not provided with surrounded exterior walls shall be the usable area under the horizontal projection of the roof or floor above. The gross floor area shall not include interior courts.

FLOOR AREA, NET. The actual occupied area not including the thickness of walls, partitions, columns, furred-in spaces, fixed cabinets, equipment, and unoccupied accessory areas such as corridors, stairways, toilet rooms, mechanical rooms and closets.

FLOOR FIRE DOOR ASSEMBLY. A combination of a fire door, a frame, hardware and other accessories installed, as an opening protective, in a horizontal plane, which together provide a specific degree of fire protection to a through opening in a fire-resistance-rated floor (see Section 712.1.13.1).

FLUE. A passageway within a chimney or vent through which gaseous combustion products pass.

FLUE APPLIANCE. The passage(s) within an appliance through which combustion products pass from the combustion chamber of the appliance to the draft hood inlet opening on an appliance equipped with a draft hood or to the outlet of the appliance on an appliance not equipped with a draft hood.

FLUE GASES. Products of combustion and excess air.

FLUE LINER (LINING). A system or material used to form the inside surface of a flue in a chimney vent, for the purpose of protecting the surrounding structure from the effects of combustion products and for conveying combustion products without leakage into the atmosphere.

FLY GALLERY. A raised floor area above a stage from which the movement of scenery and operation of other stage effects are controlled.

FOAM PLASTIC INSULATION. A plastic that is intentionally expanded by the use of a foaming agent to produce a reduced-density plastic containing voids consisting of open or closed cells distributed throughout the plastic for thermal insulating or acoustical purposes and that has a density less than 20 pounds per cubic foot (pcf) (320 kg/m3).

FOAM-EXTINGUISHING SYSTEM. A special system discharging a foam made from concentrates mechanically over the area to be protected.

FOLDING AND TELESCOPIC SEATING. Tiered seating having an overall shape and size that is capable of being reduced for purposes of moving or storing and is not a building element.

FOOD COURT. See Section 402.2.

FOOTING. A foundation element consisting of an enlargement of a foundation pier or foundation wall, wherein the soil materials along the side of and underlying the element may be visually inspected prior to and during its construction.

FOUNDATION PIER. An isolated vertical foundation member whose horizontal dimension measured at right angles to its thickness does not exceed three times its thickness and whose height is equal to or less than four times its thickness.

FREE HEADED PILE. A pile with a head that is free to rotate.

FRONTAGE SPACE. A street or an open space adjoining a building not less than 30 feet (9144 mm) in any dimension. Such open space shall be accessible from a street by a driveway, lane, private road or alley at least 20 feet (6096 mm) in width. Such open space including accessways shall be permanently maintained free of all obstructions that might interfere with its use by the Fire Department.

FUNCTIONALLY DEPENDENT FACILITY. See Section G201.1.2.

GABLE. The triangular portion of a wall beneath the end of a dual-slope, pitched, or mono-slope roof or portion thereof and above the top plates of the story or level of the ceiling below.

GAS CABINET. A fully enclosed, noncombustible enclosure used to provide an isolated environment for compressed gas containers in storage or use, including any doors and access ports for exchanging containers and accessing pressure-regulating controls.

GAS ROOM. A separately ventilated, fully enclosed room in which only compressed gases and associated equipment and supplies are stored or used.

GEOTECHNICAL CAPACITY OF DEEP FOUNDATIONS. The load that can be supported by the soil or rock surrounding deep foundation as determined using a recognized method of analysis or as established by load tests. The geotechnical capacity can be developed through skin friction, end bearing, or a combination thereof.

GLASS FIBERBOARD. Fibrous glass roof insulation consisting of inorganic glass fibers formed into rigid boards using a binder. The board has a top surface faced with asphalt and kraft reinforced with glass fiber.

GRADE (LUMBER). The classification of lumber in regard to strength and utility in accordance with American Softwood Lumber Standard DOC PS 20 and the grading rules of an approved lumber rules-writing agency.

GRADE PLANE. A reference plane representing the level of the curb as established by the city engineer in the Borough President’s office, measured at the center of the front of a building. Where a building faces on more than one street, the grade plane shall be the average of the levels of the curbs at the center of each front.

Exception: The grade plan shall not be referenced to the level of the curb, but shall be considered the average elevation of the final grade adjoining all exterior walls of a building, calculated from final grade elevations taken at intervals of 10 feet (3048 mm) around the perimeter of the building where:

1.	No curb elevation has been legally established on the city map; or

2.	Every part of the building is setback more than 25 feet (7620 mm) from a street line.

GRANDSTAND. Tiered seating supported on a dedicated structural system and two or more rows high and is not a building element (see "Bleachers").

GRANULAR SOIL. Gravel, sand, or silt (coarse grained soil) with little or no clay content. Granular soil has no cohesive strength. Some moist granular soils exhibit apparent cohesion. Granular soil cannot be molded when moist and crumbles easily when dry.

GREEN ROOF SYSTEM. See definition for “VEGETATIVE ROOF.”

GRIDIRON. The structural framing over a stage supporting equipment for hanging or flying scenery and other stage effects.

GROSS LEASABLE AREA. See Section 402.2.

GROUND SIGN. A billboard or similar type of sign that is supported by one or more uprights, poles or braces in or upon the ground other than a combination sign or pole sign, as defined by this code.

GROUP HOME. A facility for the care and maintenance of not fewer than seven nor more than 12 children, supervised by the New York State Board of Social Welfare, and operated pursuant to and meeting any additional construction requirements of Section 374-C of the New York State Social Services Law and applicable regulations of the New York State Department of Social Services. Such a facility occupied by more than 12 children shall be classified as Group I-1.

GROUT. A plastic mixture of cementitious materials, aggregates, and water, with or without admixtures, initially produced to pouring consistency without segregation of the constituents during placement, or the equivalent of such mixtures, conforming to ASTM C 476.

GUARD. A building component or a system of building components located at or near the open sides of elevated walking surfaces that minimizes the possibility of a fall from the walking surface to a lower level.

GUARDRAIL SYSTEM (SCAFFOLD). A vertical barrier as described in Section 3314.8 consisting of, but not limited to, toprails, midrails and posts, erected to prevent falling from a scaffold platform or walkway to lower levels.

GUY. A rope used to steady or secure the mast or other members in the desired position.

GYPSUM BOARD. Gypsum wallboard, gypsum sheathing, gypsum base for gypsum veneer plaster, exterior gypsum soffit board, predecorated gypsum board or water-resistant gypsum backing board complying with the standards listed in Tables 2506.2, 2507.2 and Chapter 35.

GYPSUM PANEL PRODUCTS. The general name for a family of sheet products consisting essentially of gypsum.

GYPSUM PLASTER. A mixture of calcined gypsum or calcined gypsum and lime and aggregate and other approved materials as specific in this code.

GYPSUM VENEER PLASTER. Gypsum plaster applied to an approved base in one or more coats normally not exceeding 1/4 inch (6.4 mm) in total thickness.

HABITABLE SPACE. All rooms and spaces within a dwelling unit in Group R or I-1, including bedrooms, living rooms, studies, recreation rooms, kitchens, dining rooms and other similar spaces.

Exception: The following spaces within a dwelling unit shall not be considered habitable space:

1.	A dining space 55 square feet (5.1 m2) or less located off a living room, foyer or kitchen;

2.	A kitchenette;

3.	A bathroom or toilet room;

4.	A laundry room; and

5.	A corridor, passageway, or private hall; and a foyer used as an entrance hall in a dwelling unit: not exceeding 10 percent of the total floor area of the dwelling unit; or not exceeding 20 percent of the floor area of the dwelling unit where every habitable room is at least 20 percent larger than the required minimum room sizes established by the New York City Housing Maintenance Code.

HALL CALL CONSOLE. A collection of features arranged in close proximity to one another, the purpose of which is to call a destination-oriented elevator car to an elevator landing on which the console is provided. Such features can be provided as a single assembly or as individual elements functioning together.

HALOGENATED EXTINGUISHING SYSTEM. A fire-extinguishing system using one or more atoms of an element from the halogen chemical series; fluorine, chlorine, bromine and iodine.

HANDHELD DEVICE (DEMOLITION). Equipment, mechanical or non-mechanical, utilized to physically demolish a building or structure, or elements of a building or structure, that is held, lifted, moved, and operated by a single person. A handheld device shall also include any item accessory to such equipment, including but not limited to a compressor, regardless of if such accessory item is held, lifted, moved, and operated by a single person. A handheld device does not include remote controlled equipment.

HANDLING. The movement of a material in its container, the removal of the material from its container, or any other action or process that may affect the material, other than its storage or use.

HANDRAIL. A horizontal or sloping rail intended for grasping by the hand for guidance or support.

HARDBOARD. A fibrous-felted, homogeneous panel made from lignocellulosic fibers consolidated under heat and pressure in a hot press to a density not less than 31 pcf (497 kg/m3).

HAZARDOUS MATERIALS. Those chemicals or substances that are physical hazards or health hazards as defined and classified in the New York City Fire Code and this code, whether the materials are in usable or waste condition.

HAZARDOUS PRODUCTION MATERIAL (HPM). A solid, liquid or gas associated with semiconductor manufacturing that has a degree-of-hazard rating in health, flammability or instability of Class 3 or 4 as defined in NFPA 704 and that is used directly in research, laboratory or production processes that have as their end product materials that are not hazardous.

HEAD JOINT. Vertical mortar joint placed between masonry units within the wythe at the time the masonry units are laid.

HEALTH HAZARD. A classification of a chemical for which there is statistically significant evidence that acute or chronic health effects are capable of occurring in exposed persons. The term "health hazard" includes chemicals that are toxic or highly toxic, and corrosive.

HEAVY DUTY SCAFFOLD. A supported scaffold capable of supporting loads of up to 75 pounds per square foot (366.15 kg/m2), and not more than those imposed by workers and heavy material, including but not limited to stone.

HEAVY DUTY SIDEWALK SHED. A sidewalk shed designed to carry a live load of at least 300 pounds per square foot (1465 kg/m2).

HEIGHT, BUILDING. The vertical distance from the grade plane to the average height of the highest roof surfaces.

HELICAL PILES. Helical piles are manufactured deep foundation steel elements consisting of a shaft and one or more helical bearing plates (helices) screwed into the ground by application of torque on the shaft. The various products marketed as screw piles, torque anchors, and helical piles are considered helical piles.

HELIPAD. A structural surface that is used for the landing, taking off, taxiing and parking of helicopters.

HELIPORT. An area of land or water or a structural surface that is used, or intended for the use, for the landing and taking off of helicopters, and any appurtenant areas that are used, or intended for use, for heliport buildings or other heliport facilities.

HELISTOP. The same as "heliport," except that no fueling, defueling, maintenance, repairs or storage of helicopters is permitted.

HIGHLY TOXIC MATERIAL. A chemical that is lethal at the following doses or concentrations:

1.	A chemical that has a median lethal dose (LD50) of 50 milligrams or less per kilogram of body weight when administered orally to albino rats weighing between 200 and 300 grams each;

2.	A chemical that has a median lethal dose (LD50) of 200 milligrams or less per kilogram of body weight when administered by continuous contact for 24 hours (or less if death occurs within 24 hours) with the bare skin of albino rabbits weighing between 2 and 3 kilograms each; or

3.	A chemical that has a median lethal concentration (LC50) in air of 200 parts per million by volume or less of gas or vapor, or 2 milligrams per liter or less of mist, fume or dust, when administered by continuous inhalation for 1 hour (or less if death occurs within 1 hour) to albino rats weighing between 200 and 300 grams each.

HIGH-PRESSURE DECORATIVE EXTERIOR-GRADE COMPACT LAMINATE (HPL). An exterior wall covering fabricated using HPL in a specific assembly including joints, seams, attachments, substrate, framing and other details as appropriate to a particular design.

HISTORIC STRUCTURE. A building or structure which is a designated New York City landmark or interior landmark, is located within a designated New York City historic district, or is listed on the New York State or National Register of Historic Places.

HISTORIC STRUCTURE (FLOOD-RESISTANT CONSTRUCTION). See Section G201.1.2.

HOISTING EQUIPMENT. Power or manually operated equipment that raises or lowers a suspended load. The definition of hoisting equipment shall also include a hoisting machine, bucket hoist, material hoist, personnel hoist, or industrial rope access equipment. The definition of hoisting equipment shall not include an elevator, mast climber, or scaffold.

HOISTING MACHINE. A power operated machine that lifts or lowers a suspended load utilizing a drum and a rope. The definition of hoisting machine shall also include a crane, derrick, cableway, or telehandler. The definition of hoisting machine shall not include an elevator, mast climber, or scaffold.

HOISTING MECHANISM. A hoist drum and rope reeving system used for lifting and lowering loads.

HOISTWAY. The hoistway is the opening through a building or structure for the travel of elevators, dumbwaiters, or material lifts, extending from the pit floor to the roof or floor above.

HOLD-DOWN. See “TIE-DOWN”.

HORIZONTAL ASSEMBLY. A fire-resistance-rated floor or roof assembly of materials designed to restrict the spread of fire in which continuity of the fire-resistance rating is maintained.

HOSPITALS ANDPSYCHIATRIC CENTERS. See Section 308.2.

HOUSING UNIT. See Section 408.1.1.

H-PILES. Steel H-piles are constructed by driving a steel H-shaped section into the ground.

HPM FLAMMABLE LIQUID. An HPM liquid that is defined as either a Class I flammable liquid or a Class II or Class IIIA combustible liquid.

HPM ROOM. A room used in conjunction with or serving a Group H-5 occupancy, where HPM is stored or used and that is classified as a Group H-2, H-3 or H-4 occupancy.

HURRICANE-PRONE REGIONS. New York City is within the hurricane-prone region for Risk Category II, III, and IV buildings.

HYDROGEN FUEL GAS ROOM. A separately ventilated, fully enclosed room designed to exclusively house the generation of gaseous hydrogen for immediate on-premises use in indoor fuel cells or other energy production process, and incidental indoor storage of gaseous hydrogen. A hydrogen fuel gas room is not intended to house the production or dispensing of hydrogen motor fuel.

I-4 MIX. A type of heavy duty asphaltic concrete mix containing 0.75 inch (19 mm) nominal maximum size aggregate with 25 percent to 50 percent of the aggregate capable of passing through a No. 8 sieve and in which all sand contained in the mix is crushed.

ICE-SENSITIVE STRUCTURE. A structure for which the effect of an atmospheric ice load governs the design of a structure or portion thereof. This includes, but is not limited to, lattice structures, guyed masts, overhead lines, light suspension and cable-stayed bridges, aerial cable systems (e.g., for ski lifts or logging operations), amusement rides, open catwalks and platforms, flagpoles and signs.

IMMEDIATELY DANGEROUS TO LIFE AND HEALTH (IDLH). The concentration of air-borne contaminants that poses a threat of death, immediate or delayed permanent adverse health effects, or effects that could prevent escape from such an environment as established by the National Institute of Occupational Safety and Health (NIOSH) based on both toxicity and flammability. It generally is expressed in parts per million by volume (ppm v/v) or milligrams per cubic meter (mg/m3). If adequate data do not exist for precise establishment of IDLH concentrations, an independent certified industrial hygienist, industrial toxicologist, appropriate regulatory agency or other source approved by the Fire Commissioner shall make such determination.

IMPACT LOAD. The load resulting from moving machinery, elevators, craneways, vehicles and other similar forces and kinetic loads, pressure and possible surcharge from fixed of moving loads.

IMPORTANCE FACTOR, I. A factor that accounts for the degree of hazard to human life and damage to property.

INCAPABLE OF SELF-PRESERVATION. Persons who, because of age, physical limitations, mental limitations, chemical dependency or medical treatment, cannot respond as an individual to an emergency situation.

INCIDENT. An occurrence directly caused by construction or demolition activity or site conditions that result in one or more of the following:

- A fatality to a member of the public;

- Any type of injury to a member of the public;

- A fatality to a worker;

- An injury to a worker that requires transport by emergency medical services or requires immediate emergency care at a hospital or offsite medical clinic;

- Any complete or partial structural collapse or material failure;

- Any complete or partial collapse or failure of pedestrian protection, scaffolding, hoisting equipment, or material handling equipment; or

- Any material fall exterior to the building or structure.

INCOMPATIBLE MATERIALS. Materials that, if mixed or combined, could explode, generate heat, gases or other byproducts, or react in such a way that are hazardous to life or property.

INDUSTRIAL ROPE ACCESS. The use of rope access equipment in which a person descends or ascends on a rope, or traverses along a rope, and in which the ropes are used as the primary means of support and positioning. Industrial rope access does not include window washing.

INERT GAS. A gas that is capable of reacting with other materials only under abnormal conditions such as high temperatures, pressures and similar extrinsic physical forces. Within the context of the code, inert gases do not exhibit either physical or health properties as defined (other than acting as a simple asphyxiant) or hazard properties other than those of a compressed gas. Some of the more common inert gases include argon, helium, krypton, neon, nitrogen and xenon.

INITIATING DEVICE. A system component that originates transmission of a change-of-state condition, such as in a smoke detector, manual fire alarm box or supervisory switch.

INSTALLING/INSTALLATION/INSTALL (SCAFFOLD). The initial installation or reinstallation of a scaffold at a site.

Initial installation (scaffold). The initial assembly, set-up, or placement of a scaffold at a site.

Reinstallation (scaffold). The addition, relocation, or removal of any part, component, or attachment to a scaffold at a site, including but not limited to counterweights, tie-backs, anchorages, or connections to the building or structure, that occurs subsequent to the initial installation, and which does not otherwise occur in an automated, automatic fashion, as part of the normal use of the scaffold.

INTENDED TO BE OCCUPIED AS A RESIDENCE. This refers to a dwelling unit or sleeping unit that can or will be used all or part of the time as the occupant’s place of abode.

INTERIOR EXIT RAMP. An exit component that serves to meet one or more means of egress design requirements, such as required number of exits or exit access travel distance, and provides for a protected path of egress travel to the exit discharge or public way.

INTERIOR EXIT STAIRWAY. A stairway not meeting the definition of an exterior exit stairway.

INTERIOR FINISH. Interior finish includes interior wall and ceiling finish and interior floor finish.

INTERIOR FLOOR FINISH. The exposed floor surfaces of buildings including coverings applied over a finished floor or stair, including risers.

INTERIOR FLOOR-WALL BASE. Interior floor finish trim used to provide a functional or decorative border at the intersection of walls and floors.

INTERIOR SURFACES. Surfaces other than weather-exposed surfaces.

INTERIOR WALL AND CEILING FINISH. The exposed interior surfaces of buildings including, but not limited to: fixed or movable walls and partitions; toilet room privacy partitions; columns; ceilings; and interior wainscoting, paneling or other finish applied structurally or for decoration, acoustical correction, surface insulation, structural fire resistance or similar purposes, but not including trim.

INTERLAYMENT. A layer of felt or nonbituminous saturated felt not less than 18 inches (457 mm) wide, shingled between each course of a wood-shake roof covering.

INTUMESCENT FIRE-RESISTANT COATINGS. Thin film liquid mixture applied to substrates which expands into a protective foamed layer to provide fire-resistant protection of the substrates when exposed to flame or intense heat.

JIB. An extension attached to the boom point to provide added boom length for lifting specified loads. The jib may be in line with the boom or offset to various angles in the vertical plane of the boom.

JOINT. The opening in or between adjacent assemblies that is created due to building tolerances, or is designed to allow independent movement of the building in any plane caused by thermal, seismic, wind or any other loading.

JUMP (JUMPING or CLIMBING). The raising or lowering of a tower crane to a new working height. This can include, but is not limited to, the process of adding or removing mast or tower sections to equipment that has already been erected.

KEY ELEMENT. An element of the structural system, including its connections, that meets one or more of the following criteria:

1.	An element which when lost, results in more than local collapse.

2.	An element that braces a key element, the failure of which results in failure of the key element (further secondary elements need not be considered key elements).

3.	An element whose tributary area exceeds 3,000 square feet (279 m2) on a single level.

KITCHEN. A room with 80 square feet (7.4 m2) or more of floor area that is intended, arranged, designed or used for cooking or warming of food.

KITCHENETTE. A space with less than 80 square feet (7.4 m2) of floor area that is intended, arranged, designed or used for cooking or warming of food.

L RATING. The air leakage rating of a through-penetration firestop system or a fire-resistant joint system when tested in accordance with UL 1479 or UL 2079, respectively.

LABORATORY BUILDING. See Section 427.4.

LABORATORY CHEMICAL. See Section 427.4.

LABORATORY, NONPRODUCTION. See Section 427.4.

LABORATORY UNIT. See Section 427.4.

LAYERED (SOIL). Two or more distinctly different soil or rock types arranged in layers. Micaceous seams or weakened planes in rock or shale are considered layered.

LETTER OF MAP AMENDMENT (LOMA). See Section G201.1.2.

LETTER OF MAP REVISION BASED ON FILL (LOMR-F). See Section G201.1.2.

LETTER OF MAP REVISION (LOMR). See Section G201.1.2.

LIGHT DUTY SCAFFOLD. A supported scaffold capable of supporting loads of up to 25 pounds per square foot (122.05 kg/m2), and not more than those imposed by workers and lightweight material, including but not limited to wood or paint.

LIGHT DUTY SIDEWALK SHED. A sidewalk shed designed to carry a live load of at least 150 pounds per square foot (732.3 kg/m2).

LIGHT-DIFFUSING SYSTEM. Construction consisting in whole or in part of lenses, panels, grids or baffles made with light-transmitting plastics positioned below independently mounted electrical light sources, skylights or light-transmitting plastic roof panels. Lenses, panels, grids and baffles that are part of an electrical fixture shall not be considered as a light-diffusing system.

LIGHT-TRANSMITTING PLASTIC ROOF PANELS. Structural plastic panels other than skylights that are fastened to structural members, or panels or sheathing, and that are used as light-transmitting media in the plane of the roof.

LIGHT-TRANSMITTING PLASTIC WALL PANELS. Plastic materials that are fastened to structural members, or to structural panels or sheathing, and that are used as light-transmitting media in exterior walls.

LIMIT STATE. A condition beyond which a structure or member becomes unfit for service and is judged to be no longer useful for its intended function (serviceability limit state) or to be unsafe (strength limit state).

LIMITED AREA SPRINKLER SYSTEM. An automatic sprinkler system serving fewer than 6 sprinkler heads on any single connection.

LIMITED SITE SAFETY TRAINING (SST) CARD. A card that is issued before the SST full compliance date, in a form and manner established by the department and that satisfies each of the following conditions:

1.	Such card is issued by an SST provider to a person who submits an application to such provider demonstrating, in a form and manner established by the department, that such applicant satisfies the requirements of Item 1.1, 1.2 or 1.3:

1.1.	Such applicant has successfully completed (i) an OSHA 10-hour class and (ii) 20 additional SST credits specified by the department, including eight SST credits relating to safeguarding against the dangers posed by falling workers and objects.

1.2.	Such applicant has successfully completed an OSHA 30-hour class.

1.3.	Such applicant has successfully completed a 100-hour training program.

2.	If such applicant completed the training to comply with Item 1.1, 1.2 or 1.3 but did not complete such training within the five years preceding submission of such application, such applicant has, in the one-year period preceding submission of such application, completed at least eight SST credits specified by the department.

3.	Such card is issued by an SST provider who does not require applicants to submit any information except for (i) the information necessary to establish that the requirements in Item 1 have been satisfied, as specified by the department, (ii) a photograph of the applicant and (iii) such additional information as the department may allow by rule.

4.	Such card expires on the day before the SST full compliance date and is not renewable.

LIQUEFACTION. For granular soils, liquefaction is defined as the loss of shear strength in soils resulting from increased pore-water pressure and reduced effective stress that may develop as a result of cyclic loading during earthquakes. For cohesive soils with a plasticity index of less than 20, liquefaction is defined as any transient softening and increased cyclic shear strains that may occur during earthquakes.

LIQUID. A material that has a melting point that is equal to or less than 68°F (20°C) and a boiling point that is greater than 68°F (20°C) at 14.7 pounds per square inch absolute (psia) (101 kPa). When not otherwise identified, the term "liquid" includes both flammable and combustible liquids.

LIQUID STORAGE ROOM. A room classified as Group H-3 occupancy used for the storage of flammable or combustible liquids in an unopened condition.

LIQUID USE, DISPENSING AND MIXING ROOM. A room in which Class I, II and IIIA flammable or combustible liquids are used, dispensed or mixed in open containers.

LIVE LOAD. A load produced by the use and occupancy of the building or other structure and do not include construction or environmental loads such as wind load, snow load, rain load, earthquake load, flood load or dead load.

LIVE LOAD (ROOF). A load on a roof produced:

1.	During maintenance by workers, equipment and materials;

2.	During the life of the structure by movable objects such as planters or other small decorative appurtenances that are not occupancy related; or

3.	By the use and occupancy of the roof such as for roof gardens or assembly areas.

LOAD AND RESISTANCE FACTOR DESIGN (LRFD). A method of proportioning structural members and their connections using load and resistance factors such that no applicable limit state is reached when the structure is subjected to appropriate load combinations. The term "LRFD" is used in the design of steel and wood structures.

LOAD BLOCK, LOWER. The assembly of hook or shackle, swivel, sheaves, pins, and frame suspended by the hoisting ropes.

LOAD BLOCK, UPPER. The assembly of shackle, swivel, sheaves, pins, and frame suspended from the boom point.

LOAD EFFECTS. Forces and deformations produced in structural members by the applied loads.

LOAD FACTOR. A factor that accounts for deviations of the actual load from the nominal load; for uncertainties in the analysis that transforms the load into a loud effect, and for the probability that more than one extreme load will occur simultaneously.

LOAD RATING CHART. A full and complete range of manufacturer’s load ratings at all stated operating radii, boom angles, work areas, boom lengths and configurations, jib lengths and angles (or offset), as well as alternative ratings for use and nonuse of optional equipment, such as outriggers and extra counterweights, that affect ratings.

LOAD RATINGS. Crane and derrick ratings in pounds (kilograms) established by the manufacturer in accordance with standards set forth in rules promulgated by the commissioner.

LOAD (WORKING). The external load, in pounds (kilograms), applied to the crane or derrick, including the weight or auxiliary load attaching equipment, such as lower load blocks, shackles, and slings.

LOADS. Forces or other actions that result from the weight of building materials, occupants and their possessions, environmental effects, differential movement and restrained dimensional changes. Permanent loads are those loads in which variations over time are rare or of small magnitude, such as dead loads. All other loads are variable loads (see also "Nominal loads").

LOCAL COLLAPSE. Failure of a structural element that results in the collapse of areas being directly supported by that element and not extending vertically more than three stories.

LOW ENERGY POWER-OPERATED DOOR. Swinging door that opens automatically upon an action by a pedestrian such as pressing a push plate or waving a hand in front of a sensor. The door closes automatically, and operates with decreased forces and decreased speeds (See "Power-assisted door" and "Power-operated door").

LOWER FLAMMABLE LIMIT (LFL). The minimum concentration of vapor in air at which propagation of flame will occur in the presence of an ignition source. The LFL is sometimes referred to as "LEL" or "lower explosive limit."

LOWEST FLOOR. The lowest floor of the lowest enclosed area, including crawl spaces and basements (for flood zone purposes).The lowest floor shall not include any wet floodproofed spaces usable solely for vehicle parking, building access, storage or crawl space, provided that such enclosure is not built so as to render the structure in violation of Appendix G, including that:

- Such enclosure shall allow for the automatic entry and exit of floodwaters;

- Such enclosure shall be constructed solely of flood-resistant materials and finishes;

- Such enclosure shall have a floor elevation equal to or higher than the outside adjacent grade on at least one side; and

- Such outside adjacent grade shall slope down, towards the source of flooding, providing positive drainage by gravity, thus preventing accumulations of water under or in the structure after the floodwaters recede without the use of pumps, pipes or drains.

MAILBOXES. Receptacles for the receipt of documents, packages or other deliverable matter. Mailboxes include, but are not limited to, post office boxes and receptacles provided by commercial mail-receiving agencies, apartment houses and schools.

MAIN WIND FORCE-RESISTING SYSTEM. An assemblage of structural elements assigned to provide support and stability for the overall structure. The system generally receives wind loading from more than one surface.

MAINTENANCE (SCAFFOLD). Regular or periodic upkeep as specified by the manufacturer to keep the scaffold, including all parts or components, in like new condition and safe working order, and that does not otherwise meet the definition of an installation, removal, or repair.

MAJOR BUILDING. An existing or proposed building 10 or more stories or 125 feet (38 100 mm) or more in height, or an existing or proposed building with a building footprint of 100,000 square feet (30 480 m2) or more regardless of height, or an existing or proposed building so designated by the commissioner due to unique hazards associated with the construction or demolition of the structure.

MANUAL FIRE ALARM BOX. A manually operated device used to initiate an alarm signal.

MANUFACTURE DATE (Crane). For a particular crane, the earlier of the following dates:

1.	The date the crane was originally manufactured for its intended purpose.

2.	The date that the oldest major component of the crane was originally manufactured.

MANUFACTURED HOME. See Section G201.1.2.

MANUFACTURED HOME PARK OR SUBDIVISION. See Section G201.1.2.

MARKET VALUE OF STRUCTURE. See Section G201.1.2.

MASONRY. A built-up construction or combination of building units or materials of clay, shale, concrete, glass, gypsum, stone or other approved units bonded together with or without mortar or grout or other accepted methods of joining.

Glass unit masonry. Masonry composed of glass units bonded by mortar.

Plain masonry. Masonry in which the tensile resistance of the masonry is taken into consideration and the effects of stresses in reinforcement are neglected.

Reinforced masonry. Masonry construction in which reinforcement acting in conjunction with the masonry is used to resist forces.

Solid masonry. Masonry consisting of solid masonry units laid contiguously with the joints between the units filled with mortar.

Unreinforced (plain) masonry. Masonry in which the tensile resistance of masonry is taken into consideration and the resistance of the reinforcing steel, if present, is neglected.

MASONRY UNIT. Brick, tile, stone, glass block or concrete block conforming to the requirements specified in Section 2103.

Hollow. A masonry unit whose net cross-sectional area in any plane parallel to the load-bearing surface is less than 75 percent of its gross cross-sectional area measured in the same plane.

Solid. A masonry unit whose net cross-sectional area in every plane parallel to the load-bearing surface is 75 percent of more of its gross cross-sectional area measured in the same plane.

MASS CONCRETE. Any volume of concrete with dimensions large enough to require that measures be taken to cope with generation of heat from hydration of the cement and attendant volume change to minimize cracking, reduction of compressive strength, and/or delayed ettringite formation.

MAST CLIMBER. A powered device consisting of an elevating platform mounted on a base or chassis and mast, that when erected is capable of supporting personnel, material, equipment and tools on a deck or platform that is capable of traveling vertically in infinitely adjustable increments to reach the desired work level.

MASTIC FIRE-RESISTANT COATINGS. Liquid mixture applied to a substrate by brush, roller, spray or trowel that provides fire-resistant protection of a substrate when exposed to flame or intense heat.

MATERIAL HANDLING EQUIPMENT. Power or manually operated equipment that moves or transports material or personnel during the construction or demolition of a building or structure. Material handling equipment shall not include an elevator, hoisting equipment, mast climber, or scaffold.

MATERIAL HOIST (MATERIAL HOISTING EQUIPMENT). A power or manually operated platform, car, or cage, that (i) is temporarily installed at a construction or demolition site, (ii) moves vertically on guide members to raise or lower material, and (iii) is controlled from a point outside the conveyance.

MAXIMUM CONSIDERED EARTHQUAKE GEOMETRIC MEAN (MCEG) PEAK GROUND ACCELERATION. The most severe earthquake effects considered by this standard determined for geometric mean peak ground acceleration and without adjustment for targeted risk. The MCEG peak ground acceleration adjusted for site effects (PGAM) is used in this standard for evaluation of liquefaction, lateral spreading, seismic settlements, and other soil-related issues. The PGAM values adjusted for site effects are provided in Table 1816.2.1 or can be derived from the site-specific procedures provided in Section 21.5 of ASCE 7.

MAXIMUM CONSIDERED EARTHQUAKE (MCE) GROUND MOTION. The most severe earthquake effects considered by this code more specifically defined in the terms, maximum considered earthquake geometric mean (MCEG) peak ground acceleration and risk-targeted maximum considered earthquake (MCER) ground motion response acceleration.

MEAN ROOF HEIGHT. The average of the roof eave height and the height to the highest point on the roof surface, except that eave height shall be used for roof angle of less than or equal to 10 degrees (0. 1745 rad).

MEANS OF EGRESS. A continuous and unobstructed path of vertical and horizontal egress travel from any occupied portion of a building or structure to a public way. A means of egress consists of three separate and distinct parts: the exit access, the exit and the exit discharge.

MECHANICAL-ACCESS OPEN PARKING GARAGE. Open parking garages employing parking machines, lifts, elevators or other mechanical devise for vehicles moving from and to street level and in which public occupancy is prohibited above the street level.

MECHANICAL DEMOLITION EQUIPMENT. Mechanically driven or powered equipment that is utilized to physically demolish a building or structure, or elements of a building or structure, either within or exterior to the building or structure, or that is utilized to move debris or material within the building or structure. Mechanical demolition equipment shall not include mechanically driven or powered equipment that is utilized to move debris or material outside of the building or structure.

MECHANICAL EQUIPMENT SCREEN. A partially enclosed rooftop structure used to aesthetically conceal heating, ventilating and air conditioning (HVAC) electrical or mechanical equipment from view.

MECHANICAL SYSTEMS (STRUCTURAL). For the purposes of determining seismic loads in this code, mechanical systems shall also include fire protection, plumbing and fuel gas systems as specified therein.

MEDIUM DUTY SCAFFOLD. A supported scaffold capable of supporting loads of up to 50 pounds per square foot (244.1 kg/m2), and not more than those imposed by workers and moderate material, including but not limited to brick and pipe.

MEMBRANE PENETRATION. A breach in one side of a floor-ceiling, roof-ceiling or wall assembly to accommodate an item installed into or passing through the breach.

MEMBRANE-COVERED CABLE STRUCTURE. A nonpressurized structure in which a mast and cable system provides support and tension to the membrane weather barrier and the membrane imparts stability to the structure.

MEMBRANE-COVERED FRAME STRUCTURE. A nonpressurized building wherein the structure is composed of a rigid framework to support a tensioned membrane that provides the weather barrier.

MEMBRANE-PENETRATION FIRESTOP. A material, device, or assemblage of specific materials or products that is designed, tested and fire-resistance rated to resist for a prescribed time period the passage of flame and heat through openings in a protective membrane in order to accommodate cables, cable trays, conduit, tubing, piping or similar items.

MEMBRANE-PENETRATION FIRESTOP SYSTEM. An assemblage consisting of a fire-resistance-rated floor-ceiling, roof-ceiling or wall assembly, one or more penetrating items installed into or passing through the breach in one side of the assembly and the materials or devices, or both, installed to resist the spread of fire into the assembly for a prescribed period of time.

MERCHANDISE PAD. A merchandise pad is an area for display of merchandise surrounded by aisles, permanent fixtures or walls. Merchandise pads contain elements such as nonfixed and moveable fixtures, cases, racks, counters and partitions from which customers browse or shop.

METAL COMPOSITE MATERIAL (MCM). A factory-manufactured panel consisting of metal skins bonded to both faces of a plastic core.

METAL COMPOSITE MATERIAL (MCM) SYSTEM. An exterior wall covering fabricated using MCM in a specific assembly including joints, seams, attachments, substrate, framing and other details as appropriate to a particular design.

METAL ROOF PANEL. An interlocking metal sheet having a minimum installed weather exposure of 3 square feet (.279 m2) per sheet.

METAL ROOF SHINGLE. An interlocking metal sheet having an installed weather exposure less than 3 square feet (.279 m2) per sheet.

MEZZANINE. An intermediate level or levels between the floor and ceiling of any story in accordance with Section 505.

MICROPILE. A micropile is a drilled and grouted deep foundation element with a diameter that measures 5-inches (127 mm) to 14-inches (356 mm) that develops its load-carrying capacity by means of a bond zone in soil (also commonly known as a minipile).

MINERAL BOARD. A rigid felted thermal insulation board consisting of either felted mineral fiber or cellular beads of expanded aggregate formed into flat rectangular units.

MINERAL FIBER. Insulation composed principally of fibers manufactured from rock, slag or glass, with to without binders.

MINERAL WOOL. Synthetic vitreous fiber insulation made by melting predominantly igneous rock or furnace slag, and other inorganic materials, and then physically forming the melt into fibers.

MINOR ALTERATIONS. See Section 105.4.2 of the Administrative Code.

MOBILE CRANE. A crane equipped with rubber-tired wheels or crawler treads for travel. The definition of mobile crane shall include, but is not limited, to a commercial truck mounted crane, crawler crane, wheel mounted crane (multiple control stations) or wheel mounted crane (single control station). The definition of mobile crane shall not include a truck mounted crane or a self-erecting tower crane.

MOBILE SCAFFOLD. A powered or unpowered, portable, caster, track or wheel-mounted supported scaffold.

MODIFIED BITUMEN ROOF COVERING. One or more layers of polymer-modified asphalt sheets. The sheet materials shall be fully adhered or mechanically attached to the substrate or held in place with an approved ballast layer.

MOIST (SOIL). A condition in which a soil looks and feels damp. Moist cohesive soil can easily be shaped into a ball and rolled into small diameter threads before crumbling. Moist granular soil that contains some cohesive material will exhibit signs of cohesion between particles.

MONOPOLE SIGN. A ground sign wholly supported by a single pole structure.

MORTAR. A mixture consisting of cementitious materials, fine aggregates, water, with or without admixtures, that is used to construct unit masonry assemblies.

MORTAR, SURFACE-BONDING. A mixture to bond concrete masonry units that contains hydraulic cement, glass fiber reinforcement with or without inorganic fillers or organic modifiers and water.

MULTILEVEL ASSEMBLY SEATING. Seating that is arranged in distinct levels where each level is comprised of either multiple rows, or single row of box seats accessed from a separate level.

MULTIPLE-STATION ALARM DEVICE. Two or more single-station alarm devices that can be interconnected such that actuation of one causes all integral or separate audible alarms to operate. A multiple-station alarm device can consist of one single-station alarm device having connections to other detectors or to a manual fire alarm box.

MULTIPLE-STATION SMOKE ALARM. Two or more single-station alarm devices that are capable of interconnection such that actuation of one causes the appropriate alarm signal to operate in all interconnected alarms and not connected to a fire alarm system.

MULTIPOINT ADJUSTABLE SUSPENDED SCAFFOLD. A suspended scaffold consisting of a platform(s) that is suspended by more than two ropes from overhead supports and equipped with a means to raise and lower the platform to the desired work levels.

MULTISTORY UNIT. A dwelling unit or sleeping unit with habitable space located on more than one story.

NAILING, BOUNDARY. A special nailing pattern required by design at the boundaries of diaphragms.

NAILING, EDGE. A special nailing pattern required by design at the edges of each panel within the assembly of a diaphragm or shear wall.

NAILING, FIELD. Nailing required between the sheathing panels and framing members at locations other than boundary nailing and edge nailing.

NATIONAL GEODETIC VERTICAL DATUM (NGVD). The national vertical datum standard established in 1929; used as a reference for establishing elevations within a floodplain.

NATURALLY DURABLE WOOD. The heartwood of the following species except for the occasional piece with corner sapwood, provided 90 percent or more of the width of each side on which it occurs is heartwood:

Decay resistant. Redwood, cedar, black locust and black walnut.

Termite resistant. Redwood, Alaska yellow cedar, Eastern red cedar and Western red cedar.

NEW CONSTRUCTION. See Section G201.1.2.

NOMINAL LOADS. The magnitudes of the loads specified in Chapter 16 (dead, live, soil, wind, snow, rain, flood and earthquake).

NOMINAL SIZE (LUMBER). The commercial size designation of width and depth, in standard sawn lumber and glued-laminated lumber grades; somewhat larger than the standard net size of dressed lumber, in accordance with DOC PS 20 for sawn lumber and with the ANSI/AWC NDS for glued-laminated lumber.

NONCOMBUSTIBLE MEMBRANE STRUCTURE. A membrane structure in which the membrane and all component parts of the structure are noncombustible.

NONRESIDENTIAL (FOR FLOOD ZONE PURPOSES). A building or structure that either:

1.	Contains no space classified in Group I-1, R-1, R-2, or R-3, and contains no space that is accessory, as such term is defined in the New York City Zoning Resolution, to any Group I-1, R-1, R-2, or R-3 occupancy; or

2.	Contains such space(s), but also contains space at or below the DFE that is not accessory, as such term is defined in the New York City Zoning Resolution, to a Group I-1, R-1, R-2, or R-3 occupancy.

NORMAL TEMPERATURE AND PRESSURE (NTP). A temperature of 70°F (21°C) and a pressure of 1 atmosphere (14.7 psia (101 kPa)).

NORTH AMERICAN VERTICAL DATUM (NAVD). The national vertical datum standard established in 1988, used as a reference for establishing elevations within a floodplain.

NOSING. The leading edge of treads of stairs and of landings at the top of stairway flights.

NOTATIONS. For Chapter 16, see Section 1602.1.

NOTATIONS. For Chapter 21, see Section 2102.1.

NOTIFICATION ZONE. See "Zone, notification."

NURSING HOMES. See Section 308.2.2.

OCCUPANT LOAD. The number of persons for which the means of egress of a building or portion thereof is designed.

OCCUPIABLE SPACE. A room or enclosed space, other than a habitable space, designed for human occupancy or use in which individuals may remain for a period of time for rest, amusement, treatment, education, dining, shopping, employment, labor or other similar purposes.

OPEN-ENDED CORRIDOR. An interior corridor that is open on each end and connects to an exterior stairway or ramp at each end with no intervening doors or separation from the corridor.

OPEN EXTERIOR SPACE. See Section 1002.1.2.

OPEN PARKING GARAGE. A structure or portion of a structure with the openings as described in Section 406.5.2 that is used for the parking or storage of private motor vehicles as described in Section 406.5.3.

OPEN PARKING LOT. An exterior space with surfacing at grade used for the storage or sale of more than four motor vehicles, including but not limited to parking lots, motor vehicles sales lots, and accessory open parking spaces.

OPEN SYSTEM. The use of a solid or liquid hazardous material in equipment or a vessel or system that remains open during normal operation such that vapors are emitted during the operation of such equipment, vessel or system and the material is exposed to the atmosphere during such operation. Examples of open systems for solids and liquids include dispensing from or into open beakers or containers, dip tank and plating tank operations.

ORDINARY REPAIRS. See Section 105.4.2 of the Administrative Code.

ORGANIC PEROXIDE. An organic compound having a double oxygen or peroxy (-O-O-) in its chemical structure. Organic peroxides can present an explosion hazard (detonation or deflagration), can be shock sensitive, or can be susceptible to decomposition into various unstable compounds over an extended period of time and are classified as follows based upon their hazardous properties:

Class I. Organic peroxides that are capable of deflagration but not detonation.

Class II. Organic peroxides that burn very rapidly and that pose a moderate reactivity hazard.

Class III. Organic peroxides that burn rapidly and that pose a moderate reactivity hazard.

Class IV. Organic peroxides that burn in the same manner as ordinary combustibles and that pose a minimal reactivity hazard.

Class V. Organic peroxides that burn with less intensity than ordinary combustibles or do not sustain combustion and that pose no reactivity hazard.

Unclassified detonable. Organic peroxides that are capable of detonation and pose an extremely high explosion hazard through rapid explosive decomposition.

ORTHOGONAL. To be in two horizontal directions, at 90 degrees (1.57 rad) to each other.

OSHA. The United States Department of Labor Occupational Safety and Health Administration.

OSHA 10-HOUR CLASS. A class that includes 10 or more hours in construction industry safety and health that is intended for workers and satisfies the following conditions:

1.	Such class is (i) approved by OSHA and conducted in accordance with the OSHA outreach training program or (ii) an equivalent 10 or more hour class approved by the department.

2.	Such class consists of in-person training, actively proctored online training or, if such training is conducted before the effective date of the local law that added this definition, online training.

OSHA 30-HOUR CLASS. A class that includes 30 or more hours in construction industry safety and health that is intended for supervisors and satisfies the following conditions:

1.	Such class is (i) approved by OSHA and conducted in accordance with the OSHA outreach training program or (ii) an equivalent 30 or more hour class approved by the department.

2.	Such class consists of in-person training, actively proctored online training or, if such training is conducted before the effective date of the local law that added this definition, online training.

OTHER STRUCTURES. Structures, other than buildings, for which loads are specified in Chapter 16.

OUTRIGGER (CRANE). Extendable or fixed members attached to the mounting base that rest on supports at the outer ends used to support the crane.

OUTRIGGER (SCAFFOLD). The structural member of a supported scaffold used to increase the base width of a scaffold in order to provide support for and increased stability of the scaffold.

OUTRIGGER BEAM (THRUSTOUT). The structural member of a suspended scaffold or outrigger scaffold that provides support for the scaffold by extending the scaffold point of attachment to a point out and away from the structure or building.

OUTRIGGER SCAFFOLD. A supported scaffold consisting of a platform resting on outrigger beams (thrustouts) projecting beyond the wall or face of the building or structure, the inboard ends of which are secured inside the building or structure.

OXIDIZER. A material that readily yields oxygen or other oxidizing gas or that readily reacts to promote or initiate combustion of combustible materials, and if heated or contaminated can result in vigorous self-sustained decomposition, classified as follows:

Class 4. An oxidizer that can undergo an explosive reaction due to contamination or exposure to thermal or physical shock and causes a severe increase in the burning rate of combustible materials with which it comes into contact.

Class 3. An oxidizer that causes a severe increase in the burning rate of combustible materials with which it comes in contact.

Class 2. An oxidizer that causes a moderate increase in the burning rate of combustible materials with which it comes in contact.

Class 1. An oxidizer that causes a readily measurable increase in the burning rate of combustible materials with which it comes in contact, but less than a moderate increase.

OXIDIZING GAS. A gas that can support and accelerate combustion of other materials more than air does.

PANEL (PART OF A STRUCTURE). The selection of a floor, wall or roof comprised between the supporting frame of two adjacent rows of columns and girders or column bands of floor or roof construction.

PANIC HARDWARE. A door-latching assembly incorporating a device that releases the latch upon the application of a force in the direction of egress travel.

PARTICLEBOARD. A generic term for a panel primarily composed of cellulosic materials (usually wood), generally in the form of discrete pieces or particles, as distinguished from fibers. The cellulosic material is combined with synthetic resin or other suitable bonding system by a process in which the interparticle bond is created by the bonding system under heat and pressure.

PATIENT CARE AREA (FOR FLOOD ZONE PURPOSES). Any space meeting the following conditions:

- The space is located within a building or structure, or portion thereof, that is classified in Group I-2; and

- The space is primarily used for the provision of medical services to persons, including, but not limited to, consultation, evaluation, monitoring and treatment services.

Exceptions: The following spaces shall not be considered patient care areas (for flood zone purposes):

- “Emergency rooms or departments” as defined in 10 NYCRR 700.2(a)(2) and

- Spaces primarily used for the provision of medical services identified in 10 NYCRR 703.6(c)(2)(i).

PENETRATION FIRESTOP. A through-penetration firestop or a membrane-penetration firestop.

PENTHOUSE. An enclosed rooftop structure that is designed or used for human occupancy.

PERFORMANCE CATEGORY. A designation of wood structural panels as related to the panel performance used in Chapter 23.

PERMANENT PRESTRESSED ROCK AND SOIL ANCHORS. Corrosion-protected tendons consisting of bars or strands installed in drilled and grouted holes in soil or rock that are stressed.

PERSONAL CARE SERVICE. The care of residents who do not require chronic or convalescent medical or nursing care. Personal care involves responsibility for the safety of the resident while inside the building.

PERSONNEL HOIST. A mechanism and its hoistway that is (i) temporarily installed at a construction or demolition site, and (ii) is equipped with a car that moves vertically on guide members to raise or lower workers or workers and materials.

PHOTOLUMINESCENT. Having the property of emitting light that continues for a length of time after excitation by visible or invisible light has been removed.

PHOTOVOLTAIC MODULE. A complete, environmentally protected unit consisting of solar cells, optics and other components, exclusive of tracker, designed to generate DC power when exposed to sunlight.

PHOTOVOLTAIC PANEL. A collection of modules mechanically fastened together, wired and designed to provide a field-installable unit.

PHOTOVOLTAIC PANEL SYSTEM. A system that incorporates discrete photovoltaic panels that converts solar radiation into electricity, including rack support systems.

PHOTOVOLTAIC SHINGLES. A roof covering resembling shingles that incorporates photovoltaic modules.

PHYSICAL HAZARD. A chemical for which there is evidence that it is a combustible liquid, compressed gas, cryogenic explosive, flammable gas, flammable liquid, flammable solid, organic peroxide, oxidizer, pyrophoric or unstable (reactive) or water-reactive material.

PHYSIOLOGICAL WARNING THRESHOLD LEVEL. A concentration of air-borne contaminants, normally expressed in parts per million (ppm) or milligrams per cubic meter (mg/m3), that represents the concentration at which persons can sense the presence of the contaminant due to odor, irritation or other quick-acting physiological response. When used in conjunction with the permissible exposure limit (PEL), the physiological warning threshold levels are those consistent with the classification system used to establish the PEL. See the definition of "Permissible exposure limit (PEL)" in the New York City Fire Code.

PIER FOUNDATION. A pier foundation is a shallow foundation element of masonry or cast-in-place concrete construction. Piers are relatively short in comparison to their width, with lengths less than or equal to 12 times the least horizontal dimension of the pier. Piers derive their load-carrying capacity from end bearing on soil or rock.

PILE DRIVER. Equipment that is configured to drive, hammer, press, or vibrate piles into the earth ("pile drive").

PINRAIL. A rail on or above a stage through which belaying pins are inserted and to which lines are fastened.

PLACE OF ASSEMBLY. A building, structure, or portion thereof, excluding a dwelling unit, but including outdoor spaces, used or intended to be used for the gathering of a group of persons for purposes such as civic, social, or religious functions, recreation, food or drink consumption, educational or instructional purposes, awaiting transportation, or similar group activities when such use requires a place of assembly Certificate of Operation pursuant to Section 303.7.

PLASTIC, APPROVED. Any thermoplastic, thermosetting or reinforced thermosetting plastic material that conforms to combustibility classifications specified in the section applicable to the application and plastic type.

PLASTIC, COMPOSITE. A generic designation that refers to wood/plastic composites and plastic lumber.

PLASTIC GLAZING. Plastic materials that are glazed or set in frame or sash and not held by mechanical fasteners that pass through the glazing material.

PLASTIC LUMBER. A manufactured product made primarily of plastic materials (filled or unfilled) that is generally rectangular in cross section.

PLASTIC (SOIL). A property of a soil that allows the soil to be deformed or molded without cracking, or appreciable volume change.

PLATFORM (SPECIAL USE). See Section 410.2.2.

PLATFORM. A work surface elevated above lower levels. Platforms can be constructed using individual wood planks, fabricated planks or fabricated decks.

POLE SIGN. A sign wholly supported by a sign structure in the ground.

POLYPROPYLENE SIDING. A shaped material, made principally from polypropylene homopolymer or copolymer, which in some cases contains fillers or reinforcements, that is used to clad exterior walls of buildings.

PORCELAIN TILE. Tile that conforms to the requirements of ANSI 137.1.3 for ceramic tile having an absorption of 0.5 percent or less in accordance with ANSI 137.4.1-Class Table and ANSI 137.1.6.1 Allowable Properties by Tile Type-Table 10.

POSITIVE ROOF DRAINAGE. The drainage condition in which consideration has been made for all loading deflections of the roof deck, including ponding instability, and additional slope has been provided to ensure drainage of the roof within 48 hours of precipitation.

POST-FIRE SMOKE PURGE SYSTEM. A mechanical or natural ventilation system intended to move smoke from the smoke zone to the exterior of the building. Such systems are intended for the timely restoration of operations and overhaul activities once a fire is extinguished. Post-fire smoke purge systems are not intended or designed to be life safety systems.

POST-FIRM DEVELOPMENT. See Section G201.1.2.

POST-FIRM STRUCTURE. See Section G201.1.2.

POWER BUGGIES. An automotive vehicle designed or used for the transportation of materials on or about construction or demolition sites. It shall not include automobiles, motor trucks, general purpose tractors, or excavating or similar material handling machinery.

POWER-ASSISTED DOOR. Swinging door that opens by reduced pushing or pulling force on the door-operating hardware. The door closes automatically after the pushing or pulling force is released and functions with decreased forces. See “Low-energy power-operated door” and “Power-operated door”.

POWER-OPERATED DOOR. Swinging, sliding, or folding door that opens automatically when approached by a pedestrian or opens automatically upon an action by a pedestrian. The door closes automatically and includes provisions such as presence sensors to prevent entrapment. See “Low-energy power-operated door” and “Power-assisted door”.

PRE-FIRM DEVELOPMENT. See Section G201.1.2.

PRE-FIRM STRUCTURE. See Section G201.1.2.

PREFABRICATED WOOD I-JOIST. Structural member manufactured using sawn or structural composite lumber flanges and wood structural panel webs bonded together with exterior exposure adhesives, which forms an "I" cross-sectional shape.

PRESIGNAL SYSTEM. A fire alarm system having a feature that allows initial fire alarm signals to sound in a constantly attended central location and for which a human action is subsequently required to achieve a general alarm, or a feature that allows the control equipment to delay the general alarm by more than 1 minute after the start of the alarm processing.

PRESSURIZATION. Creation and maintenance of pressure levels in zones of a building, including elevator shafts and stairwells, that are higher than the pressure level at the smoke source, such pressure levels being produced by positive pressures of a supply of uncontaminated air; by exhausting air and smoke at the smoke source; or by a combination of these methods.

PRESTRESSED MASONRY. Masonry in which internal stresses have been introduced to counteract potential tensile stresses in masonry resulting from applied loads.

PRIVATE GARAGE. An enclosed structure or portion of a structure, accessory to a Group R-2 or R-3 occupancy, used for the parking or storage of passenger motor vehicles. Such facility shall not exceed 650 square feet (60 m2) in area and one story in height.

PROJECTING SIGN. A sign other than a wall sign that projects from and is supported by a wall of a building or structure.

PROSCENIUM WALL. The wall that separates the stage from the auditorium or assembly seating area.

PUBLIC ENTRANCE. An entrance that is not a service entrance.

PUBLIC WAY. A street, alley or other parcel of land open to the outside air leading to a street that has been deeded, dedicated or otherwise permanently appropriated to the public for public use and which has a clear width and height of not less than 10 feet (3048 mm).

PUBLIC-USE AREAS. Interior or exterior rooms or spaces that are made available to the general public.

PYROPHORIC MATERIAL. A material with an auto-ignition temperature in air, at or below a temperature of 130°F (54°C).

PYROTECHNIC MATERIAL. A chemical mixture consisting predominantly of solids that, upon ignition, are capable of producing a controlled, self-sustaining, and self-contained exothermic reaction, that functions without external oxygen, resulting in a visible or audible effect by combustion, deflagration, or detonation.

QUALIFIED PERSON. A person who, by possession of a recognized degree, certificate, or professional standing, or who by extensive knowledge, training, and experience, has successfully demonstrated his or her ability to solve or resolve problems related to the subject matter, the work, or the project.

RADIANT BARRIER. A material having a low-emittance surface of 0.1 or less installed in building assemblies.

RAMP. A walking surface that has a running slope steeper than one unit vertical in 20 units horizontal (5-percent slope).

RAMP-ACCESS OPEN PARKING GARAGE. Open parking garages employing a series of continuously rising floors or a series of interconnecting ramps between floors permitting the movement of vehicles under their own power from and to the street level.

RECLAIMED ASPHALT PAVEMENT. Asphalt pavement that has been processed for reuse in asphaltic concrete.

RECORD DRAWINGS. Drawings ("as builts") that document the location of all devices, appliances, wiring sequences, wiring methods and connections of the components of a fire alarm system as installed.

RECREATIONAL VEHICLE. See Section G201.1.2.

REFUGE AREA. A floor area to which egress is made through a horizontal exit.

REMOVING/REMOVAL/REMOVE (SCAFFOLD). The final process of taking apart a scaffold in a specific sequence and removing it from the site.

REPAIR (SCAFFOLD). Work performed to restore a scaffold, or any part or component, to like new condition and safe working order following decay, wear, or damage. The definition of repair shall also include the replacement of a part or component.

REPLACEMENT (SCAFFOLD). A repair involving the exchange or substitution of one part or component with another identical or similar part or component in order to restore a scaffold, or any part or component, to like new condition and safe working order following decay, wear, or damage.

REROOFING. The process of recovering or replacing an existing roof covering. See "Roof recover" and "Roof replacement."

RESIDENTIAL AIRCRAFT HANGAR. An accessory building less than 2,000 square feet (186 m2) and 20 feet (6096 mm) in building height constructed on a one- or two-family property where aircraft are stored. Such use will be considered as a residential accessory use incidental to the dwelling.

RESIDENTIAL CARE/ASSISTED LIVING FACILITIES. A building or part thereof housing persons, on a 24-hour basis, who because of age, mental disability or other reasons, live in a supervised residential environment that provides personal care services. The occupants are capable of self-preservation and are capable of responding to an emergency situation without physical assistance from staff. This classification shall include, but not limited to, the following: residential board and care facilities, assisted living facilities, halfway houses, congregate care facilities, social rehabilitation facilities, alcohol and drug abuse rehabilitation centers and convalescent facilities.

RESIDENTIAL (FOR FLOOD ZONE PURPOSES). A building or structure containing any space that is either:

- Classified in Group I-1, R-1, R-2, or R-3; or

2.	Accessory, as such term is defined in the New York City Zoning Resolution, to any Group I-1, R-1, R-2, or R-3 occupancy.

Exception: Such a building or structure shall be considered nonresidential (for flood zone purposes) when also containing space at or below the DFE that is not accessory, as such term is defined in the New York City Zoning Resolution, to a Group I-1, R-1, R-2, or R-3 occupancy.

RESISTANCE FACTOR. A factor that accounts for deviations of the actual strength from the nominal strength and the manner of consequences of failure (also called "strength reduction factor").

RESPONSE RATIO. The ratio of an ultimate response quantity (e.g., deflection) to its value at yield.

RESTRICTED ENTRANCE. An entrance that is made available for public use but on a controlled basis, and that is not a service entrance.

RETAINING WALL. A wall that resists lateral or other forces caused by soil, rock, water or other materials, thereby limiting lateral displacement and the movement of the supported materials. Basement walls and vault walls that are parts of buildings and underground structures, including but not limited to utility vault structures, tunnels, transit stations, and swimming pools, are not considered retaining walls.

RETRACTABLE AWNING. A retractable awning is a cover with a frame that retracts against a building or other structure to which it is entirely supported.

RIM BOARD. In light-frame construction, a full depth structural member designed to transfer horizontal (shear) and vertical (compression) loads, provide attachment for diaphragm sheathing, siding and exterior deck ledgers, and provide lateral support at the ends of floor or roof joists or rafters.

RISK CATEGORY. A categorization of buildings and other structures for determination of flood, wind, snow, ice and earthquake loads based on the risk associated with unacceptable performance.

RISK-TARGETED MAXIMUM CONSIDERED EARTHQUAKE (MCER) GROUND MOTION RESPONSE ACCELERATIONS. The most severe earthquake effects considered by this standard determined for the orientation that results in the largest maximum response for horizontal ground motions and with adjustment for targeted risk. The MCER Ground Motion values can be determined from general procedure in Section 1613.3.3 or can be derived from the site specific procedures provided in Sections 21.1 and 21.2 of ASCE 7.

ROPE. A continuous line of material comprised of a number of twisted or braided strands of fiber (natural or synthetic) or metal wire.

ROOF ASSEMBLY. A system designed to provide weather protection and resistance to design loads. The system consists of a roof covering and roof deck or a single component serving as both the roof covering and the roof deck. A roof assembly includes the roof deck, vapor retarder, substrate or thermal barrier, insulation and roof covering.

ROOF COVERING. The covering applied to the roof deck for weather resistance, fire classification or appearance.

ROOF COVERING SYSTEM. See "Roof assembly."

ROOF DECK. The flat or sloped surface constructed on top of the exterior walls of a building or other supports for the purpose of enclosing the story below, or sheltering an area, to protect it from the elements, not including its supporting members or vertical supports.

ROOF RECOVER. The process of installing an additional roof covering over a prepared existing roof covering without removing the existing roof covering.

ROOF REPAIR. Reconstruction or renewal of any part of an existing roof for the purposes of its maintenance.

ROOF REPLACEMENT. The process of removing the existing roof covering, repairing any damaged substrate and installing a new roof covering.

ROOF SIGN. A sign erected on or above a roof or parapet of a building or structure.

ROOF VENTILATION. The natural or mechanical process of supplying conditioned or unconditioned air to, or removing such air from, attics, cathedral ceilings or other enclosed spaces over which a roof assembly is installed.

ROOFTOP STRUCTURE. An enclosed or unenclosed structure on or above the roof of any part of a building.

ROOMING HOUSE. A dwelling (i) which was originally erected as single- or two-family private dwelling pursuant to the New York City Building Code in effect prior to December 6, 1968, (ii) which is a "Class B converted dwelling" as such term is defined in the New York City Housing Maintenance Code, and (iii) which has more than half of its habitable rooms as sleeping units. The creation of or conversion to a rooming house shall be limited by Section 27-2077 of the New York City Housing Maintenance Code.

ROTATING TELEHANDLER. A telehandler whose boom is mounted on a rotating or slewing superstructure.

ROTATION. The angle, measured at the ends of a member, whose tangent is equal to the deflection of the member at midspan divided by half the length of the member.

RUNBACK STRUCTURE. A temporary system of hoistway landing runways, vertical supports and horizontal diaphragms designed to bridge between the hoistway and the parent structure and to transmit both vertical and horizontal loads to the supporting structure and/or foundation.

RUNNING BOND. The placement of masonry units such that head joints in successive courses are horizontally offset at least one-quarter the unit length.

SAFE AREA. See Section 1002.1.2.

SAFETY NETTING SYSTEM (SAFETY NETTING). Debris or structural nets, installed vertically or horizontally, along with all supports, components, and connections.

Horizontal safety netting. A safety netting system, installed horizontally, consisting of structural netting lined with debris netting.

Vertical safety netting. A safety netting system, installed vertically, consisting of debris netting.

SALLYPORT. See Section 408.1.1.

SAND DUNES. Naturally occurring accumulations of sand in ridges or mounds landward of a beach.

SCAFFOLD. Any temporary elevated platform and its supporting structure (including points of anchorage) used for supporting workers or workers and material, including but not limited to supported scaffolds, suspended scaffolds, and mobile scaffolds.

SCAFFOLD CONTROLLING ENTITY. The contractor or other entity that exercises responsibility for the site where the scaffold is located.

SCISSOR STAIRWAY. Two interlocking stairways providing two separate paths of egress located within one stairwell enclosure.

SCUPPER. An opening in a wall or parapet that allows water to drain from a roof.

SEATING SECTION. See Section 1002.1.2.

SEISMIC DESIGN CATEGORY. A classification assigned to a structure based on its risk category and the severity of the design earthquake ground motion at the site.

SEISMIC FORCE-RESISTING SYSTEM. The part of the structural system that has been considered in the design to provide the required resistance to the prescribed seismic forces.

SELF-CLOSING. As applied to a fire door or other opening, means equipped with a listed and approved device that will ensure closing after having been opened.

SELF-ERECTING TOWER CRANE. A tower crane that adjusts its operating radius by means of a trolley traversing a jib and that; (i) possesses a vertical or nearly vertical tower or mast that is bottom slewing and mounted on fixed, traveling, or mobile bases; and (ii) is capable of folding and unfolding to facilitate transit from site to site with minimal assembly.

SELF-LUMINOUS. Illuminated by a self-contained power source, other than batteries, and operated independently of external power sources.

SELF-SERVICE STORAGE FACILITY. Real property designed and used for the purpose of renting or leasing individual storage spaces to customers for the purpose of storing and removing personal property on a self-service basis.

SERVICE CORRIDOR. A fully enclosed passage other than one designated as a required means of egress, through which HPM can be moved during handling.

SERVICE ENTRANCE. An entrance solely for delivery of goods or services.

SERVICES. Includes, but is not limited to, toilet rooms, drinking fountains, public telephones and food.

SHADED X-ZONE. The land in the floodplain delineated as subject to a 0.2-percent or greater chance of flooding, but less than one percent chance of flooding, in any given year. Such areas are designated on the Flood Insurance Rate Map (FIRM) as shaded X-Zones.

SHAFT. An enclosed space extending through one or more stories of a building, connecting vertical openings in successive floors, or floors and roof.

SHAFT ENCLOSURE. The walls or construction forming the boundaries of a shaft.

SHALLOW FOUNDATION. A shallow foundation is an individual or strip footing, a mat foundation, a slab-on-grade foundation or a similar foundation element.

SHEAR WALL. A wall designed to resist lateral forces parallel to the plane of a wall.

Shear wall, perforated. A wood structural panel sheathed wall with openings, that has not been specifically designed and detailed for force transfer around openings.

Shear wall segment, perforated. A section of shear wall with full-height sheathing that meets the height-to-width ratio limits of Section 4.3.4 of AWC SDPWS.

SIDELITES. Fixed transparent panels that form part of or are immediately adjacent to and within 6 feet (1829 mm) horizontally of the vertical edge of an opening in which transparent doors are located. A sidelite shall consist of transparent material in which the transparent area above a reference line 18 inches (457 mm) above the adjacent ground, floor or equivalent surface is 80 percent or more of the remaining area of the panel above such reference line.

SIGN. Any letter, figure, character, mark, plane, point, marquee sign, design, poster, pictorial, picture, stroke, stripe, line, trademark, reading matter or illuminated service, which shall be constructed, placed, attached, painted, erected, fastened or manufactured in any manner whatsoever, so that the same shall be used for the attraction of the public to anyplace, subject, person, firm, corporation, public performance, article, machine or merchandise, whatsoever, which is displayed in any manner outdoors. Every sign shall be classified and conform to the requirements of that classification as set forth in this code.

SIGN STRUCTURE. Any structure that supports or is capable of supporting a sign as defined in this code.

SINGLE-PLY MEMBRANE. A roofing membrane that is field applied using one layer of membrane material (either homogeneous or composite) rather than multiple layers.

SINGLE-POINT ADJUSTABLE SUSPENDED SCAFFOLD. A suspended scaffold consisting of a platform suspended by one rope from an overhead support and equipped with means to permit the movement of the platform to desired work levels.

SINGLE-STATION SMOKE ALARM. An assembly incorporating the detector, the control equipment and the alarm-sounding device in one unit, operated from a power supply either in the unit or obtained at the point of installation.

SITE. A parcel of land bounded by a lot line or a designated portion of a public right-of-way.

SITE CLASS. A classification assigned to a site based on the types of soils present and their engineering properties as defined in Section 1613.3.2.

SITE COEFFICIENTS. The values of, Fa, and, Fv, indicated in Tables1613.3.3(1) and 1613.3.3(2), respectively.

SITE-FABRICATED STRETCH SYSTEM. A system, fabricated on site and intended for acoustical, tackable or aesthetic purposes, that is comprised of three elements: (a) a frame (constructed of plastic, wood, metal or other material) used to hold fabric in place, (b) a core material (infill, with the correct properties for the application), and (c) an outside layer, comprised of a textile, fabric or vinyl, that is stretched taut and held in place by tension or mechanical fasteners via the frame.

SITE SAFETY TRAINING (SST) CARD. A card that is issued in a form and manner established by the department and that satisfies each of the following conditions:

1.	Such card is issued by an SST provider to a person who submits an application to such provider demonstrating, in a form and manner established by the department, that such applicant satisfies the requirements of Item 1.1, 1.2 or 1.3:

1.1.	Such applicant has successfully completed (i) an OSHA 10-hour class and (ii) 30-45 additional SST credits specified by the department, including eight SST credits relating to safeguarding against the dangers posed by falling workers and objects.

1.2.	Such applicant has successfully completed (i) an OSHA 30-hour class and (ii) 10-25 additional SST credits specified by the department, including eight SST credits relating to safeguarding against the dangers posed by falling workers and objects.

1.3.	Such applicant has successfully completed a 100-hour training program.

2.	If such applicant completed the training to comply with Item 1.1, 1.2 or 1.3 but did not complete such training within the five years preceding submission of such application, such applicant has, in the one-year period preceding submission of such application, completed at least eight SST credits specified by the department.

3.	Such card is issued by an SST provider who does not require applicants to submit any information except for (i) the information necessary to establish that the requirements in Item 1 have been satisfied, as specified by the department, (ii) a photograph of the applicant and (iii) such additional information as the department may allow by rule.

4.	Such card expires five years after issuance and is renewable upon a showing by the applicant that such applicant has, in the one-year period preceding submission of such renewal application, successfully completed eight SST credits specified by the department.

SITE SAFETY TRAINING (SST) CREDIT. One hour of training that satisfies each of the requirements of Item 1, 2 and 3:

1.	Such training relates to a topic identified by department rule.

2.	If such training is conducted on or after the effective date of the local law that added this definition, such training is in-person training or actively proctored online training.

3.	If such training is conducted on or after March 1, 2018, such training is conducted by an SST provider.

SITE SAFETY TRAINING (SST) FULL COMPLIANCE DATE. March 1, 2021.

SITE SAFETY TRAINING (SST) PROVIDER. An entity that satisfies the requirements of Items 1 and 2:

1.	Such entity satisfies the conditions of Item 1.1, 1.2, 1.3 or 1.4:

1.1.	Such entity is a not-for-profit organization with a history of at least three years of experience in providing construction-related workforce development, construction-related education or site safety training, which may be demonstrated by submitting training logs to the department or in a form and manner otherwise determined by the department, and training offered by such entity is offered by a person who has (i) successfully completed all applicable OSHA or department requirements for conducting OSHA 10-hour classes and OSHA 30-hour classes and is authorized to conduct such classes and (ii) if such person is conducting training for SST credits other than training that is part of an OSHA 10-hour class or OSHA 30-hour class, such person demonstrates sufficient knowledge of this chapter in a form and manner established by the department. Such entity shall not be required to demonstrate any professional standing, approval, licensure, accreditation or certification, including approval, licensure, accreditation or certification pursuant to paragraph (2) of subdivision d of section 105-03 of subchapter E of chapter 100 of title 1 of the rules of the city of New York, as in effect on January 1, 2018, beyond showing that such entity and a person offering training on behalf of such entity satisfy the requirements set forth in the preceding sentence. Where the department provides content, developed in accordance with department-approved course requirements, for the delivery of SST credits, such entity shall deliver SST credits in accordance with such content. Where the department does not provide content for the delivery of SST credits, such entity shall be responsible for the development of content in accordance with department-approved course requirements. Such content and the delivery of such content may be subject to approval or audit by the department.

1.2.	Such entity is providing training through a 100-hour training program.

1.3.	Such entity has been approved by the department to conduct a 40-hour course approved by the department pursuant to Article 402 of Chapter 4 of Title 28 of the Administrative Code.

1.4.	The department may establish by rule additional ways for an entity to satisfy the requirements of this Item 1. If the department elects to promulgate such rules, an entity shall be deemed to satisfy this Item 1 if such entity satisfies the requirements set forth in such rules or if such entity satisfies the requirements set forth in Item 1.1, 1.2 or 1.3.

2.	On and after the SST full compliance date, such entity has certified to the department that such entity satisfies at least one of the following conditions:

2.1.	Such entity has a language access plan for training that relates to SST credits such entity offers and such plan complies with requirements established by an agency or office designated by the mayor.

2.2.	Such entity satisfies each of the following conditions:

2.2.1.	Such entity is able to provide instruction in a language that students understand.

2.2.2.	If a student’s vocabulary is limited, such entity will accommodate that limitation.

2.2.3.	A person offering training on behalf of such entity is fluent in the training language or will use translators or interpreters and any such translators or interpreters will have a background in occupational safety and health.

SITE SAFETY TRAINING (SST) SECOND COMPLIANCE DATE. December 1, 2019, or, if the department publishes a finding by September 1, 2019, that there is insufficient capacity to provide the training required by Section 3321 of the New York city building code to the workers who would need such training, a later date established by the department, provided that such date is not later than June 1, 2020.

SITE SAFETY TRAINING (SST) SUPERVISOR CARD. A card that satisfies each of the following conditions:

1.	Such card is issued in a form and manner established by the department to a person who demonstrates that such person has an SST card and has successfully completed an OSHA 30-hour class.

2.	Such card expires five years after issuance and is renewable upon a showing by the applicant that such applicant has, in the one-year period preceding such submission of such renewal application, successfully completed 16 SST credits specified by the department.

SITE SAFETY TRAINING (SST) TASK FORCE. The task force established pursuant to Section 28-103.28 of the Administrative Code.

SLEEPING UNIT. A dwelling unit, which may contain either toilet or kitchen facilities but not both. Any sleeping unit housing more than one family shall also be classified as a congregate living unit. The creation of or conversion to sleeping units shall be limited by Section 27-2077 of the New York City Housing Maintenance Code.

SLEEPING UNIT (ACCESSIBILITY). As used in Chapter 11 and Appendix E, a room or space in which people sleep, which can also include permanent provisions for living, eating, and either sanitation or kitchen facilities but not both. Such rooms and spaces that are also part of a dwelling unit are not sleeping units.

SMALL WIND TURBINE. A turbine with a swept area smaller than 200 m2 that generates a voltage below 1000 V (AC) or 1500 V (DC).

SMALL WIND TURBINE TOWER. A structure that supports a small wind turbine.

SMOKE. Air-borne solid and liquid particulates and gases evolved when a material undergoes pyrolysis or combustion, including the quality of air that is entrained or otherwise mixed into the mass.

SMOKE ALARM. A single- or multiple-station alarm responsive to smoke and not connected to a fire alarm system. See "Multiple-station smoke alarm" and "Single-station smoke alarm."

SMOKE BARRIER. A continuous membrane, either vertical or horizontal, such as a wall, floor, or ceiling assembly, that is designed and constructed in accordance with Section 709 to restrict the movement of smoke.

SMOKE COMPARTMENT. A space within a building enclosed by smoke barriers on all sides, including the top and bottom.

SMOKE CONTROL MODE. A predefined operational configuration of a system or device for the purpose of smoke control.

SMOKE CONTROL SYSTEM, MECHANICAL. An engineered system that includes all methods that can be used singly or in combination to modify smoke movement.

SMOKE CONTROL SYSTEM, PASSIVE. A system of smoke barriers arranged to limit the migration of smoke.

SMOKE CONTROL ZONE. A space within a building enclosed by smoke barriers that is part of a smoke control system.

SMOKE DAMPER. See Dampers, Types of.

SMOKE DETECTOR. A listed device that senses visible or invisible particles of combustion or smoke.

SMOKE PARTITION. A continuous vertical assembly that is designed and constructed to restrict the movement of smoke and is not generally required to have a fire-resistance rating in accordance with Section 710.

SMOKE-DEVELOPED INDEX. A comparative measure, expressed as a dimensionless number, derived from measurements of smoke obscuration versus time for a material tested in accordance with ASTM E 84.

SMOKEPROOF ENCLOSURE. An exit stairway, ramp or passageway designed and constructed so that the movement of the products of combustion produced by a fire occurring in any part of the building into the enclosure is limited.

SMOKE-PROTECTED ASSEMBLY SEATING. Seating served by means of egress that is not subject to smoke accumulation within or under a structure.

SOIL AND FOUNDATION WORK (SOIL OR FOUNDATION WORK). Excavation, fill, grading, augering, boring, or drilling, whether in soil or rock; or the installation or removal of foundations, piles, underpinning, sheeting, shoring, or supports of excavation.

SOLID. A material that has a melting point, decomposes or sublimates at a temperature greater than 68°F (20°C).

SPECIAL AMUSEMENT BUILDING. A special amusement building is any temporary or permanent building or portion thereof that is occupied for amusement, entertainment or educational purposes and that contains a device or system that conveys passengers or provides a walkway along, around or over a course in any direction so arranged that the means of egress path is not readily apparent due to visual or audio distractions or is intentionally confounded or is not readily available because of the nature of the attraction or more of conveyance through the building or structure.

SPECIAL FLOOD HAZARD AREA. Land in the floodplain subject to a 1% or greater chance of flooding in any given year; area delineated on the Flood Insurance Rate Map as Zone A, AE, A1-30, A99, AR, AO, AH, V, VO, VE, or V1-30. Such areas include A-Zones, Coastal A-Zones, and V-Zones.

SPECIAL INSPECTION, CONTINUOUS. The observation of work requiring special inspection by a special inspector who is continuously present in the area where the work is being performed while the work is being performed.

SPECIAL INSPECTION, PERIODIC. The intermittent observation of work requiring special inspection by a special inspector who is present in the area where the work has been or is being performed and at the completion of the work. All work requiring special inspection shall remain accessible and exposed until approved by the special inspector.

SPECIFIC LOCAL LOAD. A load applied to a structural element or structural system as specified in Section 1617.6.

SPECIFIC LOCAL RESISTANCE METHOD. A design approach that accounts for extreme event loads by providing sufficient strength for elements that may fail. In a specific local resistance design, key elements are designed for specific local loads as required by Section 1617.

SPECIFIED COMPRESSIVE STRENGTH OF MASONRY, f’m. Minimum compressive strength, expressed as force per unit of net cross-sectional area, required of the masonry used in construction by the approved construction documents, and upon which the project design is based. Whenever the quantity f’m is under the radical sign, the square root of numerical value only is intended and the result has units of pounds per square inch (psi) (Mpa).

SPLICE. The result of a factory and/or field method of joining or connecting two or more lengths of a fire-resistant joint system into a continuous entity.

SPRAYED FIRE-RESISTANT MATERIALS. Cementitious or fibrous materials that are sprayed to provide fire-resistant protection of the substrates.

STABLE (ROCK). A condition in which natural solid mineral matter (rock) can be excavated with vertical sides and remain intact while exposed.

STACK EFFECT. The vertical airflow within buildings caused by the temperature-created density differences between the building interior and exterior or between two interior spaces.

STAGE. A space within a building utilized for entertainment or presentations, which includes overhead hanging curtains, drops, scenery or stage effects other than lighting and sound.

STAIR. A change in elevation, consisting of two or more risers.

STAIR TOWER (SCAFFOLD STAIRWAY/TOWER). A tower comprised of scaffold components and that contains internal stairway units and rest platforms. These towers are used to provide access to scaffold platforms and other elevated points such as floors and roofs.

STAIRWAY. One or more flights of stairs, either exterior or interior, with the necessary landings and platforms connecting them, to form a continuous and uninterrupted passage from one level to another.

STAIRWAY, SPIRAL. A stairway having a closed circular form in its plan view with uniform section-shaped treads attached to and radiating from a minimum-diameter-supporting column.

STANDARD CUBIC FEET (SCF). Cubic feet of gas at normal temperature and pressure (NTP).

STANDARD GUARDRAIL SYSTEM (SCAFFOLD). See “Guardrail system (scaffold).”

STAND-OFF BRACKET (SUSPENDED SCAFFOLD). A rigid member that attaches to a cornice hook (c-hook) in order to provide additional outreach from the face of the parapet or wall.

STANDPIPE SYSTEM. Piping, installed in a building or structure, that serves to supply water to hose connections at one or more locations in a building or structure, for firefighting purposes.

STANDPIPE SYSTEM, CLASSES OF. Standpipe classes are as follows:

Class I system. A system providing 21/2-inch (64 mm) hose connections to supply water for use by the Fire Department and those trained in handling heavy fire streams.

Class II system. A system providing 11/2-inch (38 mm) hose stations to supply water for use primarily by the building occupants or by the Fire Department during initial response.

Class III system. A system providing 11/2-inch (38 mm) hose stations to supply water for use by building occupants and 21/2-inch (64 mm) hose connections to supply a larger volume of water for use by the Fire Department and those trained in handling heavy fire streams.

STANDPIPE SYSTEM, TYPES OF. Standpipe system types are as follows:

Automatic dry. A dry standpipe system, normally filled with pressurized air, that is arranged through the use of a device, such as dry pipe valve, to admit water into the system piping automatically upon the opening of a hose valve. The water supply for an automatic dry standpipe system shall be capable of supplying the system demand.

Automatic wet. A wet standpipe system that has a water supply that is capable of supplying the system demand automatically.

Manual dry. A dry standpipe system that does not have a permanent water supply attached to the system. Manual dry standpipe systems require water from a Fire Department pumper to be pumped into the system through the Fire Department connection in order to meet the system demand.

Manual wet. A wet standpipe system connected to a water supply for the purpose of maintaining water within the system but that does not have a water supply capable of delivering the system demand attached to the system. Manual-wet standpipe systems require water from a Fire Department pumper to be pumped into the system in order to meet the system demand.

Semiautomatic dry. A dry standpipe system that is arranged through the use of a device, such as a deluge valve, to admit water into the system piping upon activation of a remote control device location at a hose connection. A remote control activation device shall be provided at each hose connection. The water supply for a semiautomatic dry standpipe system shall be capable of supplying the system demand.

START OF CONSTRUCTION. See Section G201.1.2.

STEEL CONSTRUCTION, COLD-FORMED. That type of construction made up entirely or in part of steel structural members cold formed to shape from sheet or strip steel such as roof deck, floor and wall panels, studs, floor joists, roof joists and other structural elements.

STEEL ELEMENT, STRUCTURAL. Any steel structural member of a building or structure consisting of rolled shapes, pipe, hollow structural sections, plates, bars, sheets, rods or steel castings other than cold-formed steel, or steel joist members.

STEEL JOIST. Any steel structural member of a building or structure made of hot-rolled or cold-formed solid or open-web sections, or riveted or welded bars, strip or sheet steel members, or slotted and expanded, or otherwise deformed rolled sections.

STONE MASONRY. Masonry composed of field, quarried or cast stone units bonded by mortar.

STORAGE CABINET. See Section 427.4.

STORAGE, HAZARDOUS MATERIALS. The keeping, retention or leaving of hazardous materials in closed containers, tanks, cylinders, or similar vessels; or vessels supplying operations through closed connections to the vessel.

STORAGE ROOM. See Section 427.4.

STORM SHELTER. See Section 423.2.

Community storm shelter. See Section 423.2.

Residential storm shelter. See Section 423.2.

STORY. That portion of a building included between the upper surface of a floor and the upper surface of the floor or roof next above (also see "Basement" and "Mezzanine"). It is measured as the vertical distance from top to top of two successive tiers of beams or finished floor surfaces and, for the topmost story, from the top of the floor finish to the top of the ceiling joists or, where there is not a ceiling, to the top of the roof rafters.

STORY ABOVE GRADE PLANE. Any story having its finished floor surface entirely above grade plane, except that a basement shall also be considered a story above grade plane (see "Story" and "Basement").

STREET. A thoroughfare, including sidewalks and roadways, dedicated or devoted to public use by legal mapping or other lawful means, or a public way.

STREET LINE. A lot line separating a street from other land.

STRENGTH DESIGN. A method of proportioning structural members such that the computed forces produced in the members by factored loads do not exceed the member design strength (also called “load and resistance factor design” (LRFD)). The term "strength design" is used in the design of concrete and masonry structural elements.

STRENGTH.

Design strength. Nominal strength multiplied by a strength reduction factor.

Nominal strength. Strength of a member or cross-section calculated in accordance with these provisions before application of any strength-reduction factors.

Required strength. Strength of a member or cross-section required to resist factored loads.

STRENGTH, NOMINAL. The capacity of a structure or member to resist the effects of loads, as determined by computations using specified material strengths and dimensions and equations derived from accepted principles of structural mechanics or by field tests or laboratory tests of scaled models, allowing for modelling effects and differences between laboratory and field conditions.

STRENGTH, REQUIRED. Strength of a member, cross section or connection required to resist factored loads or related internal moments and forces in such combinations as stipulated by these provisions.

STRIPPING OPERATIONS. Removal on the floor of any parts of the concrete formwork including shoring, bracing and other supports.

STRUCTURAL COMPOSITE LUMBER. Structural member manufactured using wood elements bonded together with exterior adhesives. Examples of structural composite lumber are:

Laminated strand lumber (LSL). A composite of wood strand elements with wood fibers primarily oriented along the length of the member, where the least dimension of the wood strand elements is 0.10 inch (2.54 mm) or less and their average lengths not less than 150 times the least dimension of the wood strand elements.

Laminated veneer lumber (LVL). A composite of wood veneer sheet elements with wood fibers primarily oriented along the length of the member, where the veneer element thicknesses are 0.25 inches (6.4 mm) or less.

Oriented strand lumber (OSL). A composite of wood strand elements with wood fibers primarily oriented along the length of the member, where the least dimension of the wood strand elements is 0.10 inch (2.54 mm) or less and their average lengths not less than 75 times and less than 150 times the least dimension of the strand elements.

Parallel strand lumber (PSL). A composite of wood strand elements with wood fibers primarily oriented along the length of the member where the least dimension of the wood strand elements is 0.25 inches (6.4 mm) or less and their average lengths not less than 300 times the least dimension of the wood strand elements.

STRUCTURAL GLUED-LAMINATED TIMBER. An engineered, stress-rated product of a timber laminating plant, comprised of assemblies of specially selected and prepared wood laminations in which the grain of all laminations is approximately parallel longitudinally and the laminations are bonded with adhesives.

STRUCTURAL NET (STRUCTURAL NETTING). A system of nets capable of complying with the prototype test described in ANSI A10.11.

SUBMERGED SOIL. Soil which is underwater or is free seeping.

SUBSTANTIAL DAMAGE. Damage of any origin sustained by a structure whereby the cost of restoring the structure to its before-damaged condition would equal or exceed 50 percent of the market value of the structure before the damage occurred.

SUBSTANTIAL IMPROVEMENT. Any repair, reconstruction, rehabilitation, addition or improvement of a building or structure, the cost of which equals or exceeds 50 percent of the market value of the structure before the improvement or repair is started. If the structure has sustained substantial damage, any repairs are considered substantial improvement regardless of the actual repair work performed. The term does not, however, include either:

- Any project for improvement of a building required to correct pre-FIRM health, sanitary or safety code violations identified by the commissioner, the Fire Commissioner, the Commissioner of Housing Preservation and Development, or the Commissioner of Health and Mental Hygiene, and that are the minimum necessary to assure safe living conditions; or

- Any alteration of a historic structure provided that the alteration will not preclude the structure’s continued designation as a historic structure.

SUNROOM. A one-story structure attached to a building with a glazing area in excess of 40 percent of the gross area of the structure’s exterior walls and roof.

SUPERSTRUCTURE. The rotating upper frame structure of the machine and the operating machinery mounted thereon.

SUPERVISING STATION. A facility that receives signals from protected premises’ fire alarm systems and at which personnel are in attendance at all times to respond to these signals.

Supervising station, central. A supervising station that is listed and approved by the Fire Department for central station service.

Supervising station, proprietary. A supervising station under the same ownership as the protected premises’ fire alarm system(s) that it supervises (monitors) and to which alarm, supervisory, or trouble signals are received and where personnel are in attendance at all times to supervise operation and investigate signals.

Supervising station, remote. A supervising station to which alarm, supervisory, or trouble signals or any combination of those signals emanating from protected premises’ fire alarm systems are received and where personnel are in attendance at all times to respond.

SUPERVISORY SERVICE. The service required to monitor performance of guard tours and the operative condition of fixed suppression systems or other systems for the protection of life and property.

SUPERVISORY SIGNAL. A signal indicating the need for action in connection with the supervision of guard tours, fire suppression systems or equipment, fire alarm systems, or the maintenance features of related systems.

SUPERVISORY SIGNAL-INITIATING DEVICE. An initiation device, such as a valve supervisory switch, water-level indicator or low-air pressure switch on a dry-pipe sprinkler system, whose change of state signals an off-normal condition and its restoration to normal of a fire protection or life safety system, or a need for action in connection with the supervision of guard tours, fire suppression systems or equipment, fire alarm systems, or the maintenance features of related systems.

SUPPORTED SCAFFOLD. One or more platforms supported by outrigger beams, brackets, poles, legs, uprights, posts, frames, including prefabricated frames that are mechanized but not motorized, or any similar rigid support, including back structures connecting hoistways to buildings, and including structures where sidewalk protection is constructed as an integral part of the apparatus.

SUSCEPTIBLE BAY. A roof or portion thereof with:

1.	A slope less than 1/4-inch per foot (0.0208 rad); or

2.	On which water is impounded, in whole or in part, and the secondary drainage system is functional but the primary drainage system is blocked.

A roof surface with a slope of 1/4-inch per foot (0.0208 rad) or greater towards points of free drainage is not a susceptible bay.

SUSPENDED SCAFFOLD. One or more platforms suspended by ropes or other means from an overhead structure.

SUSPENDED SCAFFOLD FOREMAN. An individual, male or female, designated by and working under the direct and continuing supervision of a licensed master or special rigger, or a licensed master or special sign hanger, in accordance with the rules of the department.

SUSTAINABLE ROOFING ZONE. Areas of a roof assembly where a solar photovoltaic electricity generating system, a green roof system, or a combination thereof, is installed.

SWIMMING POOL. Any indoor or outdoor swimming, wading, spa, or special-purpose pool.

Exceptions:

- Portable, freestanding wading pools containing water less than 24 inches (610 mm) in depth.

- Float tanks or relaxation tanks sized for use by one person at a time.

- Pools used for religious purposes.

- Spa pools used for prescribed medical therapy or rehabilitation and under medical supervision.

SWIMMING POOL, PRIVATE. A swimming pool that is accessory to a one- or two-family dwelling, or to a single-dwelling unit of a multiple dwelling, and that is solely for the use of the occupants for noncommercial purposes.

SWIMMING POOL, PUBLIC. A swimming pool that is not a private swimming pool. Public swimming pools include swimming pools that are accessory to bathing establishments as such term is defined in the New York City Health Code, whether owned or operated by city agencies, or commercial interests or private entities, including, but not limited to, public or private schools, corporations, hotels, motels, camps, apartment houses, condominiums, country clubs, gymnasia and health establishments.

SWING. Rotation of the superstructure for movement of loads in a horizontal direction about the axis of rotation.

T RATING. The time period that the penetration firestop system, including the penetrating item, limits the maximum temperature rise to 325°F (163°C) above its initial temperature through the penetration on the nonfire side when tested in accordance with ASTM E 814 or UL 1479.

TECHNICAL PRODUCTION AREA. Open elevated areas or spaces intended for entertainment technicians to walk on and occupy for servicing and operating entertainment technology systems and equipment. Galleries, including fly and lighting galleries, gridirons, catwalks, and similar areas are designed for these purposes.

TELEHANDLER. A machine that consists of a powered chassis onto which is mounted an extendable boom. The outer end of the boom can be fitted with various lifting or manipulative devices, including but not limited to pallet forks.

TEMPORARY CONSTRUCTION INSTALLATIONS. Installations that are not part of the permanent structure and that are installed to facilitate construction or demolition work, and are intended to be taken apart or removed after a limited period following their installation. Such installations include, but are not limited to, scaffolds, sidewalk sheds, fences, tower cranes, run back structures, and similar construction and demolition related installations.

TEMPORARY SIGN. A sign, with display area 500 square feet (46.5 m2) or less, erected for a period of 30 days or less.

TEMPORARY SITE SAFETY TRAINING (SST) CARD. A card that is issued in a form and manner established by the department and that satisfies each of the following conditions:

1.	Such card is issued by an SST provider to a person who demonstrates that such person has successfully completed an OSHA 10-hour class and who is a new entrant to the construction or demolition work force as determined by such provider pursuant to department rules.

2.	Such card expires six months after issuance and is not renewable.

TEMPORARY STRUCTURES. Tents, grandstands, platforms, reviewing stands, outdoor bandstands, stages, sculptures, and similar miscellaneous structures erected for a limited period.

TENABLE ENVIRONMENT. An environment in which the concentration and location of smoke is limited or otherwise restricted to allow for ready evaluation through the space.

TENSILE MEMBRANE STRUCTURE. A membrane structure having a shape that is determined by tension in the membrane and in the geometry of the support structure. Typically, the structure consists of both flexible elements (e.g. membrane and cables), non-flexible elements (e.g. struts, masts beams and arches), and the anchorage (e.g. supports and foundations). This includes frame supported tensile membrane structures.

TENT. A nonpressurized membrane structure of a fabric weather barrier supported by poles and guys, in which the fabric weather barrier does not impart stability to the structure. Tents need not be fully enclosed on the sides.

THERMAL ISOLATION. Physical and space conditioning separation from conditioned space(s). The conditioned space(s) shall be controlled as separate zones for heating and cooling or conditioned by separate equipment.

THERMOPLASTIC MATERIAL. A plastic material that is capable of being repeatedly softened by increase of temperature and hardened by decrease of temperature.

THERMOSETTING MATERIAL. A plastic material that is capable of being changed into a substantially nonreformable product when cured.

THROUGH-PENETRATION. A breach in both sides of a floor, floor-ceiling or wall assembly to accommodate an item passing through the breaches.

THROUGH-PENETRATION FIRESTOP SYSTEM. An assemblage consisting of a fire-resistance-rated floor, floor-ceiling, or wall assembly, one or more penetrating items passing through the breaches in both sides of the assembly and the materials or devices, or both, installed to resist the spread of fire through the assembly for a prescribed period of time.

TIE-DOWN (HOLD-DOWN). A device used to resist uplift of the chords of shear walls.

TIE, WALL. Metal connector that connects wythes of masonry walls together.

TILE, STRUCTURAL CLAY. A hollow masonry unit composed of burned clay, shale, fire clay or mixture thereof, and having parallel cells.

TIRES, BULK STORAGE OF. Storage of tires where the area available for storage exceeds 20,000 cubic feet (566 m3).

TOOL. See “Equipment.”

TOWER CRANE. A crane that utilizes a vertical mast or tower to support a working boom (jib) in an elevated position. Loads are suspended from the working boom. While the working boom may be of the fixed type (horizontal or angled) or have luffing capability, it can always rotate to swing loads, either by rotating on the top of the tower (top slewing) or by the rotation of the tower (bottom slewing). The tower base may be fixed in one location or ballasted and moveable between locations. The definition of a tower crane shall include a climber crane. The definition of a tower crane shall not include mobile cranes that are configured with luffing jib and/or tower attachments.

TOXIC MATERIAL. A chemical that is lethal at the following doses or concentrations:

1.	A chemical that has a median lethal dose (LD50) of more than 50 milligrams per kilogram, but not more than 500 milligrams per kilogram of body weight when administered orally to albino rats weighing between 200 and 300 grams each; or

2.	A chemical that has a median lethal dose (LD50) of more than 200 milligrams per kilogram but not more than 1,000 milligrams per kilogram of body weight when administered by continuous contact for 24 hours (or less if death occurs within 24 hours) with the bare skin of albino rabbits weighing between 2 and 3 kilograms each; or

3.	A chemical that has a median lethal concentration (LC50) in air of more than 200 parts per million but not more than 2,000 parts per million by volume of gas or vapor, or more than 2 milligrams per liter but not more than 20 milligrams per liter of mist, fume or dust, when administered by continuous inhalation for 1 hour (or less if death occurs within 1 hour) to albino rats weighing between 200 and 300 grams each.

Exception: For purposes of this code, chlorine shall be classified as a highly toxic material.

TRANSIENT. Occupancy of a dwelling unit or sleeping unit for not more than 30 days.

TRANSIENT AIRCRAFT. Aircraft based at another location and that is at the transient location for not more than 90 days.

TRANSIENT LODGING. A building, facility or portion thereof, excluding inpatient medical care facilities and long-term care facilities, that contains one or more dwelling units or sleeping units. Examples of transient lodging include, but are not limited to, resorts, group homes, hotels, motels, dormitories, homeless shelters, halfway houses and social service lodging.

TRANSIT. The moving or transporting of a crane from one jobsite to another.

TRANSPARENT. The property of a material which is not opaque and through which objects lying beyond are clearly visible.

TRANSPARENT DOOR. A door, manually or power actuated, fabricated of transparent material, in which the transparent area above a reference line 18 inches (457 mm) above the bottom edge of the door is 80 percent or more of the remaining area of the door above such reference line.

TRANSPARENT SAFETY GLAZING MATERIALS. Materials which will clearly transmit light and also minimize the possibility of cutting or piercing injuries resulting from breakage of the material. Materials covered by this definition include laminated glass, heat-toughened glass, case-hardened glass or chemically tempered glass), wired glass, and plastic glazing.

TRAVEL. The function of the machine moving under its own power from one location to another on a jobsite.

TREATED WOOD. Wood products that are conditioned to enhance fire-retardant or preservative properties.

Fire-retardant-treated wood. Wood products that, when impregnated with chemicals by a pressure process or other means during manufacture, exhibit reduced surface-burning characteristics and resist propagation of fire.

Preservative-treated wood. Wood products that, conditioned with chemicals by a pressure process or other means, exhibit reduced susceptibility to damage by moisture, mold, fungi, insects or marine borers.

TRENCH. A narrow excavation (in relation to its length) made below the surface of the ground. In general, the depth is greater than the width, but the width of a trench (measured at the bottom) is not greater than 15 feet (4572 mm). If forms or other structures are installed or constructed in an excavation so as to reduce the dimension measured from the forms or structure to the side of the excavation to 15 feet (4572 mm) or less (measured at the bottom of the excavation), the excavation is also considered to be a trench.

TRIM. Picture molds, chair rails, baseboards, handrails, door and window frames and similar decorative or protective materials used in fixed applications.

TROUBLE SIGNAL. A signal initiated by the fire alarm system or device indicative of a fault in a monitored circuit or component.

TWO-POINT SUSPENDED SCAFFOLD (SWING STAGE). A suspended scaffold consisting of a platform supported by hangers (stirrups) suspended by two ropes from overhead supports and equipped with means to permit the raising and lowering of the platform to desired working levels.

TYPE A SOIL. Cohesive soils with an unconfined compressive strength of 1.5 ton per square foot (tsf) (144 kPa) or greater. Examples of cohesive soils are: clay, silty clay, sandy clay, clay loam and, in some cases, silty clay loam and sandy clay loam. Cemented soils such as caliche and hardpan are also considered Type A. However, no soil is Type A if:

(i)	The soil is fissured;

(ii)	The soil is subject to vibration from heavy traffic, pile driving, or similar effects;

(iii)	The soil has been previously disturbed;

(iv)	The soil is part of a sloped, layered system where the layers dip into the excavation on a slope of four horizontal to one vertical (4H:1V) or greater; or

(v)	The material is subject to other factors that would require it to be classified as a less stable material.

TYPE B SOIL. Soils that meet one of the following:

(i)	Cohesive soil with an unconfined compressive strength greater than 0.5 tsf (48 kPa) but less than 1.5 tsf (144 kPa);

(ii)	Granular cohesionless soils including: angular gravel (similar to crushed rock), silt, silt loam, sandy loam and, in some cases, silty clay loam and sandy clay loam;

(iii)	Previously disturbed soils except those which would otherwise be classed as Type C soil;

(iv)	Soil that meets the unconfined compressive strength or cementation requirements for Type A, but is fissured or subject to vibration;

(v)	Dry rock that is not stable; or

(vi)	Material that is part of a sloped, layered system where the layers dip into the excavation on a slope less steep than four horizontal to one vertical (4H:1V), but only if the material would otherwise be classified as Type B.

TYPE B UNIT. A dwelling unit or sleeping unit designed and constructed for accessibility in accordance with this code and the provisions for Type B units in ICC A117.1, consistent with the design and construction requirements of the federal Fair Housing Act.

TYPE B+NYC UNIT. A dwelling unit or sleeping unit designed and constructed for accessibility in accordance with this code and Section 1004 (Type B Units) of ICC A117.1, except as modified by Sections 1107.2.1 through 1107.2.8.

TYPE C SOIL. Soils that meet one of the following:

(i)	Cohesive soil with an unconfined compressive strength of 0.5 tsf (48kPa) or less;

(ii)	Granular soils including gravel, sand, and loamy sand;

(iii)	Submerged soil or soil from which water is freely seeping;

(iv)	Submerged rock that is not stable, or

(v)	Material in a sloped, layered system where the layers dip into the excavation or a slope of four horizontal to one vertical (4H:1V) or steeper.

UNCONFINED COMPRESSIVE STRENGTH (SOIL). The load per unit area at which a soil will fail in compression. It can be determined by laboratory testing, or estimated in the field using a pocket penetrometer, by thumb penetration tests, and other methods.

UNDERLAYMENT. One or more layers of approved material over which a roof covering is applied.

UNDERPINNING. The alteration of an existing foundation to transfer loads to a lower bearing stratum using new piers, piles, or other structural support elements installed below the existing foundation.

UNENCLOSED PERIMETER. Any exterior portion of a building that is not solidly enclosed with the permanent façade, including the windows; or any exterior edge of a roof that is not enclosed with its permanent parapet or guardrail.

UNSTABLE (REACTIVE) MATERIAL. A material, other than an explosive, which in the pure state or as commercially produced, will vigorously polymerize, decompose, condense or become self-reactive and undergo other violent chemical changes, including explosion, when exposed to heat, friction or shock, or in the absence of an inhibitor, or in the presence of contaminants, or in contact with incompatible materials. Unstable (reactive) materials shall be classified as follows:

Class 4. Materials that in themselves are readily capable of detonation or explosive decomposition or explosive reaction at normal temperatures and pressures. This class includes materials that are sensitive to mechanical or localized thermal shock at normal temperatures and pressures.

Class 3. Materials that in themselves are capable of detonation or of explosive decomposition or explosive reaction but which require a strong initiating source or which must be heated under confinement before initiation. This class includes materials that are sensitive to thermal or mechanical shock at elevated temperatures and pressures.

Class 2. Materials that in themselves are normally unstable and readily undergo violent chemical change but do not detonate. This class includes materials that can undergo chemical change with rapid release of energy at normal temperatures and pressures, and that can undergo violent chemical change at elevated temperatures and pressures.

Class 1. Materials that in themselves are normally stable but which can become unstable at elevated temperatures and pressure.

USE (MATERIAL). Placing a material into action, including solids, liquids and gases.

USE/USING (SCAFFOLD). Any work or activity performed on or from the scaffold. In addition, for a suspended scaffold, the use of the scaffold shall include the operation of the scaffold at the site, provided during such operation any vertical or horizontal relocation of the scaffold does not require a modification to the counterweight, or does not require the placement, relocation, or removal of any anchorage, attachment, outrigger beam, tie-back, or connection to the building or structure.

VALUE (OF ALTERATIONS, TO DETERMINE REQUIRED ACCESSIBLITY). The value of alterations shall be determined by adding the estimated cost of the proposed alteration, including minor alterations but excluding ordinary repairs, computed as of the time of submitting the application for construction document approval, or, where no permit is required, computed at the time of the work, to the actual cost of any and all alterations and minor alterations made in the preceding 12-month period. Where the alteration includes an enlargement, the value of the alteration shall include the cost of the enlargement.

VALUE (OF ALTERATIONS, TO DETERMINE REQUIRED FIRE PROTECTION). The value of alterations shall be determined by adding the estimated cost of the proposed alteration, excluding minor alterations and ordinary repairs computed as of the time of submitting the application for construction document approval, to the actual cost of any and all alterations made in the preceding 12-month period. Where the proposed alteration includes an enlargement, the value of such alteration shall also include the cost of the enlargement.

VALUE (OF EXISTING BUILDING OR SPACE). The value of an existing building shall be determined at the option of the applicant on the basis of one and one-quarter times the current assessed valuation of the building, as adjusted by the current State equalization rate, or on the basis of the current replacement cost of the building. The value of an existing space shall be determined on the basis of the current replacement cost of the space. Satisfactory evidence of current replacement cost shall be submitted to the commissioner. Where the alteration includes an enlargement, the value of the existing building shall be determined without including the value of the enlargement.

VARIANCE. See Section G201.1.2.

VAULT. Any space below the surface of a street that is covered over, except those openings that are used exclusively as places for descending, by means of steps to the cellar or basement of any building.

VEGETATIVE ROOF. A system constructed in-situ consisting of either a roof assembly and additional landscape material components, including growing media, engineered soils, filter fabric, integral drainage systems and roof surface to facilitate the growth of vegetation or a pre-vegetated tray or trays no more than 6 inches (152 mm) high and assembled on top of a roof covering.

VEHICLE BARRIER. A component or a system of components near open sides or walls of garage floors or ramps that acts as a restraint for vehicles.

VEHICULAR GATE. A gate that is intended for use at a vehicular entrance or exit and that is not intended for use by pedestrian traffic.

VENEER. A facing attached to a wall for the purpose of providing ornamentation, protection or insulation, but not counted as adding strength to the wall. Veneers are nonstructural in that they do not carry any load other than their own weight.

VINYL SIDING. A shaped material, made principally from rigid polyvinyl chloride (PVC) that is used as an exterior wall covering.

VISIBLE ALARM NOTIFICATION APPLIANCE. A notification appliance that alerts by the sense of sight.

V-ZONE. Velocity Zones V, VO, VE, or V1-30 (See Coastal High Hazard Area).

WALKABLE FLOOR (CONCRETE CONSTRUCTION). A floor where the concrete slab has been poured and the formwork stripped.

WALKABLE FLOOR (PRECAST CONCRETE CONSTRUCTION). A floor where the frame is erected and the precast concrete floor is fixed in place.

WALKABLE FLOOR (STEEL CONSTRUCTION). A floor where the frame is erected and the deck is tack welded or fixed in place.

WALL. A vertical element with a horizontal length-to-thickness ratio greater than three, used to enclose space.

Cavity wall. A wall built of masonry units or of concrete, or a combination of these materials, arranged to provide an airspace within the wall, and in which the inner and outer parts of the wall are tied together with metal ties.

Dry-stacked, surface-bonded walls. A wall built of concrete masonry units where the units are stacked dry, without mortar on the bed or head joints, and where both sides of the wall are coated with a surface-bonding mortar.

Parapet wall. The part of any wall entirely above the roof line.

WALL SIGN. Any sign attached to or erected against the wall of a building or structure, projecting no more than 15 inches (381 mm) from the face of the wall, with the exposed face of the sign in a plane parallel to the plane of said wall.

WATERPROOFING. Waterproofing is a protective measure applied to building foundation walls and slabs to prevent moistures and liquid water from passing into interior spaces.

WATER-REACTIVE MATERIAL. A material that explodes; violently reacts; produces flammable, toxic or other hazardous gases; or generates enough heat to cause auto-ignition or ignition of combustible materials upon exposure to water or moisture. Water-reactive materials are classified as follows:

Class 3. Materials that react explosively with water without requiring heat or confinement.

Class 2. Materials that react violently with water or cause water to boil upon contact; produce flammable, toxic or other hazardous gases upon contact with water; or upon contact with water generate sufficient heat to cause auto-ignition of adjoining combustible materials.

Class 1. Materials that may react with water with some release of energy, but not violently.

WATER-RESISTIVE BARRIER. A material behind an exterior wall covering that is intended to resist liquid water that has penetrated behind the exterior wall covering from further intruding into the exterior wall assembly.

WEATHER-EXPOSED SURFACES. Surfaces of walls, ceilings, floors, roofs, soffits and similar surfaces exposed to the weather except the following:

1.	Ceilings and roof soffits enclosed by walls, fascia, bulkheads or beams that extend a minimum of 12 inches (305 mm) below such ceiling or roof soffits.

2.	Walls or portions of walls beneath an unenclosed roof area, where located a horizontal distance form an open exterior opening equal to at least twice the height of the opening.

3.	Ceiling and roof soffits located a minimum horizontal distance of 10 feet (3048 mm) from the outer edges of the ceiling or roof soffits.

WET-CHEMICAL EXTINGUISHING SYSTEM. A solution of water and potassium-carbonate-based chemical, potassium-acetate-based chemical or a combination thereof, forming a fire-extinguishing agent.

WHEEL MOUNTED CRANE (MULTIPLE CONTROL STATIONS). A mobile crane consisting of a rotating superstructure, operating machinery, and operator’s station and boom, mounted on a crane carrier equipped with axles and rubber-tired wheels for travel, a power source(s), and having separate stations for driving and operating.

WHEEL MOUNTED CRANE (SINGLE CONTROL STATION). A mobile crane consisting of a rotating superstructure, operating machinery, and boom, mounted on a crane carrier equipped with axles and rubber-tired wheels for travel, a power source, and having a single control station for driving and operating.

WHEELCHAIR SPACE. A space for a single wheelchair and its occupant.

WIND SPEED, V (BASIC). Basic design wind speeds.

WIND SPEED, Vasd. (ALLOWABLE STRESS DESIGN). Allowable stress design wind speeds.

WIND-BORNE DEBRIS REGION. Areas within hurricane-prone regions located:

1. Within 1 mile (1.61 km) of the coastal mean high water line where the basic design wind speed, V, is 130 mph (58 m/s) or greater.

For Risk Category IV buildings and structures, and Risk Category III health care facilities, the wind-borne debris region shall be based on the basic design wind speed for Risk Category IV on Table 1609.3.

WINDER. A stair tread with nonparallel edges.

WIRE BACKING. Horizontal strands of tautened wire attached to surfaces of vertical supports that, when covered with the building paper, provide a backing for cement plaster.

WIRELESS PROTECTION SYSTEM. A system or a part of a system that can transmit and receive signals without the aid of wire.

WOOD SHEAR PANEL. A wood floor, roof or wall component sheathed to act as a shear wall or diaphragm.

WOOD STRUCTURAL PANEL. A panel manufactured from veneers, wood strands or wafers or a combination of veneer and wood strands or wafers bonded together with waterproof synthetic resins or other suitable bonding systems. Examples of wood structural panels are:

Composite panels. A wood structural panel that is comprised of wood veneer and reconstituted wood-based material and bonded together with waterproof adhesive;

Oriented strand board (OSB). A mat-formed wood structural panel comprised of thin rectangular wood strands arranged in cross-aligned layers with surface layers normally arranged in the long panel direction and bonded with waterproof adhesive; or

Plywood. A wood structural panel comprised of plies of wood veneer arranged in cross-aligned layers. The plies are bonded with waterproof adhesive that cures on application of heat and pressure.

WOOD/PLASTIC COMPOSITE. A composite material made primarily from wood or cellulose-based materials and plastic.

WORKING DECK (CONCRETE CONSTRUCTION). The level where the floor is being formed.

WORKING DECK (DEMOLITION). The level where the floor is being broken up.

WORKING DECK (PRECAST CONCRETE CONSTRUCTION). The level where the floor is being placed.

WORKING DECK (STEEL CONSTRUCTION). The floor where the metal decking and steel components are being placed before concrete is poured.

WORKSTATION. A defined space within a fabrication area in which a specific function, laboratory procedure or research activity relating to semiconductor manufacture is conducted. A workstation may include equipment using HPM, hazardous materials storage cabinets, flammable liquid storage cabinets or gas cabinets, ventilation equipment, fire protection devices, detection devices, and electrical devices.

WYTHE. Each continuous, vertical section of a wall, one masonry unit in thickness.

ZERO VESTIBULE CLEARANCE. A limited space on the elevator lobby between the exterior of the hoistway door and the security door attached to the elevator hoistway.

ZONE. A defined area within the protected premises. A zone can define an area from which a signal can be received, an area to which a signal can be sent or an area in which a form of control can be executed.

ZONE, NOTIFICATION. An area within a building or facility covered by notification appliances that are activated simultaneously.

§ 4.  Chapter 3 of the New York city building code, as added by local law number 33 for the year 2007, sections 302.1, 303.1, 306.1, 306.2, 306.3, 306.4, 307.1, 307.2, 307.3, 307.4, 307.5, 307.6, 307.7, 308.2, 308.2.2, 308.3, 308.4, 308.5, 309.1, 309.2, 310, 310.1.1, 310.1.2, 310.2, 311.2, and 311.3, and tables 307.1(1) and 307.1(2), and the title of section 308 as amended by, and sections 304.1.1, 307.1.1, and 308.3.1 as added by local law number 141 for the year 2013, and section 304.1 as amended by local law number 78 for the year 2015, is amended to read as follows:

CHAPTER 3
USE AND OCCUPANCY CLASSIFICATION

SECTION BC 301
GENERAL

301.1 Scope. The provisions of this chapter shall control the classification of all buildings and structures, and spaces therein, as to use and occupancy.

SECTION BC 302
CLASSIFICATION

302.1 General. Structures or portions of structures shall be classified with respect to occupancy in one or more of the groups listed below. A room or space that is intended to be occupied at different times for different purposes shall comply with all of the requirements that are applicable to each of the purposes for which the room or space will be occupied. Structures with multiple occupancies or uses shall comply with Section 508. Where a structure, or portion thereof, is proposed for a purpose [which] that is not specifically provided for in this code, such structure, or portion thereof, shall be classified in the group [which] that the occupancy most nearly resembles, according to the fire safety and relative hazard involved, and as approved by the commissioner.

1.	Assembly (see Section 303): Groups A-1, A-2, A-3, A-4 and A-5.

2.	Business (see Section 304): Group B.

3.	Educational (see Section 305): Group E.

4.	Factory and Industrial (see Section 306): Groups F-1 and F-2.

5.	High Hazard (see Section 307): Groups H-1, H-2, H-3, H-4 and H-5.

6.	Institutional (see Section 308): Groups I-1, I-2, I-3 and I-4.

7.	Mercantile (see Section 309): Group M.

8.	Residential (see Section 310): Groups R-1, R-2 and R-3.

9.	Storage (see Section 311): Groups S-1 and S-2.

10.	Utility and Miscellaneous (see Section 312): Group U.

For a listing of occupancy group classifications that corresponds with uses listed in the New York City Zoning Resolution, refer to department rules.

SECTION BC 303
ASSEMBLY GROUP A

303.1 Assembly Group A. Assembly Group A occupancy includes, among others, the use of a building or structure or a portion thereof, excluding a dwelling unit, for the gathering of any number of persons for purposes such as civic, social or religious functions, recreation, food or drink consumption, awaiting transportation, or similar group activities; or when occupied by 75 persons or more for educational or instructional purposes.

[Exceptions:]

303.1.1 Definitions. The following term is defined in Chapter 2:

PLACE OF ASSEMBLY.

303.1.2 Buildings and nonaccessory tenant spaces. [1.] A building or nonaccessory tenant space used for assembly purposes with an occupant load of fewer than 75 persons shall be classified as a Group B occupancy, except that the number of plumbing fixtures for such a building or space is permitted to be calculated in accordance with the requirements for assembly occupancies.

303.1.3 Accessory assembly spaces. [2.] A room or space used for assembly purposes with an occupant load of fewer than 75 persons and accessory to another occupancy shall be classified as a Group B occupancy or as part of that occupancy, except that the number of plumbing fixtures for such a room or space is permitted to be calculated in accordance with the requirements for assembly occupancies.

[Assembly occupancies shall include the following:][A-1] 303.2 Assembly Group A-1. Group A-1 occupancy includes assembly uses, usually with fixed seating, intended for the production and viewing of the performing arts or motion pictures including, but not limited to:

Motion picture theaters

Symphony and concert halls

Television and radio studios admitting an audience

Theaters

[A-2] 303.3 Assembly Group A-2. Group A-2 occupancy includes assembly uses intended for food and/or drink consumption including, but not limited to:

Banquet halls

Cabarets

[Cafeterias, except as provided for in A-3]

[Dance halls]

[Night clubs]

Casinos (gaming areas)

Nightclubs, including dance halls

Restaurants, cafeterias (except as provided for in A-3), and similar dining facilities

Taverns and bars

[A-3] 303.4 Assembly Group A-3. Group A-3 occupancy includes assembly uses intended for worship, recreation or amusement and other assembly uses not classified elsewhere in Group A including, but not limited to:

Amusement arcades

Art galleries

Bowling alleys

Cafeterias for children up to and including the 12th grade

Classrooms and instructional rooms with 75 persons or more; such rooms with fewer than 75 persons shall be classified as Group B or E

Community halls

Courtrooms

Custodial care facilities with 75 or more persons, providing care to persons over the age of 2, where no more than four occupants are incapable of responding to an emergency situation without physical assistance from staff

Dance studio or instruction (not including food or drink consumption)

Exhibition halls

Funeral parlors

Gymnasiums (without spectator seating)

[Religious houses of worship]

Indoor swimming pools (without spectator seating)

Indoor tennis courts (without spectator seating)

Lecture halls

Museums

Places of religious worship (Houses of worship)

[Waiting areas in transportation terminals]

Pool and billiard parlors

School auditoriums

Waiting areas in transportation terminals

[A-4] 303.5 Assembly Group A-4. Group A-4 occupancy includes assembly uses intended for viewing of indoor sporting events and activities with spectator seating including, but not limited to:

Arenas

Skating rinks

Swimming pools

Tennis courts

[A-5] 303.6 Assembly Group A-5. Group A-5 occupancy includes assembly uses intended for participation in or viewing outdoor activities including, but not limited to:

Amusement park structures

Bleachers

Grandstands

Stadiums

[303.2] 303.7 Certificate of Operation. A Certificate of Operation shall be required, as per Section 28-117.1, for the following [places of] assembly occupancies:

1.	Indoor [places of] assembly occupancies used or intended for use by 75 persons or more, including open spaces at 20 feet (6096 mm) or more above or below grade plane, such as roofs or roof terraces.

2.	Outdoor [places of] assembly occupancies used and intended for use by 200 persons or more.

SECTION BC 304
BUSINESS GROUP B

304.1 Business Group B. Business Group B occupancy includes, among others, the use of a building or structure, or a portion thereof, for office, professional, service-type transactions, or for conducting public or civic services, including the incidental storage of records and accounts and the incidental storage of limited quantities of stocks of goods for office use or purposes. Business Group B occupancies shall include, but not be limited to, the following:

Airport traffic control towers

Ambulatory [health] care facilities

Animal hospitals, kennels and pounds, veterinary clinics and pet shops

Banks

Barber and beauty shops

Civic administration offices

Clinic outpatient, including group medical centers, and neighborhood family care centers

Custodial care facilities with fewer than 75 persons, providing care to persons over the age of 2, where no more than four occupants are incapable of responding to an emergency situation without physical assistance from staff

Dry cleaning and laundries; pick-up and delivery stations and self-service

Educational occupancies for students above the 12th grade, where not classified in Group A. Such occupancy may be used occasionally for educational purposes offered to children through the 12th grade

Electronic data processing

Laboratories; nonproduction testing and research, as per Section [424] 427

Libraries when not classified in Group E

Motor vehicle showrooms

Offices

Post offices

Photocopying and printing shops using electronic printing equipment

Professional services (architects, attorneys, dentists, physicians, engineers, etc.)

Radio and television stations not admitting an audience

Telephone exchanges

Training and skill development not [within] in a school or academic program (this shall include, but not be limited to, tutoring centers, martial arts studios, gymnastics and similar uses regardless of the ages served, and where not classified as a Group A occupancy)

[304.1.1] 304.2 Definitions. The following [words and] terms [shall, for the purposes of this section and as used elsewhere in this code, have the meanings shown herein.] are defined in Chapter 2:

AMBULATORY CARE FACILITY.

CLINIC, OUTPATIENT.[Buildings or portions thereof used to provide medical care on less than a 24-hour basis to individuals who are not rendered incapable of self-preservation by the services provided.]

SECTION BC 305
EDUCATIONAL GROUP E

305.1 Educational Group E. Educational Group E occupancy includes, among others, the use of a building or structure, or a portion thereof, by five or more persons at any one time for educational purposes offered to children through the 12th grade and where no more than two children are under the age of 2, including but not limited to the following:

Academies

Day care facilities where no more than two children are under the age of 2

Libraries accessory to Group E occupancies

Schools

Exceptions:

1.	Classrooms and instructional rooms with 75 or more persons shall be classified as Group A-3.

2.	Day care services provided within a dwelling unit as described in Section 310.

3.	Custodial care facilities with up to 30 children under the age of 2 are permitted to be classified as Group E when the rooms where such children are cared for are located on the level of exit discharge and each of these child care rooms has an exit door directly to the exterior.

305.2 Reserved.

SECTION BC 306
FACTORY GROUP F

306.1 Factory Industrial Group F. Factory Industrial Group F occupancy includes, among others, the use of a building or structure, or a portion thereof, for assembling, disassembling, fabricating, finishing, manufacturing, packaging, repair, cleaning, laundering or processing operations that are not classified as a Group H hazardous occupancy. Factory Industrial Group F occupancy also includes certain mechanical and/or electrical equipment rooms in accordance with Section 306.3.

306.2 [Factory Industrial F-1 Moderate-Hazard Occupancy] Moderate-hazard factory industrial, Group F-1.

Factory industrial uses [which] that are not classified as Factory Industrial F-2 Low Hazard shall be classified as F-1 Moderate Hazard and shall include, but not be limited to, the following:

Aircraft (manufacturing, not to include repair)

Aircraft repairs

Automobiles and other motor vehicles, manufacturing

Automobiles and other motor vehicles, repairs

Bakeries

Beverages; over [16 percent] 16-percent alcohol content

Boats

Boat repairs

Brooms or brushes

Canvas or similar fabric

Carpets and rugs

Carpets and rugs, cleaning, using or storing solvents having a flash point between 100°F (38°C) and 138.2°F (59°C) (Tag closed cup)

Clothing

Disinfectants

Dry cleaning and dyeing using or storing solvents having a flash point between 100°F (38°C) and 138.2°F (59°C) (Tag closed cup)

Electric generation plants

Electrical substations

Engines (including rebuilding)

Food processing, except meat slaughtering or preparation of fish for packing

Food processing establishments and commercial kitchens not adjoining a restaurant, cafeteria or similar dining facilities

Furniture

Hemp products

Jute products

Laboratories; for production (moderate-hazard), that may involve the synthesis or storage of materials that constitute a physical or health hazard in quantities below those found in Tables 307.1(1) and 307.1(2)

Leather products

Metals; finishing, plating, grinding, sharpening, polishing, cleaning, rustproofing, heat treatment or similar processes

Millwork (sash and door)

Motion pictures filming (without spectators)

Musical instruments

Optical goods

Paper mills or products

Photographic film

Plastic products

Printing or publishing

Recreational vehicles

Refuse incineration

Shoes

Soaps and detergents

Textiles

Tobacco

Trailers

Upholstering

Wood; distillation

Woodworking (cabinet) using no more than 2 quarts (1.9 L) per day or storing no more than 20 gallons (75.7 L) of paint, varnish, lacquer or shellac

306.3 [Factory Industrial F-2] Low-hazard [Occupancy] factory industrial, Group F-2. Factory industrial uses that involve the cleaning, laundering, fabrication or manufacturing of noncombustible materials [which] that during finishing, packing or processing do not involve a significant fire hazard shall be classified as F-2 occupancies and shall include, but not be limited to, the following:

Appliances

Athletic equipment

Automobile laundries

Automobile wrecking establishments

Beverages; up to and including [16 percent] 16-percent alcohol content; bottling works

Beverages; nonalcoholic

Bicycles

Brick and masonry

Business machines

Cameras and photo equipment

Carpets and rugs, cleaning, using or storing solvents having a flash point above 138.2°F (59°C) (Tag closed cup)

Ceramic products

Commercial kitchens adjoining restaurants, cafeterias (including those classified in Group A-3), or similar dining facilities

Construction and agricultural machinery

Dry cleaning and dyeing using or storing solvents having a flash point above 138.2°F (59°C) (Tag closed cup)

Electronics

Food processing; meat slaughtering or preparation of fish for packing

Foundries

Glass products

Gypsum

Ice

Laboratories; for production (low-hazard), that may involve the synthesis or storage of materials that constitute a physical or health hazard in quantities below those found in Tables 307.1(1) and 307.1(2)

Laundries

Machinery

Mechanical and/or electrical equipment rooms that are neither identified as incidental uses in Table 509 nor classified as the occupancy within which they are located per Section 508.1

Metal products (fabrication and assembly), not including flammable metals and alloys listed in Section 307

Plastic products; nonflammable

Printing; incidental to primary use, area not exceeding 2,000 square feet (185.8 m2)

Television filming (without spectators)

306.4 Location restrictions. Locations of spaces classified in Factory Group F may be restricted within a building containing a Group R occupancy pursuant to Section 510.8.

SECTION BC 307
HIGH-HAZARD GROUP H

307.1 [High-Hazard] High-hazard Group H. [High-Hazard] High-hazard Group H occupancy includes, among others, the use of a building or structure, or a portion thereof, that involves the manufacturing, processing, generation or storage of materials that constitute a physical or health hazard in quantities in excess of those allowed in control areas complying with Section 414, based on the maximum allowable quantity limits for control areas set forth in Tables 307.1(1) and 307.1(2). Hazardous occupancies are classified in Groups H-1, H-2, H-3, H-4 and H-5 and shall be in accordance with this section, the requirements of Section 415 and the New York City Fire Code.

[Exceptions: The following shall not be classified as Group H, but shall be classified as the occupancy that they most nearly resemble.]

307.1.1 Uses other than Group H. An occupancy that stores, uses or handles hazardous materials as described in one or more of the following items shall not be classified as Group H, but shall be classified as the occupancy that it most nearly resembles.

- Buildings and structures occupied for the application of flammable finishes, provided that such buildings or areas conform to the requirements of [Section 416 and] the New York City Fire Code and Section 416 of this code.

2.	Wholesale and retail sales and storage of flammable and combustible liquids in mercantile occupancies conforming to the New York City Fire Code.

3.	Closed piping system containing flammable or combustible liquids or gases utilized for the operation of machinery or equipment.

4.	Cleaning establishments that utilize combustible liquid solvents having a flash point of 140°F (60°C) or higher in closed systems employing equipment listed by an approved testing agency, provided that this occupancy is separated from all other areas of the building by 1-hour fire barriers constructed in accordance with Section 707 or 1-hour horizontal assemblies constructed in accordance with Section [712] 711, or both.

5.	Cleaning establishments that utilize a liquid solvent having a flash point at or above 200°F (93°C).

6.	Liquor stores and distributors without bulk storage.

7.	Refrigeration systems.

8.	The storage or utilization of materials for agricultural purposes on the premises.

9.	Stationary batteries utilized for facility emergency or standby power, [uninterrupted] uninterruptable power supply or telecommunication facilities, provided that the batteries are provided with safety venting caps and ventilation is provided in accordance with the New York City Mechanical Code.

10.	[Corrosives shall not include personal or household products in their original packaging used in retail display or commonly used building materials.] Corrosive personal or household products in their original packaging used in retail display.

11.	Commonly used corrosive building materials.

[11.] 12. Buildings and structures occupied for aerosol storage shall be classified as Group S-1, provided that such buildings conform to the requirements of the New York City Fire Code.

[12.] 13.	Display and storage of nonflammable solid and nonflammable or noncombustible liquid hazardous materials in quantities not exceeding the maximum allowable quantity per control area in Group M or S occupancies complying with Section 414.2.5.

[13.] 14.	The storage of black powder, smokeless propellant and small arms primers in Groups M and R-3 and special industrial explosive devices in Groups B, F, M and S, provided such storage conforms to the quantity limits and requirements prescribed in the New York City Fire Code.

[14.] 15.	Laboratories for nonproduction testing, research, experimental, instructional or educational purposes, in compliance with Section [424] 427.

[307.1.1 Hazardous materials. Hazardous materials in any quantity shall conform to the requirements of this code, including Section 414, and the New York City Fire Code.]

| TABLE 307.1(1) MAXIMUM ALLOWABLE QUANTITY PER CONTROL AREA OF HAZARDOUS MATERIALS POSING A PHYSICAL HAZARDa,j,m,n,q |
| --- |
|  |  |  | STORAGEb | USE-CLOSED SYSTEMSb | USE-OPEN SYSTEMSb |
| MATERIAL | CLASS | GROUP WHEN THE MAXIMUM ALLOWABLE QUANTITY IS EXCEEDEDq | Solid Pounds (cubic feet) | Liquid Gallons (pounds) | Gas SCF | Solid Pounds (cubic feet) | Liquid gallons (pounds) | Gas SCF | Solid Pounds (cubic feet) | Liquid gallons (pounds) |
| Combustible Liquidc, i, r | II | H-2 or H-3 | Not Applicable | 120d, e | Not Applicable | Not Applicable | 120d | Not Applicable | Not Applicable | 30d |
|  | IIIA | H-2 or H-3 |  | 330d, e |  |  | 330d |  |  | 80d |
|  | IIIB | Not Applicable |  | 13,200e, f |  |  | 13,200f |  |  | 3,300f |
| Combustible fiber | Loose | H-3 | (100) | Not Applicable | Not Applicable | (100) | Not Applicable | Not Applicable | (20) | Not Applicable |
|  | Baleds |  | (1,000) |  |  | (1,000) |  |  | (200) |  |
| Cryogenics flammable | Not Applicable | H-2 | Not Applicable | 45d | Not Applicable | Not Applicable | 45d | Not Applicable | Not Applicable | 10d |
| Cryogenics oxidizing | Not Applicable | H-3 | Not Applicable | 45d | Not Applicable | Not Applicable | 45d | Not Applicable | Not Applicable | 10d |
| Explosives | Division 1.1 | H-1 | 1e, g | (1)e, g | Not Applicable | 0.25g | (0.25)g | Not Applicable | 0.25g | (0.25)g |
|  | Division 1.2 | H-1 | 1e, g | (1)e, g |  | 0.25g | (0.25)g |  | 0.25g | (0.25)g |
|  | Division 1.3 | H-1 or H-2 | 5e, g | (5)e, g |  | 1g | (1)g |  | 1g | (1)g |
|  | Division 1.4 | H-3 | 50e, g | (50)e, g |  | 50g | (50)g |  | Not Applicable | Not Applicable |
|  | Division 1.4G | H-3 | 125d, e, l | Not Applicable |  | Not Applicable | Not Applicable |  | Not Applicable | Not Applicable |
|  | Division 1.5 | H-1 | 1e, g | (1)e, g |  | 0.25g | (0.25)g |  | 0.25g | (0.25)g |
|  | Division 1.6 | H-1 | 1d, e, g | Not Applicable |  | Not Applicable | Not Applicable |  | Not Applicable | Not Applicable |
| Flammable gas | Gaseous | H-2 | Not Applicable | Not Applicable | 1,000d, e | Not Applicable | Not Applicable | 1,000d, e | Not Applicable | Not Applicable |
|  | Liquefied |  |  | (150)d, e | Not Applicable |  | (150)d, e | Not Applicable |  |  |
| Flammable liquidsc,k | IAo | H-2 or H-3 | Not Applicable | 30d, e | Not Applicable | Not Applicable | 30d | Not Applicable | Not Applicable | 10d |
|  | IB and IC |  |  | 120d, e |  |  | 120d |  |  | 30d |
| Combination Flammable liquid (IAo, IB, IC) | Not Applicable | H-2 or H-3 | Not Applicable | 120d, e, h | Not Applicable | Not Applicable | 120d, h | Not Applicable | Not Applicable | 30d, h |
| Flammable solids5 |  |  |  |  |  |  |  |  |  |  |
| Pigs, ingots, billets, heavy castings | Not Applicable | H-3 | 1,000d, e | Not Applicable | Not Applicable | 1,000d | Not Applicable | Not Applicable | 1,000d | Not Applicable |
| Light castings, light metallic products |  |  | 125d, e |  |  | 125d |  |  | 25d |  |
| Scraps, shavings, powders, dusts |  |  | 1d, e |  |  | 1d |  |  | 1d |  |
| All others |  |  | 125d, e |  |  | 125d |  |  | 25d |  |
| Inert gas | Gaseous | Not Applicable | Not Applicable | Not Applicable | Not Limited | Not Applicable | Not Applicable | Not Limited | Not Applicable | Not Applicable |
|  | Liquefied |  |  |  |  |  |  |  |  |  |
| Cryogenic inert | Not Applicable | Not Applicable | Not Applicable | Not Applicable | Not Limited | Not Applicable | Not Applicable | Not Limited | Not Applicable | Not Applicable |
| Organic peroxidep | Unclassified Detonable | H-1 | 1e, g | (1)e, g | Not Applicable | 0.25g | (0.25)g | Not Applicable | 0.25g | (0.25)g |
|  | I | H-2 | 5d, e | (5)d, e |  | 1d | (1)d |  | 1d | (1)d |
|  | II | H-3 | 50d, e | (50)d, e |  | 50d | (50)d |  | 10d | (10)d |
|  | III | H-3 | 125d, e | (125)d, e |  | 125d | (125)d |  | 25d | (25)d |
|  | IV | Not Applicable | Not Limited | Not Limited |  | Not Limited | Not Limited |  | Not Limited | Not Limited |
|  | V | Not Applicable | Not Limited | Not Limited |  | Not Limited | Not Limited |  | Not Limited | Not Limited |
| Oxidizer | 4 | H-1 | 1g | (1)e, g | Not Applicable | 0.25g | (0.25)g | Not Applicable | 0.25g | (0.25)g |
|  | 3k | H-2 | 10d, e | (10)d, e |  | 2d | (2)d |  | 2d | (2)d |
|  | 2 | H-3 | 250d, e | (250)d, e |  | 250d | (250)d |  | 50d | (50)d |
|  | 1 | H-3 | 4,000e,f | (4,000)e,f |  | 4,000f | (4,000)f |  | 1,000f | (1,000)f |
| Oxidizing gas | Gaseous | H-3 | Not Applicable | Not Applicable | 1,500d, e | Not Applicable | Not Applicable | 1,500d, e | Not Applicable | Not Applicable |
|  | Liquefied |  |  | (150)d, e | Not Applicable |  | (150)d, e | Not Applicable |  |  |
| Pyrophoric materialp detonable | Not Applicable | H-1 | 1e, g | (1)e, g | 10e, g | 0.25g | (0.25)g | 2e, g | 0 | 0 |
| Pyrophoric material nondetonable | Not Applicable | H-2 | 4e, g | (4)e, g | 50e, g | 1g | (1)g | 10e, g | 0 | 0 |
| Unstable (reactive)p detonable | 4 | H-1 | 1e, g | (1)e, g | 10e, g | 0.25g | (0.25)g | 2e, g | 0.25g | (0.25)g |
|  | 3 | H-1 | 1e, g | (1)e, g | 10e, g | 0.25g | (0.25)g | 2e, g | 0.25g | (0.25)g |
| Unstable (reactive) nondetonable | 4 | H-1 | 1e, g | (1)e, g | 10e, g | 0.25g | (0.25)g | 2e, g | 0.25g | (0.25)g |
|  | 3 | H-1 or H-2 | 5d, e | (5)d, e | 50d, e | 1d | (1)d | 10d, e | 1d | (1)d |
|  | 2 | H-3 | 50d, e | (50)d, e | 250d, e | 50d | (50)d | 250d, e | 10d | (10)d |
|  | 1 | Not Applicable | Not Limited | Not Limited | 750d, e | Not Limited | Not Limited | Not Limited | Not Limited | Not Limited |
| Water-reactive detonablep | 3 | H-1 | 1e, g | (1)e, g | Not Applicable | 0.25g | (0.25)g | Not Applicable | 0.25g | (0.25)g |
|  | 2 | H-1 | 1e, g | (1)e, g |  | 0.25g | (0.25)g |  | 0.25g | (0.25)g |
| Water- reactive nondetonable | 3 | H-2 | 5d, e | (5)d, e | Not Applicable | 5d | (5)d | Not Applicable | 1d | (1)d |
|  | 2 | H-3 | 50d, e | (50)d, e |  | 50d | (50)d |  | 10d | (10)d |
|  | 1 | Not Applicable | Not Limited | Not Limited |  | Not Limited | Not Limited |  | Not Limited | Not Limited |

For SI: 1 cubic foot = 0.028 m3, 1 pound = 0.454 kg, 1 gallon = 3.785 L.

- For use of control areas, see [Section 2703.8.3 of] the New York City Fire Code and Section 414.2 of this code.

- The aggregate quantity in storage, handling and use shall not exceed the quantity listed for storage.

- The quantities of alcoholic beverages in retail and wholesale sales occupancies shall not be limited providing the liquids are packaged in individual containers not exceeding 1.3 gallons. In retail and wholesale sales occupancies, the quantities of medicines, foodstuffs, consumer or industrial products, and cosmetics containing not more than 50 percent by volume of water-miscible liquids with the remainder of the solutions not being flammable shall not be limited, provided that such materials are packaged in individual containers not exceeding 1.3 gallons.

- Maximum allowable quantities, except for liquefied petroleum gas and flammable liquid motor fuel, shall be increased 100 percent in buildings protected throughout by a sprinkler system. Where Note e also applies, the increase for both notes shall be applied accumulatively.

- Maximum allowable quantities, except for liquefied petroleum gas and flammable liquid motor fuel, shall be increased 100 percent when stored in approved storage cabinets, gas cabinets, exhausted enclosures or listed safety cans. Listed safety cans shall be in accordance with [Section 2705.1.10 of] the New York City Fire Code. Where Note d also applies, the increase for both notes shall be applied accumulatively.

- Quantities shall not be limited in a building protected throughout by a sprinkler system.

- Allowed only in buildings protected throughout by a sprinkler system.

- Containing not more than the maximum allowable quantity per control area of Class IA, Class IB or Class IC flammable liquids.

- [Stationary] The maximum allowable quantity shall not apply to fuel oil storage [tanks shall comply] that complies with the requirements of [the New York City Construction Codes, including] Section 1305 of the New York City Mechanical Code.

- Quantities shown in the table in parentheses have the units shown in parentheses at the head of the column.

- A maximum quantity of 200 pounds of solid or 20 gallons of liquid Class 3 oxidizers is allowed when such materials are necessary for maintenance, and operation of equipment when the storage containers and the manner of storage are approved.

- Reserved.

- For gallons of liquids, divide the amount in pounds by 10 in accordance with [Section 2703.1.2 of] the New York City Fire Code.

- For storage and display quantities in Group M and storage quantities in Group S occupancies complying with [the requirements of Section 2703.11 of the New York City Fire Code, see Table 2703.11.1 of] the New York City Fire Code.

- For purposes of this table, gasoline and other flammable liquid motor fuels are classified as a Class IA flammable liquid.

- Unclassified detonable organic peroxides [(see Chapter 39 of the New York City Fire Code)], detonable pyrophoric materials [(see Chapter 41 of the New York City Fire Code)], detonable unstable (reactive) materials [(see Chapter 43 of the New York City Fire Code)] and detonable water-reactive materials [(see Chapter 44 of the New York City Fire Code)] shall be treated as explosives for purposes of storage, handling and use [(see Chapter 33 of the New York City Fire Code)] in accordance with the New York City Fire Code.

- The maximum allowable quantities shall be limited by [Section 2706 of] the New York City Fire Code for non-production laboratories classified as Occupancy Group B.

- For storage of flammable and combustible liquids in Group M occupancy, see [Chapter 34 of] the New York City Fire Code.

s.	Densely-packed baled cotton that complies with the packing requirements of ISO 8115 shall not be included in this material class.

| TABLE 307.1(2) MAXIMUM ALLOWABLE QUANTITY PER CONTROL AREA OF HAZARDOUS MATERIAL POSING A HEALTH HAZARDa,b,c,i,j |
| --- |
| MATERIAL | STORAGEd | USE-CLOSED SYSTEMSd | USE-OPEN SYSTEMSd |
|  | Solid pounds | Liquid gallons (pounds)e | Gas SCFe (pounds) | Solid poundse | Liquid gallons (pounds)e | Gas SCFe (pounds) | Solid poundse | Liquid gallons (pounds)e |
| Corrosive | 5,000 | 500 | Gaseous 810f Liquefied (150)h | 5,000 | 500 | Gaseous 810f Liquefied (150)h | 1,000 | 100 |
| Highly toxic | 10 | (10)h | Gaseous 20g Liquefied (4)g,h | 10 | (10)h | Gaseous 20g Liquefied (4)g, h | 3 | (3)h |
| Toxic | 500 | (500)h | Gaseous 810f Liquefied (150)f,h | 500 | (500)h | Gaseous 810f Liquefied (150)f,h | 125 | (125)h |

For SI: 1 cubic foot = 0.028 m3, 1 pound = 0.454 kg, 1 gallon = 3.785 L.

a.	For use of control areas, see the New York City Fire Code and Section 414.2 of this code.

b.	In retail and wholesale sales occupancies, the quantities of medicines, foodstuffs, consumer or industrial products, and cosmetics, containing not more than 50 percent by volume of water-miscible liquids and with the remainder of the solutions not being flammable, shall not be limited, provided that such materials are packaged in individual containers not exceeding 1.3 gallons.

c.	For storage and display quantities in Group M and storage quantities in Group S occupancies complying with the New York City Fire Code.

d.	The aggregate quantity in storage, handling and use shall not exceed the quantity listed for storage.

e.	Maximum allowable quantities shall be increased 100 percent in buildings equipped throughout with an approved automatic sprinkler system in accordance with Section 903.3.1.1. Where Note f also applies, the increase for both notes shall be applied accumulatively.

f.	Maximum allowable quantities may be increased 100 percent when stored in approved storage cabinets, gas cabinets or exhausted enclosures as specified in the New York City Fire Code. Where Note e also applies, the increase for both notes shall be applied accumulatively.

g.	Allowed only when stored in approved exhausted gas cabinets or exhausted enclosures as specified in the New York City Fire Code.

h.	Quantities shown in the table in parenthesis [indicate quantity] have the units shown in parenthesis at the head of [each] the column.

i.	For gallons of liquids, divide the amount in pounds by 10 in accordance with the New York City Fire Code.

j.	The maximum allowable quantities shall be limited by Section [424] 427 for chemical laboratories classified as Occupancy Group B and operating as nonproduction facilities for testing, research, experimental, instructional or education purposes.

307.1.2 Hazardous materials. Hazardous materials in any quantity shall conform to the requirements of this code, including Section 414, and the New York City Fire Code.

307.2 Definitions. The following [words and] terms [shall, for the purposes of this section and as used elsewhere in this code, have the meanings shown herein.] are defined in Chapter 2:

AEROSOL.[A product that is dispensed from an aerosol container by a propellant, classified as follows:]

Level 1. [Aerosol products with a total chemical heat of combustion that is greater than 0 and less than or equal to 8,600 British thermal units per pound (Btu/lb) (20 kJ/g).]

Level 2. [Aerosol products with a total chemical heat of combustion that is greater than 8,600 Btu/lb (20 kJ/g), but less than or equal to 13,000 Btu/lb (30 kJ/g).]

Level 3. [Aerosol products with a total chemical heat combustion that is greater than 13,000 Btu/lb (30 kJ/g).]

BALED COTTON. [A natural seed fiber wrapped in and secured with industry accepted materials, typically consisting of burlap, woven polypropylene, polyethylene or cotton or sheet polyethylene, secured with wire or bands. The term baled cotton includes lint removed from the cottonseed (linters) and residual materials from the ginning process (motes).]

BALED COTTON, DENSELY PACKED.[Baled cotton with a packing density of at least 22 pounds per cubic foot (360 kg/m3). A bale of densely-packed baled cotton typically measures 55 inches (1397 mm) in length, 21 inches (533.4 mm) in width, and 27.6 to 35.4 inches (701 to 899 mm) in height.]

BARRICADE.[A structure or other artificial or natural barrier constructed in connection with the storage, handling and use of explosives that is designed to withstand the rapid release of energy in an explosion and provides a shield from the impact of such explosion. A straight line from the top of any sidewall of a building containing explosives to the eaveline of any magazine or other building or to a point 12 feet (3658 mm) above the center of a railway or highway shall pass through such barrier.]

Artificial barricade. [An artificial mound or revetment, including a barrier constructed of sandbags, with a minimum thickness of 3 feet (914 mm).]

Natural barricade.[Terrain or other natural features of the ground.]

BOILING POINT. [The temperature at which the vapor pressure of a liquid equals the atmospheric pressure of 14.7 pounds per square inch (psi) (101 kPa) gage or 760 mm of mercury. Where an accurate boiling point is unavailable for the material in question, or for mixtures which do not have a constant boiling point, for the purposes of this classification, the 20-percent evaporated point of a distillation performed in accordance with ASTM D 86 shall be used as the boiling point of the liquid.]

CLOSED SYSTEM. [The use of any compressed gas and the use of a solid or liquid hazardous material in equipment or a vessel or system that remains closed during normal operations, such that vapors emitted during the operation of such equipment, vessel or system are not liberated outside of the equipment, vessel or system and the gas or hazardous material is not exposed to the atmosphere during such operation. Examples of closed systems include hazardous materials conveyed through a piping system into closed equipment or a closed vessel or system.]

COMBUSTIBLE DUST. [Finely divided solid material that is 420 microns or less in diameter, will pass through a U.S. standard No. 40 sieve and, when dispersed in air in insufficient concentrations, can be ignited by a flame, spark or other source of ignition.]

COMBUSTIBLE FIBERS. [Readily ignitable and free-burning materials in fibrous or shredded form, such as cocoa fiber, cotton, excelsior, hay, hemp, henequen, istle, jute, kapok, oakum, sisal, Spanish moss, straw, tow, wastepaper or other natural or synthetic fibers that possess similar qualities, but excluding densely packed baled cotton.]

[Exception: Moss used for medicinal purposes.]

COMBUSTIBLE LIQUID. [For the purposes of transportation, a combustible liquid as defined in the regulations of the United States Department of Transportation, as set forth in 49 CFR 173.120. For all other purposes, a liquid, other than a compressed gas or cryogenic fluid, having a closed cup flash point at or above 100°F (38°C) classified as follows:]

Class II. [Liquids having a closed cup flash point at or above 100°F (38°C) and below 140°F (60°C).]

Class IIIA. [Liquids having a closed cup flash point at or above 140°F (60°C) and below 200°F (93°C).]

Class IIIB.[Liquids having a closed cup flash point at or above 200°F (93°C).]

COMPRESSED GAS.[A material, or mixture of materials which]

[1.	Is a gas at 68°F (20°C) or less at 14.7 psia (101 kPa) of pressure; and]

[2. Has a boiling point of 68°F (20°C) or less at 14.7 psia (101 kPa) that is either liquefied, nonliquefied or in solution at that temperature and pressure, except those gases which have no other health- or physical-hazard properties are not considered to be compressed until the pressure in the packaging exceeds 41 psia (28 kPa) at 68°F (20°C).]

[The states of compressed gases are categorized as follows:]

[Nonliquefied compressed gases. Gases, other than those in solution, which are in a packaging under the charged pressure and are entirely gaseous at a temperature of 68°F (20°C).]

[Liquefied compressed gases. Gases that, in a packaging under the charged pressure, are partially liquid at a temperature of 68°F (20°C).]

[Compressed gases in solution. Nonliquefied gases that are dissolved in a solvent.]

[Compressed gas mixtures. A mixture of two or more compressed gases contained in a single packaging, the hazard properties of which are represented by the properties of the mixture as a whole.]

CONTROL AREA. [Spaces within a building where quantities of hazardous materials not exceeding the maximum allowable quantities per control area are stored, handled, or used, including any dispensing. See also definition of “Outdoor control area” in the New York City Fire Code.]

CORROSIVE MATERIAL. [A material that causes full thickness destruction of human skin at the site of contact within a specified period of time when tested by methods set forth in DOTn regulations 49 CFR 173.136 and 173.137, or a liquid that has a severe corrosion rate on steel or aluminum based on the criteria set forth in DOTn regulations 49 CFR 173.173(c)(2).]

CRYOGENIC FLUID. [A liquid having a boiling point lower than -130°F (-89.9°C) at 14.7 pounds per square inch absolute (psia) (an absolute pressure of 101.3 kPa).]

DAY BOX. [A portable magazine designed to hold explosive materials constructed in accordance with the requirements for a Type 3 magazine as defined and classified in Chapter 33 of the New York City Fire Code.]

DEFLAGRATION. [An exothermic reaction, such as the extremely rapid oxidation of a flammable dust or vapor in air, in which the reaction progresses through the unburned material at a rate less than the velocity of sound. A deflagration can have an explosive effect.]

DETONATION. [An exothermic reaction with explosive effect that utilizes shock compression as the principal heating mechanism and generates a shock wave in the material that establishes and maintains a reaction that progresses through the material at a rate greater than the velocity of sound.]

DISPENSING. [The pouring or transferring by other means of any material from a container, tank or similar vessel, which would release dusts, fumes, mists, vapors, or gases to the atmosphere, unless such release is prevented by a device, equipment or system designed for that purpose.]

EXPLOSION. [An effect produced by the sudden violent expansion of gases, whether or not accompanied by a shock wave or disruption, of enclosing materials, including the effects of the following sources of explosion:]

[1.	Chemical changes such as rapid oxidation, deflagration or detonation, decomposition of molecules and runaway polymerization (usually detonations).]

[2.	Physical changes such as pressure tank ruptures.]

[3.	Atomic changes (nuclear fission or fusion).]

EXPLOSIVE. [Any chemical compound, mixture or device, the primary or common purpose of which is to function by explosion. The term includes, but is not limited to, dynamite, black powder, pellet powder, initiating explosives, detonators, safety fuses, squibs, detonating cord, igniter cord, and igniters.]

[The term “explosive” includes any material determined to be within the scope of Chapter 40 of Title 18 of the United States Code and any material classified as an explosive by the hazardous materials regulations of the United States Department of Transportation, as set forth in 49 CFR 173.52, except fireworks. Explosives are classified in accordance with the following United States Department of Transportation classification and other terms in common usage.]

High explosive.

Low explosive.

Mass-detonating explosives.

UN/DOTn Class 1 explosives.

Division 1.1.[Explosives that have a mass explosion hazard.]

Division 1.2.[Explosives that have a projection hazard but not a mass explosion hazard.]

Division 1.3. [Explosives that have a fire hazard and either a minor blast hazard or a minor projection hazard or both, but not a mass explosion hazard.]

Division 1.4. [Explosives that pose a minor explosion hazard. The explosive effects are largely confined to the package and no projection of fragments of appreciable size or range is to be expected. Such explosives are not subject to mass explosion when exposed to fire.]

Division 1.5. [Explosives that present a mass explosion hazard, but which are so insensitive that there is very little probability of initiation or of transition from burning to detonation under normal conditions of transport.]

Division 1.6. [Explosives consisting of extremely insensitive articles that do not present a mass explosion hazard, and present a negligible probability of accidental initiation or propagation.]

[High explosive. Explosives, including dynamite, that, when detonated, are characterized by a high rate of reaction, high pressure development, and the presence of a detonation wave, and that can be caused to detonate by means of a No. 8 test blasting cap, when unconfined.]

[Low explosive. Explosives that will burn or deflagrate when ignited, and which are characterized by a rate of reaction that is less than the speed of sound, and low pressure development. Examples of low explosives include black powder, igniter cords, igniters, safety fuses, small arms ammunition and primers, and propellants, 1.3C.]

[Mass-detonating explosives. Division 1.1, 1.2 and 1.5 explosives that, whether individually or in combination, or loaded into ammunition or containers, explode virtually instantaneously when a small portion is subjected to fire, concussion, impact, the impulse of an initiating agent, or the effect of a considerable discharge of energy from without, with severe explosive effect, including the potential for structural damage to adjacent objects, and explosive propagation to other explosives stored in proximity, such that two or more quantities in proximity must be considered as one for quantity-distance purposes.]

FIREWORKS. [Any article or device that does not present a mass explosion hazard, that is manufactured or used to produce a visible or audible effect for entertainment or other display purposes by combustion, deflagration or detonation that meets the definition of 1.4G fireworks or 1.3G fireworks as set forth herein.]

Fireworks, 1.3G.[Large fireworks devices,  classified as UN0335 by the United States Department of Transportation regulations, intended for use in fireworks displays and designed to produce audible or visible effects by combustion, deflagration or detonation including firecrackers containing more than 130 milligrams (2 grains) of explosive composition, aerial shells containing more than 40 grams of pyrotechnic material, and other display pieces which exceed the limits for classification as 1.4G fireworks.]

Fireworks, 1.4G.[Small fireworks devices, classified as UN 0336 by United States Department of Transportation regulations, containing restricted amounts of pyrotechnic materials designed primarily to produce visible or audible effects by combustion.]

FLAMMABLE GAS. [A material which has a boiling point and becomes a gas at 68°F (20°C) or less at 14.7 pounds per square inch absolute (psia) (101 kPa) of pressure  which:]

[1.	Is ignitable at 14.7 psia (101 kPa) when in a mixture of 13 percent or less by volume with air, in accordance with testing procedures set forth in ASTM E 681; or]

[2.	Has a flammable range at 14.7 psia (101 kPa) with air of at least 12 percent, regardless of the lower explosive limit, in accordance with testing procedures set forth in ASTM E 681.]

[The limits specified shall be determined at 14.7 psia (101 kPa) of pressure and a temperature of 68°F (20°C) in accordance with ASTM E 681.]

FLAMMABLE LIQUEFIED GAS.[A liquefied compressed gas which, under a charged pressure, is partially liquid at a temperature of 68°F (20°C) and which is flammable.]

FLAMMABLE LIQUID. [For the purposes of transportation, a flammable liquid as defined in the regulations of the United States Department of Transportation, as set forth in 49 CFR 173.120. For all other purposes, a liquid, other than a compressed gas or cryogenic fluid, having a closed cup flash point below 100°F (3 8°C) classified as follows:]

Class IA. [Liquids having a flash point below 73°F (23°C) and a boiling point below 100°F (38°C).]

Class IB. [Liquids having a flash point below 73°F (23°C) and a boiling point at or above 100°F (38°C).]

Class IC.[Liquids having a flash point at or above 73°F (23°C) and below 100°F (38°C)]

FLAMMABLE MATERIAL. [A material capable of being readily ignited from common sources of heat or at a temperature of 600°F (316°C) or less.]

FLAMMABLE SOLID. [A solid, other than a blasting agent or other explosive, whether in elemental or alloy form, that is capable of causing fire through friction, absorption or moisture, spontaneous chemical change, or heat retained from manufacturing or processing, or which has an ignition temperature below 212°F (100°C) or which burns so vigorously and persistently when ignited as to create a serious hazard. [A chemical shall be considered a flammable solid if upon testing using the method prescribed in CPSC regulations, as set forth in 16 CFR 1500.44, if it ignites and burns with a self-sustained flame at a rate greater than 0.1 inch (2.5 mm) per second along its major axis.]

FLASH POINT. [The minimum temperature in degrees Fahrenheit at which a liquid will give off sufficient vapors to form an ignitable mixture with air near the surface or in the container, but will not sustain combustion. The flash point of a liquid shall be determined by appropriate test procedure and apparatus as specified in ASTM D 56, ASTM D 93 or ASTM D 3278.]

HANDLING. [The movement of a material in its container, the removal of the material from its container, or any other action or process that may affect the material, other than its storage or use.]

HAZARDOUS MATERIALS. [Those chemicals or substances that are physical hazards or health hazards as defined and classified in this section and the New York City Fire Code, whether the materials are in usable or waste condition.]

HEALTH HAZARD. [A classification of a chemical for which there is statistically significant evidence that acute or chronic health effects are capable of occurring in exposed persons. The term “health hazard” includes chemicals that are toxic or highly toxic, and corrosive.]

HIGHLY TOXIC MATERIAL.[A chemical that is lethal at the following doses or concentrations:]

[1.	A chemical that has a median lethal dose (LD50) of 50 milligrams or less per kilogram of body weight when administered orally to albino rats weighing between 200 and 300 grams each; or]

[2.	A chemical that has a median lethal dose (LD50) of 200 milligrams or less per kilogram of body weight when administered by continuous contact for 24 hours (or less if death occurs within 24 hours) with the bare skin of albino rabbits weighing between 2 and 3 kilograms each; or]

[3.	A chemical that has a median lethal concentration (LC50) in air of 200 parts per million by volume or less of gas or vapor, or 2 milligrams per liter or less of mist, fume or dust, when administered by continuous inhalation for 1 hour (or less if death occurs within 1 hour) to albino rats weighing between 200 and 300 grams each.]

INCOMPATIBLE MATERIALS. [Materials that, if mixed or combined, could explode, generate heat, gases or other byproducts, or react in such a way hazardous to life or property.]

INERT GAS. [A gas that is capable of reacting with other materials only under abnormal conditions such as high temperatures, pressures and similar extrinsic physical forces. Within the context of the code, inert gases do not exhibit either physical or health properties as defined (other than acting as a simple asphyxiant) or hazard properties other than those of a compressed gas. Some of the more common inert gases include argon, helium, krypton, neon, nitrogen and xenon.]

OPEN SYSTEM. [The use of a solid or liquid hazardous material in equipment or a vessel or system that remains open during normal operation such that vapors are emitted during the operation of such equipment, vessel or system and the material is exposed to the atmosphere during such operation. Examples of open systems for solids and liquids include dispensing from or into open beakers or containers, dip tank and plating tank operations.]

ORGANIC PEROXIDE. [An organic compound having a double oxygen or peroxy (-O-O-) in its chemical structure. Organic peroxides can present an explosion hazard (detonation or deflagration), can be shock sensitive, or can be susceptible to decomposition into various unstable compounds over an extended period of time and are classified as follows based upon their hazardous properties:]

Class I. [Organic peroxides that are capable of deflagration but not detonation.]

Class II. [Organic peroxides that burn very rapidly and that pose a moderate reactivity hazard.]

Class III. [Organic peroxides that burn rapidly and that pose a moderate reactivity hazard.]

Class IV. [Organic peroxides that burn in the same manner as ordinary combustibles and that pose a minimal reactivity hazard.]

Class V. [Organic peroxides that burn with less intensity than ordinary combustibles or do not sustain combustion and that pose no reactivity hazard.]

Unclassified detonable.[Organic peroxides that are capable of detonation and pose an extremely high explosion hazard through rapid explosive decomposition.]

OXIDIZER. [A material that readily yields oxygen or other oxidizing gas or that readily reacts to promote or initiate combustion of combustible materials, and if heated or contaminated can result in vigorous self-sustained decomposition, classified as follows:]

[Class 1. An oxidizer that causes a readily measurable increase in the burning rate of combustible materials with which it comes in contact, but less than a moderate increase.]

[Class 2. An oxidizer that causes a moderate increase in the burning rate of combustible materials with which it comes in contact.]

[Class 3. An oxidizer that causes a severe increase in the burning rate of combustible materials with which it comes in contact.]

[Class 4. An oxidizer that can undergo an explosive reaction due to contamination or exposure to thermal or physical shock and causes a severe increase in the burning rate of combustible materials with which it comes into contact.]

Class 4.

Class 3.

Class 2.

Class 1.

OXIDIZING GAS. [A gas that can support and accelerate combustion of other materials more than air does.]

PHYSICAL HAZARD. [A chemical for which there is evidence that it is a combustible liquid, compressed gas, cryogenic, explosive, flammable gas, flammable liquid, flammable solid, organic peroxide, oxidizer, pyrophoric or unstable (reactive) or water-reactive material.]

PYROPHORIC MATERIAL.[A material with an autoignition temperature in air, at or below a temperature of 130°F (54°C).]

PYROTECHNIC MATERIAL.[A chemical mixture consisting predominantly of solids that, upon ignition, are capable of producing a controlled, self-sustaining, and self-contained exothermic reaction, that functions without external oxygen, resulting in a visible or audible effect by combustion, deflagration, or detonation.]

STANDARD CUBIC FEET (SCF).[Cubic feet of gas at normal temperature and pressure (NTP).]

TOXIC MATERIAL.[A chemical that is lethal at the following doses or concentrations:]

[1.	A chemical that has a median lethal dose (LD50) of more than 50 milligrams per kilogram, but not more than 500 milligrams per kilogram of body weight when administered orally to albino rats weighing between 200 and 300 grams each; or]

[2.	A chemical that has a median lethal dose (LD50) of more than 200 milligrams per kilogram but not more than 1,000 milligrams per kilogram of body weight when administered by continuous contact for 24 hours (or less if death occurs within 24 hours) with the bare skin of albino rabbits weighing between 2 and 3 kilograms each; or]

[3.	A chemical that has a median lethal concentration (LC50) in air of more than 200 parts per million but not more than 2,000 parts per million by volume of gas or vapor, or more than 2 milligrams per liter but not more than 20 milligrams per liter of mist, fume or dust, when administered by continuous inhalation for 1 hour (or less if death occurs within 1 hour) to albino rats weighing between 200 and 300 grams each.]

[Exception: For purposes of this code, chlorine shall be classified as a highly toxic material.]

UNSTABLE (REACTIVE) MATERIAL.[A material, other than an explosive, which in the pure state or as commercially produced, will vigorously polymerize, decompose, condense or become self-reactive and undergo other violent chemical changes, including explosion, when exposed to heat, friction or shock, or in the absence of an inhibitor, or in the presence of contaminants, or in contact with incompatible materials. Unstable (reactive) materials are shall be classified as follows:]

[Class 1. Materials that in themselves are normally stable but which can become unstable at elevated temperatures and pressure.]

[Class 2. Materials that in themselves are normally unstable and readily undergo violent chemical change but do not detonate. This class includes materials that can undergo chemical change with rapid release of energy at normal temperatures and pressures, and that can undergo violent chemical change at elevated temperatures and pressures.]

[Class 3. Materials that in themselves are capable of detonation or of explosive decomposition or explosive reaction but which require a strong initiating source or which must be heated under confinement before initiation. This class includes materials that are sensitive to thermal or mechanical shock at elevated temperatures and pressures.]

[Class 4. Materials that in themselves are readily capable of detonation or explosive decomposition or explosive reaction at normal temperatures and pressures. This class includes materials that are sensitive to mechanical or localized thermal shock at normal temperatures and pressures.]

Class 4.

Class 3.

Class 2.

Class 1.

WATER-REACTIVE MATERIAL. [A material that explodes; violently reacts; produces flammable, toxic or other hazardous gases; or generates enough heat to cause auto-ignition or ignition of combustible materials upon exposure to water or moisture. Water-reactive materials are classified as follows:]

[Class 1. Materials that may react with water with some release of energy, but not violently.]

[Class 2. Materials that react violently with water or cause water to boil upon contact; produce flammable, toxic or other hazardous gases upon contact with water; or upon contact with water generate sufficient heat to cause auto-ignition of adjoining combustible materials.]

[Class 3. Materials that react explosively with water without requiring heat or confinement.]

Class 3.

Class 2.

Class 1.

307.3 [High-Hazard] High-hazard Group H-1. Buildings and structures containing materials that [present] pose a detonation hazard shall be classified as Group H-1. Such materials shall include, but not be limited to, the following:

Detonable pyrophoric materials

Explosives:

Division 1.1

Division 1.2

Division 1.3

Division 1.4

Division 1.5

Division 1.6

Organic peroxides, unclassified detonable

Oxidizers, Class 4

Unstable (reactive) materials, Class 3 detonable and Class 4

[Exception: Materials]

307.3.1 Occupancies containing explosives not classified as H-1. The following occupancies containing explosive materials shall be classified as follows:

1.	Division 1.3 explosive materials that are used and maintained in a form where either confinement or configuration will not elevate the hazard from a mass fire to mass explosion hazard shall be allowed in H-2 occupancies.

[Division 1.4]

[Exception:]

2.	Articles, including articles packaged for shipment, that are not regulated as [an] a Division 1.4 explosive under Bureau of Alcohol, Tobacco [and], Firearms [regulations] and Explosives regulations, or unpackaged articles used in process operations that do not propagate a detonation or deflagration between articles shall be allowed in H-3 occupancies.

[Division 1.5]

[Division 1.6]

[Organic peroxides, unclassified detonable]

[Oxidizers, Class 4]

[Unstable (reactive) materials, Class 3 detonable and Class 4]

[Pyrophoric materials, detonable]

[Water-reactive materials, Class 2 and 3, detonable]

No part of this section shall be construed to authorize the manufacture, storage, sale or use of explosives, including fireworks, if otherwise prohibited by the New York City Fire Code and unless in compliance with the requirements of the New York City Fire Code.

307.4 [High-Hazard] High-hazard Group H-2. Buildings and structures containing materials that [present] pose a deflagration hazard or a hazard from accelerated burning shall be classified as Group H-2. Such materials shall include, but not be limited to, the following:

Class I, II or IIIA flammable or combustible liquids [which] that are used or stored in normally open containers or systems, or in closed containers or systems pressurized at more than 15 [psi (103.4 kPa) gage.] pounds per square inch gauge (103.4 kPa)

Combustible dusts where manufactured, generated or used in such a manner that the concentration and conditions create a fire or explosion hazard based on information prepared in accordance with Section 414.1.3

Cryogenic fluids, flammable

Flammable gases

Organic peroxides, Class I

Oxidizers, Class 3, that are used or stored in normally open containers or systems, or in closed containers or systems pressurized at more than 15 [psi (103.3 kPa) gage.] pounds per square inch gauge (103 kPa)

Pyrophoric liquids, solids and gases, nondetonable

Unstable (reactive) materials, Class 3, nondetonable

Water-reactive materials, Class 3, nondetonable

No part of this section shall be construed to authorize an LPG-distribution facility if otherwise prohibited by the New York City Fire Code.

307.5 [High-Hazard] High-hazard Group H-3. Buildings and structures containing materials that readily support combustion or [present] that pose a physical hazard shall be classified as Group H-3. Such materials shall include, but not be limited to, the following:

Class I, II or IIIA flammable or combustible liquids [which] that are used or stored in normally closed containers or systems pressurized at [less than 15 psi (103.3 kPa) gage.] 15 pounds per square inch gauge (103 kPa) or less

Combustible fibers, other than densely packed baled cotton, where manufactured, generated or used in such a manner that the concentration and conditions create a fire or explosion hazard based on information prepared in accordance with Section 414.1.3

Cryogenic fluids, oxidizing

Flammable solids

Organic peroxides, [Classes] Class II and III

Oxidizers, [Classes] Class 1 and 2

Oxidizing gases

Unstable (reactive) materials, Class 2

Water-reactive materials, Class 2, nondetonable

307.6 [High-Hazard] High-hazard Group H-4. Buildings and structures containing materials that are health hazards shall be classified as Group H-4. Such materials shall include, but not be limited to, the following:

Corrosives

Highly toxic materials

Toxic materials

307.7 High-hazard Group H-5[structures]. Semiconductor fabrication facilities and comparable research and development areas in which hazardous production materials (HPM) are used and the aggregate quantity of materials is in excess of those listed in Tables 307.1(1) and 307.1(2) shall be classified as Group H-5. Such facilities and areas shall be designed and constructed in accordance with Section [415.8] 415.11.

307.8 Multiple hazards. Buildings and structures containing a material or materials representing hazards that are classified in one or more of Groups H-1, H-2, H-3 and H-4 shall conform to the code requirements for each of the occupancies so classified.

SECTION BC 308
INSTITUTIONAL GROUP I

308.1 Institutional Group I. Institutional Group I occupancy includes, among others, the use of a building or structure, or a portion thereof, in which [people are cared for or live in a supervised environment, having physical limitations because of health or age are harbored for medical treatment or other care or treatment,] care or supervision is provided to persons who are or are not capable of self-preservation without physical assistance or in which [people] persons are detained for penal or correctional purposes or in which the liberty of the occupants is restricted. Institutional occupancies shall be classified as Group I-1, I-2, I-3 or I-4.

[308.1.1] 308.2 Definitions.[For definitions of terms related to Group I occupancy classification, see Section 310.2.] This section contains provisions for definitions of terms defined elsewhere in this code as well as the terms with definitions specific to this section.

308.2.1 Terms defined elsewhere in this code. The following terms are defined in Chapter 2:

24-HOUR BASIS.

CARE SUITE.

INCAPABLE OF SELF-PRESERVATION.

308.2.2 Definitions specific to this section. The following words and terms shall, for the purposes of this section, have the meanings shown herein:

CHILD CARE FACILITIES. Facilities that provide care on a 24-hour basis to more than 5 children, under the age of 2.

DETOXIFICATION FACILITIES. Facilities that serve patients who are provided treatment for substance abuse on a 24-hour basis and who are incapable of self-preservation or who are harmful to themselves or others.

HOSPITALS AND PSYCHIATRIC CENTERS. Buildings or portions thereof used on a 24-hour basis for the medical, psychiatric, obstetrical or surgical treatment of inpatients who are incapable of self-preservation.

NURSING HOMES. Nursing homes are long-term care facilities on a 24-hour basis, including both intermediate care facilities and skilled nursing facilities, serving more than five persons and any of the persons are incapable of self-preservation.

[308.2] 308.3 Institutional Group I-1. [This] Institutional Group I-1 occupancy shall include buildings, structures or parts thereof housing persons, on a 24-hour basis, who because of age, mental disability or other reasons, live in a supervised residential environment that provides personal care services. The occupants are capable of self-preservation and capable of responding to an emergency situation without physical assistance from staff. Such occupancy shall be subject to the New York State Multiple Dwelling Law. This group shall include, but not be limited to, the following:

Adult homes, where occupants are capable of self-preservation (see Section [308.2.1] 308.3.1)

Alcohol and drug abuse rehabilitation centers

Assisted living facilities

Community residences or intermediate-care facilities (see Section [308.2.2] 308.3.2)

Congregate care facilities

Convalescent facilities

Enriched housing, where occupants are capable of self-preservation (see Section [308.2.1] 308.3.1)

Halfway houses

Overnight facilities for children where all supervised occupants are under the age of 18, with no more than two children under the age of 2

Residential care facilities

Social rehabilitation facilities

[308.2.1] 308.3.1 Adult homes and enriched housing. Adult homes and enriched housing facilities operated pursuant to and meeting the additional construction requirements of Section 460 of the New York State Social Services Law and regulations of the New York State Department of Health offering care on a 24-hour basis to persons capable of self-preservation, in the same building, shall be classified as Group I-1.

Exception: Such a facility offering supervised care on a 24-hour basis for no more than 16 occupants capable of self-preservation, in the same building, may be classified in Group R in accordance with Section 310.

[308.2.2] 308.3.2 Community residences or intermediate-care facilities. Community residences or intermediate-care facilities, operated pursuant to and meeting the additional construction requirements of the New York State Mental Hygiene Law and applicable regulations of the New York State Office of Mental Health and Office for People with Developmental Disabilities shall be classified as Group I-1.

Exceptions: Such facilities limited to 14 residents capable of self-preservation and three staff members per dwelling unit shall be classified as:

- Group R-1, where such facility does not occupy more than two dwelling units in a residential building classified as R-1 of Type I or II construction, or one dwelling unit in any other type of construction, and occupied on a transient basis; or

- Group R-2 where such facility does not occupy more than two dwelling units in a residential building classified R-2 of Type I or II construction, or one dwelling unit in any other type of construction, and occupied on a long-term basis; or

3.	Group R-3 where the number of dwelling units in the building does not exceed two.

[308.3] 308.4 Institutional Group I-2. [This occupancy] Institutional Group I-2 shall include buildings and structures used for medical, surgical, psychiatric, nursing or personal care on a 24-hour basis or overnight of more than two children under the age of 2, or more than three persons who are not capable of self-preservation and not capable of responding to an emergency situation without physical assistance from staff. This group shall include, but not be limited to, the following:

Adult homes, where occupants are not capable of self-preservation[, operated pursuant to and meeting the additional construction requirements of Section 460 of the New York State Social Services Law and regulations of the New York State Department of Health] (see Section 308.4.1)

Child care facilities

Community residences or intermediate-care facilities, where occupants are not capable of self-preservation, operated pursuant to and meeting the additional construction requirements of the New York State Mental Hygiene Law and applicable regulations of the New York State Office of Mental Health and Office for People with Developmental Disabilities

Detoxification facilities

Exception: Such a facility offering care on a 24-hour basis for three or fewer persons who are not capable of self-preservation may occupy not more than one dwelling unit in a Group R occupancy.

Enriched Housing, where occupants are not capable of self-preservation[, operated pursuant to and meeting the additional construction requirements of Section 460 of the New York State Social Services Law and regulations of the New York State Department of Health] (see Section 308.4.1)

Hospitals

Nursing homes

[Mental hospitals] Psychiatric centers where patients are not under restraint

[Detoxification facilities]

[Exception: Such a facility offering care on a 24-hour basis for three or fewer persons who are not capable of self-preservation may occupy not more than one dwelling unit in a Group R occupancy.]

308.4.1 Adult homes and enriched housing. Adult homes and enriched housing facilities operated pursuant to and meeting the additional construction requirements of Section 460 of the New York State Social Services Law and regulations of the New York State Department of Health offering care on a 24-hour basis to persons not capable of self-preservation, in the same building, shall be classified as Group I-2.

[308.3.1 Definitions. The following words and terms shall, for the purposes of this section and as used elsewhere in this code, have the meanings shown herein.]

[CHILD CARE FACILITIES. Facilities that provide care on a 24-hour basis to more than five children, under the age of 2.]

[DETOXIFICATION FACILITIES. Facilities that serve patients who are provided treatment for substance abuse on a 24-hour basis and who are incapable of self-preservation or who are harmful to themselves or others.]

[HOSPITALS AND MENTAL HOSPITALS. Buildings or portions thereof used on a 24-hour basis for the medical, psychiatric, obstetrical or surgical treatment of inpatients who are incapable of self-preservation.]

[NURSING HOMES. Nursing homes are long-term care facilities on a 24-hour basis, including both intermediate care facilities and skilled nursing facilities, serving more than five persons and any of the persons are incapable of self-preservation.]

[308.4] 308.5 Institutional Group I-3. [This] Institutional Group I-3 occupancy shall include buildings and structures that are inhabited by more than five persons who are under restraint or security. [An] A Group I-3 facility is occupied by persons who are generally incapable of self-preservation due to security measures not under the occupants’ control. This group shall include, but not be limited to, the following:

Correctional centers

Detention centers

Jails

[Mental hospitals] Psychiatric centers where patients are under restraint

Prerelease centers

Prisons

Reformatories

Buildings of Group I-3 shall be classified as one of the occupancy conditions [indicated] specified in [Section 408.1] Sections 308.5.1 through 308.5.5.

308.5.1 Condition 1. This occupancy condition shall include buildings in which free movement is allowed from sleeping areas, and other spaces where access or occupancy is permitted, to the exterior via means of egress without restraint. A Condition 1 facility is permitted to be constructed as Group R.

308.5.2 Condition 2. This occupancy condition shall include buildings in which free movement is allowed from sleeping areas and any other occupied smoke compartment to one or more other smoke compartments. Egress to the exterior is impeded by locked exits.

308.5.3 Condition 3. This occupancy condition shall include buildings in which free movement is allowed within individual smoke compartments, such as within a residential unit comprised of individual sleeping units and group activity spaces, where egress is impeded by remote controlled release of means of egress from such a smoke compartment to another smoke compartment.

308.5.4 Condition 4. This occupancy condition shall include buildings in which free movement is restricted from an occupied space. Remote-controlled release is provided to permit movement from sleeping units, activity spaces and other occupied areas within the smoke compartment to other smoke compartments.

308.5.5 Condition 5. This occupancy condition shall include buildings in which free movement is restricted from an occupied space. Staff-controlled manual release is provided to permit movement from sleeping units, activity spaces and other occupied areas within the smoke compartment to other smoke compartments.

[308.5] 308.6 Institutional Group I-4. [This group] Institutional Group I-4 occupancy shall include custodial care facilities providing care to more than two children under the age of 2, or to more than four persons over the age of 2 who are not capable of responding to an emergency situation without physical assistance from the staff. Such occupancy shall include, but not be limited to, adult custodial care facilities and day nurseries.

Exceptions:

- Custodial care facility as described in Section 303.

- Custodial care facility as described in Section 304.

- Custodial care facility as described in Exception 3 of Section 305.1.

- Such facility providing care within a dwelling unit as described in Section 310.

5.	Such facility providing care to children under the age of 2 in religious houses of worship during religious functions.

SECTION BC 309
MERCANTILE GROUP M

309.1 Mercantile Group M. Mercantile Group M occupancy includes, among others, the use of a building or structure or a portion thereof[,] for the display and sale of merchandise, and involves stocks of goods, wares or merchandise incidental to such purposes and accessible to the public. Mercantile occupancies shall include, but not be limited to, the following:

Department stores

Drug stores

Markets

Motor fuel-dispensing facilities

Retail or wholesale stores

Sales rooms

309.2 Quantity of hazardous materials. The aggregate quantity of nonflammable solid and nonflammable or noncombustible liquid hazardous materials stored or displayed in a single control area of a Group M occupancy shall not exceed the quantities in Table 414.2.5(1).

SECTION BC 310
RESIDENTIAL GROUP R

310.1 Residential Group R. Residential Group R includes, among others, the use of a building or structure, or a portion thereof, for dwelling or sleeping purposes when not classified as an Institutional Group I. Buildings containing three or more dwelling units shall be subject to the New York State Multiple Dwelling Law. Residential occupancies shall be classified as Group R-1, R-2, or R-3.

[310.1.1 Group R-1. This occupancy shall include:]

[1.	Residential buildings or spaces occupied, as a rule, transiently, for a period less than one month, as the more or less temporary abode of individuals or families who are lodged with or without meals, including, but not limited to, the following:]

[Class B multiple dwellings as defined in Section 27-2004 of the New York City Housing Maintenance Code and Section 4 of the New York State Multiple Dwelling Law, where not classified in Group I-1.]

[Club houses]

[Hotels (transient)]

[Motels (transient)]

[Rooming houses (boarding houses—transient)]

[Settlement houses]

[Vacation timeshares]

[2.	College or school student dormitories, except for student apartments classified as an R-2 occupancy]

[3.	Congregate living units owned and operated by a government agency or not-for-profit organization, where the number of occupants in the dwelling unit exceeds the limitations of a family as defined, including, but not limited to, the following:]

[Adult homes or enriched housing with 16 or fewer occupants requiring supervised care within the same building on a 24-hour basis]

[Fraternity and sorority houses]

[Homeless shelters]

[310.1.2 Group R-2. This occupancy shall include buildings or portions thereof containing sleeping units or more than two dwelling units that are occupied for permanent resident purposes as defined in subparagraph (a) of paragraph eight of subdivision a of Section 27-2004 of the New York City Housing Maintenance Code. Such occupancy shall be subject to the New York State Multiple Dwelling Law. This group shall include, but not be limited to, the following:]

[Adult homes or enriched housing with 16 or fewer occupants requiring supervised care on a 24-hour basis in the same building, provided that the number of occupants per dwelling unit does not exceed the definition of a family]

[Apartment houses]

[Apartment hotels (nontransient)]

[Class A multiple dwellings as defined in Section 27-2004 of the New York City Housing Maintenance Code and Section 4 of the New York State Multiple Dwelling Law, where not classified in Group I-1:]

[1.	Dwelling units where the resident of the unit provides custodial care to no more than four persons on less than a 24-hour basis and not overnight, where not classified in Group I-1.]

[2.	Dwelling units where the resident of the unit provides child custodial care as a family day care home registered with the New York City Department of Health and Mental Hygiene in accordance with the New York State Social Services Law with no more than six children between the ages of 2 and 13, or with no more than five children if any are under the age of 2, receiving supervised care on less than a 24-hour basis and not overnight, where not classified in Group I-1.]

[Convents and monasteries with more than 20 occupants in the building]

[Student apartments]

[310.1.3 Group R-3. This occupancy shall include buildings or portions thereof containing no more than 2 dwelling units, occupied, as a rule, for shelter and sleeping accommodation on a long-term basis for a month or more at a time, and are not classified in Group R-1, R-2 or I. This group shall include, but not be limited to, the following:]

[Convents and monasteries with fewer than 20 occupants in the building]

[Group homes]

[One- and two-family dwellings, including the following:]

[1.	Dwelling units where the resident of the unit provides custodial care to no more than four persons on less than a 24-hour basis and not overnight.]

[2.	Dwelling units where the resident of the unit provides child custodial care as a family day care home registered with the New York City Department of Health and Mental Hygiene in accordance with the New York State Social Services Law with no more than six children between the ages of 2 and 13, or with no more than five children if any are under the age of 2, receiving supervised care on less than a 24-hour basis and not overnight.]

310.2 Definitions. The following [words and] terms [shall, for the purposes of this section and as used elsewhere in this code, have the meanings shown herein.] are defined in Chapter 2:

APARTMENT. [A dwelling unit providing permanent provisions for both sanitation and kitchen facilities, occupied or arranged to be occupied by not more than one family maintaining a common household.]

APARTMENT, STUDENT.[An apartment occupied or arranged to be occupied by students enrolled at a single accredited college or university and maintaining a common household pursuant to a lease, sublease, or occupancy agreement directly with such college or university.]

BOARDER (ROOMER, LODGER).[A person who pays a consideration for living within the household and does not occupy such space as an incident of employment.]

CONGREGATE LIVING UNIT. [A dwelling unit, comprised of one or more habitable rooms separated by nonrated partitions, occupied or arranged to be occupied by more than one family or by persons who are not maintaining a common household. Creation of or conversion to such unit shall be subject to Section 27-2077 of the New York City Housing Maintenance Code.]

CUSTODIAL CARE FACILITY. [A building or part thereof occupied by persons, on less than a 24-hour basis and not overnight, who because of age, disability or other reasons, receive personal care services by individuals other than parents or guardians, relatives by blood, marriage, domestic partnership, or adoption, in a place other than the home of the person cared for.]

DWELLING. [A building or structure which is occupied in whole or in part as the home, residence or sleeping place of one or more families.]

DWELLING, MULTIPLE. [A dwelling which is either rented, leased, let or hired out, to be occupied, or is occupied, as the residence or home of three or more families living independently of each other. A multiple dwelling does not include a building used for occupancies in Groups I-2, I-3 or I-4.]

DWELLING, ONE-FAMILY. [Any building or structure designed and occupied exclusively for residence purposes on a long-term basis for more than a month at a time by not more than one family. One-family dwellings shall also be deemed to include a dwelling located in a series of one-family dwellings each of which faces or is accessible to a legal street or public thoroughfare, provided that each such dwelling unit is equipped as a separate dwelling unit with all essential services, and also provided that each such unit is arranged so that it may be approved as a legal one-family dwelling.]

DWELLING, TWO-FAMILY. [Any building or structure designed and occupied exclusively for residence purposes on a long-term basis for more than a month at a time by not more than two families. Two-family dwellings shall also be deemed to include a dwelling located in a series of two-family dwellings each of which faces or is accessible to a legal street or public thoroughfare, provided that each such dwelling is equipped as a separate dwelling with all essential services, and also provided that each such dwelling is arranged so that it may be approved as a legal two-family dwelling.]

DWELLING UNIT. [A single unit consisting of one or more habitable rooms and occupied or arranged to be occupied as a unit separate from all other units within a dwelling.]

FAMILY.

[1. A single person occupying a dwelling unit and maintaining a common household with not more than two boarders, roomers or lodgers; or]

[2. Two or more persons related by blood, adoption, legal guardianship, marriage or domestic partnership; occupying a dwelling unit and maintaining a common household with not more than two boarders, roomers or lodgers; or]

[3.	Not more than three unrelated persons occupying a dwelling unit and maintaining a common household; or]

[4.	Not more than three unrelated persons occupying a dwelling unit in a congregate housing or shared living arrangement and maintaining a common household; or]

[5.	Members of a group home; or]

[6.	Foster children placed in accordance with provisions of the New York State Social Services Law, their foster parent(s), and other persons related to the foster parents by blood, marriage or domestic partnership; where all residents occupy and maintain a common household with not more than two boarders, roomers or lodgers; or]

[7.	Up to seven unrelated students enrolled at a single accredited college or university occupying a student apartment and maintaining a common household pursuant to a lease, sublease, or occupancy agreement directly with such college or university, provided that:]

[7.1. The entire structure in which the dwelling unit is located is fully sprinklered in accordance with Chapter 9; and]

[7.2. Such occupancy does not exceed the maximums contained in Section 27-2075(a) of the New York City Housing Maintenance Code; and]

[7.3. Prior to commencement of such occupancy, and on an annual basis thereafter such college or university has submitted a fire safety plan containing fire safety and evacuation procedures for such dwelling unit that is acceptable to the fire commissioner and in compliance with any rules promulgated by the Fire Commissioner; and]

[7.4. The dwelling unit complies with additional occupancy and construction requirements as may be established by rule by the Housing Preservation and Development Commissioner.]

[A common household is deemed to exist if all household members have access to all parts of the dwelling unit. Lack of access to all parts of the dwelling unit establishes a rebuttable presumption that no common household exists.]

GROUP HOME. [A facility for the care and maintenance of not fewer than seven nor more than 12 children, supervised by the New York State Board of Social Welfare, and operated pursuant to and meeting any additional construction requirements of Section 374-C of the New York State Social Services Law and applicable regulations of the New York State Department of Social Services. Such a facility occupied by more than 12 children shall be classified as Group I-1.]

PERSONAL CARE SERVICE. [The care of residents who do not require chronic or convalescent medical or nursing care. Personal care involves responsibility for the safety of the resident while inside the building.]

RESIDENTIAL CARE/ASSISTED LIVING FACILITIES. [A building or part thereof housing persons, on a 24-hour basis, who because of age, mental disability or other reasons, live in a supervised residential environment which provides personal care services. The occupants are capable of self-preservation and are capable of responding to an emergency situation without physical assistance from staff. This classification shall include, but not be limited to, the following: residential board and care facilities, assisted living facilities, halfway houses, congregate care facilities, social rehabilitation facilities, alcohol and drug abuse rehabilitation centers and convalescent facilities.]

ROOMING HOUSE. [A dwelling (i) which was originally erected as a single- or two-family private dwelling pursuant to the New York City Building Code in effect prior to December 6, 1968, (ii) which is a “Class B converted dwelling” as such term is defined in the New York City Housing Maintenance Code, and (iii) which has more than half of its habitable rooms as sleeping units. The creation of or conversion to a rooming house shall be limited by Section 27-2077 of the New York City Housing Maintenance Code.]

SLEEPING UNIT. [A dwelling unit, which may contain either toilet or kitchen facilities but not both. Any sleeping unit housing more than one family shall also be classified as a congregate living unit. The creation of or conversion to sleeping units shall be limited by Section 27-2077 of the New York City Housing Maintenance Code.]

TRANSIENT. [Occupancy of a dwelling unit or sleeping unit for not more than 30 days.]

310.3 Residential Group R-1. Residential Group R-1 occupancies shall include:

1.	Residential buildings or spaces occupied, as a rule, transiently, for a period less than one month, as the more or less temporary abode of individuals or families who are lodged with or without meals, including, but not limited to, the following:

Class B multiple dwellings as defined in Section 27-2004 of the New York City Housing Maintenance Code and Section 4 of the New York State Multiple Dwelling Law, where not classified in Group I-1.

Club houses

Hotels (transient)

Motels (transient)

Rooming houses (boarding houses—transient)

Settlement houses

Vacation timeshares

2.	College or school student dormitories, except for student apartments classified as an R-2 occupancy

3.	Congregate living units owned and operated by a government agency or not-for-profit organization, where the number of occupants in the dwelling unit exceeds the limitations of a family as defined, including, but not limited to, the following:

Adult homes or enriched housing with 16 or fewer occupants requiring supervised care within the same building on a 24-hour basis

Fraternity and sorority houses

Homeless shelters

310.4 Residential Group R-2. Residential Group R-2 occupancies shall include buildings or portions thereof containing sleeping units or more than two dwelling units that are occupied for permanent resident purposes as defined in subparagraph (a) of paragraph eight of subdivision a of Section 27-2004 of the New York City Housing Maintenance Code. Such occupancy shall be subject to the New York State Multiple Dwelling Law. This group shall include, but not be limited to, the following:

Adult homes or enriched housing with 16 or fewer occupants requiring supervised care on a 24-hour basis in the same building, provided that the number of occupants per dwelling unit does not exceed the definition of a family

Apartment houses

Apartment hotels (nontransient)

Class A multiple dwellings as defined in Section 27-2004 of the New York City Housing Maintenance Code and Section 4 of the New York State Multiple Dwelling Law, where not classified in Group I, including the following:

1.	Dwelling units where the resident of the unit provides custodial care to no more than four persons on less than a 24-hour basis and not overnight, where not classified in Group I.

2.	Dwelling units where the resident of the unit provides child custodial care as a family day care home registered with the New York City Department of Health and Mental Hygiene in accordance with the New York State Social Services Law, with no more than six children between the ages of 2 and 13, or with no more than five children if any are under the age of 2, receiving supervised care on less than a 24-hour basis and not overnight, where not classified in Group I.

Convents and monasteries with more than 20 occupants in the building

Student apartments

310.5 Residential Group R-3. Residential Group R-3 occupancies shall include buildings or portions thereof containing no more than 2 dwelling units, occupied, as a rule, for shelter and sleeping accommodation on a long-term basis for a month or more at a time, and are not classified in Group R-1, R-2 or I. This group shall include, but not be limited to, the following:

Convents and monasteries with 20 or fewer occupants in the building

Group homes

One- and two-family dwellings, including the following:

1.	Dwelling units where the resident of the unit provides custodial care to no more than four persons on less than a 24-hour basis and not overnight.

2.	Dwelling units where the resident of the unit provides child custodial care as a family day care home registered with the New York City Department of Health and Mental Hygiene in accordance with the New York State Social Services Law for three to six children for more than three hours per day per child but less than twenty-four hours per day. A family day care provider may, however, care for seven or eight children at any one time if no more than six of the children are less than school age and such children receive services only during the periods set forth in the New York State Social Services Law.

3.	Dwelling units where the resident of the unit provides child custodial care as a group family day care home registered with the New York City Department of Health and Mental Hygiene in accordance with the New York State Social Services Law for seven to twelve children of all ages for more than three hours a day per child but less than twenty-four hours per day. There may be an additional four children if such children are of school age and such children receive services only during the periods set forth in the New York State Social Services Law.

SECTION BC 311
STORAGE GROUP S

311.1 Storage Group S. Storage Group S occupancy includes, among others, the use of a building or structure, or a portion thereof, for storage, such as for warehouses, storage rooms, freight depots and distribution centers, when not classified as a hazardous occupancy.

311.1.1 Accessory storage spaces. A room or space used for storage purposes that is less than 100 square feet (9.3 m2) in area and accessory to another occupancy shall be classified as part of that occupancy. The aggregate area of such rooms or spaces shall not exceed the allowable area limits of Section 508.2.3.

311.2 Moderate-hazard storage, Group S-1.[Buildings] Storage Group S-1 occupancies are buildings occupied for storing any flammable or combustible materials that are likely to permit the development and production of fire with moderate rapidity including, but not limited to, storage of the following:

Aerosols, Levels 2 and 3

Aircraft hangar (storage and repair)

Bags; cloth, burlap and paper

Bamboos and rattan

Baskets

Belting; canvas and leather

Books and paper in rolls or packs

Boots and shoes

Buttons, including cloth covered, pearl or bone

Cardboard and cardboard boxes

Clothing, woolen wearing apparel

Cordage

Dry boat storage (indoor, not accessory to Group R)

Furniture

Furs

Glues, mucilage, pastes and size

Grains

Horns and combs, other than celluloid

Leather

Linoleum

Lumber

Photo engravings

Resilient flooring

Silks

Soaps

Sugar

Tires, bulk storage of

Tobacco, cigars, cigarettes and snuff

Upholstery and mattresses

Wax candles

311.3 Low-hazard storage, Group S-2. [Includes] Storage Group S-2 occupancies include, among others, buildings used for the storage of noncombustible materials such as products on wood pallets or in paper cartons with or without single thickness divisions; or in paper wrappings. Such products are permitted to have a negligible amount of plastic trim, such as knobs, handles or film wrapping. Group S-2 storage uses shall include, but not be limited to, storage of the following:

Asbestos

Beverages up to and including [16 percent] 16-percent alcohol in metal, glass or ceramic containers

Cement in bags

Chalk and crayons

Dairy products in nonwaxed coated paper containers

Dry cell batteries

Electrical coils

Electrical motors

Empty cans

Food products

Foods in noncombustible containers

Fresh fruits and vegetables in nonplastic trays or containers

Frozen foods

Glass

Glass bottles, empty or filled with noncombustible liquids

Gypsum board

Inert pigments

Ivory

Meats

Metal cabinets

Metal desks with plastic tops and trim

Metal parts

Metals

Mirrors

Oil-filled and other types of distribution transformers

Parking garages, open or enclosed

Porcelain and pottery

Stoves

Talc and soapstones

Washers and dryers

SECTION BC 312
UTILITY AND MISCELLANEOUS GROUP U

312.1 General. Buildings and structures of an accessory character and miscellaneous structures not classified in any specific occupancy shall be constructed, equipped and maintained to conform to the requirements of this code commensurate with the fire and life hazard incidental to their occupancy. Group U shall include, but not be limited to, the following:

Carports

Fences more than 6 feet (1829 mm) [high] in height

Private garages as per Section 406.1

Retaining walls

Sheds or greenhouses accessory to Group R-3 occupancies, that are freestanding, less than 120 square feet (11.15 m2) in area, not permanently affixed to the ground, and used for household goods or items associated with the garden or lawn. Any other shed shall be classified as either S-1 or S-2.

Tanks

Towers

§ 5.  Chapter 4 of the New York city building code, as added by local law number 33 of 2007, sections 402, 403, 404, 405, 406, 407, 408, 409, 410, 411, 412, 413, 414, 415, 416, 417, 418 as amended by, sections 419, 420, 421, 422, 423 as added by, local law number 141 for the year 2013, section 402.3 as amended by local law 195 for the year 2018, section 403.4.8.2 as amended by local law number 51 for the year 2014, is amended to read as follows:

CHAPTER 4
SPECIAL DETAILED REQUIREMENTS BASED ON USE AND OCCUPANCY

SECTION BC 401
SCOPE

401.1 Detailed use and occupancy requirements.  In addition to the occupancy and construction requirements in this code, the provisions of this chapter apply to the special uses and occupancies described herein.

SECTION BC 402
COVERED MALL AND OPEN MALL BUILDINGS

402.1 [Scope] Applicability.  The provisions of this section shall apply to buildings or structures defined herein as covered or open mall buildings not exceeding three floor levels at any point nor more than three stories above grade plane. Except as specifically required by this section, covered and open mall buildings shall meet applicable provisions of this code.

Exceptions:

1.	Foyers and lobbies of Groups B, R-1 and R-2 are not required to comply with this section.

2.	Buildings need not comply with the provisions of this section where they fully comply with other applicable provisions of this code.

402.1.1 Occupancy classification. A mall in compliance with the provisions of this section shall be classified as occupancy [group] Group M.

402.1.2 Open space. A covered mall building and attached anchor buildings and parking garages shall be surrounded on all sides by a permanent open space of not less than 60 feet (18 288 mm). An open mall building and anchor buildings and parking garages adjoining the perimeter line shall be surrounded on all sides by a permanent open space of not less than 60 feet (18 288 mm).

Exception: The permanent open space of 60 feet (18 288 mm) shall be permitted to be reduced to not less than 40 feet (12 192 mm), provided the following requirements are met:

1.	The reduced open space shall not be allowed for more than 75 percent of the perimeter of the covered mall building and anchor buildings or of the perimeter line of the open mall building and anchor buildings;

2.	The exterior wall facing the reduced open space shall have a fire-resistance rating of not less than 3 hours;

3.	Openings in the exterior wall facing the reduced open space shall have opening protectives with a fire protection rating of not less than 3 hours; and

4.	Group E, H, I or R occupancies are not located within the covered or open mall building or anchor buildings.

402.1.3 Open mall building perimeter line.  For the purpose of this code, a perimeter line shall be established. The perimeter line shall encircle all buildings and structures that comprise the open mall building and shall encompass any open-air interior walkways, open-air courtyards or similar open-air spaces. The perimeter line shall define the extent of the open mall building. Anchor buildings and parking structures shall be outside of the perimeter line and are not considered as part of the open mall building.

402.2 Definitions. [The following words and terms shall, for the purposes of this chapter and as used elsewhere in this code, have the meanings shown herein.] This section contains terms defined elsewhere in this code, and terms with definitions that are specific to this section.

402.2.1 Terms defined elsewhere in this code. The following terms are defined in Chapter 2:

ANCHOR BUILDING. [An exterior perimeter building of a group other than H having direct access to a covered mall building but having required means of egress independent of the mall.]

COVERED MALL BUILDING. [A single building enclosing a number of tenants and occupants such as retail stores, drinking and dining establishments, entertainment and amusement facilities, passenger transportation terminals, offices, and other similar uses wherein two or more tenants have a main entrance into one or more malls. For the purpose of this chapter, anchor buildings shall not be considered as a part of the covered mall building. The term “covered mall building” shall include open mall buildings as defined below.]

Mall. [A roofed or covered common pedestrian area within a covered mall building that serves as access for two or more tenants and not to exceed three levels that are open to each other. The term “mall” shall include open malls as defined below.]

Open mall. [An unroofed common pedestrian way serving a number of tenants not exceeding three levels. Circulation at levels above grade shall be permitted to include open exterior balconies leading to exits discharging at grade.]

Open mall building. [Several structures housing a number of tenants, such as retail stores, drinking and dining establishments, entertainment and amusement facilities, offices, and other similar uses, wherein two or more tenants have a main entrance into one or more open malls. For the purpose of Chapter 4, anchor buildings are not considered as a part of the open mall building.]

402.2.2 Definitions specific to this section. The following terms shall, for the purposes of this section, have the meanings shown herein:

FOOD COURT. A public seating area located in the mall that serves adjacent food preparation tenant spaces.

GROSS LEASABLE AREA. The total floor area designed for tenant occupancy and exclusive use. The area of tenant occupancy is measured from the centerlines of joint partitions to the outside of the tenant walls. All tenant areas, including areas used for storage, shall be included in calculating gross leasable area.

402.3 Fire protection plan. A fire protection plan shall be provided to the Fire Department pursuant to Article 109 of Title 28.

[402.4 Means of egress. The covered mall building shall be provided with means of egress as required by this code. Where there is a conflict between the requirements of this code and the requirements of this section, the requirements of this section shall apply.]

[402.4.1 Occupant load. The calculated occupant load used to determine the required number of means of egress shall be in accordance with this section.]

[402.4.1.1 Occupant load of tenant spaces. The occupant load permitted in any individual tenant space in a covered mall building shall be determined in accordance with Chapter 10. Means of egress requirements for individual tenant spaces shall be based on the occupant load thus determined.]

[402.4.1.2 Occupant load of mall. In determining required means of egress of the mall, the total occupant load in the mall shall include the occupant load attributed to the mall as determined by Section 402.4.1.2.1, plus the occupant load of the food court as determined by Section 402.4.1.2.3, if any.]

[402.4.1.2.1 Occupant load formula. To determine the occupant load attributed to the mall, the gross leasable area (square feet), excluding any food court and anchor buildings, shall be divided by the occupant load factor (OLF) value determined by Equation 4-1.]

[]	[(Equation 4-1)]

[where:]

[]

[]

[Exception: Tenant spaces attached to a covered mall building but with a means of egress system that is totally independent of the covered mall building shall not be considered as gross leasable area for determining the required means of egress for the covered mall building.]

[402.4.1.2.2 OLF range. The occupant load factor (OLF) is not required to be less than 30 and shall not exceed 50.]

[402.4.1.2.3 Food courts. The occupant load of a food court shall be determined in accordance with Section 1004 and shall be added to the occupant load of the mall.]

[402.4.1.3 Anchor buildings. The occupant load of anchor buildings opening into the mall shall not be included in computing the total number of occupants for the covered mall building.]

[402.4.2 Number of means of egress. The required number of means of egress shall be determined in accordance with this section.]

[402.4.2.1 Number of means of egress within tenant spaces. Wherever the distance of travel to the mall from any location within a tenant space used by persons other than employees exceeds 75 feet (22 860 mm) or the tenant space exceeds an occupant load of 50, no fewer than two means of egress shall be provided.]

[402.4.2.2 Number of means of egress from the mall. The number of means of egress from the mall shall be determined in accordance with Chapter 10 and shall be based upon an occupant load calculated in accordance with Section 402.4.1.2.]

[402.4.3 Arrangements of means of egress. Means of egress shall be arranged in accordance with this section.]

[402.4.3.1 Anchor building means of egress. Required means of egress for anchor buildings shall be provided independently from the mall means of egress system. The occupant load of anchor buildings opening into the mall shall not be included in determining means of egress requirements for the mall. The path of egress travel of malls shall not exit through anchor buildings. Malls terminating at an anchor building where no other means of egress has been provided shall be considered as a dead-end mall.]

[402.4.3.2 Tenant spaces requiring more than one means of egress. Where more than one means of egress is required from an individual tenant space as determined by Chapter 10, not more than 50 percent of the occupant load shall discharge into the mall.]

[402.4.3.3 Large assembly occupancy. Assembly occupancies with an occupant load of 500 or more shall be so located in the covered mall building such that their entrance will be immediately adjacent to a principal entrance to the mall and shall have not less than one-half of their required means of egress opening directly to the exterior of the covered mall building.]

[402.4.4 Distance to exits. The maximum permitted travel distance to exits in covered mall buildings shall be in accordance with this section.]

[402.4.4.1 Distance to exits within tenant spaces. The maximum travel distance from any point within an individual tenant space to its entrance to the mall or to an exit shall not exceed 200 feet (60 960 mm).]

[402.4.4.2 Distance to exits within the mall. The maximum distance of travel from any point within a mall to an exit shall not exceed 200 feet (60 960 mm).]

[402.4.5 Access to exits. Where more than one exit is required, they shall be so arranged that it is possible to travel in either direction from any point in a mall to separate exits. However, in dead ends not exceeding a length equal to twice the width of the mall measured at the narrowest location within the dead end portion of the mall, one direction of travel shall be permitted. The minimum width of an exit passageway or corridor from a mall shall be 66 inches (1676 mm).]

[402.4.5.1 Exit passageway enclosures. Where exit passageway enclosures provide a secondary means of egress from a tenant space, doors to the exit passageway enclosures shall be minimum 1-hour fire doors with panic hardware. Such doors shall be self-closing and be so maintained or shall be automatic closing by smoke detection.]

[402.4.6 Service areas fronting on exit passageways. Mechanical rooms, electrical rooms, building service areas and service elevators are permitted to open directly into exit passageways provided that the exit passageway is separated from such rooms by fire barriers providing the same fire-resistance rating as required for the exit passageway. Door swings from these rooms shall not project into the minimum width of such exit passageways.]

[402.5 Mall width. For the purpose of providing required egress, malls are permitted to be considered as corridors but need not comply with the requirements of Section 1005.1 of this code where the width of the mall is as specified in this section.]

[402.5.1 Minimum width. The minimum width of the mall shall be 20 feet (6096 mm). The mall width shall be sufficient to accommodate the occupant load served. There shall be a minimum of 10 feet (3048 mm) clear width to a height of 8 feet (2438 mm) between any projection of a tenant space bordering the mall and the nearest kiosk, vending machine, bench, display opening, food court or other obstruction to means of egress travel.]

[402.5.2 Minimum width open mall. The minimum floor and roof opening width above grade shall be 20 feet (6096 mm) in open malls.]

[402.6 Types of construction. Covered mall buildings, including anchor buildings, shall be only of Type I, II, and IV construction. Their areas shall not be limited provided that the covered mall building and attached anchor buildings and parking garages are surrounded on all sides by a permanent open space of not less than 60 feet (18 288 mm) and the anchor buildings do not exceed three stories in height. The height of covered mall buildings, including anchor buildings, of Type IIB construction shall be limited to one story. The allowable height and area of anchor buildings greater than three stories in height shall comply with Section 503, as modified by Sections 504 and 506. The construction type of open parking garages and enclosed parking garages shall comply with Sections 406.3 and 406.4, respectively.]

[402.6.1 Reduced open space. The permanent open space of 60 feet (18 288 mm) shall be permitted to be reduced to not less than 40 feet (12 192 mm), provided the following requirements are met:]

[1.	The reduced open space shall not be allowed for more than 75 percent of the perimeter of the covered mall building and anchor buildings.]

[2.	The exterior wall facing the reduced open space shall have a minimum fire-resistance rating of 3 hours.]

[3.	Openings in the exterior wall facing the reduced open space shall have opening protectives with a minimum fire protection rating of 3 hours.]

[4.	Group E, H, I or R occupancies are not within the covered mall building or anchor stores.]

402.4 Construction.  The construction of covered and open mall buildings, anchor buildings and parking garages associated with a mall building shall comply with Sections 402.4.1 through 402.4.3.

402.4.1 Area and types of construction.  The building area and type of construction of covered mall or open mall buildings, anchor buildings and parking garages shall comply with this section.

402.4.1.1 Covered and open mall buildings.  Covered and open mall buildings shall be of Type I, II, or IV construction. The height of covered mall buildings of Type IIB construction shall be limited to one story. The areas of covered mall buildings or open mall buildings shall not be limited provided that the covered mall building or open mall building and attached anchor buildings and parking garages are surrounded on all sides by a permanent open space in accordance with Section 402.1.2.

402.4.1.2 Anchor buildings.  Anchor buildings shall be of Type I, II, or IV construction. The height of anchor buildings, of Type IIB construction, shall be limited to one story. The allowable height and area of anchor buildings greater than three stories in height shall comply with Section 503, as modified by Sections 504 and 506.

402.4.1.3 Parking garage. The building area and building height of any parking garage, open or enclosed, shall be based on the type of construction as required by Sections 406.5 and 406.6, respectively.

[402.7] 402.4.2 Fire-resistance-rated separation. Fire-resistance-rated separation is not required between tenant spaces and the mall. Fire-resistance-rated separation is not required between a food court and adjacent tenant spaces or the mall.

402.4.2.1 Tenant separations.  Each tenant space shall be separated from other tenant spaces by a fire partition complying with Section 708. A tenant separation wall is not required between any tenant space and the mall.

402.4.2.2 Anchor building separation.  An anchor building shall be separated from the covered or open mall building by fire walls complying with Section 706.

Exceptions:

1.	Anchor buildings of not more than three stories above grade that have an occupancy classification of the same uses permitted as tenants of the covered mall building shall be separated by 2-hour fire-resistance-rated fire barriers complying with Section 707. Openings between such buildings and the mall need not be protected.

2.	The exterior walls of anchor buildings separated from an open mall building by an open mall shall comply with Table 602.

[402.7.1] 402.4.2.3 [Attached garage] Parking garages. An attached [parking] garage for the storage of passenger vehicles having a capacity of not more than nine persons and open parking garages shall be considered as a separate building where it is separated from the covered or open mall building or anchor building by not less than 2-hour fire barriers constructed in accordance with Section 707 or horizontal assemblies constructed in accordance with Section [712] 711, or both.

[Exception: Where an] Parking garages, open [parking garage] or enclosed [parking garage is], which are separated from [the] covered mall [building] buildings, open mall buildings or anchor [building by a distance greater than 10 feet (3048 mm), the] buildings, shall comply with the provisions of Table 602[shall apply].

Pedestrian walkways and tunnels that [attach the open parking garage or enclosed parking garage] connect garages to the [covered] mall [building] buildings or anchor [building] buildings shall be constructed in accordance with Section 3104.

[402.7.2 Tenant separations. Each tenant space shall be separated from other tenant spaces by a fire partition complying with Section 709. A tenant separation wall is not required between any tenant space and the mall.]

402.4.3 Open mall construction. Floor assemblies in, and roof assemblies over, the open mall of an open mall building shall be open to the atmosphere for not less than 20 feet (9096 mm), measured perpendicular from the face of the tenant spaces on the lowest level, from edge of balcony to edge of balcony on upper floors and from edge of roof line to edge of roof line. The openings within, or the unroofed area of, an open mall shall extend from the lowest/grade level of the open mall through the entire roof assembly. Balconies on upper levels of the mall shall not project into the required width of the opening.

402.4.3.1 Pedestrian walkways. Pedestrian walkways connecting balconies in an open mall shall be located not less than 20 feet (9096 mm) from any other pedestrian walkway.

[402.7.3 Anchor building separation. An anchor building shall be separated from the covered mall building by fire walls complying with Section 706.]

[Exception: Anchor buildings of not more than three stories above grade that have an occupancy classification of the same uses permitted as tenants of the covered mall building shall be separated by 2-hour fire resistive fire barriers complying with Section 707. Openings between such buildings and the mall need not be protected.]

[402.8 Interior finish. Interior wall and ceiling finishes within the mall and exits shall have a minimum flame spread index and smoke-developed index of Class B in accordance with Chapter 8. Interior floor finishes shall meet the requirements of Section 804.]

[402.9] 402.5 Automatic sprinkler system. [The covered] Covered and open mall [building] buildings and buildings connected shall be [provided] equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1, [that] which shall comply with all of the following:

1.	The automatic sprinkler system shall be complete and operative throughout occupied space in the [covered] mall building prior to occupancy of any of the tenant spaces. Unoccupied tenant spaces shall be similarly protected unless provided with approved [alternate] alternative protection.

2.	Sprinkler protection for the mall of a covered mall building shall be controlled independently [independent] from that provided for tenant spaces or [anchors] anchor buildings.

3.	Sprinkler protection for the tenant spaces of an open mall building shall be controlled independently from that provided for anchor buildings.

4.	Sprinkler protection shall be provided beneath exterior circulation balconies located adjacent to an open mall.

5.	Where tenant spaces are supplied by the same system, they shall be independently controlled.

Exception: An automatic sprinkler system shall not be required in spaces or areas of open parking garages separated from the covered or open mall building in accordance with Section 402.4.2.3 and constructed in accordance with Section [406.2] 406.5.

[402.9.1 Standpipe system. The covered mall building shall be equipped with a standpipe system as required by Section 905.3.3.]

402.6 Interior finishes and features. Interior finishes within the mall and installations within the mall shall comply with Sections 402.6.1 through 402.6.4.

402.6.1 Interior finish. Interior wall and ceiling finishes within the mall of a covered mall building and within the exits of covered or open mall buildings shall have a minimum flame spread index and smoke-developed index of Class B in accordance with Chapter 8. Interior floor finishes shall meet the requirements of Section 804.

[402.10 Smoke control. A smoke control system shall be provided in accordance with Section 909 for malls greater than one story in height.]

[Exception: A smoke control system is not required in an open mall.]

[402.11] 402.6.2 Kiosks. Kiosks and similar structures (temporary or permanent) located within the mall of a covered mall building or within the perimeter line of an open mall building shall meet the following requirements:

1.	Combustible kiosks or other similar structures shall not be located within [the] a covered or open mall unless constructed of any of the following materials:

1.1.	Fire-retardant-treated wood complying with Section 2303.2.

1.2.	Foam plastics having a maximum heat release rate not greater than 100 kW (105 Btu/h) when tested in accordance with the exhibit booth protocol in UL 1975 or when tested in accordance with NFPA 289 using the 20 kW ignition source.

1.3.	Aluminum composite material (ACM) having a flame spread index of not more than 25 and a smoke-developed index of not more than 450 when tested as an assembly in the maximum thickness intended for use in accordance with ASTM E 84 or UL 723.

2.	[Kiosks] Covered kiosks or similar covered structures located within the covered mall building shall be provided with an approved [fire suppression and detection] automatic sprinkler system and detection devices where required by the New York City Fire Code and Section 903.3.3 of this code.

3.	The [minimum] horizontal separation between kiosks or groupings thereof and other similar structures within the mall shall be not less than 20 feet (6096 mm).

4.	Each kiosk or similar structure or groupings thereof shall have [a maximum] an area [of] not greater than 300 square feet (28 m2).

[402.12] 402.6.3 Children’s [playground] play structures. [Structures intended as children’s playgrounds that exceed 10 feet (3048 mm) in height and 150 square feet (14 m2) in area shall comply with Sections 402.12.1 through 402.12.4.] Children’s play structures located within the mall of a covered mall building or within the perimeter line of an open mall building shall comply with Section 424. The horizontal separation between children’s play structures, kiosks and similar structures within the mall shall be not less than 20 feet (6096 mm).

[402.12.1 Materials. Children’s playground structures shall be constructed of noncombustible materials or of combustible materials that comply with the following:]

[1.	Fire-retardant-treated wood.]

[2.	Light-transmitting plastics complying with Section 2606.]

[3.	Foam plastics (including the pipe foam used in soft-contained play equipment structures) having a maximum heat-release rate not greater than 100 kilowatts when tested in accordance with UL 1975.]

[4.	Aluminum composite material (ACM) meeting the requirements of Class A interior finish in accordance with Chapter 8 when tested as an assembly in the maximum thickness intended for use.]

[5.	Textiles and films complying with the flame propagation performance criteria contained in NFPA 701.]

[6.	Plastic materials used to construct rigid components of soft-contained play equipment structures (such as tubes, windows, panels, junction boxes, pipes, slides and decks) exhibiting a peak rate of heat release not exceeding 400 kW/m2 when tested in accordance with ASTM E 1354 at an incident heat flux of 50 kW/m2 in the horizontal orientation at a thickness of 6 mm .]

[7.	Ball pool balls, used in soft-contained play equipment structures, having a maximum heat-release rate not greater than 100 kilowatts when tested in accordance with UL 1975. The minimum specimen test size shall be 36 inches by 36 inches (914 mm by 914 mm) by an average of 21 inches (533 mm) deep, and the balls shall be held in a box constructed of galvanized steel poultry netting wire mesh.]

[8.	Foam plastics shall be covered by a fabric, coating or film meeting the flame propagation performance criteria of NFPA 701.]

[9.	The floor covering placed under the children’s playground structure shall exhibit a Class I interior floor finish classification, as described in Section 804, when tested in accordance with NFPA 253.]

[402.12.2 Fire protection. Children’s playground structures located within the mall shall be provided with the same level of approved fire suppression and detection devices required for kiosks and similar structures.]

[402.12.3 Separation. Children’s playground structures shall have a minimum horizontal separation from other structures within the mall of 20 feet (6090 mm).]

[402.12.4 Area limits. Children’s playground structures shall not exceed 300 square feet (28 m2) in area.]

[402.13 Security grilles and doors. Horizontal sliding or vertical security grilles or doors that are a part of a required means of egress shall conform to the following:]

[1.	They shall remain in the full open position during the period of occupancy by the general public.]

[2.	Doors or grilles shall not be brought to the closed position when there are 10 or more persons occupying spaces served by a single exit or 50 or more persons occupying spaces served by more than one exit.]

[3.	The doors or grilles shall be openable from within without the use of any special knowledge or effort where the space is occupied.]

[4.	Where two or more exits are required, not more than one-half of the exits shall be permitted to include either a horizontal sliding or vertical rolling grille or doors.]

[402.14 Standby power. Covered mall buildings exceeding 50,000 square feet (4645 m2) shall be provided with standby power systems that are capable of operating the emergency voice/alarm communication system.]

[402.15 Emergency voice/alarm communication system. Covered mall buildings exceeding 50,000 square feet (4645 m2) in total floor area shall be provided with an emergency voice/alarm communication system. Emergency voice/alarm communication systems serving a mall, required or otherwise, shall be accessible to the Fire Department. The system shall be provided in accordance with Section 907.2.12.2.]

[402.16] 402.6.4 Plastic signs. Plastic signs affixed to the storefront of any tenant space facing [the] a mall or open mall shall be limited as specified in Sections [402.16.1] 402.6.4.1 through [402.16.5] 402.6.4.5.

[402.16.1] 402.6.4.1 Area. Plastic signs shall be not [exceed] more than 20 percent of the wall area facing the mall.

[402.16.2] 402.6.4.2 Height and width.  Plastic signs shall be not [exceed a height of] greater than 36 inches (914 mm) in height, except [if] that where the sign is vertical, the height shall be not [exceed] greater than 96 inches (2438 mm) and the width shall be not [exceed] greater than 36 inches (914 mm).

[402.16.3] 402.6.4.3 Location.  Plastic signs shall be located [a minimum distance of] not less than 18 inches (457 mm) from adjacent tenants.

[402.16.4] 402.6.4.4 Plastics other than foam plastics. Plastics other than foam plastics used in signs shall be [light-transmitting] lighttransmitting plastics complying with Section 2606.4 or shall have a self-ignition temperature of 650°F (343°C) or greater when tested in accordance with ASTM D 1929, and a flame spread index not greater than 75 and smoke-developed index not greater than 450 when tested in the manner intended for use in accordance with ASTM E 84 or UL 723 or meet the acceptance criteria of Section [803.2.1] 803.1.2.1 when tested in accordance with NFPA 286.

[402.16.4.1] 402.6.4.4.1 Encasement. Edges and backs of plastic signs in the mall shall be fully encased in metal.

[402.16.5] 402.6.4.5 Foam plastics. Foam plastics used in signs shall have flame-retardant characteristics such that the sign has a maximum heat-release rate of 150 kilowatts when tested in accordance with UL 1975 or when tested in accordance with NFPA 289 using the 20 kW ignition source, and the foam plastics shall have the physical characteristics specified in this section. Foam plastics used in signs installed in accordance with Section [402.14] 402.6.4 shall not be required to comply with the flame spread and smoke-developed [indexes] indices specified in Section 2603.3.

[402.16.5.1] 402.6.4.5.1 Density. The [minimum] density of foam plastics used in signs shall be not [be] less than 20 pounds per cubic foot (pcf) (320 kg/m3).

[402.16.5.2] 402.6.4.5.2 Thickness.  The thickness of foam plastic signs shall be not [be] greater than 1/2 inch (12.7 mm).

402.7 Emergency systems. Covered and open mall buildings, anchor buildings and associated parking garages shall be provided with emergency systems complying with Sections 402.7.1 through 402.7.5.

402.7.1 Standpipe system. Covered and open mall buildings shall be equipped throughout with a standpipe system as required by Section 905.3.3.

402.7.2 Smoke control.  Where a covered mall building contains an atrium, a smoke control system shall be provided in accordance with Section 404.5.

402.7.3 Emergency power. Covered mall buildings greater than 50,000 square feet (4645 m2) in area and open mall buildings greater than 50,000 square feet (4645 m2) within the established perimeter line shall be provided with emergency power that is capable of operating the emergency voice/alarm communication system in accordance with Section 2702.

402.7.4 Emergency voice/alarm communication system. Where the total floor area is greater than 50,000 square feet (4645 m2) within either a covered mall building or within the perimeter line of an open mall building, an emergency voice/alarm communication system shall be provided.

Emergency voice/alarm communication systems serving a mall, required or otherwise, shall be accessible to the fire department. The systems shall be provided in accordance with Section 907.5.2.2.

[402.17] 402.7.5 Fire Department access to equipment. Rooms or areas containing controls for air-conditioning systems, automatic fire-extinguishing systems, automatic sprinkler systems or other detection, suppression or control elements shall be identified for use by the Fire Department.

402.8 Means of egress. Covered mall buildings, open mall buildings and each tenant space within a mall building shall be provided with means of egress as required by this section and this code. Where there is a conflict between the requirements of this code and the requirements of Sections 402.8.1 through 402.8.8, the requirements of Sections 402.8.1 through 402.8.8 shall apply.

402.8.1 Mall width. For the purpose of providing required egress, malls are permitted to be considered as corridors but need not comply with the requirements of Section 1005.1 of this code where the width of the mall is as specified in this section.

402.8.1.1 Minimum width. The aggregate clear egress width of the mall in either a covered or open mall building shall be not less than 20 feet (6096 mm). The mall width shall be sufficient to accommodate the occupant load served. No portion of the minimum required aggregate egress width shall be less than 10 feet (3048 mm) measured to a height of 8 feet (2438 mm) between any projection of a tenant space bordering the mall and the nearest kiosk, vending machine, bench, display opening, food court or other obstruction to means of egress travel.

402.8.2 Occupant load. The calculated occupant load used to determine the required number of means of egress shall be in accordance with this section.

402.8.2.1 Occupant load of tenant spaces. The occupant load permitted in any individual tenant space in a covered mall building shall be determined in accordance with Chapter 10. Means of egress requirements for individual tenant spaces shall be based on the occupant load thus determined.

402.8.2.2 Occupant load of mall. In determining required means of egress of the mall, the total occupant load in the mall shall include the occupant load attributed to the mall as determined by Section 402.8.2.3, plus the occupant load of the food court as determined by Section 402.8.2.5, if any.

402.8.2.3 Occupant load formula. To determine the occupant load attributed to the mall, the gross leasable area (square feet), excluding any food court and anchor buildings, shall be divided by the occupant load factor (OLF) value determined by Equation 4-1.

(Equation 4-1)

where:

Exception: Tenant spaces attached to a covered mall building but with a means of egress system that is totally independent of the covered mall building shall not be considered as gross leasable area for determining the required means of egress for the covered mall building.

402.8.2.4 OLF range. The occupant load factor (OLF) is not required to be less than 30 and shall not exceed 50.

402.8.2.5 Food courts. The occupant load of a food court shall be determined in accordance with Section 1004 and shall be added to the occupant load of the mall.

402.8.2.6 Anchor buildings. The occupant load of anchor buildings opening into the mall shall not be included in computing the total number of occupants for the covered mall building.

402.8.3 Number of means of egress. The required number of means of egress shall be determined in accordance with this section.

402.8.3.1 Number of means of egress within tenant spaces. Wherever the distance of travel to the mall from any location within a tenant space used by persons other than employees exceeds 75 feet (22 860 mm) or the tenant space exceeds an occupant load of 74, no fewer than two means of egress shall be provided.

402.8.3.2 Number of means of egress from the mall. The number of means of egress from the mall shall be determined in accordance with Chapter 10 and shall be based upon an occupant load calculated in accordance with Section 402.8.2.

402.8.4 Arrangements of means of egress. Means of egress shall be arranged in accordance with this section.

402.8.4.1 Anchor building means of egress. Required means of egress for anchor buildings shall be provided independently from the mall means of egress system. The occupant load of anchor buildings opening into the mall shall not be included in determining means of egress requirements for the mall. The path of egress travel of malls shall not exit through anchor buildings. Malls terminating at an anchor building where no other means of egress has been provided shall be considered as a dead-end mall.

402.8.4.2 Tenant spaces requiring more than one means of egress. Where more than one means of egress is required from an individual tenant space as determined by Chapter 10, not more than 50 percent of the occupant load shall discharge into the mall.

402.8.4.3 Large assembly occupancy. Assembly occupancies with an occupant load of 500 or more shall be so located in the covered mall building such that their entrance will be immediately adjacent to a principal entrance to the mall and shall have not less than one-half of their required means of egress opening directly to the exterior of the covered mall building.

402.8.5 Distance to exits. Within each individual tenant space in a covered or open mall building, the distance of travel from any point to an exit or entrance to the mall shall be not greater than 200 feet (60 960 mm).

The distance of travel from any point within a mall of a covered mall building to an exit shall be not greater than 200 feet (60 960 mm). The maximum distance of travel from any point within an open mall to the perimeter line of the open mall building shall be not greater than 200 feet (60 960 mm).

402.8.6 Access to exits. Where more than one exit is required, they shall be so arranged that it is possible to travel in either direction from any point in a mall of a covered mall building to separate exits or from any point in an open mall of an open mall building to two separate locations on the perimeter line, provided neither location is an exterior wall of an anchor building or parking garage. The width of an exit passageway or corridor from a mall shall be not less than 66 inches (1676 mm).

Exception: Access to exits is permitted by way of a dead-end mall that does not exceed a length equal to twice the width of the mall measured at the narrowest location within the dead-end portion of the mall.

402.8.6.1 Exit passageway enclosures. Where exit passageway enclosures provide a secondary means of egress from a tenant space, doors to the exit passageway enclosures shall be minimum 1-hour fire doors with panic hardware. Such doors shall be self-closing and be so maintained or shall be automatic closing by smoke detection.

402.8.7 Service areas fronting on exit passageways. Mechanical rooms, electrical rooms, building service areas and service elevators are permitted to open directly into exit passageways provided that the exit passageway is separated from such rooms by fire barriers providing the same fire-resistance rating as required for the exit passageway. Door swings from these rooms shall not project into the minimum width of such exit passageways.

402.8.8 Security grilles and doors. Horizontal sliding or vertical security grilles or doors that are a part of a required means of egress shall conform to the following:

1.	Doors and grilles shall remain in the full open position during the period of occupancy by the general public.

2.	Doors or grilles shall not be brought to the closed position when there are 10 or more persons occupying spaces served by a single exit or 50 or more persons occupying spaces served by more than one exit.

3.	The doors or grilles shall be openable from within without the use of any special knowledge or effort where the space is occupied.

4.	Where two or more exits are required, not more than one-half of the exits shall be permitted to include either a horizontal sliding or vertical rolling grille or door.

SECTION BC 403
HIGH-RISE BUILDINGS

403.1 Applicability. High-rise buildings shall comply with Sections 403.2 through 403.8.

Exception: The provisions of [this section] Sections 403.2 through 403.8 shall not apply to the following buildings and structures:

1.	Air traffic control towers in accordance with Section 412.3.

2.	Buildings occupied entirely by Group R-3 classification.

3.	Open parking garages in accordance with Section [406.3] 406.5.

4.	[Buildings with an occupancy in] The portion of a building containing a Group A-5 occupancy in accordance with Section [303.1] 303.6.

5.	[Low-hazard special] Special industrial occupancies in accordance with Section 503.1.1.

6.	Buildings with [an occupancy in]:

6.1.	A Group H-1[,] occupancy;

6.2.	A Group H-2 [or H-3] occupancy in accordance with Section [415] 415.8, 415.9.2, 415.9.3 or 426.1; or

6.3.	A Group H-3 occupancy in accordance with Section 415.8.

403.2 Construction. The construction of high-rise buildings shall comply with the provisions of Sections 403.2.1 through 403.2.4.

403.2.1 Types of construction. The following modifications to the minimum fire-resistance rating of the building elements in Table 601 shall be as follows:

1.	High rise buildings 420 feet (128 m) or greater in building height shall be constructed of Type IA construction.

2.	For high rise buildings not greater than 420 feet (128 m) in building height, and constructed to meet the fire-resistance rating requirements of Type IB or IIA construction, the required fire-resistance rating of columns supporting floors shall be constructed to meet Type IA construction.

403.2.2 Seismic considerations. For seismic considerations, see Chapter 16.

403.2.3 Structural integrity of interior exit [enclosures] stairways and elevator hoistway enclosures. For all high-rise buildings, exit enclosures for interior exit stairways and elevator hoistway enclosures shall comply with Sections 403.2.3.1 through 403.2.3.4.

Exception: Where fire-resistance rating is not required by this code for the enclosure or  portions thereof.

403.2.3.1 Wall assembly. The wall assemblies making up the [exit] enclosures for interior exit stairways and elevator hoistway enclosures shall meet or exceed Soft Body Impact Classification Level 2 as measured by the test method described in ASTM C 1629/C 1629M.

403.2.3.2 Wall assembly materials. The face of the wall assemblies making up the [exit] enclosures for interior exit stairways and elevator hoistway enclosures that are not exposed to the interior of the enclosures for interior exit [enclosure] stairways or elevator hoistway enclosure shall be constructed in accordance with one of the following methods:

1.	The wall assembly shall incorporate [not less] no fewer than two layers of impact-resistant construction board each of which meets or exceeds Hard Body Impact Classification Level 2 as measured by the test method described in ASTM C 1629/C 1629M.

2.	The wall assembly shall incorporate [not less] no fewer than one layer of impact-resistant construction material that meets or exceeds Hard Body Impact Classification Level 3 as measured by the test method described in ASTM C 1629/C 1629M.

3.	The wall assembly incorporates multiple layers of any material, tested in tandem, that [meet] meets or [exceed] exceeds Hard Body Impact Classification Level 3 as measured by the test method described in ASTM C 1629/C 1629M.

403.2.3.3 Concrete and masonry walls. Concrete or masonry walls shall be deemed to satisfy the requirements of Sections 403.2.3.1 and 403.2.3.2.

403.2.3.4 Other wall assemblies. Any other wall assembly that provides impact resistance equivalent to that required by Sections 403.2.3.1 and 403.2.3.2 for Hard Body Impact Classification Level 3, as measured by the test method described in ASTM C 1629/C 1629M, shall be permitted.

403.2.4 Sprayed fire-resistant materials (SFRM). The bond strength of the SFRM installed throughout the building shall be in accordance with Table 403.2.4.

TABLE 403.2.4
MINIMUM BOND STRENGTH

| HEIGHT OF BUILDINGa | SFRM MINIMUM BOND STRENGTH |
| --- | --- |
| Up to 420 feet | 430 psf |
| Greater than 420 feet | 1,000 psf |

For SI: 1 foot = 304.8 mm, 1 pound per square foot (psf) = 0.0479 kW/m2.

a.	Above the lowest level of fire department vehicle access.

403.3 Automatic sprinkler system. Buildings and structures shall be equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1[. A] and a secondary water supply [shall be provided] where required by Section [903.3.5.2] 403.3.3.

403.3.1 Number of sprinkler risers and system design. Each sprinkler system zone in buildings that are more than 300 feet [(9144 m)] (91 440 mm) in building height shall be supplied by [a minimum of] no fewer than two risers. Each riser shall supply sprinklers on alternate floors. If more than two risers are provided for a zone, sprinklers on adjacent floors shall not be supplied from the same riser.

403.3.1.1 Riser location. [Each sprinkler riser] Sprinkler risers shall be placed in interior exit [enclosures] stairways and ramps that are remotely located in accordance with Section [1015.2] 1007.1.

403.3.2 Water supply to required fire pumps. Required fire pumps shall be provided with water supplies in accordance with Section 905.2 and NFPA 14 as modified by Appendix Q.

403.3.3 Secondary on-site water supply. A secondary on-site water supply equal to the hydraulically calculated sprinkler demand, including the hose stream requirement, shall be provided for high-rise buildings in Seismic Design Category C or D as determined by this code, and in any high-rise building with occupied floors located more than 500 feet (152 m) above the lowest level of fire department vehicle access. The secondary on-site water supply shall have a duration of not less than 30 minutes as determined by the occupancy hazard classification in accordance with NFPA 13 as modified by Appendix Q.

403.3.4 Fire pump room. Fire pumps shall be located in rooms protected in accordance with Section 913.2.1.

403.4 Emergency systems. The detection, alarm and emergency systems of high-rise buildings shall comply with Sections 403.4.1 through 403.4.8.

403.4.1 Smoke detection. Smoke detection shall be provided in accordance with Section 907.2.13.1.

403.4.2 Fire [alarms systems] alarm system. A fire alarm system shall be provided in accordance with Section 907.2.13.

403.4.3 Standpipe system. A high-rise building shall be equipped with a standpipe system as required by Section 905.3.

403.4.4 Emergency voice/alarm communication [systems] system. An emergency voice/alarm communication system shall be provided in accordance with Section 907.5.2.2.

[403.4.4] 403.4.5 Emergency responder radio coverage. Emergency responder radio coverage shall be provided in accordance with the New York City Fire Code and Section 907.2.13.2 of this code.

[403.4.5] 403.4.6 Fire command. A fire command center complying with Section 911 shall be provided in a location approved by the Fire Department.

[403.4.6] 403.4.7 Post-fire smoke purge. A post-fire smoke purge system shall be installed in accordance with Section [916] 917.

[403.4.7] 403.4.8 Standby and emergency power. A standby power system complying with Section 2702 and Section 3003 shall be provided for the standby power loads specified in [Section 403.4.7.2 and 403.4.7.3] Section 403.4.8.3. An emergency power system complying with Section 2702 shall be provided for the emergency power loads specified in Section 403.4.8.4.

[403.4.7.1 Special requirements for standby power systems.] 403.4.8.1 Equipment room. If the standby or emergency power system [is] includes a generator set inside a building, the system shall be located in a separate room [enclosed with 2-hour fire-resistance-rated fire barrier assemblies. System supervision with manual start and transfer features shall be provided at the fire command center] in accordance with Section 2702.1.2.2.

403.4.8.2 Fuel line piping protection. Fuel lines supplying a generator set inside a building shall comply with Section 1305.9 of the New York City Mechanical Code.

403.4.8.3 Standby power systems. A standby power system complying with Section 2702 shall be provided for standby power loads specified in Sections 403.4.8.3.1 and 403.4.8.3.2. Fuel sources for generators shall be in accordance with Section 2702.1.1.

[403.4.7.2] 403.4.8.3.1 Standby power loads in occupancies other than Group R-2. In buildings of any occupancy group other than Group R-2, the following are classified as standby power loads:

1.	Power and lighting for fire command center required by Section [403.4.5] 403.4.6;

2.	Ventilation and automatic fire detection equipment for smokeproof enclosures;

3.	Elevators, in accordance with Section 3003; and

4.	Stair pressurization systems when provided.

[403.4.7.3] 403.4.8.3.2 Standby power loads in Group R-2 occupancies. Group R-2 occupancies in buildings greater than 125 feet (38 100 mm) in height shall be required to provide a standby power system to support the following loads:

- Power and lighting for fire command center required by Section [403.4.5] 403.4.6;

- Ventilation and automatic fire detection equipment for smokeproof enclosures;

- At least one elevator serving all floors, or one elevator per bank where different banks serve different portions of the building; and

- Stair pressurization systems when provided.

[403.4.8] 403.4.8.4 Emergency power systems. An emergency power system complying with Section 2702 shall be provided for emergency power loads specified in Sections [403.4.8.1] 403.4.8.4.1 and [403.4.8.2] 403.4.8.4.3. Fuel sources for generators shall be in accordance with Section 2702.1.1.

[403.4.8.1] 403.4.8.4.1 Emergency power loads in occupancies other than Group R-2. In buildings of any occupancy group other than Group R-2, the following are classified as emergency power loads:

1.	Exit signs and means of egress illumination required by Chapter 10;

2.	Elevator car lighting;

3.	Emergency voice/alarm communications systems, including Fire Department in-building Auxiliary Radio Communication systems (ARCs);

4.	Automatic fire detection systems;

5.	Fire alarm systems; and

6.	Electrically powered fire pumps, including manual fire pumps, automatic fire pumps, and sprinkler booster pumps.

[403.4.8.2] 403.4.8.4.2 Emergency power loads in Group R-2 occupancies. Group R-2 occupancies in buildings greater than 125 feet (38 100 mm) in height shall be required to provide an emergency power system to support the following loads:

- Exit signs and means of egress illumination required by Chapter 10;

2.	Emergency voice communications systems, including Fire Department in-building Auxiliary Radio Communication systems (ARCs); and

3.	Electrically powered fire pumps, unless electrical power to the motor is taken ahead of the main from the street side of the house service switch.

403.4.8.4.3 Emergency power loads in Group R-2 occupancies 125 feet or less in height. Group R-2 occupancies in buildings 125 feet (38 100 mm) or less in height shall be required to provide an emergency power system to support the following loads:

1.	Emergency voice communications systems in buildings containing Group R-2 occupancies in accordance with Section 907.5.2.2, or where otherwise provided. Batteries in accordance with the New York City Electrical Code are permitted to serve as the secondary power supply for such systems.

2.	Fire Department in-building Auxiliary Radio Communication systems (ARCs) in buildings containing Group R-2 occupancies in accordance with Section 916.3, or where otherwise provided. Batteries in accordance with the New York City Electrical Code are permitted to serve as the secondary power supply for such systems.

403.5 Means of egress and evacuation. The means of egress in high-rise buildings shall comply with Sections 403.5.1 through 403.5.6.

403.5.1 Remoteness of interior exit [stairway enclosures] stairways. [The required] Required interior exit [stairway enclosures] stairways shall be separated by a distance not less than 30 feet (9144 mm) or not less than one-fourth of the length of the maximum overall diagonal dimension of the building or area to be served, whichever is less. The distance shall be measured in a straight line between the nearest points of the enclosure surrounding the interior exit [stairway enclosures] stairways. In buildings with three or more interior exit [stairway enclosures, at least] stairways, no fewer than two of the interior exit [stairway enclosures] stairways shall comply with this section. Stairs sharing any common wall, floors, ceilings, scissor stair assemblies, or other enclosures shall be counted as one interior exit stairway.

Exception: Group R-2 occupancies.

403.5.2 Additional exit stairway. For buildings other than Group R-2 that are more than 420 feet (128 m) in building height, one additional exit stairway meeting the requirements of Sections [1009] 1011 and [1022] 1023 shall be provided in addition to the minimum number of exits required by Section [1021.1] 1006.3. The total width of any combination of remaining exit stairways with one exit stairway removed shall not be less than the total width required by Section 1005.1. Stairs sharing any common wall, floors, ceilings, scissor stair assemblies, or other enclosures shall not be considered the additional exit stairway required by this section.

Exceptions: An additional exit stairway shall not be required to be installed in any of the following instances:

- In buildings where all passenger elevators for general public use and all other elevators used for occupant self-evacuation comply with Sections 3008.1 through 3008.11;

- In buildings where all of the following conditions are met:

2.1.	The commissioner has approved a timed egress analysis establishing the egress time it would take for a full building evacuation, utilizing the stairs required by Section [1021.1] 1006 and the additional stair that would have been required pursuant to Section 403.5.2;

2.2.	The commissioner has approved a timed egress analysis establishing the egress time it would take for a full building evacuation, utilizing the combination of the stairs required by Section [1021.1] 1006 and elevators used for occupant self-evacuation as follows:

2.2.1.	Such analysis need only utilize a number of designated elevators designed for occupant self-evacuation necessary to demonstrate an evacuation time that is less than the time established in Exception 2.1; and

2.2.2.	Every bank of passenger elevators for general public use shall be served by at least one such designated elevator;

2.3.	All elevators in the building that either are passenger elevators for general public use or are used for occupant self-evacuation shall comply with Sections 3008.1 through 3008.11. However, the standby power generating equipment required by Section 3008.9 need only be sized to satisfy the loads required to simultaneously operate those elevators identified in the timed egress analysis described in Exception 2.2.

The minimum number of exits required by Section [1021.1] 1006 are all at least 25 percent wider than the exit width required by Chapter 10. The increase in the stair width shall not be utilized in the timed egress analyses required by Exceptions 2.1 and 2.2[; or].

[3.	Where the application for construction document approval is submitted within 18 months after the date of enactment of the local law that added this section.]

403.5.3 Stairway door operation. Doors opening into interior stair enclosures shall not be locked from either side. However, a door locked from the stair side may be permitted provided that such door is equipped with an automatic fail safe system for opening in the event of the activation of any automatic fire detection system, or when any elevator recall is activated, or when any signal is received from the fire command center. Such door shall be deemed as openable from the stair side. Stair reentry signs shall be posted throughout the stairway indicating that reentry is provided only during fire emergencies. Such signs shall be in accordance with Section [1030.4.2] 1031.4.2.

Exception: In schools classified as Group E occupancies that require “lockdown drills” as per New York State Education Law 807, stairway egress doors from occupied spaces are permitted to be locked from the side opposite the egress side for the duration of the lockdown drill, provided they are openable from the occupied side for egress and are unlocked upon directions from the school administrative personnel following the completion of the lockdown drill.

403.5.3.1 Stairway communication system. A telephone or other two-way communications system connected to an approved constantly attended station shall be provided at not less than every fifth floor in each stairway where the doors to the stairway are locked in accordance with Section 403.5.3.

403.5.4 Smokeproof [exit] enclosures. Every required interior exit stairway serving floors more than 75 feet (22 860 mm) above the lowest level of fire department vehicle access shall comply with Sections 909.20 and [1022.9] 1023.11.

Exception [for R-2 occupancies]: Smokeproof enclosures are not required in occupancy Group R-2 unless provided pursuant to Exception 2 of Section [916.1] 917.1.

403.5.5 Luminous egress path markings. Luminous egress path markings shall be provided in accordance with Section [1024] 1025 and Appendix S.

Exception: Egress paths serving Group R-2.

403.5.6 Emergency escape and rescue. Emergency escape and rescue openings [required by] specified in Section [1029] 1030 are not required.

403.6 Elevators. Elevator [operation and] installation and operation in high-rise buildings shall [be in accordance] comply with Chapter 30 and Sections 403.6.1 and 403.6.2.

403.6.1 Fire service access elevator. In buildings with an occupied floor more than 120 feet (36 576 mm) above the lowest level of fire department vehicle access, a minimum of one fire service access elevator shall be provided in accordance with Section 3007.

403.6.2 Occupant evacuation elevators. Where installed in accordance with Section 3008, passenger elevators for general public use shall be permitted to be used for occupant self-evacuation.

403.6.3 Elevator lobbies. Elevator lobbies shall be provided in accordance with Sections [708.14.1 and 708.14.2] 3006.1.1 and 3006.1.2.

403.7 Outdoor air intakes. For high-rise buildings, outdoor air intakes serving spaces above the second story and serving spaces greater than 10,000 square feet (929 m2) of floor area shall be located in accordance with Section 401.5 of the New York City Mechanical Code.

Exception: Group R-2 occupancy.

403.8 Open web steel joists. The use of open web steel joists shall be prohibited in high-rise buildings until the commissioner promulgates rules establishing minimum acceptable fireproofing methods.

SECTION BC 404
ATRIUMS

404.1 General. In other than Group H occupancies, and where permitted by [Exception 5 in] Section [708.2] 712.1.7, the provisions of [this section] Sections 404.1 through 404.10 shall apply to buildings or structures containing vertical openings defined [herein] as [atriums.]“Atriums.”

404.1.1 [Definition] Definitions. The following [word and] term [shall, for the purposes of this chapter and as used elsewhere in this code, have the meaning shown herein.] is defined in Chapter 2:

ATRIUM.[An opening connecting three or more stories other than enclosed stairways, elevators, hoistways, escalators, plumbing, electrical, air-conditioning or any other vertical openings that are not required to be enclosed by other provisions of this code, which is closed at the top and not defined as a mall. Stories, as used in this definition, do not include balconies within assembly groups or mezzanines that comply with Section 505.]

404.2 Use. The floor of the atrium shall not be used for other than low fire hazard uses[,] and only approved materials and decorations in accordance with the New York City Fire Code shall be used in the atrium space.

Exception: The atrium floor area is permitted to be used for any approved use where the individual space is provided with an automatic sprinkler system in accordance with Section 903.3.1.1.

404.3 Automatic sprinkler protection. An approved automatic sprinkler system shall be installed throughout the entire building.

Exceptions:

1.	That area of a building adjacent to or above the atrium need not be sprinklered provided that portion of the building is separated from the atrium portion by not less than 2-hour fire barriers constructed in accordance with Section 707 or horizontal assemblies constructed in accordance with Section [712] 711, or both.

2.	Where the ceiling of the atrium is more than 55 feet (16 764 mm) above the floor, sprinkler protection at the ceiling of the atrium is not required.

404.4 Fire alarm system. A fire alarm system shall be provided in accordance with Section 907.2.14.

404.5 Smoke control. A smoke control system shall be installed in accordance with Section 909.

Exception: In other than Groups I-1 and I-2, and covered mall buildings containing an atrium pursuant to Section 402.7.2, smoke control is not required for atriums that connect only two stories.

404.6 Enclosure of atriums. Atrium spaces shall be separated from adjacent spaces by a 1-hour fire barrier constructed in accordance with Section 707 or a horizontal assembly constructed in accordance with Section [712] 711, or both.

Exceptions:

1.	A fire barrier is not required where a glass or glass-block wall forming a smoke partition [where automatic] is provided. The glass or glass-block wall shall comply with all of the following:

1.1.	Automatic sprinklers are [spaced 6 feet (1829 mm) or less] provided along both sides of the separation wall and doors, or on the room side only if there is not a walkway on the atrium side[, and]. The sprinklers shall be located between 4 inches and 12 inches (102 mm and 305 mm) away from the glass and [so] at intervals along the glass not greater than 6 feet (1829 mm). The sprinkler system shall be designed so that the entire surface of the glass is wet upon activation of the sprinkler system without obstruction[. The glass shall be installed in a gasketed frame so that the framing system deflects without breaking (loading) the glass before the sprinkler system operates.];

1.2.	The glass wall shall be installed in a gasketed frame in a manner that the framing system deflects without breaking (loading) the glass before the sprinkler system operates; and

1.3.	Where glass doors are provided in the glass wall, they shall be either self-closing or automatic-closing.

2.	The adjacent spaces of any three floors of the atrium shall not be required to be separated from the atrium where such spaces are accounted for in the design of the smoke control system.

404.7 Standby power. Equipment required to provide smoke control shall be [connected to a] provided with standby power [system] in accordance with Section 909.11.

404.8 Interior finish. The interior finish of walls and ceilings of the atrium shall be not [be] less than Class B with no reduction in class for sprinkler protection.

404.9 [Travel distance. In other than the lowest level of the atrium, where the required means of egress is through the atrium space, the portion of exit access travel distance within the atrium space shall not exceed 200 feet (60 960 mm). The travel distance requirements for areas of buildings open to the atrium and where access to the exits is not through the atrium, shall comply with the requirements of Section 1016.] Exit access travel distance. Exit access travel distance for areas open to an atrium shall comply with the requirements of this section.

404.9.1 Egress not through the atrium. Where required access to the exits is not through the atrium, exit access travel distance shall comply with Section 1017.

404.9.2 Exit access travel distance at the level of exit discharge. Where the path of egress travel is through an atrium space, exit access travel distance at the level of exit discharge shall be determined in accordance with Section 1017.

404.9.3 Exit access travel distance at other than the level of exit discharge. Where the path of egress travel is not at the level of exit discharge from the atrium, that portion of the total permitted exit access travel distance that occurs within the atrium shall be not greater than 200 feet (60 960 mm).

404.10 Interior exit stairways. A maximum of 50 percent of interior exit stairways are permitted to egress through an atrium on the level of exit discharge in accordance with Section 1028.

SECTION BC 405
UNDERGROUND BUILDINGS AND SPACES

405.1 General. The provisions of [this section] Sections 405.2 through 405.9 apply to building spaces having a floor level used for human occupancy more than 30 feet (9144 mm) below the finished floor of the lowest level of exit discharge.

Exceptions: The provisions of Section 405 are not applicable to the following buildings or portions of buildings:

1.	One- and two-family dwellings, sprinklered in accordance with Section 903.3.1.3.

2.	Parking garages provided with automatic sprinkler systems in compliance with Section 405.3.

3.	Fixed guideway transit systems.

4.	Grandstands, bleachers, stadiums, arenas and similar facilities.

5.	Where the lowest story is the only story that would qualify the building as an underground building and has an area not [exceeding] greater than 1,500 square feet (139 m2) and has an occupant load less than 10.

6.	Pumping stations and other similar mechanical spaces intended only for limited periodic use by service or maintenance personnel.

405.2 Construction requirements. The underground portion of the building shall be of Type I construction.

405.3 Automatic sprinkler system. The highest level of exit discharge serving the underground portions of the building and all levels below shall be equipped with an automatic sprinkler system installed in accordance with Section 903.3.1.1. Water-flow switches and control valves shall be supervised in accordance with Section 903.4.

405.4 Compartmentation. Compartmentation shall be in accordance with Sections 405.4.1 through 405.4.3.

405.4.1 Number of compartments. A building having a floor level more than 60 feet (18 288 mm) below the finished floor of the lowest level of exit discharge shall be divided into [a minimum of] no fewer than two compartments of approximately equal size. Such compartmentation shall extend through the highest level of exit discharge serving the underground portions of the building and all levels below.

Exception: The lowest story need not be compartmented where the area [does] is not [exceed] greater than 1,500 square feet (139 m2) and has an occupant load of less than 10.

405.4.2 Compartment separation. The separation between the two compartments shall be of minimum 2-hour fire barrier wall construction that shall extend from floor slab to floor deck above. Penetrations between the two compartments shall be limited to plumbing and electrical piping and conduit that are firestopped in accordance with Section [713] 714. Doorways shall be protected by fire door assemblies that are automatic-closing by smoke detection in accordance with Section [715.4.8.3] 716.5.9.3 and are installed in accordance with NFPA 105 and Section [715.4.3] 716.5.3. Where provided, each compartment shall have an air supply and an exhaust system independent of the other compartments.

405.4.3 Elevators. Where elevators are provided, each compartment shall have direct access to an elevator. Where an elevator serves more than one compartment, an elevator lobby shall be provided and shall be separated from each compartment by a 2-hour fire barrier. Doors shall be gasketed, have a drop sill, and be automatic-closing by smoke detection [installed] in accordance with Section [715.4.8.3] 716.5.9.3.

405.5 Smoke control system. A smoke control system shall be provided in accordance with Sections 405.5.1 and 405.5.2.

405.5.1 Control system. A smoke control system is required to control the migration of products of combustion in accordance with Section 909 and the provisions of this section. Smoke control shall restrict movement of smoke to the general area of fire origin and maintain means of egress in a usable condition.

405.5.2 Compartment smoke control system. Where compartmentation is required, each compartment shall have an independent smoke control system. The system shall be automatically activated and capable of manual operation in accordance with Sections 907.2.18 and 907.2.19.

405.6 Fire alarm systems. A fire alarm system shall be provided where required by Sections 907.2.18 and 907.2.19.

405.7 Means of egress. Means of egress shall be in accordance with Sections 405.7.1 and 405.7.2.

405.7.1 Number of exits. Each floor level shall be provided with [a minimum of] no fewer than two exits. Where compartmentation is required by Section 405.4, each compartment shall have [a minimum of] no fewer than one exit and shall also have [an] no fewer than one exit access doorway into the adjoining compartment.

405.7.2 Smokeproof enclosure. Every required stairway serving floor levels more than 30 feet (9144 mm) below its level of exit discharge shall comply with the requirements for a smokeproof enclosure as provided in Section [1022.9] 1023.11.

405.8 Standby and emergency power. A standby power system complying with Section 2702 shall be provided for the standby power loads specified in Section 405.8.1. An emergency power system complying with Section 2702 shall be provided for the emergency power loads specified in Section 405.8.2.

405.8.1 Standby power loads. The following loads are classified as standby power loads:

1.	Smoke control system[;].

2.	Ventilation and automatic fire detection equipment for smokeproof enclosures[;].

3.	Fire pumps[;].

4.	Elevators, as required in [accordance with] Section 3003; and

5.	Stair pressurization systems when provided.

[405.9 Emergency power. An emergency power system complying with Section 2702 shall be provided for emergency power loads specified in Section 405.9.1.]

[405.9.1] 405.8.2 Emergency power loads. The following loads are classified as emergency power loads:

1.	Emergency voice/alarm communications systems, including Fire Department in-building Auxiliary Radio Communication systems (ARCs) provided where required or installed voluntarily in accordance with Section [917] 916;

2.	Fire alarm systems;

3.	Automatic fire detection systems;

4.	Elevator car lighting; and

5.	Means of egress and exit sign illumination as required by Chapter 10.

[405.10] 405.9 Standpipe system. The underground building shall be [provided] equipped throughout with a standpipe system in accordance with Section 905.

SECTION BC 406
MOTOR-VEHICLE-RELATED OCCUPANCIES

406.1 [Private garages and carports.] General. Motor-vehicle-related occupancies shall comply with Sections 406.1 through 406.8.

406.2 Definitions. The following terms are defined in Chapter 2:

CARPORT.

MECHANICAL-ACCESS OPEN PARKING GARAGE.

OPEN PARKING GARAGE.

PRIVATE GARAGE.

RAMP-ACCESS OPEN PARKING GARAGE.

406.3 Private garages and carports. Private garages and carports shall comply with Sections 406.3.1 through 406.3.5.

[406.1.1] 406.3.1 Classification. Private garages and carports[, as defined by this section,] shall be classified as Group U occupancy.

[406.1.2 Definitions. The following words and terms shall, for the purposes of this chapter and as used elsewhere in this code, have the meanings shown herein.]

[CARPORT. A structure or portion of a structure, accessory to a Group R-2 or R-3 occupancy, open on at least two sides and unenclosed for at least 50 percent of perimeter, used for the parking or storage of passenger motor vehicles. Such facility shall not exceed 650 square feet (60.45 m2) in area and one story in height.]

[PRIVATE GARAGE. An enclosed structure or portion of a structure, accessory to a Group R-2 or R-3 occupancy, used for the parking or storage of passenger motor vehicles. Such facility shall not exceed 650 square feet (60 m2) in area and one story in height.]

406.3.2 Clear height. In private garages and carports, the clear height in vehicle and pedestrian traffic areas shall be not less than 7 feet (2134 mm). Vehicle and pedestrian areas accommodating van-accessible parking shall comply with Section 1106.5.

[406.1.3] 406.3.3 Floor construction. Private garage and carport floors shall be of concrete or equivalent noncombustible material that will not absorb flammable liquids. The area of floor used for parking of vehicles shall be sloped to facilitate the movement of liquids to a drain. The sills of all door openings connecting a dwelling unit to a private garage shall be raised at least 4 inches (102 mm) above the floor level of the garage.

Exception: Asphalt surfaces shall be permitted at ground level in carports.

[406.1.3.1] 406.3.3.1 Ramps. Ramps shall have a gradient not exceeding one in seven, with nonslip surfaces, and shall be located entirely within the property line. However, upon application to the commissioner, steeper gradients may be accepted, but in no event greater than one in three.

[406.1.4] 406.3.4 Separation. Separations shall comply with the following:

- The private garage shall be separated from the dwelling unit and its attic area by means of a minimum 1-hour fire-rated construction. Garages beneath habitable rooms shall be separated from all habitable rooms above by not less than 1-hour fire-rated construction. Openings from a private garage directly into a room used for sleeping purposes shall not be permitted.

- No air used for heating, cooling or ventilation shall be circulated through private garages to dwelling areas.

- A separation is not required between a Group R-3 occupancy and a carport, provided the carport does not have any enclosed areas above.

- For free standing private garages where the fire separation distance from the nearest exterior wall is less than 5 feet (1524 mm), such exterior walls shall have a fire-resistance rating not less than one hour.

[406.1.5] 406.3.5 Automatic garage door openers. Automatic garage door openers, [if] where provided, shall be listed in accordance with UL 325.

[406.2 Parking garages, open or enclosed] 406.4 Public parking garages.

[406.2.1 Classification.] Parking garages, other than private parking garages, shall be classified as public parking garages and shall comply with the provisions of Sections 406.4.2 through 406.4.10 and shall be classified as either an open parking garage [, as per Section 406.3,] or an enclosed [, as per Section 406.4] parking garage. Open parking garages shall also comply with Section 406.5. Enclosed parking garages shall also comply with Section 406.6. [Parking garages shall also comply with the special provisions of] See Section 510 for special provisions for parking garages.

[406.2.2] 406.4.1 Clear height. The clear height of each floor level in vehicle and pedestrian traffic areas shall be not [be] less than 7 feet (2134 mm). Vehicle and pedestrian areas accommodating van-accessible parking [required by Section 1106.5] shall [conform to ICC A117.1] comply with Section 1106.5.

[406.2.3] 406.4.2 Guards. Guards shall be provided in accordance with Section [1013] 1015. Guards serving as vehicle barrier systems shall comply with Sections [406.2.4] 406.4.3 and [1013] 1015.

[406.2.4] 406.4.3 Vehicle barrier systems. Vehicle [barrier systems] barriers not less than 2 feet 9 inches (835 mm) [high] in height shall be placed [at the end of drive lanes and at the end of parking spaces] where the vertical distance from the floor of a drive lane or parking space to the ground or surface directly below is greater than 1 foot (305 mm). Vehicle [barrier systems] barriers shall comply with the loading requirements of Section [1607.7.3] 1607.9.

Exception: Vehicle barriers are not required in vehicle storage compartments in a mechanical access parking garage.

[406.2.5] 406.4.4 Ramps. Ramps shall have a gradient not exceeding one in seven, with nonslip surfaces. A level landing having a minimum dimension of 20 feet (6096 mm) shall be provided at the discharge point of all ramps at the street level, within the property line. Ramps used for the movement of motor vehicles need not be enclosed when serving tiers above grade. Vehicle ramps may serve as part of a means of egress [provided that such ramp complies with the requirements of Sections 1018.1.1 and 1018.1.2] in accordance with Section 1006.4.

[406.2.6] 406.4.5 Floor surface. Parking surfaces shall be of concrete or similar noncombustible and nonabsorbent materials.

The area of floor used for parking of vehicles shall be sloped to facilitate the movement of liquids to a drain.

Exceptions:

- Asphalt parking surfaces [are] shall be permitted at ground level.

- Floors of Group S-2 parking garages shall not be required to have a sloped surface.

[406.2.7] 406.4.6 Separation. Parking garages shall be separated from other occupancies in accordance with Section [510] 508.1.

[406.2.8] 406.4.7 Special hazards. [Openings from a parking garage to] Connection of a parking garage with any room in which there is a fuel-fired appliance shall be by means of a vestibule providing a two-doorway separation. Such vestibule and doorway shall be minimum 1-hour rated construction.

Exception: A single door[, in compliance with Table 715.4,] shall be [permitted,] allowed provided the sources of ignition in the appliance are [at least] not less than 18 inches (457 mm) above the floor.

[406.2.9] 406.4.8 Attached to rooms. Openings from a parking garage directly into a room used for sleeping purposes shall not be permitted.

[406.2.10] 406.4.9 Fire-fighter aisles. In any parking garage or lot, one or more aisles, at least 24 inches (610 mm) in width, shall be provided to permit access by fire-fighting personnel to all parts of the garage or lot. There shall not be more than three rows of parked motor vehicles between aisles.

[406.2.11] 406.4.10 Electric vehicle charging stations. Parking garages shall be capable of supporting electrical vehicle charging stations in accordance with this section. Electrical raceway to the electrical supply panel serving the garage shall be capable of providing a minimum of 3.1 kW of electrical capacity to at least 20 percent of the parking spaces of the garage. The electrical room supplying the garage must have the physical space for an electrical supply panel sufficient to provide 3.1kW of electrical capacity to at least 20 percent of the parking spaces of the garage. Such raceway and all components and work appurtenant thereto shall be in accordance with the New York City Electrical Code.

Exceptions:

- The provisions of this section shall not apply to parking garages for buildings of Occupancy Group M (Mercantile).

- The commissioner may waive compliance with this section if the commissioner determines that the parking garage is a temporary facility that will be in service no longer than 3 years.

3.	The provisions of this section shall not apply to parking garages for buildings in which not less than fifty percent of the residential units are for households earning up to sixty percent of the area median income as determined by the United States Department of Housing and Urban Development.

[406.3] 406.5 Open parking garages. Open parking garages shall comply with Sections 406.5.1 through 406.5.11.

[406.3.1 Scope. Except where specific provisions are made in Sections 406.3.2 through 406.3.13, other requirements of this code shall apply.]

[406.3.2 Definitions. The following words and terms shall, for the purposes of this chapter and as used elsewhere in this code, have the meanings shown herein.]

[MECHANICAL-ACCESS OPEN PARKING GARAGES. Open parking garages employing parking machines, lifts, elevators or other mechanical devices for vehicles moving from and to street level and in which public occupancy is prohibited above the street level.]

[OPEN PARKING GARAGE. A structure or portion of a structure with the openings as described in Section 406.3.3.1 that is used for the parking or storage of private motor vehicles as described in Section 406.3.4.]

[RAMP-ACCESS OPEN PARKING GARAGES. Open parking garages employing a series of continuously rising floors or a series of interconnecting ramps between floors permitting the movement of vehicles under their own power from and to the street level.]

[406.3.3] 406.5.1 Construction. Open parking garages shall be of Type I, II or IV construction. Open parking garages shall meet the design requirements of Chapter 16. For vehicle [barrier systems] barriers, see Section [406.2.4] 406.4.3.

[406.3.3.1] 406.5.2 Openings. For natural ventilation purposes, the exterior side of the structure shall have uniformly distributed openings on two or more sides. The area of such openings in exterior walls on a tier [must] shall be [at least] not less than 20 percent of the total perimeter wall area of each tier. The aggregate length of the openings considered to be providing natural ventilation shall [constitute a minimum of] be not less than 40 percent of the perimeter of the tier. Interior walls shall be [at least] not less than 20 percent open with uniformly distributed openings.

Exception: Openings are not required to be distributed over 40 percent of the building perimeter where the required openings are uniformly distributed over two opposing sides of the building.

406.5.2.1 Openings below grade. Where openings below grade provide required natural ventilation, the outside horizontal clear space shall be one and one-half times the depth of the opening. The width of the horizontal clear space shall be maintained from grade down to the bottom of the lowest required opening.

[406.3.4] 406.5.3 Uses. Mixed uses shall be allowed in the same building as an open parking garage subject to the provisions of Sections [402.7.1] 402.4.2.3, [406.3.13] 406.5.11, 508.1, 510.3, 510.4[,] and 510.7.

[406.3.5] 406.5.4 Area and height. Area and height of open parking garages shall be limited as set forth in Chapter 5 for Group S-2 occupancies.

TABLE [406.3.5] 406.5.4
OPEN PARKING GARAGES AREA AND HEIGHT

| TYPE OF CONSTRUCTION | AREA PER TIER (square feet) | HEIGHT (in tiers) |
| --- | --- | --- |
|  |  | Ramp access | Mechanical access |
|  |  |  | Automatic sprinkler system |
|  |  |  | No | Yes |
| IA | Unlimited | Unlimited | Unlimited | Unlimited |
| IB | Unlimited | 12 tiers | 12 tiers | 18 tiers |
| IIA | 50,000 | 10 tiers | 10 tiers | 15 tiers |
| IIB | 50,000 | 8 tiers | 8 tiers | 12 tiers |
| IV | 50,000 | 4 tiers | 4 tiers | 4 tiers |

For SI: 1 square foot = 0.0929 m2.

[406.3.5.1] 406.5.4.1 Single use. [When] Where the open parking garage is used exclusively for the parking or storage of private motor vehicles, with no other uses in the building, the area and height shall be permitted to comply with Table [406.3.5] 406.5.4.

Exception: The grade-level tier is permitted to contain an office, waiting and toilet rooms having a total combined area of not more than 1,000 square feet (93 m2). Such area need not be separated from the open parking garage.

In open parking garages having a spiral or sloping floor, the horizontal projection of the structure at any cross section shall not exceed the allowable area per parking tier. In the case of an open parking garage having a continuous spiral floor, each 9 feet 6 inches (2896 mm) of height, or portion thereof, shall be considered a tier.

The clear height of a parking tier shall be not [be] less than 7 feet (2134 mm), except that a lower clear height is permitted in mechanical-access open parking garages where approved by the commissioner.

[406.3.6] 406.5.5 Area and height increases. The allowable area and height of open parking garages shall be increased in accordance with the provisions of this section. Garages with sides open on three-fourths of the building’s perimeter are permitted to be increased by 25 percent in area and one tier in height. Garages with sides open around the entire building’s perimeter are permitted to be increased by 50 percent in area and one tier in height. For a side to be considered open under the above provisions, the total area of openings along the side shall not be less than 50 percent of the interior area of the side at each tier and such openings shall be equally distributed along the length of the tier. For purposes of calculating the interior area of the side, the height shall not exceed 7 feet (2134 mm).

Allowable tier areas in Table [406.3.5] 406.5.4 shall be increased for open parking garages constructed to heights less than the table maximum. The gross tier area of the garage shall not exceed that permitted for the higher structure. [At least] No fewer than three sides of each such larger tier shall have continuous horizontal openings not less than 30 inches (762 mm) in clear height extending for [at least] not less than 80 percent of the length of the sides and no part of such larger tier shall be more than 200 feet (60 960 mm) horizontally from such an opening. In addition, each such opening shall face a street or yard accessible to a street with a width of [at least] not less than 30 feet (9144 mm) for the full length of the opening, and standpipes shall be provided in each such tier.

Open parking garages of Type II construction, with all sides open, shall be unlimited in allowable area where the building height does not exceed 75 feet (22 860 mm). For a side to be considered open, the total area of openings along the side shall be not [be] less than 50 percent of the interior area of the side at each tier and such openings shall be equally distributed along the length of the tier. For purposes of calculating the interior area of the side, the height shall not exceed 7 feet (2134 mm). All portions of tiers shall be within 200 feet (60 960 mm) horizontally from such openings or other natural ventilation openings as defined in Section [406.3.3.1] 406.5.2. These openings shall be permitted to be provided in courts with a minimum dimension of 20 feet (6096 mm) for the full width of the openings.

[406.3.7] 406.5.6 Fire separation distance. Exterior walls and openings in exterior walls shall comply with Tables 601 and 602. The distance from an adjacent property line shall be determined in accordance with Table 602 and Section 705.

[406.3.8] 406.5.7 Means of egress. Open parking garages shall meet the means of egress requirements of Chapter 10. However, where no persons other than parking attendants are permitted, required exit stairways shall not be less than 36 inches (914 mm) wide.

[406.3.9] 406.5.8 Standpipes. Standpipes shall be installed where required by the provisions of Section 905.

[406.3.10 Sprinkler systems. Automatic sprinkler systems and standpipes shall be installed in accordance with the provisions of Section 903. An automatic dry sprinkler system may be installed in unheated garages.]

[406.3.11] 406.5.9 Enclosure of vertical openings. Enclosure shall not be required for vertical openings.

[406.3.12] 406.5.10 Ventilation. Openings specified in Section [406.3.3.1] 406.5.2 shall satisfy natural ventilation requirements. Additional mechanical ventilation shall not be required.

[406.3.13] 406.5.11 Prohibitions. The following uses and alterations are not permitted:

1.	Vehicle repair work.

2.	Parking of commercial vehicles, buses, trucks and similar vehicles.

3.	Partial or complete closing of required openings in exterior walls by tarpaulins or any other means.

4.	Dispensing of fuel.

[406.4] 406.6 Enclosed parking garages. Parking garages and portions thereof that do not meet the definition of “Open parking garages” shall be classified as an enclosed parking garage and shall meet the requirements of this section.

[406.4.1] 406.6.1 Heights and areas. Enclosed parking garages shall be limited to the allowable heights and areas specified in [Table 503 as modified by Sections 504, 506, and 507] Chapter 5. Permitted roof parking shall not be considered as a separate story.

[406.4.2] 406.6.2 Ventilation. A mechanical ventilation system shall be provided in accordance with the New York City Mechanical Code.

406.6.3 Automatic sprinkler system. Automatic sprinkler systems and standpipes shall be installed in accordance with the provisions of Section 903. An automatic dry sprinkler system may be installed in unheated garages.

406.6.4 Means of egress. Enclosed parking garages shall meet the means of egress requirements of Chapter 10.

[406.5] 406.7 Motor fuel-dispensing facilities.

[406.5.1 Construction.] Motor fuel-dispensing facilities shall be designed and constructed in accordance with the New York City Fire Code and Sections [406.5.1] 406.7.1 through [406.5.3] 406.7.3 of this code.

[406.5.2] 406.7.1 Vehicle fueling pad. The vehicle shall be fueled on noncoated concrete or other approved paving material having a resistance not exceeding 1 megohm as determined by the methodology in [EN] CEN 1081.

[406.5.3] 406.7.2 Canopies. Canopies under which fuels are dispensed shall have a clear, unobstructed height of not less than 14 feet (4267 mm) to the lowest projecting element in the vehicle drive-through area. Canopies and their supports over pumps shall be of noncombustible materials. However, panels constructed of light-transmitting plastic materials shall be permitted to be installed in canopies erected over motor vehicle fuel-dispensing station fuel dispensers, provided the panels are located [at least] not less than 10 feet (3048 mm) from any building on the same property and face yards or streets not less than 40 feet (12 192 mm) in width on the other sides. The aggregate areas of plastics shall be not [exceed] greater than 1,000 square feet (93 m2). The maximum area of any individual panel shall be not [exceed] greater than 100 square feet (9.3 m2).

[406.5.3.1] 406.7.2.1 Canopies used to support gaseous hydrogen systems. Where flammable compressed gases are permitted by the New York City Fire Code to be located on the roof of a canopy that is used to shelter dispensing operations, such canopy shall be in accordance with the following:

1.	The canopy shall meet or exceed Type I construction requirements.

2.	Operations located under canopies shall be limited to refueling only.

3.	The canopy shall be constructed in a manner that prevents the accumulation of hydrogen gas.

[406.5.4] 406.7.3 Storage tanks. Motor fuel storage tanks shall be installed below ground, except as authorized by the rules of the Fire Department. The installation and venting of storage tanks shall be in accordance with the rules of the Fire Department and the requirements of the New York City Fire Code. Storage tanks installed below ground shall comply with the following:

- The top of the storage tanks shall be at least 24 inches (610 mm) below finished grade and at least 24 inches (610 mm) below the level of any cellar or basement floor within 10 feet (3048 mm) of the tanks.

- Storage tanks shall be located so that the forces from any building foundation and support loads are not transmitted to the tanks. The distance from any part of a storage tank to the nearest wall of any basement, pit or cellar, or from any property line that may be built upon, shall not be less than 36 inches (914 mm).

- Storage tanks shall be covered with a structurally supported reinforced concrete slab at least 8 inches (203 mm) thick, extending at least 12 inches (305 mm) beyond the horizontal outlines of the storage tanks, and placed over a cover of suitable clean backfill material. Such slab shall be designed and reinforced in accordance with ACI 318. All concrete shall have a minimum compressive strength of 4,000 pounds per square inch (27 580 kPa) at 28 days.

4.	Storage tanks shall be placed on a 12-inch (305 mm) thick concrete base slab or installed in such other manner, secured against flotation, and approved by the department.

[406.6] 406.8 Repair garages.

[406.6.1 General.] Repair garages shall be constructed in accordance with the New York City Fire Code and Sections [406.6.1] 406.8.1 through [406.6.6] 406.8.6 of this code. This occupancy shall not include motor fuel-dispensing facilities, as regulated in Section [406.5] 406.7.

[406.6.2] 406.8.1 Mixed uses. Mixed uses shall be allowed in the same building as a repair garage subject to the provisions of Section 508.1.

[406.6.3] 406.8.2 Ventilation. Repair garages shall be mechanically ventilated in accordance with the New York City Mechanical Code. The ventilation system shall be controlled at the entrance to the garage.

[406.6.4] 406.8.3 Floor surface. Repair garage floors shall be of concrete or similar noncombustible and nonabsorbent materials.

Exception: Slip-resistant, nonabsorbent, interior floor finishes having a critical radiant flux not more than 0.45 W/cm2, as determined by NFPA 253, shall be permitted.

[406.6.5] 406.8.4 Heating equipment. Heating equipment shall be installed in accordance with the New York City Mechanical Code.

[406.6.6] 406.8.5 Gas detection system. Repair garages used for the repair of vehicles fueled by CNG, LNG, or hydrogen, shall be provided with an approved flammable gas-detection system.

[406.6.6.1] 406.8.5.1 System design. The flammable gas-detection system shall be listed or approved and shall be calibrated to the types of fuels or gases used by vehicles to be repaired. The gas detection system shall be designed to activate when the level of flammable gas exceeds 25 percent of the lower [explosive] flammable limit (LFL). Gas detection shall [also] be provided in lubrication or chassis [repair] service pits of repair garages used for repairing nonodorized LNG-fueled vehicles.

406.8.5.1.1 Gas detection system components. Gas detection system control units shall be listed and labeled in accordance with UL 864 or UL 2017. Gas detectors shall be listed and labeled in accordance with UL 2075 for use with the gases and vapors being detected.

[406.6.6.2] 406.8.5.2 Operation. Activation of the gas detection system shall result in all of the following:

1.	Initiation of distinct audible and visual alarm signals in the repair garage.

2.	Deactivation of all heating systems located in the repair garage.

3.	Activation of the mechanical ventilation and exhaust system, where the system is interlocked with gas detection.

[406.6.6.3] 406.8.5.3 Failure of the gas detection system. Failure of the gas detection system shall result in the deactivation of the heating system, activation of the mechanical ventilation system [when] where the system is [inter-locked] interlocked with the gas detection system and cause a trouble signal to sound in an approved location.

406.8.6 Automatic sprinkler system. A repair garage shall be equipped with an automatic sprinkler system in accordance with Section 903.2.4.2.

[406.7] 406.9 Open parking lots.

[406.7.1 General.] The provisions of this section shall govern the construction of open parking lots and to all such existing premises hereafter enlarged or changed in location.

[406.7.2] 406.9.1 Definitions. The following [words and terms shall, for the purposes of this chapter and as used elsewhere in this code, have the meanings shown herein.] term is defined in Chapter 2:

OPEN PARKING LOT. [An exterior space with surfacing at grade used for the storage or sale of more than four motor vehicles, including but not limited to parking lots, motor vehicles sales lots, and accessory open parking spaces.]

[406.7.3] 406.9.2 Permit required. Any premise intended to be occupied for the storage or sale of motor vehicles on an open parking lot shall require an application to be filed with the department in order to obtain a Certificate of Occupancy. Such Certificate of Occupancy shall indicate the maximum number of vehicles to be accommodated and the type of vehicle, whether private passenger or commercial, to be stored. An application for or including an open parking lot shall be accompanied by a plan exhibiting the following:

- Dimensions of the lot and its location in relation to adjoining streets; [and]

- Any structure(s) existing or to be erected on the plot; [and]

- The relative elevations of the parking area, curbs and adjoining yards or courts; [and]

- Structures, retaining walls, and open spaces on adjoining premises; [and]

- Retaining walls to be built; [and]

- Location and dimensions of curb cuts, driveways, and enclosures; [and]

- Drainage diagram; [and]

- Specification of surfacing material; [and]

- Parking stall layout with dimensions; [and]

- Analysis exhibiting compliance with the New York City Zoning Resolution; and

- Other information as may be requested by the commissioner.

A copy of the plan or diagram approved by the department shall be kept on the premises. Certified, reduced size, legible copies may be used for this purpose. When an attendant’s shelter is provided on the parking lot, the Certificate of Occupancy issued shall be posted and maintained under glass in the shelter.

[406.7.4] 406.9.3 Locations prohibited. All vehicular activities associated with the operation of open parking lots shall be entirely within the property lines of the premises. Vehicles shall not be permitted to encroach upon the sidewalks. No motor vehicle may be stored or parked in any location where it would obstruct a required window or required exit of any adjacent building.

[406.7.5] 406.9.4 Surfacing. All driveways, parking stalls, and open spaces used for the parking or storage of motor vehicles shall be surfaced with concrete asphalt, or equivalent durable, dustless material.

[406.7.5.1] 406.9.4.1 Drainage. Open parking lots shall be graded and maintained such that no drainage will flow onto abutting sidewalks and adjoining properties.

[406.7.5.2] 406.9.4.2 Nonporous surfaces. Where the surface paving of an open parking lot is nonporous, such lot shall be drained as required by the New York City Plumbing Code.

[406.7.5.3] 406.9.4.3 Resurfacing. Resurfacing of existing open parking lots shall comply with this section.

[406.7.6 Curb cuts. For the purpose of this section, a curb cut shall include all splays when determining the total length of cut curb. Unless otherwise required by the New York City Zoning Resolution, all curb cuts shall comply with the following requirements:]

[1.	The aggregate length of curb cuts shall not exceed 60 percent of any street frontage 100 feet (30 480 mm) or less in length. No single curb cut shall exceed 30 feet (9144 mm) in length, and there shall not be more than two curb cuts on any street frontage 100 feet (30 480 mm) or less in length. The minimum distance between two curb cuts shall be 5 feet (1524 mm).]

[2.	For each 50 feet (15 240 mm) of street frontage length over 100 feet (30 480 mm), an additional curb cut no greater than 30 feet (9144 mm) in length may be permitted.]

[3.	No curb cut shall commence within 8 feet (2438 mm) of a side lot line, except that on corner lots and lots with street frontage length of 50 feet (15 240 mm) or less, the curb cut may commence 30 inches (762 mm) from the side lot line.]

[4.	No curb cut, including splays, shall be less than 10 feet (3048 mm) in length.]

[406.7.7 Driveways. Driveways serving passenger vehicles shall be a minimum of 8 feet (2438 mm) in width and shall not exceed the length of the curb cut, not including the lengths of the splays. For all other motor vehicles, the minimum width of driveways shall be 10 feet (3048 mm). Portions of the driveway located between the curb line and the lot line shall be paved in accordance with the requirements of the Department of Transportation for the construction of sidewalks.]

[406.7.8] 406.9.5 Curbs and bumpers. Open parking lots shall be completely separated from adjoining premises and public sidewalks by curbs or bumpers of concrete, masonry, steel, heavy timber, or other similar and equally substantial materials, and shall be securely anchored so as to stop motor vehicles. Curbs and bumpers shall be at least 8 inches (203 mm) high and 8 inches (203 mm) wide.

[406.7.8.1] 406.9.5.1 Openings. Openings in required perimeter curbs and bumpers shall be permitted only for drainage, for motor vehicle entrances and exits, and for pedestrian entrances and exits. The width of an opening for motor vehicle access shall not exceed the length of the curb cut, not including the lengths of the splays. When an opening for pedestrian access is adjacent to a motor vehicle access opening, the two openings shall be separated by a permanent and substantial post. In no case shall any pedestrian entrance or exit exceed 5 feet (1524 mm) in width.

[406.7.9] 406.9.6 Accessory uses and occupancies. Parking lot offices, attendant shelters, storage facilities, and similar structures used in conjunction with open parking lots may be provided as an accessory use and shall comply with the applicable code provisions. Such accessory structures may be constructed of combustible materials subject to the limitations of Section D105.1 of Appendix D.

[406.7.9.1] 406.9.6.1 Motor fuel-dispensing facilities. Motor fuel-dispensing facilities, accessory to open parking lots, shall comply with the requirements of the New York City Fire Code and Section [406.5] 406.8 of this code. Motor fuel pumps shall be located at least 30 feet (9144 mm) from any parking space or interior lot line.

[406.7.10] 406.9.7 Special provisions applicable to large open parking lots. Open parking lots storing 10 or more motor vehicles shall also be subject to the special provisions of this section.

[406.7.10.1] 406.9.7.1 Curbs and bumpers. Bumpers shall be situated not less than 1 foot (305 mm) from the perimeter edge of the open parking lot where vehicles are parked parallel to such perimeter edge, and not less than 4 feet (1219 mm) from the perimeter edge where vehicles are parked perpendicular to such perimeter edge. Openings shall be limited as provided for in Section [406.7.8.1] 406.9.5.1.

Exception: A steel guardrail or other substantial barrier designed in accordance with the provisions of Section [1607.7.3]  1607.9, that will prevent any part of a vehicle from extending across a property line, may be accepted in lieu of bumpers.

[406.7.10.2] 406.9.7.2 Screen enclosures. Open parking lots shall provide a perimeter screen enclosure as per this section unless otherwise required by the New York City Zoning Resolution. Such screen enclosure may be constructed as a masonry wall, woven wire fence, iron picket fence, or uniformly painted fence of fire-resistant material at least 4 feet (1219 mm) high, but not more than 8 feet (2438 mm) above finished grade, subject to the limitations of Section 3111. Such enclosures shall completely separate the lot from adjoining premises and public sidewalks. Openings shall be limited as provided for in Section [406.7.8.1] 406.9.5.1.

Exception: Screening shall not be required for any portion of the lot adjacent to an existing wall located at the lot line.

[406.7.10.3] 406.9.7.3 Illumination. Open parking lots operating between 6 p.m. and 6 a.m. shall be adequately illuminated to a minimum of 1 foot-candle (10.8 lux) measured at grade level, distributed over the entire area. Illumination provided with reflectors or floodlights shall be arranged such that the illumination is directed downward and away from adjacent premises.

[406.7.10.4] 406.9.7.4 Fire-fighter aisles. In any open parking lot, one or more aisles, at least 24 inches (610 mm) in width, shall be provided to permit access by [fire fighting] fire-fighting personnel to all parts of the garage or lot. There shall not be more than three rows of parked motor vehicles between aisles.

[406.7.11] 406.9.8 Electric vehicle charging stations. Open parking lots shall be capable of supporting electric vehicle charging stations in accordance with this section. A minimum of 20 percent of the parking spaces in an open parking lot shall be equipped with electrical raceway capable of providing a minimum supply of 11.5 kVA to an [EVSE] electrical vehicle supply equipment (EVSE) from an electrical supply panel. The raceway shall be no smaller than 1 inch (25 mm). The electrical supply panel serving such parking spaces must have at least 3.1 kW of available capacity for each stall connected to it with raceway. Such raceway and all components and work appurtenant thereto shall be in accordance with the New York City Electrical Code.

Exceptions:

- The provisions of this section shall not apply to open parking lots for buildings of [occupancy group] Occupancy Group M (Mercantile).

- The commissioner may waive compliance with this section if the commissioner determines that the open parking lot is a temporary facility that will be in service no longer than 3 years.

- The provisions of this section shall not apply to open parking lots for buildings in which not less than fifty percent of the residential units are for households earning up to sixty percent of the area median income as determined by the United States Department of Housing and Urban Development.

406.10 Curb cuts and driveways. Except where specifically provided for in the New York City Zoning Resolution, all curb cuts and driveways shall be constructed in accordance with Sections 406.10.1 and 406.10.2.  All sidewalks and driveways or portions thereof that are structurally supported shall be designed for loads prescribed in Chapter 16.

406.10.1 Curb cuts. For the purpose of this section, a curb cut shall include all splays when determining the total length of cut curb. All curb cuts shall comply with the following requirements:

1.	The aggregate length of curb cuts shall not exceed 60 percent of any street frontage 100 feet (30 480 mm) or less in length. No single curb cut shall exceed 30 feet (9144 mm) in length, and there shall not be more than two curb cuts on any street frontage 100 feet (30 480 mm) or less in length. The minimum distance between two curb cuts shall be 5 feet (1524 mm).

2.	For each 50 feet (15 240 mm) of street frontage length over 100 feet (30 480 mm), an additional curb cut no greater than 30 feet (9144 mm) in length may be permitted.

3.	No curb cut shall commence within 8 feet (2438 mm) of a side lot line.

Exceptions:

1.	For open parking lots on corner lots and on lots with street frontage length of 50 feet (15 240 mm) or less, the curb cut may commence no less than 30 inches (762 mm) from the side lot line.

2.	In open or enclosed parking garages where a level landing having a minimum dimension of 20 feet (6096 mm) is provided at the discharge point of all ramps at the street level within the property line, the curb cut may commence no less than 30 inches (762 mm) from a side lot line.

4.	No curb cut, including splays, shall be less than 10 feet (3048 mm) in length.

406.10.2 Driveways. Driveways serving passenger vehicles shall be a minimum of 8 feet (2438 mm) in width and shall not exceed the length of the curb cut, not including the lengths of the splays. For all other motor vehicles, the minimum width of driveways shall be 10 feet (3048 mm). Portions of the driveway located between the curb line and the lot line shall be paved in accordance with the requirements of the Department of Transportation for the construction of sidewalks.

SECTION BC 407
GROUP I-2

407.1 General. Occupancies in Group I-2 shall comply with the provisions of Sections 407.1 through [407.9] 407.10 and other applicable provisions of this code.

407.2 Corridors continuity and separation. Corridors in occupancies in Group I-2 shall be continuous to the exits and shall be separated from other areas in accordance with Section 407.3 except spaces conforming to Sections 407.2.1 through [407.2.4] 407.2.6.

407.2.1 Waiting and similar areas. Waiting areas and similar spaces constructed as required for corridors shall be permitted to be open to a corridor, only where all of the following criteria are met:

1.	The spaces are not occupied [for patient] as care recipient’s sleeping [units] rooms, treatment rooms, [hazardous or] incidental [accessory occupancies] uses in accordance with Section [508.2] 509, or hazardous uses.

2.	The open space is protected by an automatic fire detection system installed in accordance with Section 907.

3.	The corridors onto which the spaces open, in the same smoke compartment, are protected by an automatic fire detection system installed in accordance with Section 907, or the smoke compartment in which the spaces are located is equipped throughout with quick-response sprinklers in accordance with Section 903.3.2.

4.	The space is arranged so as not to obstruct access to the required exits.

407.2.2 [Nurses’] Care providers’ stations. Spaces for care providers’, supervisory staff, doctors’ and nurses’ charting, communications and related clerical areas shall be permitted to be open to the corridor, [when] where such spaces are constructed as required for corridors.

407.2.3 [Mental health] Psychiatric treatment areas. Areas wherein [mental health patients] psychiatric care recipients who are not capable of self-preservation are housed, or group meeting or multipurpose therapeutic spaces other than incidental [accessory occupancies] uses in accordance with Section 509, under continuous supervision by facility staff, shall be permitted to be open to the corridor, where the following criteria are met:

1.	Each area does not exceed 1,500 square feet (140 m2).

2.	The area is located to permit supervision by the facility staff.

3.	The area is arranged so as not to obstruct any access to the required exits.

4.	The area is equipped with an automatic fire detection system installed in accordance with Section 907.2.

5.	Not more than one such space is permitted in any one smoke compartment.

6.	The walls and ceilings of the space are constructed as required for corridors.

407.2.4 Gift shops. Gift shops and associated storage that are less than 500 square feet (46 m2) in area shall be permitted to be open to the corridor [provided the gift shop and storage areas are fully sprinklered and storage areas are protected in accordance with Section 508.2.] where such spaces are constructed as required for corridors.

407.2.5 Nursing home housing units. In Group I-2 occupancies, in areas where nursing home residents are housed, shared living spaces, group meeting or multipurpose therapeutic spaces shall be permitted to be open to the corridor, where all of the following criteria are met:

1.	The walls and ceilings of the space are constructed as required for corridors.

2.	The spaces are not occupied as resident sleeping rooms, treatment rooms, incidental uses in accordance with Section 509, or hazardous uses.

3.	The open space is protected by an automatic fire detection system installed in accordance with Section 907.

4.	The corridors onto which the spaces open, in the same smoke compartment, are protected by an automatic fire detection system installed in accordance with Section 907, or the smoke compartment in which the spaces are located is equipped throughout with quick-response sprinklers in accordance with Section 903.3.2.

5.	The space is arranged so as not to obstruct access to the required exits.

407.2.6 Nursing home cooking facilities. In Group I-2 occupancies, rooms or spaces that contain a cooking facility with domestic cooking appliances shall be permitted to be open to the corridor where all of the following criteria are met:

1.	The number of care recipients housed in the smoke compartment is not greater than 30.

2.	The number of care recipients served by the cooking facility is not greater than 30.

3.	Only one cooking facility area is permitted in a smoke compartment.

4.	The types of domestic cooking appliances permitted are limited to ovens, cooktops, ranges, warmers and microwaves.

5.	The corridor is a clearly identified space delineated by construction or floor pattern, material or color.

6.	The space containing the domestic cooking facility shall be arranged so as not to obstruct access to the required exit.

7.	A domestic cooking hood installed and constructed in accordance with Section 505 of the New York City Mechanical Code is provided over the cooktop or range.

8.	The domestic cooking hood provided over the cooktop or range shall be equipped with an automatic fire-extinguishing system of a type recognized for protection of domestic cooking equipment. Preengineered automatic extinguishing systems shall be tested in accordance with UL 300A and listed and labeled for the intended application. The system shall be installed in accordance with this code, its listing and the manufacturer’s instructions.

9.	A manual actuation device for the hood suppression system shall be installed in accordance with Sections 904.12.1 and 904.12.2.

10.	An interlock device shall be provided such that upon activation of the hood suppression system, the power or fuel supply to the cooktop or range will be turned off.

11.	A shut-off for the fuel and electrical power supply to the cooking equipment shall be provided in a location that is accessible only to staff.

12.	A timer shall be provided that automatically deactivates the cooking appliances within a period of not more than 120 minutes.

13.	A portable fire extinguisher shall be installed in accordance with Section 906 of the New York City Fire Code.

407.3 Corridor [walls] wall construction. Corridor walls shall be constructed as smoke partitions in accordance with Section [711] 710.

407.3.1 Corridor doors. Corridor doors, other than those in a wall required to be rated by Section 509.4 or for the enclosure of a vertical opening or an exit, shall not have a required fire protection rating and shall not be required to be equipped with self-closing or automatic-closing devices, but shall provide an effective barrier to limit the transfer of smoke and shall be equipped with positive latching. Roller latches are not permitted. Other doors shall conform to Section [715.4] 716.5.

407.4 Means of egress. Group I-2 occupancies shall be provided with means of egress complying with Chapter 10 and Sections 407.4.1 through 407.4.4. The fire and emergency preparedness plans provided in accordance with Section 1001.4 shall identify the building components necessary to support a defend-in-place emergency response in accordance with the New York City Fire Code.

407.4.1 Direct access to a corridor. Habitable rooms in Group I-2 occupancies shall have an exit access door leading directly to a corridor.

Exceptions:

1.	Rooms with exit doors opening directly to the outside at ground level.

2.	Rooms arranged as care suites complying with Section 407.4.4.

[407.3.2] 407.4.1.1 Locking devices. Locking devices that restrict access to [the patient] a care recipient’s room from the corridor[,] and that are operable only by staff from the corridor side[,] shall not restrict the means of egress from the [patient] care recipient’s room [except for patient rooms in mental health facilities].

Exceptions:

1.	This section shall not apply to rooms in psychiatric treatment and similar care areas.

2.	Locking arrangements in accordance with Section 1010.1.9.6.

407.4.2 Distance of travel. The distance of travel between any point in a Group I-2 occupancy sleeping room, not located in a care suite, and an exit access door in that room shall be not greater than 50 feet (15 240 mm).

407.4.3 Projections in nursing home corridors. In nursing homes of Group I-2 occupancies, where the corridor width is a minimum of 96 inches (2440 mm), projections shall be permitted for furniture where all of the following criteria are met:

1.	The furniture is attached to the floor or to the wall.

2.	The furniture does not reduce the clear width of the corridor to less than 72 inches (1830 mm) except where other encroachments are permitted in accordance with Section 1005.7.

3.	The furniture is positioned on only one side of the corridor.

4.	Each arrangement of furniture is 50 square feet (4.6 m2) maximum in area.

5.	Furniture arrangements are separated by 10 feet (3048 mm) minimum.

6.	Placement of furniture is considered as part of the fire and emergency preparedness plans in accordance with Section 1001.4.

407.4.4 Group I-2 care suites. Care suites in Group I-2 shall comply with Sections 407.4.4.1 through 407.4.4.4 and either Section 407.4.4.5 or 407.4.4.6.

407.4.4.1 Exit access through care suites. Exit access from all other portions of a building not classified as a care suite shall not pass through a care suite. In a care suite required to have more than one exit, one exit access is permitted to pass through an adjacent care suite provided all of the other requirements of Sections 407.4 and 1016.2 are satisfied.

407.4.4.2 Separation. Care suites shall be separated from other portions of the building, including other care suites, by a smoke partition complying with Section 710.

407.4.4.3 Access to corridor. Movement from habitable rooms shall not require passage through more than three doors and 100 feet (30 480 mm) distance of travel within the suite.

Exception: The distance of travel shall be permitted to be increased to 125 feet (38 100 mm) where an automatic smoke detection system is provided throughout the care suite and installed in accordance with NFPA 72 as modified by Appendix Q.

407.4.4.4 Doors within care suites. Doors in care suites serving habitable rooms shall be permitted to comply with one of the following:

1.	Manually operated horizontal sliding doors permitted in accordance with Exception 9 to Section 1010.1.2.1.

2.	Power-operated doors permitted in accordance with Exception 7 to Section 1010.1.2.1.

3.	Means of egress doors complying with Section 1010.

407.4.4.5 Care suites containing sleeping room areas. Sleeping rooms shall be permitted to be grouped into care suites where one of the following criteria is met:

1.	The care suite is not used as an exit access for more than eight care recipient beds.

2.	The arrangement of the care suite allows for direct and constant visual supervision into the sleeping rooms by care providers.

3.	An automatic smoke detection system is provided in the sleeping rooms and installed in accordance with NFPA 72 as modified by Appendix Q.

407.4.4.5.1 Area. Care suites containing sleeping rooms shall be not greater than 7,500 square feet (696 m2) in area.

Exception: Care suites containing sleeping rooms shall be permitted to be not greater than 10,000 square feet (929 m2) in area where an automatic smoke detection system is provided throughout the care suite and installed in accordance with NFPA 72 as modified by Appendix Q.

407.4.4.5.2 Exit access. Any sleeping room, or any care suite that contains sleeping rooms, of more than 1,000 square feet (93 m2) shall have no fewer than two exit access doors from the care suite located in accordance with Section 1007.

407.4.4.6 Care suites not containing sleeping rooms. Areas not containing sleeping rooms, but only treatment areas and the associated rooms, spaces or circulation space, shall be permitted to be grouped into care suites and shall conform to the limitations in Sections 407.4.4.6.1 and 407.4.4.6.2.

407.4.4.6.1 Area. Care suites of rooms, other than sleeping rooms, shall have an area not greater than 12,500 square feet (1161 m2).

Exception: Care suites not containing sleeping rooms shall be permitted to be not greater than 15,000 square feet (1394 m2) in area where an automatic smoke detection system is provided throughout the care suite in accordance with Section 907.

407.4.4.6.2 Exit access. Care suites, other than sleeping rooms, with an area of more than 2,500 square feet (232 m2) shall have no fewer than two exit access doors from the care suite located in accordance with Section 1007.1.

[407.4] 407.5 Smoke barriers. Smoke barriers shall be provided to subdivide every story used by [patients for sleeping or] persons receiving care, treatment or sleeping and to divide other stories with an occupant load of 50 or more persons, into [at least] no fewer than two smoke compartments. Such stories shall be divided into smoke compartments with an area of not more than 22,500 square feet [(2090 m2)] (2092 m2) in nursing homes in Group I-2, and not more than 40,000 square feet (3716 m2) in detoxification facilities, hospitals and psychiatric centers in Group I-2, and the [travel] distance of travel from any point in a smoke compartment to a smoke barrier door shall be not [exceed] greater than 200 feet (60 960 mm). The smoke barrier shall be in accordance with Section [710] 709.

[407.4.1] 407.5.1 Refuge area. [At least 30 net square feet (2.8 m2) per patient shall be provided within the aggregate area of corridors, patient rooms, treatment rooms, lounge or dining areas and other low-hazard areas on each side of each smoke barrier. On floors not housing patients confined to a bed or litter, at least 6 net square feet (0.56 m2) per occupant shall be provided on each side of each smoke barrier for the total number of occupants in adjoining smoke compartments.] Refuge areas shall be provided within each smoke compartment. The size of the refuge area shall accommodate the occupants and care recipients from the adjoining smoke compartment. Where a smoke compartment is adjoined by two or more smoke compartments, the minimum area of the refuge area shall accommodate the largest occupant load of the adjoining compartments. The size of the refuge area shall provide the following:

1.	Not less than 30 net square feet (2.8 m2) for each care recipient confined to bed or stretcher.

2.	Not less than 6 square feet (0.56 m2) for each ambulatory care recipient not confined to bed or stretcher and for other occupants.

Areas or spaces permitted to be included in the calculation of refuge area are corridors, sleeping areas, treatment rooms, lounge or dining areas and other low-hazard areas.

[407.4.2] 407.5.2 Independent egress. A means of egress shall be provided from each smoke compartment created by smoke barriers without having to return through the smoke compartment from which means of egress originated.

[407.4.3] 407.5.3 Horizontal assemblies. Horizontal assemblies supporting smoke barriers required by this section shall be designed to resist the movement of smoke [and shall comply with Section 712.9]. Elevator lobbies shall be in accordance with Section 3006.1.

[407.5] 407.6 Automatic sprinkler system. Smoke compartments containing [patient] sleeping [units] rooms shall be equipped throughout with an automatic fire sprinkler system in accordance with [Section] Sections 903.3.1.1 and 903.3.2. [The smoke compartments shall be equipped with approved quick-response or residential sprinklers in accordance with Section 903.3.2.]

407.7 Fire alarm system. A fire alarm system shall be provided in accordance with Section 907.2.6.

[407.7] 407.8 Automatic fire detection. Corridors in nursing homes (both intermediate-care and skilled nursing facilities)[, detoxification facilities] and spaces permitted to be open to the corridors by Section 407.2 shall be equipped with an automatic fire detection system installed in accordance with Section 907. [Hospitals] Detoxification facilities, hospitals and psychiatric centers shall be equipped with smoke detection as required in Section 407.2.

Exceptions:

1.	Corridor smoke detection is not required where [patient] sleeping [units] rooms are provided with smoke detectors that comply with UL 268. Such detectors shall provide a visual display on the corridor side of each [patient] sleeping [unit] room and an audible and visual alarm at the [nursing] care provider’s station attending each unit.

2.	Corridor smoke detection is not required where [patient] sleeping [unit] room doors are equipped with automatic door-closing devices with integral smoke detectors on the unit sides installed in accordance with their listing, provided that the integral detectors perform the required alerting function.

[407.8] 407.9 Secured yards. Grounds are permitted to be fenced and gates therein are permitted to be equipped with locks, provided that safe dispersal areas having 30 net square feet (2.8 m2) for bed and [litter patients] stretcher care recipients and 6 net square feet (0.56 m2) for [ambulatory patients] ambulatory care recipients and other occupants are located between the building and the fence. Such provided safe dispersal areas shall [not] be located not less than 50 feet (15 240 mm) from the building they serve.

[407.9 Hyperbaric facilities. Hyperbaric facilities in Group I-2 occupancies shall meet the requirements contained in Chapter 20 of NFPA 99.] 407.10 Electrical systems. In Group I-2 occupancies, the essential electrical system for electrical components, equipment and systems shall be designed and constructed in accordance with the provisions of NFPA 99 and Chapter 27 of this code.

SECTION BC 408
GROUP I-3

408.1 General. Occupancies in Group I-3 shall comply with the provisions of Sections 408.1 through [408.10] 408.11 and other applicable provisions of this code (see Section [308.4] 308.5).

408.1.1 [Definition] Definitions specific to this section. The following [words and] terms shall, for the purposes of this [chapter and as used elsewhere in this code] section, have the meanings shown herein[.]:

CELL. A room within a housing unit in a detention or correctional facility used to confine inmates or prisoners.

CELL TIER. Levels of cells vertically stacked above one another within a housing unit.

HOUSING UNIT. A dormitory or a group of cells with a common dayroom in Group I-3.

SALLYPORT. A security vestibule with two or more doors or gates where the intended purpose is to prevent continuous and unobstructed passage by allowing the release of only one door or gate at a time.

[408.1.2 Occupancy conditions. Buildings of Group I-3 shall be classified as one of the occupancy conditions indicated in Sections 408.1.2.1 through 408.1.2.5.]

[408.1.2.1 Condition 1. This occupancy condition shall include buildings in which free movement is allowed from sleeping areas, and other spaces where access or occupancy is permitted, to the exterior via means of egress without restraint. A Condition 1 facility is permitted to be constructed as Group R.]

[408.1.2.2 Condition 2. This occupancy condition shall include buildings in which free movement is allowed from sleeping areas and any other occupied smoke compartment to one or more other smoke compartments. Egress to the exterior is impeded by locked exits and exit is not under an occupant’s control.]

[408.1.2.3 Condition 3. This occupancy condition shall include buildings in which free movement is allowed within individual smoke compartments, such as within a residential unit comprised of individual sleeping unit(s) and/or group activity spaces, where egress is impeded by remote-controlled door release, leading by means of egress from such a smoke compartment to another smoke compartment.]

[408.1.2.4 Condition 4. This occupancy condition shall include buildings in which free movement is restricted from an occupied space. Remote-controlled release is provided to permit movement from sleeping units, activity spaces and other occupied areas within the smoke compartment to other smoke compartments and egress to the outside is impeded by locked exit and remote door release.]

[408.1.2.5 Condition 5. This occupancy condition shall include buildings in which free movement is restricted from an occupied space. Staff-controlled manual release is provided to permit movement from sleeping units, activity spaces and other occupied areas within the smoke compartment to other smoke compartments.]

408.2 Other occupancies. Buildings or portions of buildings in Group I-3 occupancies where security operations necessitate the locking of required means of egress shall be permitted to be classified as a different occupancy. Occupancies classified as other than Group I-3 shall meet the applicable requirements of this code for that occupancy [provided] where provisions [shall be] are made for the release of occupants at all times.

Means of egress from detention and correctional occupancies that traverse other use areas shall, as a minimum, conform to requirements for detention and correctional occupancies.

Exception: It is permissible to exit through a horizontal exit into other contiguous occupancies that do not conform to detention and correctional occupancy egress provisions but that do comply with requirements set forth in the appropriate occupancy, as long as the occupancy is not a Group H use.

408.3 Means of egress. Except as modified or as provided for in this section, the means of egress provisions of Chapter 10 shall apply.

408.3.1 Door width. Doors to resident sleeping units shall have a clear width of not less than 28 inches (711 mm).

408.3.2 Sliding doors. Where doors in a means of egress are of the horizontal-sliding type, the force to slide the door to its fully open position shall be not [exceed] greater than 50 pounds (220 N) with a perpendicular force against the door of 50 pounds (220 N).

408.3.3 Guard tower doors. A hatch or trap door not less than 16 square feet [(610 m2)] (1.49 m2) in area through the floor and having [minimum] dimensions of not less than 2 feet (610 mm) in any direction shall be permitted to be used as a portion of the means of egress from guard towers.

408.3.4 Spiral stairways. Spiral stairways that conform to the requirements of Section [1009.9]  1011.10 are permitted for access to and between staff locations.

408.3.5 Ship ladders. Ship ladders shall be permitted for egress from control rooms or elevated facility observation rooms in accordance with Section [1009.11]  1011.15.

408.3.6 Exit discharge. Exits are permitted to discharge into a fenced or walled courtyard. Enclosed yards or courts shall be of a size to accommodate all occupants, [a minimum of] be located not less than 50 feet (15 240 mm) from the building [with a net] and have an area of not less than 15 square feet (1.4 m2) per person.

408.3.7 Sallyports. A sallyport shall be permitted in a means of egress where there are provisions for continuous and unobstructed passage through the sallyport during an emergency egress condition.

408.3.8 [Exit enclosures. One of the required exit enclosures] Interior exit stairway and ramp construction. One interior exit stairway or ramp in each building shall be permitted to have glazing installed in doors and interior walls at each landing level providing access to the [enclosure] interior exit stairway or ramp, provided that the following conditions are met:

1.	The [vertical] interior exit [enclosure] stairway or ramp shall not serve more than four floor levels.

2.	Exit doors shall be not [be] less than [3/4-hour] 3/4 hour fire [doors] door assemblies complying with Section [715.4] 716.5.

3.	The total area of glazing at each floor level shall not exceed 5,000 square inches [(3 m2)] 3.2 m2) and individual panels of glazing shall not exceed 1,296 square inches (0.84 m2).

4.	The glazing shall be protected on both sides by an automatic sprinkler system. The sprinkler system shall be designed to wet completely the entire surface of any glazing affected by fire when actuated.

5.	The glazing shall be in a gasketed frame and installed in such a manner that the framing system will deflect without breaking (loading) the glass before the sprinkler system operates.

6.	Obstructions, such as curtain rods, drapery traverse rods, curtains, drapes or similar materials shall not be installed between the automatic sprinklers and the glazing.

408.4 Locks. Egress doors are permitted to be locked in accordance with the applicable use condition. Doors from a refuge area to the [exterior] outside are permitted to be locked with a key in lieu of locking methods described in Section 408.4.1. The keys to unlock the exterior doors shall be available at all times and the locks shall be operable from both sides of the door.

408.4.1 Remote release. Remote release of locks on doors in a means of egress shall be provided with reliable means of operation, remote from the resident living areas, to release locks on all required doors. In Occupancy [Conditions] Condition 3 or 4, the arrangement, accessibility and security of the release [mechanism(s)] mechanisms required for egress shall be such that with the minimum available staff at any time, the lock mechanisms are capable of being released within 2 minutes.

Exception: Provisions for remote locking and unlocking of occupied rooms in Occupancy Condition 4 are not required provided that not more than 10 locks are necessary to be unlocked in order to move occupants from one smoke compartment to a refuge area within 3 minutes. The opening of necessary locks shall be accomplished with not more than two separate keys.

408.4.2 Power-operated doors and locks. Power-operated sliding doors or power-operated locks for swinging doors shall be operable by a manual release mechanism at the door[, and either emergency]. Emergency power [or a remote mechanical operating release] shall be provided for the doors and locks in accordance with Section 2702.

[Exception] Exceptions:

1.	Emergency power is not required in facilities with 10 or fewer locks [or less] complying with the exception to Section 408.4.1.

2.	Emergency power is not required where remote mechanical operating releases are provided.

408.4.3 Redundant operation. Remote release, mechanically operated sliding doors or remote release, mechanically operated locks shall be provided with a mechanically operated release mechanism at each door, or shall be provided with a redundant remote release control.

408.4.4 Relock capability. Doors remotely unlocked under emergency conditions shall not automatically relock when closed unless specific action is taken at the remote location to enable doors to relock.

408.5 Protection of vertical openings. Any vertical opening shall be protected by a shaft enclosure in accordance with Section [708] 713, or shall be in accordance with Sections 408.5.1 and 408.5.2.

408.5.1 Floor openings. Openings in floors within a housing unit are permitted without a shaft enclosure, provided all of the following conditions are met:

1.	The entire normally occupied areas so interconnected are open and unobstructed so as to enable observation of the areas by supervisory personnel;

2.	Means of egress capacity is sufficient for all occupants from all interconnected cell tiers and areas;

3.	The height difference between the floor levels of the highest and lowest cell tiers shall not exceed 23 feet (7010 mm); and

4.	Egress from any portion of the cell tier to an exit or exit access door shall not require travel on more than one additional floor level within the housing unit.

408.5.2 Shaft openings in communicating floor levels. Where a floor opening is permitted between communicating floor levels of a housing unit in accordance with Section 408.5.1, plumbing chases serving vertically stacked individual cells contained within the housing unit shall be permitted without a shaft enclosure.

408.6 Smoke barrier. Occupancies in Group I-3 shall have smoke barriers complying with Sections 408.8 and [710] 709 to divide every story occupied by residents for sleeping, or any other story having an occupant load of 50 or more persons, into [at least] no fewer than two smoke compartments.

Exception: Spaces having a direct exit to one of the following, provided that the locking arrangement of the doors involved complies with the requirements for doors at the smoke barrier for the use condition involved:

1.	A public way.

2.	A building separated from the resident housing area by a 2-hour fire-resistance-rated assembly or 50 feet (15 240 mm) of open space.

3.	A secured yard or court having a holding space 50 feet (15 240 mm) from the housing area that provides 6 square feet (0.56 m2) or more of refuge area per occupant, including residents, staff and visitors.

408.6.1 Smoke compartments. The [maximum] number of residents in any smoke compartment shall be not more than 200. The [travel] distance of travel to a door in a smoke barrier from any room door required as exit access shall be not [exceed] greater than 150 feet (45 720 mm). The [travel] distance of travel to a door in a smoke barrier from any point in a room shall be not [exceed] greater than 200 feet (60 960 mm).

408.6.2 Refuge area. [At least] Not less than 6 net square feet (0.56 m2) per occupant shall be provided on each side of each smoke barrier for the total number of occupants in adjoining smoke compartments. This space shall be readily available wherever the occupants are moved across the smoke barrier in a fire emergency.

408.6.3 Independent egress. A means of egress shall be provided from each smoke compartment created by smoke barriers without having to return through the smoke compartment from which means of egress originates.

408.7 Security glazing. In occupancies in Group I-3, windows and doors in 1-hour fire barriers constructed in accordance with Section 707, fire partitions constructed in accordance with Section [709] 708 and smoke barriers constructed in accordance with Section [710] 709 shall be permitted to have security glazing installed provided that the following conditions are met. Such glazing shall be subject to the requirements in Chapter 24.

1.	Individual panels of glazing shall not exceed 1,296 square inches (0.84 m2).

2.	The glazing shall be protected on both sides by an automatic sprinkler system. The sprinkler system shall be designed to, when actuated, wet completely the entire surface of any glazing affected by fire.

3.	The glazing shall be in a gasketed frame and installed in such a manner that the framing system will deflect without breaking (loading) the glass before the sprinkler system operates.

4.	Obstructions, such as curtain rods, drapery traverse rods, curtains, drapes or similar materials shall not be installed between the automatic sprinklers and the glazing.

408.8 Subdivision of resident housing areas. Sleeping areas and any contiguous day room, group activity space or other common spaces where residents are housed shall be separated from other spaces in accordance with Sections 408.8.1 through 408.8.4.

408.8.1 Occupancy Conditions 3 and 4. Each sleeping area in Occupancy Conditions 3 and 4 shall be separated from the adjacent common spaces by a smoke-tight partition where the [travel] distance of travel from the sleeping area through the common space to the corridor exceeds 50 feet (15 240 mm).

408.8.2 Occupancy Condition 5. Each sleeping area in Occupancy Condition 5 shall be separated from adjacent sleeping areas, corridors and common spaces by a smoke-tight partition. Additionally, common spaces shall be separated from the corridor by a smoke-tight partition.

408.8.3 Openings in room face.  The aggregate area of openings in a solid sleeping room face in Occupancy Conditions 2, 3, 4 and 5 shall not exceed 120 square inches [(77 419 mm2)] (0.077 m2). The aggregate area shall include all openings including door undercuts, food passes and grilles. Openings shall be not more than 36 inches (914 mm) above the floor. In Occupancy Condition 5, the openings shall be closeable from the room side.

408.8.4 Smoke-tight doors. Doors in openings in partitions required to be smoke tight by Section 408.8 shall be substantial doors, of construction that will resist the passage of smoke. Latches and door closures are not required on cell doors.

408.9 Windowless buildings. For the purposes of this section, a windowless building or portion of a building is one with nonopenable windows, windows not readily breakable or without windows. Windowless buildings shall be provided with an engineered smoke control system to provide a tenable environment for exiting from the smoke compartment in the area of fire origin in accordance with Section 909 for each windowless smoke compartment.

408.10 Fire alarm system. A fire alarm system shall be provided in accordance with Section 907.2.6.3.

408.11 Automatic sprinkler system. Group I-3 occupancies shall be equipped throughout with an automatic sprinkler system in accordance with Section 903.2.6.

SECTION BC 409
MOTION PICTURE PROJECTION ROOMS

409.1 General. The provisions of Sections 409.1 through 409.5 shall apply to rooms in which ribbon-type cellulose acetate or other safety film is utilized in conjunction with electric arc, xenon or other light-source projection equipment that develops hazardous gases, dust or radiation. The projection, use or storage of film having a nitrocellulose base (commonly known as nitrate film) shall not be permitted except under conditions specified in special permits when issued by the Fire Department. Safety film meeting the specification and test standards of NFPA 40 may be projected, used or stored.

409.1.1 Projection room required. Every motion picture machine projecting film as mentioned within the scope of this section shall be enclosed in a projection room. Appurtenant electrical equipment, such as rheostats, transformers and generators, shall be within the projection room or in an adjacent room of equivalent construction.

409.2 Construction of projection rooms. Every projection room shall be of permanent construction consistent with the construction requirements for the type of building in which the projection room is located. Openings are not required to be protected.

The room shall have a floor area of not less than 80 square feet (7.44 m2) for a single machine and [at least] not less than 40 square feet (3.7 m2) for each additional machine. Each motion picture projector, floodlight, spotlight or similar piece of equipment shall have a clear working space of not less than 30 inches by 30 inches (762 mm by 762 mm) on each side and at the rear thereof, but only one such space shall be required between two adjacent projectors. The projection room and the rooms appurtenant thereto shall have a ceiling height of not less than 7 feet 6 inches (2286 mm). The aggregate of openings for projection equipment shall not exceed 25 percent of the area of the wall between the projection room and the auditorium. Openings shall be provided with glass or other approved material, so as to close completely the opening.

409.3 Projection room and equipment ventilation. Ventilation shall be provided in accordance with the New York City Mechanical Code.

409.3.1 Supply air. Each projection room shall be provided with adequate air supply inlets so arranged as to provide well-distributed air throughout the room. Air inlet ducts shall provide an amount of air equivalent to the amount of air being exhausted by projection equipment. Air is permitted to be taken from the outside; from adjacent spaces within the building, provided the volume and infiltration rate is sufficient; or from the building air-conditioning system, provided it is so arranged as to provide sufficient air when other systems are not in operation.

409.3.2 Exhaust air. Projection rooms are permitted to be exhausted through the lamp exhaust system. The lamp exhaust system shall be positively interconnected with the lamp so that the lamp will not operate unless there is the required airflow. Exhaust air ducts shall terminate at the exterior of the building in such a location that the exhaust air cannot be readily recirculated into any air supply system. The projection room ventilation system is permitted to also serve appurtenant rooms, such as the generator and rewind rooms.

409.3.3 Projection machines. Each projection machine shall be provided with an exhaust duct that will draw air from each lamp and exhaust it directly to the outside of the building. The lamp exhaust is permitted to serve to exhaust air from the projection room to provide room air circulation. Such ducts shall be of rigid materials, except for a flexible connector approved for the purpose. The projection lamp or projection room exhaust system, or both, is permitted to be combined but shall not be interconnected with any other exhaust or return system, or both, within the building.

409.4 Lighting control. Provisions shall be made for control of the auditorium lighting and the means of egress lighting systems of theaters from inside the projection room and from [at least] not less than one other convenient point in the building.

409.5 Miscellaneous equipment. Each projection room shall be provided with rewind and film storage facilities.

SECTION BC 410
STAGES[AND], PLATFORMS AND TECHNICAL PRODUCTION AREAS

410.1 Applicability. The provisions of Sections 410.1 through [410.10] 410.11 shall apply to all parts of buildings and structures that contain stages or platforms and similar appurtenances as herein defined.

410.2 Definitions. [The following words and terms shall, for the purposes of this section and as used elsewhere in this code, have the meanings shown herein.] This section contains terms defined elsewhere in the code, and terms with definitions that are specific to this section.

410.2.1 Terms defined elsewhere in the code. The following terms are defined in Chapter 2:

FLY GALLERY. [A raised floor area above a stage from which the movement of scenery and operation of other stage effects are controlled.]

GRIDIRON. [The structural framing over a stage supporting equipment for hanging or flying scenery and other stage effects.]

PINRAIL. [A rail on or above a stage through which belaying pins are inserted and to which lines are fastened.]

[PLATFORM. A raised area within a building used for worship, the presentation of music, plays or other entertainment; the head table for special guests; the raised area for lecturers and speakers; boxing and wrestling rings; theater- in-the-round stages; and similar purposes wherein there are no overhead hanging curtains, drops, scenery or stage effects other than lighting and sound. A temporary platform is one installed for not more than 30 days.]

PROSCENIUM WALL. [The wall that separates the stage from the auditorium or assembly seating area.]

STAGE. [A space within a building utilized for entertainment or presentations, which includes overhead hanging curtains, drops, scenery or stage effects other than lighting and sound.]

TECHNICAL PRODUCTION AREA.

410.2.2 Definitions specific to this section. The following term shall, for the purposes of this section, have the meaning shown herein:

PLATFORM. A raised area within a building used for worship, the presentation of music, plays or other entertainment; the head table for special guests; the raised area for lecturers and speakers; boxing and wrestling rings; theater-in-the-round stages; and similar purposes wherein, other than horizontal sliding curtains, there are no overhead hanging curtains, drops, scenery or stage effects other than lighting and sound. A temporary platform is one installed for not more than 30 days.

410.3 Stages. Stage construction shall comply with Sections 410.3.1 through 410.3.7.

410.3.1 Stage construction. Stage floors shall be constructed of materials as required for floors for the type of construction of the building in which such stages are located. Where areas below the stage are used for other occupancies, such stage floor shall be constructed in accordance with the requirements for separated occupancies as per Chapter 5.

Exceptions:

1.	Stages of Type IIB or IV construction with a nominal 2-inch (51 mm) wood deck, provided that the stage is separated from other areas in accordance with Section 410.3.4.

2.	In all types of construction, the finished floor shall be constructed of wood or approved noncombustible materials. Openings through stage floors shall be equipped with tight-fitting, solid wood trap doors with approved safety locks. The room or space below the stage into which the traps or lifts open shall be completely enclosed by construction having at least the fire-resistance rating required for the stage floor, and such room or space shall not be used as a workshop or storage area. Storage shall not be deemed to include the location in this area of scenery or scenic elements used during a performance. However, no combustible material that has a flame spread rating greater than 25 or that has not been rendered flameproof in accordance with the rules of the Fire Commissioner may be stored in this location at any time.

410.3.1.1 Stage height and area. Stage areas shall be measured to include the entire performance area and adjacent backstage and support areas not separated from the performance area by fire-resistance-rated construction. Stage height shall be measured from the lowest point on the stage floor to the highest point of the roof or floor deck above the stage.

410.3.2 [Galleries] Technical production areas: galleries, gridirons, catwalks and pinrails. Beams designed only for the attachment of portable or fixed theater equipment, gridirons, galleries and catwalks shall be constructed of noncombustible materials. Floors of fly galleries and catwalks shall be constructed of noncombustible material. These areas shall not be considered to be floors, stories, mezzanines or levels in applying this code.

410.3.3 Exterior stage doors. Where protection of openings is required, exterior exit doors shall be protected with fire door assemblies that comply with Section [715] 716. Exterior openings that are located on the stage for means of egress or loading and unloading purposes, and that are likely to be open during occupancy of the theater, shall be constructed with vestibules to prevent air drafts into the auditorium.

410.3.4 Proscenium wall. Where the stage height is greater than 40 feet (12 192 mm), all portions of the stage shall be completely separated from the seating area by a proscenium wall with not less than a 2-hour fire-resistance rating extending continuously from the foundation to the roof.

410.3.5 Proscenium curtain. Where a proscenium wall is required to have a fire-resistance rating, the stage opening shall be provided with one of the following:

- A fire curtain complying with NFPA 80; or

- An approved stage water curtain and sprinklers complying with Section 410.7 and Section 903.3.1.1, and the following:

2.1.	A deluge valve actuated by a “rate of rise system” and “fixed temperature system” shall control the water curtain system;

2.2.	The heat actuating devices shall be located on not more than 10-foot (3048 mm) centers around the perimeter of the sprinklered area stage or as otherwise required for the type of device used to assure operation of the system;

2.3.	In addition to the automatic controls, manual-operating devices shall be located at the voice/alarm communication system required by Section [410.8] 410.9, and adjacent to at least one exit from the stage. Such exit shall be remote from the voice/alarm communication system; [and]

2.4.	[The operation of the deluge valve shall activate the emergency ventilating equipment required in Section 410.3.7 and the deluge valve shall be provided with central station supervision in addition to a local alarm.] All valves controlling deluge and sprinkler supplies on stages where the stage height is greater than 40 feet (12 192 mm) shall be provided with tamper switches wired to an annunciator panel located at the voice/alarm communication system required by Section 410.9;

2.5	The operation of any section of the sprinkler system on stages where the stage height is greater than 40 feet (12 192 mm) or the operation of the deluge system shall activate the emergency ventilating equipment required in Section 410.3.7 and shall be provided with central station supervision in addition to the required local alarm; and

2.6	The water flow alarm, tamper switches, the sprinkler system on stages where the stage height is greater than 40 feet (12 192 mm), and deluge system equipment shall be provided with central station supervision in addition to the required local alarm.

410.3.6 Scenery. All scenery or scenic elements shall be of noncombustible materials, or of materials having a flame-spread rating not exceeding 25, or of materials that have been rendered flameproof in compliance with the rules of the Fire Commissioner. Scenery and scenic elements not complying with the above requirements may be used only when expressly permitted by the Fire Department.

410.3.7 Stage ventilation. Emergency ventilation shall be provided for stages larger than 1,000 square feet (93 m2) in floor area, or with a stage height greater than 40 feet (12 192 mm). Such ventilation shall comply with Section 410.3.7.1 or 410.3.7.2.

410.3.7.1 Roof vents. Two or more vents constructed to open automatically by approved heat-activated devices and with an aggregate clear opening area of not less than 5 percent of the area of the stage shall be located near the center and above the highest part of the stage area. Supplemental means shall be provided for manual operation of the ventilator. Curbs shall be provided as required for skylights in Section 2610.2. Vents shall be labeled.

410.3.7.2 Smoke control. Smoke control in accordance with Section 909 shall be provided to maintain the smoke layer interface not less than 6 feet (1829 mm) above the highest level of the assembly seating or above the top of the proscenium opening where a proscenium wall is provided in compliance with Section 410.3.4.

410.4 Platform construction. Permanent platforms shall be constructed of materials as required for the type of construction of the building in which the permanent platform is located. Permanent platforms are permitted to be constructed in accordance with the following:

1.	The area below the platform shall be enclosed on all sides with solid construction.

- Platforms constructed of untreated wood shall not exceed an area of 400 square feet (37 m2). Platforms constructed of fire-retardant-treated wood shall not exceed an area of 1,200 square feet (111 m2). Platforms constructed of noncombustible materials shall not be limited in area.

- Where wood is used, the floor of the platform shall be at least 1-inch (25 mm) nominal thickness. Such floor shall be laid on a solid, noncombustible backing, or shall have all spaces between supporting members fireblocked with noncombustible material.

Where the space beneath the permanent platform is used for storage or any other purpose other than equipment, wiring or plumbing, the floor construction shall not be less than 1-hour fire-resistant-rated construction. Where the space beneath the permanent platform is used only for equipment, wiring or plumbing, the underside of the permanent platform need not be protected.

410.4.1 Temporary platforms. Platforms installed for a period of not more than 30 days are permitted to be constructed of any materials permitted by [the] this code. The space between the floor and the platform above shall only be used for plumbing and electrical wiring to platform equipment.

410.5 Dressing and appurtenant rooms. Dressing and appurtenant rooms shall comply with Sections 410.5.1 [through] and [410.5.4] 410.5.2.

410.5.1 Separation from stage. The stage shall be separated from dressing rooms, scene docks, property rooms, workshops, storerooms and compartments appurtenant to the stage and other parts of the building by fire barriers constructed in accordance with Section 707 or horizontal assemblies constructed in accordance with Section [712] 711, or both. The [minimum] fire-resistance rating shall be not less than 2 hours for stage heights greater than 50 feet (15 240 mm) and not less than 1 hour for stage heights of 50 feet (15 240 mm) or less.

410.5.2 Separation from each other. Dressing rooms, scene docks, property rooms, workshops, storerooms and compartments appurtenant to the stage shall be separated from each other by not less than 1-hour fire barriers constructed in accordance with Section 707 or horizontal assemblies constructed in accordance with Section [712] 711, or both.

410.6 Means of egress. Except as modified or as provided for in this section, the provisions of Chapter 10 shall apply.

[410.5.3 Stage exits. At least one approved means of egress shall be provided from each side of the stage; and from each side of the space under the stage. At least one means of escape shall be provided from each fly gallery and from the gridiron. A steel ladder, alternating tread device or spiral stairway is permitted to be provided from the gridiron to a scuttle in the stage roof.] 410.6.1 Stage exits. No fewer than one exit or exit access doorway shall be provided from each side of the stage and from each side of the space under the stage. Technical production areas shall comply with Section 410.6.3.

410.6.2 Stairway and ramp enclosure. Exit access stairways and ramps serving a stage or platform are not required to be enclosed. Exit access stairways and ramps serving technical production areas are not required to be enclosed.

410.6.3 Technical production areas. Technical production areas shall be provided with means of egress and means of escape in accordance with Sections 410.6.3.1 through 410.6.3.5.

410.6.3.1 Number of means of egress. No fewer than one means of egress shall be provided from technical production areas.

410.6.3.2 Exit access travel distance. The exit access travel distance shall be not greater than 300 feet (91 440 mm) for buildings without a sprinkler system and 400 feet (121 900 mm) for buildings equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1.

410.6.3.3 Two means of egress. Where two means of egress are required, the common path of travel shall be not greater than 100 feet (30 480 mm).

Exception: A means of escape to a roof in place of a second means of egress is permitted.

410.6.3.4 Path of egress travel. The following exit access components are permitted where serving technical production areas:

1.	Stairways.

2.	Ramps.

3.	Spiral stairways.

4.	Catwalks.

5.	Alternating tread devices.

6.	Permanent ladders.

410.6.3.5 Width. The path of egress travel within and from technical support areas shall be not less than 22 inches (559 mm) in width.

[410.6] 410.7 Automatic sprinkler system. [Stages shall be equipped with an automatic fire-extinguishing system in accordance with Chapter 9. Sprinklers shall be installed under the roof and gridiron, and under all catwalks and galleries over the stage. Sprinklers shall be installed in dressing rooms, performer lounges, workshops and storerooms accessory to such stages:]

[1.	Automatic sprinklers shall be placed above all rigging lofts; and above all stage areas, other than those portions of stage areas specifically designated on approved plans as performing areas that do not have rigging lofts above and that are not at any time used for storage purposes. Sprinklers above rigging lofts shall be located so that no gridiron or other obstruction intervenes between the sprinkler heads and the scenery or scenic elements.]

[2.	When openings are provided in the stage floor for stage lifts, trap doors or stairs, sprinklers spaced 5 feet (1524 mm) on centers shall be provided around the opening at the ceiling below the stage, and baffles at least 12 inches (305 mm) in depth shall be installed around the perimeter of the opening.]

[3.	All valves controlling sprinkler supplies shall be provided with tamper switches wired to an annunciator panel located at the voice/alarm communication system required by Section 410.8.]

[4.	The operation of any section of the sprinkler system and the deluge system shall activate the emergency ventilating equipment required in Section 410.3.7 and shall be provided with central station supervision in addition to the required local alarm.]

[5.	The water flow alarm, tamper switches and deluge system equipment shall be provided with central station supervision in addition to the required local alarm.]

An automatic sprinkler system in accordance with Section 903.3.1.1 shall be provided in the following areas when located within a place of assembly:

1.	Stages including those with stage height greater than 40 feet (12 192 mm);

2.	Technical production areas over the stage including under the roof, above and below the gridiron, catwalks and galleries;

3.	Dressing rooms, performer lounges, shops and storerooms accessory to stages or platforms, with live entertainment;

4.	Platforms with live entertainment;

5.	Cabarets; or

6.	When openings are provided in the stage floor for stage lifts, trap doors or stairs, sprinklers spaced 5 feet (1524 mm) on centers shall be provided around the opening at the ceiling below the stage, and baffles at least 12 inches (305 mm) in depth shall be installed around the perimeter of the opening.

Exceptions:

1.	Sprinklers are not required under [stage areas] stages or platforms less than 4 feet (1219 mm) in clear height [utilized] that are utilized exclusively for storage of tables and chairs, provided the concealed space is separated from the adjacent spaces by [not less than 5/8-inch (15.9 mm)] Type X gypsum board not less than 5/8-inch (15.9 mm) in thickness.

2.	Sprinklers are not required within portable orchestra enclosures on stages.

[410.7] 410.8 Standpipes. Standpipe systems shall be provided in accordance with Section 905.

[410.8] 410.9 Voice/alarm communication system. Stages shall be provided with a voice/alarm communication system in accordance with Section 907.2.1.1.

[410.9] 410.10 Construction in seating areas. Construction in seating areas shall be in accordance with Sections 410.10.1 and 410.10.2.

[410.9.1] 410.10.1 Scenery and scenic elements in seating areas. Scenery or scenic elements may be placed in seating sections if such elements:

- Are noncombustible, or of materials that have been rendered flameproof in accordance with the rules of the [fire commissioner] Fire Commissioner, or have a flame spread rating of 25 or less.

- Are adequately braced or secured.

3.	Do not obstruct the required visibility of, or paths of travel to, exit openings.

[410.9.2] 410.10.2 Platforms or runways in seating areas. Platforms or runways for performances, to accommodate the operation of cameras, electronic equipment, or motion picture projection machines not using carbon-arc or other light source that emits a gaseous discharge may be constructed in seating sections, provided such platforms or runways comply with the requirements of Section 410.4, except Item 1, and Section [410.8] 410.9.

[410.10] 410.11 Stage lighting. Stage lights shall be placed such that they will not develop temperatures on the surface of any material that will cause that material to ignite, or smoke, or cause its flameproofing to deteriorate.

SECTION BC 411
SPECIAL AMUSEMENT BUILDINGS

411.1 General. Special amusement buildings having an occupant load of 75 or more shall comply with the requirements for the appropriate Group A occupancy and Sections 411.1 through 411.8. [Amusement] Special amusement buildings having an occupant load of less than 75 shall comply with the requirements for a Group B occupancy and Sections 411.1 through 411.8.

Exception: [Amusement] Special amusement buildings or portions thereof that are without walls or a roof and constructed to prevent the accumulation of smoke. All decorative material shall be noncombustible or composed of flame-retardant fabric.

411.2 [Definition] Definitions. The following [word and] term [shall, for the purpose of this section and as used elsewhere] is defined in [this code,  have the meaning shown herein.] Chapter 2:

SPECIAL AMUSEMENT BUILDING. [A special amusement building is any temporary or permanent building or portion thereof that is occupied for amusement, entertainment or educational purposes and that contains a device or system that conveys passengers or provides a walkway along, around or over a course in any direction so arranged that the means of egress path is not readily apparent due to visual or audio distractions or is intentionally confounded or is not readily available because of the nature of the attraction or mode of conveyance through the building or structure.]

411.3 Automatic fire detection. Special amusement buildings shall be equipped with an automatic fire detection system[,] in accordance with Section 907.

411.4 Automatic sprinkler system. Special amusement buildings shall be equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1. Where the special amusement building is temporary, the sprinkler water supply shall be of an approved temporary means.

Exception: Automatic [fire] sprinklers are not required where the total floor area of a temporary special amusement building is less than 1,000 square feet (93 m2) and the exit access travel distance from any point to an exit is less than 50 feet (15 240 mm).

411.5 Alarm. Actuation of a single smoke detector, the automatic sprinkler system or other automatic fire detection device shall [immediately sound an alarm at the building] initiate a pre-signal system in accordance with NFPA 72 as modified by Appendix Q at a constantly attended location from which [emergency action can be] the Fire Department shall be notified and live voice evacuation instructions shall be initiated [including the capability of manual initiation of requirements] using an emergency voice/alarm communications system in accordance with Section [907.2.12.2] 907.5.2.2.

411.6 Emergency voice/alarm communications system. An emergency voice/alarm communications system shall be provided in accordance with Sections [907.2.12.3] 907.2.12 and 907.5.2.2, which is also permitted to serve as a public address system and shall be audible throughout the entire special amusement building.

411.7 Exit marking. Exit signs shall be installed at the required exit or exit access doorways of amusement buildings in accordance with this section and Section [1011]  1013. Approved directional exit markings listed in accordance with UL 1994, shall also be provided. Where mirrors, mazes or other designs are utilized that disguise the path of egress travel such that they are not apparent, approved low-level exit signs that comply with Section [1011.4]  1013.5, and directional path markings shall be provided and located not more than 8 inches (203 mm) above the walking surface and on or near the path of egress travel. Such markings shall become visible in an emergency. The directional exit marking shall be activated by the automatic fire detection system and the automatic sprinkler system in accordance with Section 907.2.12.2.

411.8 Interior finish. The interior finish shall be Class A in accordance with Section 803.1.

SECTION BC 412
AIRCRAFT-RELATED OCCUPANCIES

412.1 General. Aircraft-related occupancies shall comply with [Sections 412.1 through 412.7 and] the New York City Fire Code and Sections 412.1 through 412.8 of this code.

412.2 Definitions. The following [words and] terms [shall, for the purposes of this chapter and as used elsewhere in this code, have the meanings shown herein.] are defined in Chapter 2:

FIXED BASE OPERATOR (FBO). [A commercial business granted the right by the airport sponsor to operate on an airport and provide aeronautical services, such as fueling, hangaring, tie-down and parking, aircraft rental, aircraft maintenance and flight instruction.]

HELIPORT. [An area of land or water or a structural surface that is used, or intended for the use, for the landing and taking off of helicopters, and any appurtenant areas that are used, or intended for use, for heliport buildings or other heliport facilities.]

HELISTOP. [The same as “heliport,” except that no fueling, defueling, maintenance, repairs or storage of helicopters is permitted.]

RESIDENTIAL AIRCRAFT HANGAR. [An accessory building less than 2,000 square feet (186 m2) and 20 feet (6096 mm) in building height constructed on a one- or two-family property where aircraft are stored. Such use will be considered as a residential accessory use incidental to the dwelling.]

TRANSIENT AIRCRAFT. [Aircraft based at another location and that is at the transient location for not more than 90 days.]

412.3 Airport traffic control towers.

[412.3.1 General.] The provisions of Sections 412.3.1 through [412.3.6] 412.3.9 shall apply to airport traffic control towers [not exceeding 1,500 square feet (140 m2) per floor] occupied only for the following uses:

1.	Airport traffic control cab.

2.	Electrical and mechanical equipment rooms.

3.	Airport terminal radar and electronics rooms.

4.	Office spaces incidental to the tower operation.

5.	Lounges for employees, including sanitary facilities.

[412.3.2] 412.3.1 Type of construction. Airport traffic control towers shall be constructed to comply with the height [and area] limitations of Table [412.3.2] 412.3.1.

##### TABLE [412.3.2] 412.3.1
HEIGHT [AND AREA] LIMITATIONS FOR
AIRPORT TRAFFIC CONTROL TOWERS

| TYPE OF CONSTRUCTION | HEIGHTa (feet) | [MAXIMUM AREA (square feet)] |
| --- | --- | --- |
| IA | Unlimited | [1,500] |
| IB | 240 | [1,500] |
| IIA | 100 | [1,500] |
| IIB | 85 | [1,500] |
| IIIA | 65 | [1,500] |

For SI: 1 foot = 304.8 mm, 1 square foot = 0.0929 m2.

a.	Height to be measured from grade plane to cab floor.

[412.3.3 Egress. A minimum of one exit stairway shall be permitted for airport traffic control towers of any height provided that the occupant load per floor does not exceed 15. The stairway shall conform to the requirements of Section 1009. The stairway shall be separated from elevators by a minimum distance of one-half of the diagonal of the area served measured in a straight line. The exit stairway and elevator hoistway are permitted to be located in the same shaft enclosure, provided they are separated from each other by a 4-hour fire barrier having no openings. Such stairway shall be pressurized to a minimum of 0.15 inch of water column (43 Pa) and a maximum of 0.35 inch of water column (101 Pa) in the shaft relative to the building with stairway doors closed. Stairways need not extend to the roof as specified in Section 1009.13. The provisions of Section 403 do not apply.]

[Exception: Smokeproof enclosures as set forth in Section 1022.9 are not required where required stairways are pressurized.]

412.3.2 Stairways. Stairways in airport traffic control towers shall be in accordance with Section 1011. Stairways in airport traffic control towers are not required to comply with Section 1011.12. Stairways shall be smokeproof enclosures complying with one of the alternatives provided in Section 909.20. The stairway shall be separated from elevators by a minimum distance of one-half of the diagonal of the area served measured in a straight line.

Exception: The stairway and elevator hoistway are permitted to be located in the same shaft enclosure without the minimum separation distance, provided they are separated from each other by a 4-hour fire barrier having no openings. Such stairway shall be pressurized to a minimum of 0.15 inch of water column (43 Pa) and a maximum of 0.35 inch of water column (101 Pa) in the shaft relative to the building with stairway doors closed.

412.3.3 Exit access. From observation levels, airport traffic control towers shall be permitted to have a single means of exit access for a distance of travel not greater than 100 feet (30 480 mm). Exit access stairways from the observation level need not be enclosed.

412.3.4 Number of exits. Not less than one exit stairway shall be permitted for airport traffic control towers of any height provided that the occupant load per floor is not greater than 15 and the area per floor does not exceed 1,500 square feet (140 m2).

412.3.4.1 Interior finish. Where an airport traffic control tower is provided with only one exit stairway, interior wall and ceiling finishes shall be either Class A or Class B.

[412.3.4] 412.3.5 Automatic fire detection systems. Airport traffic control towers shall be provided with an automatic fire detection system installed in accordance with Section 907.2.

[412.3.5 Standby power. A standby power system that conforms to Chapter 27 shall be provided in airport traffic control towers more than 65 feet (19 812 mm) in height. Power shall be provided to the following equipment:

- Pressurization equipment, mechanical equipment and lighting.

- Elevator operating equipment.

3.	Fire alarm and smoke detection systems.]

412.3.6 Automatic sprinkler system. Where an occupied floor is located more than 35 feet (10 668 mm) above the lowest level of fire department vehicle access, airport traffic control towers shall be equipped with an automatic sprinkler system in accordance with Section 903.3.1.1.

412.3.7 Elevator protection. Wires or cables that provide normal or standby power, control signals, communication with the car, lighting, heating, air conditioning, ventilation and fire detecting systems to elevators shall be protected by construction having a fire-resistance rating of not less than 1 hour, or shall be circuit integrity cable having a fire-resistance rating of not less than 1 hour.

412.3.7.1 Elevators for occupant evacuation. Where provided in addition to an exit stairway, occupant evacuation elevators shall be in accordance with Section 3008.

[412.3.6] 412.3.8 Accessibility. Airport traffic control towers need not be accessible as specified in the provisions of Chapter 11.

412.3.9 Standby power and emergency power. A standby power system and an emergency power system that conform to Chapter 27 shall be provided in airport traffic control towers more than 65 feet (19 812 mm) in height. Standby power shall be provided to the following equipment:

1.	Pressurization equipment and mechanical equipment provided in accordance with Section 412.3.2.

2.	Elevator operating equipment.

3.	Fire alarm and smoke detection systems.

412.3.9.1 Means of egress illumination. Emergency power shall be provided for means of egress illumination in accordance with Sections 1008.3.4 and 1008.3.5.

412.4 Aircraft hangars. Aircraft hangars shall be in accordance with Sections 412.4.1 through 412.4.6.

412.4.1 Exterior walls. Exterior walls located less than 30 feet (9144 mm) from lot lines or a public way shall have a fire-resistance rating not less than 2 hours.

412.4.2 Basements. Where hangars have basements, floors over basements shall be of Type IA construction and shall be made tight against seepage of water, oil or vapors. There shall be no opening or communication between basements and the hangar. Access to basements shall be from outside only.

412.4.3 Floor surface. Floors shall be graded and drained to prevent water or fuel from remaining on the floor. Floor drains shall discharge through an oil separator to the sewer or to an outside vented sump.

Exception: Aircraft hangars with individual lease spaces not exceeding 2,000 square feet (186 m2) each in which servicing, repairing or washing is not conducted and fuel is not dispensed shall have floors that are graded toward the door, but shall not require a separator.

412.4.4 Heating equipment. Heating equipment shall be placed in another room separated by 2-hour fire barriers constructed in accordance with Section 707 or horizontal assemblies constructed in accordance with Section [712] 711, or both. Entrance shall be from the outside or by means of a vestibule providing a two-doorway separation.

Exceptions:

1.	Unit heaters and vented infrared radiant heating equipment suspended [at least] not less than 10 feet (3048 mm) above the upper surface of wings or engine enclosures of the highest aircraft that are permitted to be housed in the hangar [and at least] need not be located in a separate room provided they are mounted not less than 8 feet (2438 mm) above the floor in shops, offices and other sections of the hangar communicating with storage or service areas.

2.	[A] Entrance to the separated room shall be permitted by a single interior door [shall be allowed,] provided the sources of ignition in the appliances are [at least] not less than 18 inches (457 mm) above the floor.

412.4.5 Finishing. The process of “doping,” involving use of a volatile flammable solvent, or of painting, shall be carried on in a separate detached building equipped with automatic fire-extinguishing equipment in accordance with Section 903.

412.4.6 Fire suppression. Aircraft hangars shall be provided with a fire suppression system designed in accordance with NFPA 409, based upon the classification for the hangar given in Table 412.4.6.

Exception: [When] Where a fixed base operator has separate repair facilities on site, Group II hangars operated by a fixed base operator used for storage of transient aircraft only shall have a fire suppression system, but the system is exempt from foam requirements.

TABLE 412.4.6
HANGAR FIRE SUPPRESSION REQUIREMENTSa,b,c

| MAXIMUM SINGLE FIRE AREA [, (SQ. FT.)] (square feet) | TYPE OF CONSTRUCTION |
| --- | --- |
|  | IA | IB | IIA | IIB | IIIA | IIIB | IV | VAd | VBd |
| [>]> 40,001 | Group I | Group I | Group I | Group I | Group I | Group I | Group I | Group I | Group I |
| 40,000 | Group II | Group II | Group II | Group II | Group II | Group II | Group II | Group II | Group II |
| 30,000 | Group III | Group II | Group II | Group II | Group II | Group II | Group II | Group II | Group II |
| 20,000 | Group III | Group III | Group II | Group II | Group II | Group II | Group II | Group II | Group II |
| 15,000 | Group III | Group III | Group III | Group II | Group III | Group II | Group III | Group II | Group II |
| 12,000 | Group III | Group III | Group III | Group III | Group III | Group III | Group III | Group II | Group II |
| 8,000 | Group III | Group III | Group III | Group III | Group III | Group III | Group III | Group III | Group II |
| 5,000 | Group III | Group III | Group III | Group III | Group III | Group III | Group III | Group II | Group II |

For SI: 1 foot = 304.8 mm, 1 square foot = 0.0929m2.

a.	Aircraft hangars with a door height greater than 28 feet shall be provided with fire suppression for a Group I hangar regardless of maximum fire area.

b.	Groups shall be as classified in accordance with NFPA 409.

c.	Membrane structures complying with Section 3102 shall be classified as a Group IV hangar.

d.	Construction Types VA and VB are not permitted in Fire Districts. See [BC Table 503] Tables 504.3, 504.4 and 506.2.

412.4.6.1 Hazardous operations. Any Group III aircraft hangar according to Table 412.4.6 that contains hazardous operations including, but not limited to, the following shall be provided with a Group I or II fire suppression system in accordance with NFPA 409 as applicable:

1.	Doping.

2.	Hot work including, but not limited to, welding, torch cutting and torch soldering.

3.	Fuel transfer.

4.	Fuel tank repair or maintenance not including defueled tanks in accordance with NFPA 409, inerted tanks or tanks that have never been fueled.

5.	Spray finishing operations.

6.	Total fuel capacity of all aircraft within the unsprinklered single fire area in excess of 1,600 gallons (6057 L).

7.	Total fuel capacity of all aircraft within the maximum single fire area in excess of 7,500 gallons (28 390 L) for a hangar with an automatic sprinkler system in accordance with Section 903.3.1.1.

412.4.6.2 Separation of maximum single fire areas. Maximum single fire areas established in accordance with hangar classification and construction type in Table 412.4.6 shall be separated by 2-hour fire walls constructed in accordance with Section 706. In determining the maximum single fire area as set forth in Table 412.4.6, ancillary uses that are separated from aircraft servicing areas by a fire barrier of not less than 1 hour, constructed in accordance with Section 707, shall not be included in the area.

412.5 Residential aircraft hangars. Residential aircraft hangars [as defined in Section 412.2] shall comply with Sections 412.5.1 through [412.5.2] 412.5.5.

412.5.1 Fire separation. A hangar shall not be attached to a dwelling unless separated by a fire barrier having a fire-resistance rating of not less than 1 hour. Such separation shall be continuous from the foundation to the underside of the roof and unpierced except for doors leading to the dwelling unit. Doors into the dwelling unit [must] shall be equipped with self-closing devices and conform to the requirements of Section [715] 716 with [at least a 4-inch (102 mm)] a noncombustible raised sill not less than 4 inches (102 mm) in height. Openings from a [hanger] hangar directly into a room used for sleeping purposes shall not be permitted.

412.5.2 Egress. A hangar shall provide two means of egress. One of the doors into the dwelling shall be considered as meeting only one of the two means of egress.

412.5.3 Smoke alarms. Smoke alarms shall be provided within the hangar in accordance with Section [907.2.11] 907.2.11.

412.5.4 Independent systems. Electrical, mechanical and plumbing drain, waste and vent (DWV) systems installed within the hangar shall be independent of the systems installed within the dwelling. Building sewer lines shall be permitted to be connected outside the structures.

Exception: Smoke detector wiring and feed for electrical subpanels in the hangar.

412.5.5 Height and area limits. Residential aircraft hangars shall be not [exceed] greater than 2,000 square feet (186 m2) in area and 20 feet (6096 mm) in building height.

412.6 Aircraft paint hangars. Aircraft painting operations where flammable liquids are used in excess of the maximum allowable quantities per control area listed in Table [307.7(1)] 307.1(1) shall be conducted in an aircraft paint hangar that complies with the provisions of Sections 412.6.1 through 412.6.6.

412.6.1 Occupancy group. Aircraft paint hangars shall be classified as Group H-2. Aircraft paint hangars shall comply with the applicable requirements of [this code and] the New York City Fire Code and this code for such occupancy.

412.6.2 Construction. The aircraft paint hangar shall be of Type I or II construction.

412.6.3 Operations. Only those flammable liquids necessary for painting operations shall be permitted in quantities less than the maximum allowable quantities per control area in Table 307.1(1). Spray equipment cleaning operations shall be conducted in a liquid use, dispensing and mixing room.

412.6.4 Storage. Storage of flammable liquids shall be in a liquid storage room.

412.6.5 Fire suppression. Aircraft paint hangars shall be provided with fire suppression as required by NFPA 409.

412.6.6 Ventilation. Aircraft paint hangars shall be provided with ventilation as required in the New York City Mechanical Code.

412.7 Aircraft manufacturing facilities. In buildings used for the manufacturing of aircraft, exit access travel distances indicated in Section 1017.1 shall be increased in accordance with the following:

1.	The building shall be of Type I or II construction.

2.	Exit access travel distance shall not exceed the distances given in Table 412.7.

TABLE 412.7
AIRCRAFT MANUFACTURING EXIT ACCESS TRAVEL DISTANCE

| HEIGHT (feet)b | MANUFACTURING AREA (sq. ft.)a |
| --- | --- |
|  | > 150,000 | > 200,000 | > 250,000 | > 500,000 | > 750,000 | > 1,000,000 |
| > 25 | 400 | 450 | 500 | 500 | 500 | 500 |
| > 50 | 400 | 500 | 600 | 700 | 700 | 700 |
| > 75 | 400 | 500 | 700 | 850 | 1,000 | 1,000 |
| > 100 | 400 | 500 | 750 | 1,000 | 1,250 | 1,500 |

For SI: 1 foot = 304.8 mm.

a.	Contiguous floor area of the aircraft manufacturing facility having the indicated height.

#### b.	Minimum height from finished floor to bottom of ceiling or roof slab or deck.

412.7.1 Ancillary areas. Rooms, areas and spaces ancillary to the primary manufacturing area shall be permitted to egress through such area having a minimum height as indicated in Table 412.7. Exit access travel distance within the ancillary room, area or space shall not exceed that indicated in Table 1017.2 based on the occupancy classification of that ancillary area. Total exit access travel distance shall not exceed that indicated in Table 412.7.

412.8 Heliports and helistops. Heliports and helistops [may] shall be permitted to be erected on buildings or other locations where they are constructed in accordance with Sections [412.7.1] 412.8.1 through [412.7.4] 412.8.5.

[412.7.1] 412.8.1 Size. The [touchdown or] landing area for helicopters [of] less than 3,500 pounds (1588 kg) shall be [a minimum of] not less than 20 feet (6096 mm) in length and width. The [touchdown] landing area shall be surrounded on all sides by a clear area having a minimum average width at roof level of 15 feet (4572 mm) but with no width less than 5 feet (1524 mm).

[412.7.2] 412.8.2 Design. Helicopter landing areas and the supports thereof on the roof of a building shall be noncombustible construction. Landing areas shall be designed to confine any flammable liquid spillage to the landing area itself and provisions shall be made to drain such spillage away from any exit or stairway serving the helicopter landing area or from a structure housing such exit or stairway. For structural design requirements, see Section [1605.4]  1607.6.

[412.7.3] 412.8.3 Means of egress. The means of egress from heliports and helistops shall comply with the provisions of Chapter 10. Landing areas located on buildings or structures shall have two or more means of egress. For landing [platforms or roof] areas less than 60 feet (18 288 mm) in length[,] or less than 2,000 square feet (186 m2) in area, the second means of egress is permitted to be a fire escape, alternating tread device[,] or ladder leading to the floor below.

[412.7.4] 412.8.4 Rooftop heliports and helistops. Rooftop heliports and helistops shall comply with NFPA 418 and the New York City Fire Code.

412.8.5 Standpipe system. In buildings equipped with a standpipe system, the standpipe shall extend to the roof level in accordance with Section 905.3.6.

SECTION BC 413
COMBUSTIBLE STORAGE

413.1 General. Storage of combustible materials in attics, under-floor spaces, concealed spaces, and below-grade storage rooms shall comply with this section.

413.2 Attic, under-floor and concealed spaces. Attic, under-floor and concealed spaces used for storage of combustible materials shall be protected on the storage side as required for 1-hour [fire-resistant] fire-resistance-rated construction. Openings shall be protected by assemblies that are self-closing and are of noncombustible construction or solid wood core not less than 13/4 inch (45 mm) in thickness.

[Exceptions] Exception: Neither fire-resistance-rated construction nor opening protectives are required in any of the following locations:

1.	Areas protected by approved automatic sprinkler systems.

2.	Group R-3 and U occupancies.

413.3 High-piled stock or rack storage. High-piled stock or rack storage in any occupancy group shall comply with the New York City Fire Code, including the requirement for permit approval.

SECTION BC 414
HAZARDOUS MATERIALS

414.1 General. The provisions of Sections 414.1 through [414.7] 414.6 shall apply to buildings and structures occupied for the manufacturing, processing, dispensing, use or storage of hazardous materials.

414.1.1 Other provisions. Buildings and structures with an occupancy in Group H shall [also] comply with this section and the applicable provisions of the New York City Fire Code and Section 415 of this code, including, but not limited to, location, installation and mechanical provisions.

414.1.2 Materials. The safe design of hazardous material occupancies is material dependent. Individual material requirements are also found in the New York City Mechanical Code, the New York City Fire Code, and Sections 307 and 415 of this code.

414.1.2.1 Aerosols. Level 2 and 3 aerosol products shall be stored and displayed in accordance with the New York City Fire Code. See the New York City Fire Code and Section 311.2 of this code for occupancy group requirements.

414.1.3 Information required. A report shall be submitted to the [department] Fire Department identifying the maximum expected quantities of hazardous materials to be stored, used in a closed system and used in an open system, and subdivided to separately address hazardous material classification categories based on Tables 307.1(1) and 307.1(2). The methods of protection from such hazards, including but not limited to control areas, fire protection systems and Group H occupancies shall be indicated in the report and on the construction documents. The opinion and report shall be prepared by a qualified person, firm or corporation approved by the [commissioner] Fire Commissioner and [shall be] provided without charge to the [department] Fire Department.

For buildings and structures with an occupancy in Group H, separate floor plans shall be submitted identifying the locations of anticipated contents and processes so as to reflect the nature of each occupied portion of every building and structure.

414.2 Control areas. Control areas shall comply with the New York City Fire Code and Sections 414.2.1 through 414.2.5 of this code.

414.2.1 Construction requirements. Control areas shall be separated from each other by fire barriers constructed in accordance with [Sections] Section 707 or horizontal assemblies constructed in accordance with Section [712] 711, or both.

414.2.2 Percentage of maximum allowable quantities. The percentage of maximum allowable quantities of hazardous materials per control area permitted at each floor level within a building shall be in accordance with Table 414.2.2.

TABLE 414.2.2
DESIGN AND NUMBER OF CONTROL AREAS

| FLOOR LEVEL | PERCENTAGE OF THE MAXIMUM ALLOWABLE QUANTITY PER CONTROL AREAa | NUMBER OF CONTROL AREAS PER FLOORb | FIRE-RESISTANCE RATING FOR FIRE BARRIERS IN HOURSb |
| --- | --- | --- | --- |
| Above grade | Higher than 9 | 5 | 1 | 2 |
|  | 7-9 | 5 | 2 | 2 |
|  | 6 | 12.5 | 2 | 2 |
|  | 5 | 12.5 | 2 | 2 |
|  | 4 | 12.5 | 2 | 2 |
|  | 3 | 50 | 2 | 1 |
|  | 2 | 75 | 3 | 1 |
|  | 1 | 100 | 4 | 1 |
| Below grade | 1 | 75 | 3 | 1 |
|  | 2 | 50 | 2 | 1 |
|  | Lower than 2 | Not Allowed | Not Allowed | Not Allowed |

a.	Percentages shall be of the maximum allowable quantity per control area shown in Tables 307.1(1) and 307.1(2), with all increases allowed in the notes to those tables.

##### b.	[Fire] Separation shall include fire barriers and [shall include walls and floors] horizontal assemblies as necessary to provide separation from other portions of the building.

414.2.3 Number. The maximum number of control areas within a building shall be in accordance with Table 414.2.2.

414.2.4 Fire-resistance-rating requirements. The required fire-resistance rating for fire barriers shall be in accordance with Table 414.2.2. The floor assembly of the control area [,] and the construction supporting the floor of the control area [,] shall have a [minimum 2-hour] fire-resistance rating [and shall comply with the requirements the New York City Fire Code] of not less than 2 hours.

Exception: The floor assembly of the control area and the construction supporting the floor of the control area are allowed to be 1-hour fire-resistance rated in buildings of Types IIA, IIIA and VA construction, provided that both of the following conditions exist:

1.	The building is equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1; and

2.	The building is three or fewer stories above grade plane.

414.2.5 Hazardous material in Group M display and storage areas and in Group S storage areas. The aggregate quantity of nonflammable solid and nonflammable or noncombustible liquid hazardous materials permitted within a single control area of a Group M display and storage area, a Group S storage area or an outdoor control area is permitted to exceed the maximum allowable quantities per control area specified in Tables 307.1(1) and 307.1(2) without classifying the building or use as a Group H occupancy, provided that the materials are displayed and stored in accordance with the New York City Fire Code and quantities do not exceed the maximum allowable specified in Table 414.2.5(1) of this code.

In Group M occupancy wholesale and retail sales uses, indoor storage of flammable and combustible liquids shall not exceed the maximum allowable quantities per control area as indicated in Table 414.2.5(2) of this code, provided that the materials are displayed and stored in accordance with the New York City Fire Code.

The maximum quantity of aerosol products in Group M occupancy retail display areas, storage areas adjacent to retail display areas and retail storage areas shall be in accordance with the New York City Fire Code.

414.2.5.1 Below-grade storage of flammable or combustible mixtures accessory to Group M establishments. Class I liquids shall not be stored in below-grade locations. Storage of Class II and Class III liquids, accessory to retail stores, and partly or completely below grade shall be permitted, provided that such below-grade area is equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1 and enclosed by fire barriers having a fire-resistance rating of at least 2 hours, constructed in accordance with the construction type of the building. Openings shall be protected by self-closing assemblies having a fire-resistance rating of at least 11/2 hours.

Exception: Class IIIB liquids may be stored in below-grade locations that are not provided throughout with an automatic sprinkler system when such liquids are stored in a room that is separated, vertically and horizontally, from surrounding spaces by fire barriers of not less than 2-hour fire-resistance rating and such room is provided with an automatic sprinkler system.

TABLE [414.2.5.(1)] 414.2.5(1)
MAXIMUM ALLOWABLE QUANTITY PER INDOOR AND OUTDOOR CONTROL AREA IN GROUP M AND S OCCUPANCIES NONFLAMMABLE SOLIDS AND NONFLAMMABLE AND NONCOMBUSTIBLE LIQUIDSd,e,f

| CONDITION | MAXIMUM ALLOWABLE QUANTITY PER CONTROL AREA |
| --- | --- |
| Materiala | Class | Solids pounds | Liquids gallons |
| A. Health-hazard materials—nonflammable and noncombustible solids and liquids |
| 1. Corrosivesb,c | Not Applicable | 9,750 | 975 |
| 2. Highly toxics | Not Applicable | 20b,c | 2b,c |
| 3. Toxicsb,c | Not Applicable | 1,000 | 100 |
| B. Physical-hazard materials—nonflammable and noncombustible solids and liquids |
| 1. Oxidizersb,c | 4 | Not Allowed | Not Allowed |
|  | 3 | 1,150g | 115 |
|  | 2 | 2,250h | 225 |
|  | 1 | 18,000i,j | 18,000i,j |
| 2. [Nondetonable unstable] Unstable (reactives)b,c | 4 | Not Allowed | Not Allowed |
|  | 3 | 550 | 55 |
|  | 2 | 1,150 | 115 |
|  | 1 | Not Limited | Not Limited |
| 3. [Nondetonable water-] Water reactives | 3b,c | 550 | 55 |
|  | 2b,c | 1,150 | 115 |
|  | 1 | Not Limited | Not Limited |

For SI: 1 pound = 0.454 kg, 1 gallon = 3.785 L.

a.	Hazard categories are as specified in the New York City Fire Code.

b.	Maximum allowable quantities shall be increased 100 percent in buildings that are sprinklered in accordance with Section 903.3.1.1. When Note c also applies, the increase for both notes shall be applied accumulatively.

c.	Maximum allowable quantities shall be increased 100 percent when stored in approved storage cabinets, in accordance with the New York City Fire Code. When Note b also applies, the increase for both notes shall be applied accumulatively.

d.	See Table 414.2.2 for design and number of control areas.

e.	Allowable quantities for other hazardous material categories shall be in accordance with Section 307.

f.	Maximum quantities shall be increased 100 percent in outdoor control areas.

g.	Maximum amounts [are permitted to] shall be increased to 2,250 pounds when individual packages are in the original sealed containers from the manufacturer or packager and do not exceed 10 pounds each.

h.	Maximum amounts [are permitted to] shall be increased to 4,500 pounds when individual packages are in the original sealed containers from the manufacturer or packager and do not exceed 10 pounds each.

i.	The permitted quantities shall not be limited in a building equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1.

j.	Quantities are unlimited in an outdoor control area.

TABLE 414.2.5(2)
MAXIMUM ALLOWABLE QUANTITY OF FLAMMABLE AND
COMBUSTIBLE LIQUIDS IN WHOLESALE AND RETAIL SALES OCCUPANCIES PER CONTROL AREAa

| TYPE OF LIQUID | MAXIMUM ALLOWABLE QUANTITY PER CONTROL AREA (gallons) |
| --- | --- |
|  | Sprinklered in accordance with note b densities and arrangements | Sprinklered in accordance with Tables 3404.3.6.3(4) through 3404.3.6.3(8) and Table 3404.3.7.5.1 of the New York City Fire Code | Nonsprinklered |
| Class IA | 60 | 60 | 30 |
| Class IB, IC, II and IIIA | 7,500c | 15,000c | 1,600 |
| Class IIIB | Unlimited | Unlimited | 13,200 |

For SI: 1 foot = 304.8 mm, 1 square foot = 0.0929m2, 1 gallon = 3.785 L, 1 gallon per minute per square foot = 40.75 L/min/m2.

a.	Control areas shall be separated from each other by not less than a 1-hour fire barrier wall.

b.	To be considered as sprinklered, a building shall be equipped throughout with an approved automatic sprinkler system with a design providing minimum densities as follows:

1.	For uncartoned commodities on shelves 6 feet or less in height where the ceiling height does not exceed 18 feet, quantities are those permitted with a minimum sprinkler design density of Ordinary Hazard Group 2.

2.	For cartoned, palletized or racked commodities where storage is 4 feet 6 inches or less in height and where the ceiling height does not exceed 18 feet, quantities are those permitted with a minimum sprinkler design density of 0.21 gallon per minute per square foot over the most remote 1,500-square-foot area.

c.	Where wholesale and retail sales or storage areas exceed 50,000 square feet in area, the maximum allowable quantities are allowed to be increased by 2 percent for each 1,000 square feet of area in excess of 50,000 square feet, up to a maximum of 100 percent of the table amounts. A control area separation is not required. The cumulative amounts, including amounts attained by having an additional control area, shall not exceed 30,000 gallons.

414.3 Ventilation. Rooms, areas or spaces [of Group H] in which explosive, corrosive, combustible, flammable or highly toxic dusts, mists, fumes, vapors or gases are or may be emitted due to the processing, use, handling or storage of materials shall be mechanically ventilated [as] where required by the New York City Fire Code [and] or the New York City Mechanical Code.[Ducts conveying explosives or flammable vapors, fumes or dusts shall extend directly to the exterior of the building without entering other spaces. Exhaust ducts shall not extend into or through ducts and plenums.]

[Exception: Ducts conveying vapor or fumes having flammable constituents less than 25 percent of their lower flammable limit (LFL) are permitted to pass through other spaces.]

Emissions generated at workstations shall be confined to the area in which they are generated as specified in the New York City Fire Code and the New York City Mechanical Code.

[The location of supply and exhaust openings shall be in accordance with the New York City Mechanical Code. Exhaust air contaminated by highly toxic material shall be treated in accordance with the New York City Fire Code.]

[A manual shutoff control for ventilation equipment required by this section shall be provided outside the room adjacent to the principal access door to the room. The switch shall be of the break-glass type and shall be labeled: VENTILATION SYSTEM EMERGENCY SHUTOFF.]

414.4 Hazardous material systems. Systems involving hazardous materials shall be suitable for the intended application. Controls shall be designed to prevent materials from entering or leaving process or reaction systems at other than the intended time, rate or path. Automatic controls, where provided, shall be designed to be fail safe.

414.5 Inside storage, dispensing and use. The inside storage, dispensing and use of hazardous materials [in excess of the maximum allowable quantities per control area of Tables 307.1(1) and 307.1(2)] shall be in accordance with the New York City Fire Code and Sections 414.5.1 through [414.5.5] 414.5.4 of this code.

414.5.1 Explosion control. Explosion control shall be provided in accordance with the New York City Fire Code as required by Table 414.5.1 where quantities of hazardous materials specified in that table exceed the maximum allowable quantities in Table [307.7(1)] 307.1(1) or where a structure, room or space is occupied for purposes involving explosion hazards as required by the New York City Fire Code or Section 415 of this code.

TABLE 414.5.1
EXPLOSION CONTROL REQUIREMENTSa,h

| MATERIAL | CLASS | EXPLOSION CONTROL METHODS |
| --- | --- | --- |
|  |  | Barricade construction | Explosion (deflagration) venting or explosion (deflagration) prevention systemsb |
| HAZARD CATEGORY |  |
| Combustible dustsc | — | Not Required | Required |
| Cryogenic flammables | — | Not Required | Required |
| Explosives | Division 1.1 Division 1.2 Division 1.3 Division 1.4 Division 1.5 Division 1.6 | Required Required Not Required Not Required Required Required | Not Required Not Required Required Required Not Required Not Required |
| Flammable gas | Gaseous Liquefied | Not Required Not Required | Required Required |
| Flammable liquid | IAd IBe | Not Required Not Required | Required Required |
| Organic peroxides[g] | [Unclassified detonable] U I | Required Required | Not Permitted Not Permitted |
| Oxidizer liquids and solids | 4 | Required | Not Permitted |
| [Pyrophoric materialg] | [Detonable] | [Required] | [Required] |
| Pyrophoric gas[g] | [Nondetonable]— | Not Required | Required |
| Unstable (reactive) | 4 3 Detonable 3 Nondetonable | Required Required Not Required | Not Permitted Not Permitted Required |
| Water-reactive liquids and solids[g] | 3 [Detonable] [3 Nondetonable] [2 Detonable] 2g [Nondetonable] | [Required] Not Required [Required} Not Required | [Not Permitted] Required [Not Permitted] Required |
| SPECIAL USES |  |
| [Acetylene generator rooms] | [—] | [Not Required] | [Required] |
| Grain processing | — | Not Required | Required |
| [Liquefied petroleum gas-distribution facilities] | [—] | [Not Required] | [Required] |
| Where explosion hazards existf | Detonation Deflagration | Required Not Required | Not Permitted Required |

a.	See Section 414.1.3.

b.	See the New York City Fire Code.

c.	As generated during manufacturing or processing. [See definition of “Combustible dust” in Chapter 3.]

d.	Storage or use.

e.	In open use or dispensing.

f.	Rooms containing dispensing and use of hazardous materials when an explosive environment can occur because of the characteristics or nature of the hazardous materials or as a result of the dispensing or use process.

g.	A method of explosion control shall be provided when Class 2 water-reactive materials can form potentially explosive mixtures. [Considered as explosives for the purposes of storage.]

h.	Explosion venting is not required for Group H-5 fabrication areas complying with the New York City Fire Code and Section 415.11.1 of this code.

[414.5.2 Monitor control equipment. Monitor control equipment shall be provided where required by the New York City Fire Code.]

[414.5.3 Automatic fire detection systems. Group H occupancies shall be provided with an automatic fire detection system in accordance with Section 907.2.]

[414.5.4] 414.5.2 Emergency or standby power. Where required by the New York City Fire Code or this code, mechanical ventilation, treatment systems, temperature control, alarm, detection or other electrically operated systems [are required, such systems] shall be provided with [an] emergency or standby power [system] in accordance with [Chapter 27] Section 2702. For storage and use areas for highly toxic or toxic materials, see the New York City Fire Code.

414.5.2.1 Exempt applications. Emergency or standby power is not required for the mechanical ventilation systems provided for any of the following:

[Exceptions:]

1.	[Mechanical ventilation for storage] Storage of Class IB and [Class] IC flammable and combustible liquids in closed containers not exceeding 6.5 gallons (25 L) capacity.

2.	Storage [areas for] of Class 1 and 2 oxidizers.

3.	Storage [areas for] of Class II, III, IV and V organic peroxides.

4.	[For storage, use and handling areas for highly toxic or toxic materials, see Chapter 37 of the New York City Fire Code] Storage of asphyxiant, irritant and radioactive gases.

[5.] 414.5.2.2 Fail-safe engineered systems. Standby power for mechanical ventilation, treatment systems and temperature control systems shall not be required where an approved fail-safe engineered system is installed.

[414.5.5] 414.5.3 Spill control, drainage and containment. Rooms, buildings or areas occupied for the storage of solid and liquid hazardous materials shall be provided with a means to control spillage and to contain or drain off spillage and fire protection water discharged in the storage area where required in the New York City Fire Code. The methods of spill control shall be in accordance with the New York City Fire Code.

[414.5.6] 414.5.4 Storage of medical gases. When required by the New York City Fire Code, a one-hour room shall be provided for the storage of medical gases inside of buildings, with the protected openings and ventilation provisions as required by the New York City Fire Code.

414.6 Outdoor storage, dispensing and use. The outdoor storage, dispensing and use of hazardous materials shall be in accordance with the New York City Fire Code.

414.6.1 Weather protection. Where weather protection is provided for sheltering outdoor hazardous material storage or use areas, such areas shall be considered outdoor storage or use when the weather protection structure complies with Sections 414.6.1.1 through 414.6.1.3[:].

414.6.1.1 Walls. Walls shall not obstruct more than one side of the structure.

Exception: Walls shall be permitted to obstruct portions of multiple sides of the structure, provided that the obstructed area [does] is not [exceed] greater than 25 percent of the structure’s perimeter.

414.6.1.2 Separation distance. The distance from the structure to buildings, lot lines, public ways or means of egress to a public way shall be not [be] less than the distance required for an outside hazardous material storage or use area without weather protection.

414.6.1.3 Noncombustible construction. The overhead structure shall be of approved noncombustible construction with a maximum area of 1,500 square feet (140 m2).

Exception: The [increases] maximum area is permitted to be increased as provided by Section 506[apply].

SECTION BC 415
GROUPS H-1, H-2, H-3, H-4 AND H-5

415.1 Scope. The provisions of Sections 415.1 through 415.11 shall apply to the storage and use of hazardous materials in excess of the maximum allowable quantities per control area listed in Section 307.1. Buildings and structures with an occupancy in Group H shall also comply with the applicable provisions of the New York City Fire Code and Section 414 of this code including, but not limited to, location and installation provisions.

415.2 Definitions. The following terms are defined in Chapter 2:

CONTINUOUS GAS DETECTION SYSTEM.

DETACHED BUILDING.

EMERGENCY CONTROL STATION.

EXHAUSTED ENCLOSURE.

FABRICATION AREA.

FLAMMABLE VAPORS OR FUMES.

GAS CABINET.

GAS ROOM.

HAZARDOUS PRODUCTION MATERIAL (HPM).

HPM FLAMMABLE LIQUID.

HPM ROOM.

IMMEDIATELY DANGEROUS TO LIFE AND HEALTH (IDLH).

LIQUID.

LIQUID STORAGE ROOM.

LIQUID USE, DISPENSING AND MIXING ROOM.

LOWER FLAMMABLE LIMIT (LFL).

NORMAL TEMPERATURE AND PRESSURE (NTP).

PHYSIOLOGICAL WARNING THRESHOLD LEVEL.

SERVICE CORRIDOR.

SOLID.

STORAGE, HAZARDOUS MATERIALS.

USE (MATERIAL).

WORKSTATION.

415.3 Automatic fire detection systems. Group H occupancies shall be provided with an automatic fire detection system in accordance with Section 907.2.

415.4 Automatic sprinkler system. Group H occupancies shall be equipped throughout with an automatic sprinkler system in accordance with Section 903.2.5.

[414.7] 415.5 Emergency alarms. Emergency alarms for the detection and notification of an emergency condition in Group H occupancies shall be provided as set forth herein.

[414.7.1] 415.5.1 Storage. An approved manual emergency alarm system shall be provided in buildings, rooms or areas used for storage of hazardous materials. Emergency alarm-initiating devices shall be installed outside of each interior exit or exit access door of storage buildings, rooms or areas. Activation of an emergency alarm-initiating device shall sound a local alarm to alert occupants of an emergency situation involving hazardous materials.

[414.7.2] 415.5.2 Dispensing, use and handling. Where hazardous materials having a hazard ranking of 3 or 4 in accordance with NFPA 704 are transported through corridors [or exit enclosures], interior exit stairways or ramps, or exit passageways, there shall be an emergency telephone system, a local manual alarm station or an approved alarm-initiating device at not more than 150-foot (45 720 mm) intervals and at each exit and exit access doorway throughout the transport route. The signal shall be relayed to an approved central, [station,] proprietary or remote [supervising] station service or constantly attended on-site location and shall [also] initiate a local audible alarm.

[414.7.3] 415.5.3 Supervision. Emergency alarm systems shall be supervised by an approved central, proprietary or remote station service or shall initiate an audible and visual signal at a constantly attended on-site location.

415.5.4 Emergency alarm systems. Emergency alarm systems shall be provided with emergency power in accordance with Section 2702.

[SECTION BC 415]
[GROUPS H-1, H-2, H-3, H-4 AND H-5]

[415.1 Scope. The provisions of Sections 415.1 through 415.8 shall apply to the storage and use of hazardous materials in excess of the maximum allowable quantities per control area listed in Section 307.1. Buildings and structures with an occupancy in Group H shall also comply with the applicable provisions of Section 414 and the New York City Fire Code, including, but not limited to, location and installation provisions.]

[415.2 Definitions. The following words and terms shall, for the purposes of this chapter and as used elsewhere in the code, have the meanings shown herein.]

[CONTINUOUS GAS-DETECTION SYSTEM. A gas detection system where the analytical instrument is maintained in continuous operation and sampling is performed without interruption. Analysis is allowed to be performed on a cyclical basis at intervals not to exceed 30 minutes.]

[DETACHED BUILDING. A separate single-story building, without a basement or crawl space, used for the storage, handling or use of hazardous materials and located an approved distance from other buildings and structures.]

[EMERGENCY CONTROL STATION. An approved location on the premises of a semiconductor fabrication facility staffed by trained personnel that monitor the operation of equipment and systems including alert and alarm signals.]

[EXHAUSTED ENCLOSURE. A device, typically consisting of a hood equipped with a fan, that serves to capture and exhaust fumes, mist, vapors and gases generated at a workstation or other local environment. An exhausted enclosure does not include a room provided with general ventilation.]

[FABRICATION AREA. An area within a semiconductor fabrication facility in which processes using hazardous production materials are conducted.]

[FLAMMABLE VAPORS OR FUMES. The concentration of flammable constituents in air that exceed 25 percent of their lower flammable limit (LFL).]

[GAS CABINET. A fully enclosed, noncombustible enclosure used to provide an isolated environment for compressed gas containers in storage or use, including any doors and access ports for exchanging containers and accessing pressure-regulating controls.]

[GAS ROOM. A separately ventilated, fully enclosed room in which only compressed gases and associated equipment and supplies are stored or used.]

[HAZARDOUS PRODUCTION MATERIAL (HPM). A solid, liquid or gas associated with semiconductor manufacturing that has a degree-of-hazard rating in health, flammability or instability of Class 3 or 4 as defined in NFPA 704 and that is used directly in research, laboratory or production processes which have as their end product materials that are not hazardous.]

[HPM FLAMMABLE LIQUID. An HPM liquid that is defined as either a Class I flammable liquid or a Class II or Class IIIA combustible liquid.]

[HPM ROOM. A room used in conjunction with or serving a Group H-5 occupancy, where HPM is stored or used and that is classified as a Group H-2, H-3 or H-4 occupancy.]

[IMMEDIATELY DANGEROUS TO LIFE AND HEALTH (IDLH). The concentration of air-borne contaminants that poses a threat of death, immediate or delayed permanent adverse health effects, or effects that could prevent escape from such an environment as established by the National Institute of Occupational Safety and Health (NIOSH) based on both toxicity and flammability. It generally is expressed in parts per million by volume (ppm v/v) or milligrams per cubic meter (mg/m3). If adequate data do not exist for precise establishment of IDLH concentrations, an independent certified industrial hygienist, industrial toxicologist, appropriate regulatory agency or other source approved by the Fire Commissioner shall make such determination.]

[LIQUID. A material that has a melting point that is equal to or less than 68°F (20°C) and a boiling point that is greater than 68°F (20°C) at 14.7 pounds per square inch absolute (psia) (101 kPa). When not otherwise identified, the term “liquid” includes both flammable and combustible liquids.]

[LIQUID STORAGE ROOM. A room classified as a Group H-3 occupancy used for the storage of flammable or combustible liquids in an unopened condition.]

[LIQUID USE, DISPENSING AND MIXING ROOM. A room in which Class I, II and IIIA flammable or combustible liquids are used, dispensed or mixed in open containers.]

[LOWER FLAMMABLE LIMIT (LFL). The minimum concentration of vapor in air at which propagation of flame will occur in the presence of an ignition source. The LFL is sometimes referred to as “LEL” or “lower explosive limit.”]

[NORMAL TEMPERATURE AND PRESSURE (NTP). A temperature of 70°F (21°C) and a pressure of 1 atmosphere [14.7 psia (101 kPa)].]

[PHYSIOLOGICAL WARNING THRESHOLD LEVEL. A concentration of air-borne contaminants, normally expressed in parts per million (ppm) or milligrams per cubic meter (mg/m3), that represents the concentration at which persons can sense the presence of the contaminant due to odor, irritation or other quick-acting physiological response. When used in conjunction with the permissible exposure limit (PEL) the physiological warning threshold levels are those consistent with the classification system used to establish the PEL. See the definition of “Permissible exposure limit (PEL)” in the New York City Fire Code.]

[SERVICE CORRIDOR. A fully enclosed passage other than one designated as a required means of egress, through which HPM can be moved during handling.]

[SOLID. A material that has a melting point, decomposes or sublimates at a temperature greater than 68°F (20°C).]

[WORKSTATION. A defined space within a fabrication area in which a specific function, laboratory procedure or research activity relating to semiconductor manufacture is conducted. A workstation may include equipment using HPM, hazardous materials storage cabinets, flammable liquid storage cabinets or gas cabinets, ventilation equipment, fire protection devices, detection devices, and electrical devices.]

[415.3] 415.6 Fire [Separation] separation distance. Group H occupancies shall be located on property in accordance with the other provisions of this chapter. In Groups H-2 and H-3, not less than 25 percent of the perimeter wall of the occupancy shall be an exterior wall.

Exceptions:

1.	Liquid use, dispensing and mixing rooms having a floor area of not more than 500 square feet [(47 m2)] (46.5 m2) need not be located on the outer perimeter of the building where they are in accordance with the New York City Fire Code and NFPA 30.

2.	Liquid storage rooms having a floor area of not more than 1,000 square feet (93 m2) need not be located on the outer perimeter where they are in accordance with the New York City Fire Code and NFPA 30.

3.	Spray paint booths that comply with the New York City Fire Code need not be located on the outer perimeter.

[415.3.1] 415.6.1 Group H occupancy minimum fire separation distance. Regardless of any other provisions, buildings containing Group H occupancies shall be set back to the minimum fire separation distance as set forth in [Items 1] Sections 415.6.1.1 through [4 below] 415.6.1.4. Distances shall be measured from the walls enclosing the occupancy to lot lines, including those on a public way. Distances to assumed [tax] lot lines established for the [purposes] purpose of determining exterior wall and opening protection[, in accordance with Section 705.3,] are not to be used to establish the minimum fire separation distance for buildings on sites where explosives are manufactured or used when separation is provided in accordance with the quantity distance tables specified for explosive materials in the New York City Fire Code.

[1.	] 415.6.1.1 Group H-1.[Not] Group H-1 occupancies shall be set back not less than 75 feet (22 860 mm) and not less than required by the New York City Fire Code.

Exceptions:

- Fireworks manufacturing buildings separated in accordance with NFPA 1124.

- Buildings containing the following materials when separated in accordance with Table [415.3.1] 415.6.1:

2.1.	Organic peroxides, unclassified detonable.

2.2.	Unstable reactive materials Class 4.

2.3.	Unstable reactive materials, Class 3 detonable.

2.4.	Detonable pyrophoric materials.

[2.	] 415.6.1.2 Group H-2. [Not] Group H-2 occupancies shall be set back not less than 30 feet (9144 mm) where the area of the occupancy exceeds 1,000 square feet (93 m2), and it is not required to be located in a detached building.

[3.	] 415.6.1.3 Groups H-2 and H-3. [Not] Group H-2 and H-3 occupancies shall be set back not less than 50 feet (15 240 mm) where a detached building is required (see Table [415.3.2] 415.6.2).

[4.	Groups H-2 and H-3. Occupancies containing materials with explosive characteristics shall be separated as required by the New York City Fire Code. Where separations are not specified, the distances required shall not be less than the distances required by Table 415.3.1.]

415.6.1.4 Explosive materials. Group H-2 and H-3 occupancies containing materials with explosive characteristics shall be separated as required by the New York City Fire Code. Where separations are not specified, the distances required shall not be less than the distances required by Table 415.6.1.

TABLE [415.3.1] 415.6.1
MINIMUM SEPARATION DISTANCES FOR BUILDINGS CONTAINING EXPLOSIVE MATERIALSf

| QUANTITY OF EXPLOSIVE MATERIALa,d | MINIMUM DISTANCE (feet) |
| --- | --- |
|  | Lot linesb and inhabited buildingsc | Separation of magazinese |
| Pounds over | Pounds not over | Barricaded | Unbarricaded |  |
| 0 | 5 | 70 | 140 | 12 |
| 5 | 10 | 90 | 180 | 16 |
| 10 | 20 | 110 | 220 | 20 |
| 20 | 30 | 125 | 250 | 22 |
| 30 | 40 | 140 | 280 | 24 |
| 40 | 50 | 150 | 300 | 28 |
| 50 | 75 | 170 | 340 | 30 |
| 75 | 100 | 190 | 380 | 32 |
| 100 | 125 | 200 | 400 | 36 |
| 125 | 150 | 215 | 430 | 38 |
| 150 | 200 | 235 | 470 | 42 |
| 200 | 250 | 255 | 510 | 46 |
| 250 | 300 | 270 | 540 | 48 |
| 300 | 400 | 295 | 590 | 54 |
| 400 | 500 | 320 | 640 | 58 |
| 500 | 600 | 340 | 680 | 62 |
| 600 | 700 | 355 | 710 | 64 |
| 700 | 800 | 375 | 750 | 66 |
| 800 | 900 | 390 | 780 | 70 |
| 900 | 1,000 | 400 | 800 | 72 |

For SI: 1 pound = 0.454 kg, 1 foot = 304.8 mm.

- The number of pounds of explosives listed is the number of pounds of trinitrotoluene (TNT) or the equivalent pounds of other explosive.

- The distance listed is the distance to lot line, including lot lines at public ways.

- For the purpose of this table, an inhabited building is any building on the same tax lot that is regularly occupied by people. Where two or more buildings containing explosives or magazines are located on the tax lot, each building or magazine shall comply with the minimum [distance] distances specified from inhabited buildings and, in addition, they shall be separated from each other by not less than the distance shown for “Separation of magazines,” except that the quantity of [explosives] explosive materials contained in detonator buildings or magazines shall govern in regard to the spacing of said detonator buildings or magazines from buildings or magazines containing other explosive materials. If any two or more buildings or magazines are separated from each other by less than the specified "Separation of magazines” distances, then such two or more buildings or magazines, as a group, shall be considered as one building or magazine, and the total quantity of [explosives] explosive materials stored in such group shall be treated as if the explosive were in a single building or magazine located on the site of any building or magazine of the group, and shall comply with the minimum distance specified from other magazines or inhabited buildings.

- Storage of explosives in a quantity exceeding 1,000 pounds in one magazine is prohibited.

- Magazine is a building or structure, other than an operating building, approved for storage of explosive materials. Portable or mobile magazines not exceeding 120 square feet (11 m2) in area need not comply with the requirements of this code, however, all magazines shall comply with the New York City Fire Code.

- This table shall not apply to the temporary storage incidental to transportation.

[415.3.2] 415.6.2 Detached buildings for Group H-1[and], H-2 or H-3 occupancy. The storage or use of hazardous materials in excess of those amounts listed in Table [415.3.2] 415.6.2 shall be in accordance with the applicable provisions of Sections [415.4] 415.7 and [415.5] 415.8.

##### TABLE [415.3.2] 415.6.2
[REQUIRED] DETACHED [STORAGE] BUILDING REQUIRED

| A DETACHED [STORAGE] BUILDING IS REQUIRED WHEN THE QUANTITY OF MATERIAL EXCEEDS THAT LISTED HEREIN |
| --- |
| Material | Class | Solids and Liquids (tons)a,b | Gases (cubic feet)a,b |
| Explosives | Division 1.1 Division 1.2 Division 1.3 Division 1.4 Division 1.4c Division 1.5 Division 1.6 | Maximum Allowable Quantity Maximum Allowable Quantity Maximum Allowable Quantity Maximum Allowable Quantity 1 Maximum Allowable Quantity Maximum Allowable Quantity | Not Applicable |
| Oxidizers | Class 4 | Maximum Allowable Quantity | Maximum Allowable Quantity |
| Unstable (reactives) detonable | Class 3 or 4 | Maximum Allowable Quantity | Maximum Allowable Quantity |
| [Water-reactives detonable] | [Class 2 or 3] | [Maximum Allowable Quantity] | [Not Applicable] |
| Oxidizer, liquids and solids | Class 3 Class 2 | 1,200 2,000 | Not Applicable Not Applicable |
| Organic peroxides | [Unclassified] Detonable Class I Class II Class III | Maximum Allowable Quantity Maximum Allowable Quantity 25 50 | Not Applicable Not Applicable Not Applicable Not Applicable |
| Unstable (reactives) nondetonable | Class 3 Class 2 | 1 25 | 2,000 10,000 |
| Water reactives [nondetonable] | Class 3 Class 2 | 1 25 | Not Applicable Not Applicable |
| [Pyrophoric materials detonable] | [Not Applicable] | [Maximum Allowable Quantity] | [Maximum Allowable Quantity] |
| Pyrophoric gases [and nondetonables] | Not Applicable | Not Applicable | 2,000 |

For SI: 1 ton = [2,000 pounds =] 906 kg, 1 cubic foot = 0.02832m3, 1 pound = 0.454 kg.

a.	For materials that are detonable, the distance to other buildings or lot lines shall be as specified in Table [415.3.1] 415.6.1 based on trinitrotoluene (TNT) equivalence of the material. For materials classified as explosives, see the New York City Fire Code. Unclassified detonable organic peroxides, detonable pyrophoric materials, detonable unstable (reactive) materials and detonable water-reactive materials shall be considered as explosives for the purposes of storage.

b.	“Maximum Allowable Quantity” means the maximum allowable quantity per control area set forth in Table 307.1(1).

c.	Limited to Division 1.4 materials and articles, including articles packaged for shipment, that are not regulated as an explosive under Bureau of Alcohol, Tobacco [and,] Firearms and Explosives (BATF) regulations or unpackaged articles used in process operations that do not propagate a detonation or deflagration between articles, [providing] provided the net explosive weight of individual articles does not exceed 1 pound.

415.6.2.1 Wall and opening protection. Where a detached building is required by Table [415.3.2] 415.6.2, there are no requirements for wall and opening protection based on fire separation distance.

[415.4] 415.7 Special provisions for Group H-1 occupancies. Group H-1 occupancies shall be in detached buildings used for no other purpose, shall not exceed one story in height and be without basements, crawl spaces or other under-floor spaces. Roofs shall be of lightweight construction with suitable thermal insulation to prevent sensitive material from reaching its decomposition temperature. Group H-1 occupancies containing materials that are in themselves both physical and health hazards in quantities exceeding the maximum allowable quantities per control area in Table [307.7(2)] 307.1(2) shall comply with requirements for both Group H-1 and H-4 occupancies.

[415.4.1] 415.7.1 Floors in storage rooms. Floors in storage areas for organic peroxides, pyrophoric materials and unstable (reactive) materials shall be of liquid-tight, noncombustible construction.

[415.5] 415.8 Special provisions for [Groups] Group H-2 and H-3 occupancies. Group H-2 and H-3 occupancies containing quantities of hazardous materials in excess of those set forth in Table [415.3.2] 415.6.2 shall be in detached buildings used for [no other purpose, shall not exceed one story] manufacturing, processing, dispensing, use or storage of hazardous materials. Materials listed for Group H-1 occupancies in [height and shall] Section 307.3 are permitted to be [without basements, crawl spaces or other under-floor spaces] located within Group H-2 or H-3 detached buildings provided the amount of materials per control area do not exceed the maximum allowed quantity specified in Table 307.1(1).

415.8.1 Multiple hazards. Group H-2 or H-3 occupancies containing materials that are in themselves both physical and health hazards in quantities exceeding the maximum allowable quantities per control area in Table 307.1(2) shall comply with requirements for Group H-2, H-3 or H-4 occupancies as applicable.

415.8.2 Separation of incompatible materials. Hazardous materials other than those listed in Table 415.6.2 shall be allowed in manufacturing, processing, dispensing, use or storage areas when separated from incompatible materials in accordance with the provisions of the New York City Fire Code.

415.8.3 Water reactives. Group H-2 and H-3 occupancies containing water-reactive materials shall be resistant to water penetration. Piping for conveying liquids shall not be over or through areas containing water reactives, unless isolated by approved liquid-tight construction.

Exception: Fire protection piping shall be permitted over or through areas containing water reactives without isolating it with liquid-tight construction.

[415.5.1] 415.8.4 Floors in storage rooms. Floors in storage areas for organic peroxides, oxidizers, pyrophoric materials, unstable (reactive) materials and water-reactive solids and liquids shall be of liquid-tight, noncombustible construction.

[415.5.2] 415.8.5 Waterproof room. Rooms or areas used for the storage of water-reactive solids and liquids shall be constructed in a manner that resists the penetration of water through the use of waterproof materials. Piping carrying water for other than approved automatic [fire] sprinkler systems shall not be within such rooms or areas.

[415.6] 415.9 Group H-2. Occupancies in Group H-2 shall be constructed in accordance with the New York City Fire Code and Sections [415.6.1] 415.9.1 through [415.6.4] 415.9.3 of this code.

[415.6.1 Combustible dusts, grain processing and storage. The provisions of Sections 415.6.1.1 through 415.6.1.5 shall apply to buildings in which materials that produce combustible dusts are stored or handled. Buildings that store or handle combustible dusts shall comply with the applicable provisions of NFPA 61, NFPA 69, NFPA 120, NFPA 484, NFPA 651, NFPA 654, NFPA 655, NFPA 664 and NFPA 85, and the New York City Fire Code.]

[415.6.1.1 Type of construction and height exceptions. Buildings shall be constructed in compliance with the height and area limitations of Table 503 for Group H-2; except that where erected of Type I or II construction, the heights and areas of grain elevators and similar structures shall be unlimited, and where of Type IV construction, the maximum height shall be 65 feet (19 812 mm) and except further that, in isolated areas, the maximum height of Type IV structures shall be increased to 85 feet (25 908 mm).]

[415.6.1.2 Grinding rooms. Every room or space occupied for grinding or other operations that produce combustible dusts shall be enclosed with fire barriers constructed in accordance with Section 707 or horizontal assemblies constructed in accordance with Section 712, or both. The minimum fire-resistance rating shall be 2 hours where the area is not more than 3,000 square feet (279 m2), and 4 hours where the area is greater than 3,000 square feet (279 m2).]

[415.6.1.3 Conveyors. Conveyors, chutes, piping and similar equipment passing through the enclosures of rooms or spaces shall be constructed dirt tight and vapor tight, and be of approved noncombustible materials complying with Chapter 30.]

[415.6.1.4 Explosion control. Explosion control shall be provided as specified in the New York City Fire Code, or spaces shall be equipped with the equivalent mechanical ventilation complying with the New York City Mechanical Code.]

[415.6.1.5 Grain elevators. Grain elevators, malt houses and buildings for similar occupancies shall not be located within 30 feet (9144 mm) of interior lot lines or structures on the same lot, except where erected along a railroad right-of-way.]

[415.6.1.6 Coal pockets. Coal pockets located less than 30 feet (9144 mm) from interior lot lines or from structures on the same lot shall be constructed of not less than Type IB construction. Where more than 30 feet (9144 mm) from interior lot lines, or where erected along a railroad right-of-way, the minimum type of construction of such structures not more than 65 feet (19 812 mm) in building height shall be Type IV.]

[415.6.2] 415.9.1 Flammable and combustible liquids. The storage, handling, processing and transporting of flammable and combustible liquids in [Groups] Group H-2 and H-3 occupancies shall be in accordance with the New York City Mechanical Code, the New York City Fire Code, and Sections [415.6.2.1] 415.9.1.1 through [415.6.2.10] 415.9.1.9 of this code.

[415.6.2.1] 415.9.1.1 Mixed occupancies. Where the storage tank area is located in a building of two or more occupancies and the quantity of liquid exceeds the maximum allowable quantity for one control area, the use shall be completely separated from adjacent fire areas in accordance with the requirements of Section 508.4.

[415.6.2.1.1] 415.9.1.1.1 Height exception. Where storage tanks are located within a building no more than one story above grade plane, the height limitation of Section [503] 504 shall not apply for Group H.

[415.6.2.2] 415.9.1.2 Tank protection. Storage tanks shall be noncombustible and protected from physical damage. Fire barriers or horizontal assemblies or both around the storage [tank(s)] tanks shall be permitted as the method of protection from physical damage.

[415.6.2.3] 415.9.1.2.1 Tanks. Storage tanks shall be approved tanks conforming to the requirements of the New York City Fire Code.

[415.6.2.4] 415.9.1.3 Suppression. Group H shall be equipped throughout with an approved automatic sprinkler system, installed in accordance with Section 903.

[415.6.2.5] 415.9.1.4 Leakage containment. A liquid-tight containment area compatible with the stored liquid shall be provided. The method of spill control, drainage control and secondary containment shall be in accordance with the New York City Fire Code.

Exception: Rooms where only double-wall storage tanks conforming to Section [415.6.2.3] 415.9.1.3 are used to store Class I, II and IIIA flammable and combustible liquids shall not be required to have a leakage containment area.

[415.6.2.6] 415.9.1.5 Leakage alarm. An approved automatic alarm shall be provided to indicate a leak in a storage tank and room. The alarm shall sound an audible signal, 15 dBa above the ambient sound level, at every point of entry into the room in which the leaking storage tank is located. An approved sign shall be posted on every entry door to the tank storage room indicating the potential hazard of the interior room environment, or the sign shall state: WARNING, WHEN ALARM SOUNDS, THE ENVIRONMENT WITHIN THE ROOM MAY BE HAZARDOUS. The leakage alarm shall also be supervised in accordance with Chapter 9 to transmit a trouble signal.

[415.6.2.7] 415.9.1.6 Tank vent. Storage tank vents for Class I, II or IIIA liquids shall terminate to the outdoor air in accordance with the New York City Fire Code.

[415.6.2.8] 415.9.1.7 Room ventilation. Storage tank areas storing Class I, II or IIIA liquids shall be provided with mechanical ventilation. The mechanical ventilation system shall be in accordance with the New York City Mechanical Code and the New York City Fire Code.

[415.6.2.9] 415.9.1.8 Explosion venting. Where Class I liquids are being stored, explosion venting shall be provided in accordance with the New York City Fire Code.

[415.6.2.10] 415.9.1.9 Tank openings other than vents. Tank openings other than vents from tanks inside buildings shall be designed to ensure that liquids or vapor concentrations are not released inside the building.

[415.6.3] 415.9.2 Liquefied petroleum gas-distribution facilities. The construction and installation of liquefied petroleum gas facilities shall be in accordance with the requirements of this code, the New York City Fire Code, the New York City Mechanical Code, the New York City Fuel Gas Code and NFPA 58.

[415.6.4] 415.9.3 Dry cleaning plants. The construction and installation of dry cleaning plants shall be in accordance with the requirements of this code, the New York City Mechanical Code, the New York City Plumbing Code and NFPA 32. Dry cleaning solvents and systems shall be classified in accordance with the New York City Fire Code.

[415.7] 415.10 Groups H-3 and H-4. Groups H-3 and H-4 shall be constructed in accordance with the applicable provisions of this code and the New York City Fire Code.

[415.7.1] 415.10.1 Flammable and combustible liquids. The storage, handling, processing and transporting of flammable and combustible liquids in Group H-3 occupancies shall be in accordance with Section [415.6.2] 415.9.1.

[415.7.2] 415.10.2 Gas rooms. [When] Where gas rooms are provided, such rooms shall be separated from other areas by not less than 1-hour fire barriers constructed in accordance with Section 707 or horizontal assemblies constructed in accordance with Section [712] 711, or both.

[415.7.3] 415.10.3 Floors in storage rooms. Floors in storage areas for corrosive liquids and highly toxic or toxic materials shall be of liquid-tight, noncombustible construction.

[415.7.4] 415.10.4 Separation-highly toxic solids and liquids. Highly toxic solids and liquids not stored in approved hazardous materials storage cabinets shall be isolated from other hazardous materials storage by not less than 1-hour fire-resistance rating.

[415.8 Group H-5.]

[415.8.1 General.]

415.11 Group H-5. In addition to the requirements set forth elsewhere in this code, Group H-5 shall comply with the provisions of the New York City Fire Code and Section 415.9 of this code, including, but not limited to, automatic sprinkler protection for workstations, gas cabinets, exhausted enclosures, pass-throughs in exit access corridors and exhaust ducts.

[415.8.2] 415.11.1 Fabrication areas. Fabrication areas shall comply with Sections 415.11.1.1 through 415.11.1.8.

[415.8.2.1] 415.11.1.1 Hazardous materials [in fabrication areas]. Hazardous materials and hazardous production materials (HPM) shall comply with Sections 415.11.1.1.1 through 415.11.1.1.2.

[415.8.2.1.1] 415.11.1.1.1 Aggregate quantities. The aggregate quantities of hazardous materials stored and used in a single fabrication area shall not exceed the quantities set forth in Table [415.8.2.1.1] 415.11.1.1.1.

Exception: The quantity limitations for any hazard category in Table [415.8.2.1.1] 415.11.1.1.1 shall not apply where the fabrication area contains quantities of hazardous materials not exceeding the maximum allowable quantities per control area established by Tables 307.1(1) and 307.1(2).

TABLE [415.8.2.1.1] 415.11.1.1.1
QUANTITY LIMITS FOR HAZARDOUS MATERIALS IN A SINGLE FABRICATION AREA IN GROUP H-5a

| HAZARD CATEGORY | SOLIDS (pounds per square [feet] foot) | LIQUIDS (gallons per square [feet] foot) | GAS [SCF] (cubic feet @ NTP/square [feet] foot) |
| --- | --- | --- | --- |
| PHYSICAL-HAZARD MATERIALS |
| Combustible dust | Note b | Not Applicable | Not Applicable |
| Combustible fiber | Loose Baled | Note b Notes b, c | Not Applicable | Not Applicable |
| Combustible liquid | II IIIA IIIB | Not Applicable | 0.01 0.02 Not Limited 0.04 | Not Applicable |
| Combination Class | I, II and IIIA |  |  |  |
| Cryogenic gas | Flammable Oxidizing | Not Applicable | Not Applicable | Note [c] d 1.25 |
| Explosives | Note b | Note b | Note b |
| Flammable gas | Gaseous Liquefied | Not Applicable | Not Applicable | Note [c] d Note [c] d |
| Flammable liquid | IA IB IC | Not Applicable | 0.0025 0.025 0.025 0.025 0.04 | Not Applicable |
| Combination Class | IA, IB and IC |  |  |  |
| Combination | Class I, II and IIIA |  |  |  |
| Flammable solid | 0.001 | Not Applicable | Not Applicable |
| Organic peroxide | Unclassified detonable |  | Not Applicable | Not Applicable |
|  |  | Note b |  |  |
|  | Class I | Note b |  |  |
|  | Class II | 0.025 |  |  |
|  | Class III | 0.1 |  |  |
|  | Class IV | Not Limited |  |  |
|  | Class V | Not Limited |  |  |
| Oxidizing gas | Gaseous Liquefied | Not Applicable | Not Applicable | 1.25 1.25 |
| Combination of gaseous and liquefied |  |  | 1.25 |
| Oxidizer | Class 4 Class 3 Class 2 Class 1 | Note b 0.003 0.003 0.003 0.003 | Note b 0.03 0.03 0.03 0.03 | Not Applicable |
| Combination Class | 1, 2, 3 |  |  |  |
| Pyrophoric materials | [Note b] 0.01 | 0.00125 | Notes d and e |
| Unstable (reactive) | Class 4 Class 3 Class 2 Class 1 | Note b 0.025 0.1 Not Limited | Note b 0.0025 0.01 Not Limited | Note b Note b Note b Not Limited |
| Water reactive | Class 3 Class 2 Class 1 | Note b 0.25 Not Limited | 0.00125 0.025 Not Limited | Not Applicable |

| HEALTH-HAZARD MATERIALS |
| --- |
| Corrosives | Not Limited | Not Limited | Not Limited |
| Highly toxic | Not Limited | Not Limited | Note d |
| Toxics | Not Limited | Not Limited | Note d |

For SI: 1 pound per square foot = 4.882 kg/m2, 1 gallon per square foot = 40.7 L/m2, 1 cubic foot @ NTP/square foot = 0.305 m3 @ NTP/m2 1 cubic foot = 0.02832 m3.

a.	Hazardous materials within piping shall not be included in the calculated quantities.

b.	Quantity of hazardous materials in a single fabrication shall not exceed the maximum allowable quantities per control area in Tables 307.1(1) and 307.1(2).

c.	Densely packed baled cotton that complies with the packing requirements of ISO 8115 shall not be included in this material class.

d.	The aggregate quantity of flammable, pyrophoric, toxic and highly toxic gases shall not exceed 9,000 [SCF] cubic feet at NTP.

e.	The aggregate quantity of pyrophoric gases in the building shall not exceed the amounts set forth in Table [415.3.2] 415.6.2.

[415.8.2.1.2] 415.11.1.1.2 Hazardous production materials. The maximum quantities of hazardous production materials (HPM) stored in a single fabrication area shall not exceed the maximum allowable quantities per control area established by Tables 307.1(1) and 307.1(2).

[415.8.2.2] 415.11.1.2 Separation. Fabrication areas, whose sizes are limited by the quantity of hazardous materials allowed by Table [415.8.2.1.1] 415.11.1.1.1, shall be separated from each other, from corridors[,] and from other parts of the building by not less than 1-hour fire barriers constructed in accordance with Section 707 or horizontal assemblies constructed in accordance with Section [712] 711, or both.

Exceptions:

1.	Doors within such fire barrier walls, including doors to corridors, shall be only self-closing fire door assemblies having a [fire-protection] fire protection rating of not less than 3/4 hour.

2.	Windows between fabrication areas and exit access corridors are permitted to be fixed glazing listed and labeled for a fire protection rating of [at least] not less than 3/4 hour in accordance with Section [715] 716.

[415.8.2.3] 415.11.1.3 Location of occupied levels. Occupied levels of fabrication areas shall be located at or above the first story above grade plane.

[415.8.2.4] 415.11.1.4 Floors. Except for surfacing, floors within fabrication areas shall be of noncombustible construction.

Openings through floors of fabrication areas are permitted to be unprotected where the interconnected levels are used solely for mechanical equipment directly related to such fabrication areas (see also Section [415.8.2.5] 415.11.1.5).[Floors forming a part of an occupancy separation shall be liquid tight.]

Floors forming a part of an occupancy separation shall be liquid tight.

[415.8.2.5] 415.11.1.5 Shafts and openings through floors. Elevator [shafts] hoistways, vent shafts and other openings through floors shall be enclosed [when] where required by [Section 708] Sections 712 and 713. Mechanical, duct and piping penetrations within a fabrication area shall not extend through more than two floors. The annular space around penetrations for cables, cable trays, tubing, piping, conduit or ducts shall be sealed at the floor level to restrict the movement of air. The fabrication area, including the areas through which the ductwork and piping extend, shall be considered a single conditioned environment.

[415.8.2.6] 415.11.1.6 Ventilation. Mechanical exhaust ventilation at the rate of not less than 1 cubic foot per minute per square foot [[0.0051 m3/(s · m2)]] (0.0051 m3/(s · m2)) of floor area shall be provided throughout portions of the fabrication area where HPM are used or stored. The exhaust air duct system of one fabrication area shall not connect to another duct system outside that fabrication area within the building.

A ventilation system shall be provided to capture and exhaust fumes and vapors at workstations.

Two or more operations at a workstation shall not be connected to the same exhaust system where either one or the combination of the substances removed could constitute a fire, explosion or hazardous chemical reaction within the exhaust duct system.

Exhaust ducts penetrating [occupancy separations] fire barriers constructed in accordance with Section 707 or horizontal assemblies constructed in accordance with Section 711 shall be contained in a shaft of equivalent fire-resistance-rated construction. Exhaust ducts shall not penetrate [firewalls] fire walls.

Fire dampers shall not be installed in exhaust ducts.

[415.8.2.7] 415.11.1.7 Transporting hazardous production materials to fabrication areas. [Hazardous production materials] HPM shall be transported to fabrication areas through enclosed piping or tubing systems that comply with Section [415.8.6.1] 415.11.6, through service corridors complying with Section [415.8.4] 415.11.3, or in exit access corridors as permitted in the exception to Section [415.8.3] 415.11.2. The handling or transporting of [hazardous production materials] HPM within service corridors shall comply with the New York City Fire Code.

[415.8.2.8] 415.11.1.8 Electrical.

[415.8.2.8.1 General.] Electrical equipment and devices within the fabrication area shall comply with the New York City Electrical Code. The requirements for hazardous locations need not be applied where the average air change is at least four times that set forth in Section [415.8.2.6] 415.11.1.6 and where the number of air changes at any location is not less than three times that required by Section [415.8.2.6] 415.11.1.6. The use of recirculated air shall be permitted.

[415.8.2.8.2] 415.11.1.8.1 Workstations. Workstations shall not be energized without adequate exhaust ventilation. See Section [415.8.2.6] 415.11.1.6 for workstation exhaust ventilation requirements.

[415.8.3] 415.11.2 Corridors. Corridors shall comply with Chapter 10 and shall be separated from fabrication areas as specified in Section [415.8.2.2] 415.11.1.2. Corridors shall not contain HPM [HPM] and shall not be used for transporting such materials[,] except through closed piping systems as provided in Section [415.8.6.3] 415.11.6.

Exception: Where existing fabrication areas are altered or modified, HPM [HPM] is allowed to be transported in existing corridors, subject to the following conditions:

1.	Nonproduction HPM is allowed to be transported in corridors if utilized for maintenance, lab work and testing.

[1.] 2.	Corridors. Corridors adjacent to the fabrication area where the alteration work is to be done shall comply with Section [1018] 1020 for a length determined as follows:

[1.1.] 2.1.	The length of the common wall of the corridor and the fabrication area; and

[1.2.] 2.2.	For the distance along the corridor to the point of entry of HPM into the corridor serving that fabrication area.

[2.] 3.	Emergency alarm system. There shall be an emergency telephone system, a local manual alarm station or other approved alarm-initiating device within corridors at not more than 150-foot (45 720 mm) intervals and at each exit and doorway. The signal shall be relayed to an approved central, proprietary or remote station service or the emergency control station and shall also initiate a locale audible alarm.

[3.] 4.	Pass-throughs. Self-closing doors having a fire-protection rating of not less than 1 hour shall separate pass-throughs from existing corridors. Pass-throughs shall be constructed as required for the corridors, and protected by an approved automatic fire-extinguishing system.

[415.8.4] 415.11.3 Service corridors. Service corridors within a Group H-5 occupancy shall comply with Sections 415.11.3.1 through 415.11.3.4.

[415.8.4.1 Occupancy. Service corridors shall be classified as Group H-5.]

[415.8.4.2] 415.11.3.1 Use conditions. Service corridors shall be separated from exit access corridors as required by Section [415.8.2.2] 415.11.1.2. Service corridors shall not be used as a required exit access corridor.

[415.8.4.3] 415.11.3.2 Mechanical ventilation. Service corridors shall be mechanically ventilated as required by Section [415.8.2.6] 415.11.1.6 or at not less than six air changes per hour[, whichever is greater].

[415.8.4.4] 415.11.3.3 Means of egress. The [maximum] distance of travel from any point in a service corridor to an exit, exit access corridor or door into a fabrication area shall be not [exceed] greater than 75 feet (22 860 mm). Dead ends shall be not [exceed] greater than 4 feet (1219 mm) in length. There shall be not less than two exits, and not more than one-half of the required means of egress shall require travel into a fabrication area. Doors from service corridors shall swing in the direction of egress travel and shall be self-closing.

[415.8.4.5] 415.11.3.4 Minimum width. The [minimum] clear width of a service corridor shall be not less than 5 feet (1524 mm), or 33 inches (838 mm) wider than the widest cart or truck used in the service corridor, whichever is greater.

[415.8.4.6] 415.11.3.5 Emergency alarm system. Emergency alarm systems shall be provided in accordance with this section and Sections [414.7.1] 415.5.1 and [414.7.2] 415.5.2. The maximum allowable quantity per control area provisions shall not apply to emergency alarm systems required for HPM.

[415.8.4.6.1] 415.11.3.5.1 Service corridors. An emergency alarm system shall be provided in service corridors, with [at least] no fewer than one alarm device in each service corridor.

[415.8.4.6.2] 415.11.3.5.2 Exit access corridors and exit enclosures. Emergency alarms for exit access corridors and exit enclosures shall comply with Section [414.7.2] 415.5.2.

[415.8.4.6.3] 415.11.3.5.3 Liquid storage rooms, HPM rooms and gas rooms. Emergency alarms for liquid storage rooms, HPM rooms and gas rooms shall comply with Section [414.7.1] 415.5.1.

[415.8.4.6.4] 415.11.3.5.4 Alarm-initiating devices. An approved emergency telephone system, local alarm manual pull stations, or other approved alarm-initiating devices are allowed to be used as emergency alarm-initiating devices.

[415.8.4.6.5] 415.11.3.5.5 Alarm signals. Activation of the emergency alarm system shall sound a local alarm and transmit a signal to the emergency control station.

[415.8.5] 415.11.4 Storage of hazardous production materials.

[415.8.5.1 General.] Storage of HPM in fabrication areas shall be within approved or listed storage cabinets or gas cabinets[,] or within a workstation. The storage of [hazardous production materials (HPM)] HPM in quantities greater than those listed [in Section 1804.2 of] the New York City Fire Code shall be in liquid storage rooms, HPM rooms or gas rooms as appropriate for the materials stored. The storage of other hazardous materials shall be in accordance with other applicable provisions of this code and the New York City Fire Code.

[415.8.5.2 Construction.]

[415.8.5.2.1] 415.11.5 HPM rooms [and], gas rooms, liquid storage room construction. HPM rooms [and], gas rooms and liquid shall be [separated from other areas by fire barriers] constructed in accordance with [Section 707 or horizontal assemblies constructed in accordance with Section 712, or both.  The minimum fire-resistance rating shall be 2 hours where the area is 300 square feet (27.9 m2) or more and 1-hour where the area is less than 300 square feet (27.9 m2)] Sections 415.11.5.1 through 415.11.5.9.

415.11.5.1 HPM rooms and gas rooms. HPM rooms and gas rooms shall be separated from other areas by fire barriers constructed in accordance with Section 707 or horizontal assemblies constructed in accordance with Section 711, or both. The fire-resistance rating shall be not less than 2 hours where the area is 300 square feet (27.9 m2) or more and not less than 1 hour where the area is less than 300 square feet (27.9 m2).

[415.8.5.2.2] 415.11.5.2 Liquid storage rooms. Liquid storage rooms shall be constructed in accordance with the following requirements:

- Rooms [in excess of] greater than 500 square feet (46.5 m2) in area, shall have [at least] no fewer than one exterior door approved for Fire Department access.

- Rooms shall be separated from other areas by fire barriers constructed in accordance with Section 707 or horizontal assemblies constructed in accordance with Section [712] 711, or both. The fire-resistance rating shall be [at least 1-hour] not less than 1 hour for rooms up to 150 square feet (13.9 m2) in area and not less than 2 hours where the room is more than 150 square feet (13.9 m2) in area.

- Shelving, racks and [wainscoting] wainscotting in such areas shall be of noncombustible construction or wood of not less than 1-inch (25 mm) nominal thickness or fire-retardant-treated wood complying with Section 2303.2.

- Rooms used for the storage of Class I flammable liquids shall not be located in a basement.

[415.8.5.2.3] 415.11.5.3 Floors. Except for surfacing, floors of HPM rooms and liquid storage rooms shall be of noncombustible liquid-tight construction. Raised grating over floors shall be of noncombustible materials.

[415.8.5.3] 415.11.5.4 Location. Where HPM rooms, liquid storage rooms and gas rooms are provided, they shall have [at least] no fewer than one exterior wall and such wall shall be not less than 30 feet (9144 mm) from tax-lot lines, including tax-lot lines adjacent to public ways.

[415.8.5.4] 415.11.5.5 Explosion control. Explosion control shall be provided where required by Section 414.5.1.

[415.8.5.5] 415.11.5.6 Exits. Where two exits are required from HPM rooms, liquid storage rooms and gas rooms, one shall be directly to the outside of the building.

[415.8.5.6] 415.11.5.7 Doors. Doors in a fire barrier wall, including doors to corridors, shall be self-closing fire door assemblies having a fire-protection rating of not less than 3/4 hour.

[415.8.5.7] 415.11.5.8 Ventilation. Mechanical exhaust ventilation shall be provided in liquid storage rooms, HPM rooms and gas rooms at the rate of not less than 1 cubic foot per minute per square foot [(0.044 L/S/m2)] (0.044 L/s/m2) of floor area or six air changes per hour[, whichever is greater, for categories of material].

Exhaust ventilation for gas rooms shall be designed to operate at a negative pressure in relation to the surrounding areas and direct the exhaust ventilation to an exhaust system.

[415.8.5.8] 415.11.5.9 Emergency alarm system. An approved emergency alarm system shall be provided for HPM rooms, liquid storage rooms and gas rooms.

Emergency alarm-initiating devices shall be installed outside of each interior exit door of such rooms.

Activation of an emergency alarm-initiating device shall sound a local alarm and transmit a signal to the emergency control station.

An approved emergency telephone system, local alarm manual pull stations or other approved alarm-initiating devices are allowed to be used as emergency alarm-initiating devices.

[415.8.6] 415.11.6 Piping and tubing.

[415.8.6.1 General.] Hazardous production materials piping and tubing shall comply with [Sections 416.8.6.1 through 416.8.6.4] this section and ASME B31.3.

[415.8.6.2 Supply piping and tubing.]

[415.8.6.2.1] 415.11.6.1 HPM having a health-hazard ranking of 3 or 4. Systems supplying HPM liquids or gases having a health-hazard ranking of 3 or 4 shall be welded throughout, except for connections, to the systems that are within a ventilated enclosure if the material is a gas, or an approved method of drainage or containment is provided for the connections if the material is a liquid.

[415.8.6.2.2] 415.11.6.2 Location in service corridors. Hazardous production materials supply piping or tubing in service corridors shall be exposed to view.

[415.8.6.2.3] 415.11.6.3 Excess flow control. Where HPM gases or liquids are carried in pressurized piping above 15 pounds per square inch gauge (psig) (103.4 kPa), excess flow control shall be provided. Where the piping originates from within a liquid storage room, HPM room or gas room, the excess flow control shall be located within the liquid storage room, HPM room or gas room. Where the piping originates from a bulk source, the excess flow control shall be located as close to the bulk source as practical.

[415.8.6.3] 415.11.6.4 Installations in corridors and above other occupancies. The installation of HPM piping and tubing within the space defined by the walls of exit access corridors and the floor or roof above, or in concealed spaces above other occupancies, shall be in accordance with [Section 415.8.6.2] Sections 415.11.6.1 through 415.11.6.3 and the following conditions:

1.	Automatic sprinklers shall be installed within the space unless the space is less than 6 inches (152 mm) in the least dimension.

2.	Ventilation not less than six air changes per hour shall be provided. The space shall not be used to convey air from any other area.

3.	Where the piping or tubing is used to transport HPM liquids, a receptor shall be installed below such piping or tubing. The receptor shall be designed to collect any discharge or leakage and drain it to an approved location. The 1-hour enclosure shall not be used as part of the receptor.

4.	HPM supply piping and tubing and nonmetallic waste lines shall be separated from the corridor and from occupancies other than Group H-5 by fire barriers or by an approved method or assembly that [have] has a fire-resistance rating of not less than 1 hour. [Where gypsum wallboard is used, joints on the piping side of the enclosure are not required to be taped, provided the joints occur over framing members.] Access openings into the enclosure shall be protected by approved fire-resistance-rated assemblies.

5.	Readily accessible manual or automatic remotely activated fail-safe emergency shutoff valves shall be installed on piping and tubing other than waste lines at the following locations:

5.1.	At branch connections into the fabrication area.

5.2.	At entries into exit access corridors.

Exception: Transverse crossings of the corridors by supply piping that is enclosed within a ferrous pipe or tube for the width of the corridor need not comply with Items 1 through 5.

[415.8.6.4] 415.11.6.5 Identification. Piping, tubing and HPM waste lines shall be identified in accordance with ANSI A13.1 to indicate the material being transported.

[415.8.7] 415.11.7 Continuous [gas-detection] gas detection systems. A continuous [gas-detection] gas detection system shall be provided for HPM gases [when] where the physiological warning threshold level of the gas is at a higher level than the accepted permissible exposure limit (PEL) for the gas and for flammable gases in accordance with [this section] Sections 415.11.7.1 and 415.11.7.2.

[415.8.7.1] 415.11.7.1 Where required. A continuous [gas-detection] gas detection system shall be provided in the areas identified in Sections [415.8.7.1.1] 415.11.7.1.1 through [415.8.7.1.4] 415.11.7.1.4.

[415.8.7.1.1] 415.11.7.1.1 Fabrication areas. A continuous [gas-detection] gas detection system shall be provided in fabrication areas [when] where gas is used in the fabrication area.

[415.8.7.1.2] 415.11.7.1.2 HPM rooms. A continuous [gas-detection] gas detection system shall be provided in HPM rooms [when] where gas is used in the room.

[415.8.7.1.3] 415.11.7.1.3 Gas cabinets, exhausted enclosures and gas rooms. A continuous [gas-detection] gas detection system shall be provided in gas cabinets and exhausted enclosures. A continuous [gas-detection] gas detection system shall be provided in gas rooms [when] where gases are not located in gas cabinets or exhausted enclosures.

[415.8.7.1.4] 415.11.7.1.4 Corridors. [When] Where gases are transported in piping placed within the space defined by the walls of a corridor[,] and the floor or roof above the corridor, a continuous [gas-detection] gas detection system shall be provided where piping is located and in the corridor.

Exception: A continuous [gas-detection] gas detection system is not required for occasional transverse crossings of the corridors by supply piping that is enclosed in a ferrous pipe or tube for the width of the corridor.

[415.8.7.2] 415.11.7.2 [Gas-detection] Gas detection system operation. The continuous [gas-detection] gas detection system shall be capable of monitoring the room, area or equipment in which the gas is located at or below all the following gas concentrations:

1.	Immediately dangerous to life and health (IDLH) values [when] where the monitoring point is within an exhausted enclosure, ventilated enclosure or gas cabinet.

2.	Permissible exposure limit (PEL) levels [when] where the monitoring point is in an area outside an exhausted enclosure, ventilated enclosure or gas cabinet.

3.	For flammable gases, the monitoring detection threshold level shall be vapor concentrations in excess of 25 percent of the lower flammable limit (LFL) [when] where the monitoring is within or outside an exhausted enclosure, ventilated enclosure or gas cabinet.

4.	Except as noted in this section, monitoring for highly toxic and toxic gases shall also comply with [Chapter 37 of] the New York City Fire Code.

[415.8.7.2.1] 415.11.7.2.1 Alarms. The gas detection system shall initiate a local alarm and transmit a signal to the emergency control station when a short-term hazard condition is detected. The alarm shall be both visual and audible and shall provide warning both inside and outside the area where the gas is detected. The audible alarm shall be distinct from all other alarms.

[415.8.7.2.2] 415.11.7.2.2 Shutoff of gas supply. The gas detection system shall automatically close the shutoff valve at the source on gas supply piping and tubing related to the system being monitored for which gas is detected when a short-term hazard condition is detected. Automatic closure of shutoff valves shall comply with the following:

1.	Where the gas detection sampling point initiating the gas detection system alarm is within a gas cabinet or exhausted enclosure, the shutoff valve in the gas cabinet or exhausted enclosure for the specific gas detected shall automatically close.

2.	Where the gas detection sampling point initiating the gas detection system alarm is within a room and compressed gas containers are not in gas cabinets or an exhausted enclosure, the shutoff valves on all gas lines for the specific gas detected shall automatically close.

3.	Where the gas detection sampling point initiating the gas detection system alarm is within a piping distribution manifold enclosure, the shutoff valve supplying the manifold for the compressed gas container of the specific gas detected shall automatically close.

Exception: Where the [gas-detection] gas detection sampling point initiating the gas detection system alarm is at the use location or within a gas valve enclosure of a branch line downstream of a piping distribution manifold, the shutoff valve for the branch line located in the piping distribution manifold enclosure shall automatically close.

[415.8.8] 415.11.8 Manual fire alarm system. An approved manual fire alarm system shall be provided throughout buildings containing Group H-5. Activation of the alarm system shall initiate a local alarm and transmit a signal to the emergency control station. The fire alarm system shall be designed and installed in accordance with Section 907.

[415.8.9] 415.11.9 Emergency control station. An emergency control station shall be provided in accordance with Sections [415.8.9.1] 415.11.9.1 through [415.8.9.3] 415.11.9.3.

[415.8.9.1] 415.11.9.1 Location. The emergency control station shall be located on the premises at an approved location outside the fabrication area.

[415.8.9.2] 415.11.9.2 Staffing. Trained personnel shall continuously staff the emergency control station.

[415.8.9.3] 415.11.9.3 Signals. The emergency control station shall monitor signals from emergency equipment and alarm and detection systems. Such emergency equipment and alarm and detection systems shall include the following systems, whether required by this code or the New York City Construction Codes or voluntarily installed:

1.	Automatic sprinkler system alarm and monitoring systems.

2.	Manual fire alarm systems.

3.	Emergency alarm systems.

4.	Continuous gas detection systems.

5.	Smoke detection systems.

6.	Emergency power system.

7.	Automatic detection and alarm systems for pyrophoric liquids and Class 3 water-reactive liquids required in [Section 1803 of] the New York City Fire Code.

8.	Exhaust ventilation flow alarm devices for pyrophoric liquids and Class 3 water-reactive liquids cabinet exhaust ventilation systems required in [Section 1803 of] the New York City Fire Code.

[415.8.10] 415.11.10 Emergency power system. An emergency power system shall be provided in Group H-5 occupancies [where required] in accordance with Section [415.8.10.1] 2702. The emergency power system shall [be designed to] supply power automatically to [required] the electrical systems specified in Section 415.11.10.1 when the normal electrical supply system is interrupted.

[415.8.10.1] 415.11.10.1 Required electrical systems. Emergency power shall be provided for electrically operated equipment and connected control circuits for the following systems:

1.	HPM exhaust ventilation systems.

2.	HPM gas cabinet ventilation systems.

3.	HPM exhausted enclosure ventilation systems.

4.	HPM gas room ventilation systems.

5.	HPM gas detection systems.

6.	Emergency alarm systems.

7.	Manual and automatic fire alarm systems.

8.	Automatic sprinkler system monitoring and alarm systems.

9.	Automatic alarm and detection systems for pyrophoric liquids and Class 3 water-reactive liquids required in [Section 1803 of] the New York City Fire Code.

10.	Flow alarm switches for pyrophoric liquids and Class 3 water-reactive liquids cabinet exhaust ventilation systems required in [Section 1803 of] the New York City Fire Code.

11.	Electrically operated systems required elsewhere in this code applicable to the use, storage or handling of HPM.

[415.8.10.2] 415.11.10.2 Exhaust ventilation systems.  Exhaust ventilation systems are allowed to be designed to operate at not less than one-half the normal fan speed on the emergency power system where it is demonstrated that the level of exhaust will maintain a safe atmosphere.

[415.8.11] 415.11.11 Automatic sprinkler system protection in exhaust ducts for HPM.

[415.8.11.1 Exhaust ducts for HPM.] An approved automatic fire sprinkler system shall be provided in exhaust ducts conveying vapors, fumes, mists or dusts generated from HPM in accordance with [this section and] the New York City Mechanical Code and Sections 415.11.11.1 through 415.11.11.3 of this code.

[415.11.2] 415.11.11.1 Metallic and noncombustible[,] nonmetallic exhaust ducts. An approved automatic sprinkler system shall be provided in metallic and noncombustible nonmetallic exhaust ducts [when] where all of the following conditions apply:

1.	Where the largest cross-sectional diameter is equal to or greater than 10 inches (254 mm).

2.	The ducts are within the building.

3.	The ducts are conveying flammable gases, vapors or fumes.

[415.8.11.3] 415.11.11.2 Combustible nonmetallic exhaust ducts. Automatic fire sprinkler system protection shall be provided in combustible nonmetallic exhaust ducts where the largest cross-sectional diameter of the duct is equal to or greater than 10 inches (254 mm).

[Exceptions:] Exception: Ducts need not be provided with automatic sprinkler protection as follows:

1.	Ducts listed or approved for applications without automatic [fire] sprinkler system protection.

2.	Ducts not more than 12 feet (3658 mm) in length installed below ceiling level.

[415.8.11.4] 415.11.11.3 Automatic sprinkler locations.  Sprinkler systems shall be installed at 12-foot (3658 mm) intervals in horizontal ducts and at changes in direction. In vertical ducts, sprinklers shall be installed at the top and at alternate floor levels.

SECTION BC 416
APPLICATION OF FLAMMABLE FINISHES

416.1 General. The provisions of this section shall apply to the construction, installation and use of buildings and structures, or parts thereof, for the [spraying] application of flammable paints, varnishes and lacquers or other flammable materials or mixtures or compounds used for painting, varnishing, staining or similar purposes. Such construction and equipment shall comply with the New York City Fire Code.

416.2 Spray rooms. Spray rooms shall be enclosed with not less than 2-hour fire barriers constructed in accordance with Section 707[,] or horizontal assemblies constructed in accordance with Section [712] 711, or both. [The enclosure shall be at least 2-hour fire-resistance rated.] Floors shall be waterproofed and drained in an approved manner.

416.2.1 Surfaces. The interior surfaces of spray rooms shall be smooth and shall be so constructed to permit the free passage of exhaust air from all parts of the interior and to facilitate washing and cleaning, and shall be so designed to confine residues within the room. Aluminum shall not be used.

416.2.2 Ventilation. Mechanical ventilation and interlocks with the spraying operation shall be in accordance with the New York City Mechanical Code.

416.3 Spraying spaces. Spraying spaces shall be ventilated with an exhaust system capable of at least six air changes per hour to prevent the accumulation of flammable mist or vapors in accordance with the New York City Mechanical Code. Where such spaces are not separately enclosed, noncombustible spray curtains shall be provided to restrict the spread of flammable vapors.

416.3.1 Surfaces. The interior surfaces of spraying spaces shall be smooth and continuous without edges[, and]; shall be so constructed to permit the free passage of exhaust air from all parts of the interior and to facilitate washing and cleaning; and shall be so designed to confine residues within the spraying space. Aluminum shall not be used.

416.4 Spray booths. Spray booths shall be designed, constructed and operated in accordance with the New York City Fire Code.

416.5 Fire protection. An automatic sprinkler system or fire-extinguishing system shall be provided in all spray, dip and immersing spaces and storage rooms[,] and shall be installed in accordance with Chapter 9.

SECTION BC 417
DRYING ROOMS

417.1 General. A drying room or dry kiln installed within a building shall be constructed entirely of approved noncombustible materials or assemblies of such materials regulated by the approved rules or as required in the general and specific sections of [Chapter 4] this chapter for special occupancies, where applicable to the general requirements of Chapter 28, and in accordance with the New York City Fire Code.

417.2 Piping clearance. Overhead heating pipes shall have a clearance of not less than 2 inches (51 mm) from combustible contents in the dryer.

417.3 Insulation. Where the operating temperature of the dryer is 175°F (79°C) or more, metal enclosures shall be insulated from adjacent combustible materials by not less than 12 inches (305 mm) of airspace, or the metal walls shall be lined with 1/4-inch (6.4 mm) insulating mill board or other approved equivalent insulation.

417.4 Fire protection. Drying rooms designed for high-hazard materials and processes, including special occupancies as provided for in [Chapter 4] this chapter, shall be protected by an approved automatic [sprinkler or] fire-extinguishing system [conforming to] complying with the provisions of Chapter 9.

SECTION BC 418
ORGANIC COATINGS

418.1 Building features. Manufacturing of organic coatings shall be done only in buildings that do not have pits or basements and shall comply with the New York City Fire Code. Such buildings shall be protected by an approved automatic sprinkler system in accordance with Chapter 9 of this code.

418.2 Location. Organic coating manufacturing operations and operations incidental to or connected therewith shall not be located in buildings having other occupancies.

418.3 Process mills. Mills operating with close clearances and that process flammable and heat-sensitive materials, such as nitrocellulose, shall be classified as Group H-1 occupancy.

418.4 Tank storage. Storage areas for flammable and combustible liquid tanks inside of structures shall be located at or above grade and shall be separated from the processing area by not less than 2-hour fire-resistance-rated fire barriers constructed in accordance with Section 707 or horizontal assemblies constructed in accordance with Section [712] 711, or both.

418.5 Nitrocellulose storage. Nitrocellulose storage shall be located on a detached pad or in a separate structure or a room enclosed with no less than 2-hour fire-resistance-rated fire barriers.

418.6 Finished products. Storage rooms for finished products that are flammable or combustible liquids shall be separated from the processing area by fire barriers constructed in accordance with Section 707 or horizontal assemblies constructed in accordance with Section [712] 711, or both having a fire-resistance rating of at least 2 hours, and openings in the walls shall be protected with approved opening protectives.

SECTION 419
RESERVED

SECTION BC 420
GROUPS I-1, R-1, R-2, R-3

420.1 General. Occupancies in Groups I-1, R-1, R-2 and R-3 shall comply with the provisions of [this section] Sections 420.1 through 420.6 and other applicable provisions of this code.

420.2 Separation walls. Walls separating dwelling units in the same building, walls separating sleeping units in the same building and walls separating dwelling or sleeping units from other occupancies contiguous to them in the same building shall be constructed as fire barriers constructed in accordance with Section 707 and shall be at least 1-hour fire-resistance-rated.

420.3 Horizontal separation. Floor assemblies separating dwelling units in the same buildings, floor assemblies separating sleeping units in the same building and floor assemblies separating dwelling or sleeping units from other occupancies contiguous to them in the same building shall be constructed as horizontal assemblies in accordance with Section [712] 711.

420.4 Reserved.

420.5 Automatic sprinkler system. Group R occupancies shall be equipped throughout with an automatic sprinkler system in accordance with Section 903.2.8. Group I-1 occupancies shall be equipped throughout with an automatic sprinkler system in accordance with Section 903.2.6. Quick response or residential automatic sprinklers shall be installed in accordance with Section 903.3.2.

420.6 Fire alarm systems and smoke alarms.  Fire alarm systems and smoke alarms shall be provided in Group I-1, R-1, and R-2 occupancies in accordance with Sections 907.2.6, 907.2.8 and 907.2.9, respectively. Single or multiple station smoke alarms shall be provided in Groups I-1, R-2, and R-3 in accordance with Section 907.2.11.

SECTION BC 421
[RESERVED]
HYDROGEN FUEL GAS ROOMS

421.1 General. Where required by the New York City Fire Code, hydrogen fuel gas rooms shall be designed and constructed in accordance with Sections 421.1 through 421.7.

421.1.1 Scope. Hydrogen fuel gas rooms shall be separately ventilated, fully enclosed, and shall contain all equipment and piping for the immediate on-premises use of hydrogen in indoor fuel cells or other energy production process, and incidental indoor storage of gaseous hydrogen in accordance with the New York City Fire Code. A hydrogen fuel gas room shall not be used to house production or dispensing of hydrogen motor fuel.

421.1.2 Storage. Hydrogen fuel gas rooms shall not be used for storage of gaseous hydrogen in quantities exceeding the maximum allowable quantity per control area set forth in Table 307.1(1). Where approved by the Fire Department, such hydrogen fuel gas rooms permitted to store greater quantities shall be classified as Occupancy Group H.

421.1.3 Definitions. The following term is defined in Chapter 2:

HYDROGEN FUEL GAS ROOM.

421.2 Location. Hydrogen fuel gas rooms shall not be located below grade.

421.3 Design and construction. Hydrogen fuel gas rooms not classified as Occupancy Group H shall be separated from other areas of the building in accordance with Section 509.1. Such separation shall have a fire-resistance rating of not less than 2 hours for all occupancy groups.

421.3.1 Pressure control. Hydrogen fuel gas rooms shall be provided with a ventilation system designed to maintain the room at a negative pressure in relation to surrounding area.

421.3.2 Windows. Operable windows in interior walls shall not be permitted. Fixed windows shall be permitted where in accordance with Section 716.

421.4 Exhaust ventilation. Hydrogen fuel gas rooms shall be separately ventilated and provided with mechanical exhaust ventilation in accordance with the applicable provisions of NFPA 2.

421.5 Gas detection system. Hydrogen fuel gas rooms shall be provided with a gas detection system that complies with Sections 421.5.1, 421.5.2, and 918.

421.5.1 System activation. Activation of a gas detection alarm shall initiate the following notification and action:

1.	Initiation of distinct audible and visible alarm signals both inside and outside of the hydrogen fuel gas room.

2.	Automatic activation of the mechanical exhaust ventilation system.

421.5.2 Failure of the gas detection system. Failure of the gas detection system shall automatically discontinue hydrogen generation, activate the mechanical exhaust ventilation system and transmit a supervisory signal to the control panel and a central station.

421.6 Explosion control. Explosion control shall be provided where required by Section 414.5.1.

421.7 Emergency power. Mechanical exhaust ventilation and gas detection systems shall be provided with an emergency power system in accordance with Section 2702.

SECTION BC 422
AMBULATORY [HEALTH] CARE FACILITIES

422.1 General. [Occupancies classified as Group B ambulatory] Ambulatory [health] care facilities shall comply with the provisions of Sections 422.1 through [422.6] 422.5 and other applicable provisions of this code.

422.2 Separation. Ambulatory care facilities where the potential for four or more care recipients are to be incapable of self-preservation at any time, whether rendered incapable by staff or staff accepted responsibility for a care recipient already incapable, shall be separated from adjacent spaces, corridors or tenants with a fire partition installed in accordance with Section 708.

422.3 Smoke [barriers] compartments. [Smoke barriers shall be provided to subdivide every] Where the aggregate area of one or more ambulatory care [facility] facilities is greater than 10,000 square feet (929 m2) on one story, the story shall be provided with a smoke barrier to subdivide the story into [a minimum of] no fewer than two smoke compartments [per story]. The [travel] area of any one such smoke compartment shall be not greater than 22,500 square feet (2092 m2). The distance of travel from any point in a smoke compartment to a smoke barrier door shall be not [exceed] greater than 200 feet (60 960 mm). The smoke barrier shall be installed in accordance with Section [710] 709 with the exception that smoke barriers shall be continuous from outside wall to an outside wall, a floor to a floor, or from a smoke barrier to a smoke barrier or a combination thereof.

422.3.1 Means of egress. Where ambulatory care facilities require smoke compartmentation in accordance with Section 422.3, the fire protection and emergency preparedness plans shall comply with the applicable provisions of the New York City Fire Code and shall be in accordance with Section 1001.4 of this code.

[422.3] 422.3.2 Refuge area. [At least] Not less than 30 net square feet (2.8 m2) [per] for each nonambulatory [patient] care recipient shall be provided within the aggregate area of corridors, [patient] care recipient rooms, treatment rooms, lounge or dining areas and other low-hazard areas [on each side of each smoke barrier] within each smoke compartment. Each occupant of an ambulatory care facility shall be provided with access to a refuge area without passing through or utilizing adjacent tenant spaces.

[422.4] 422.3.3 Independent egress. A means of egress shall be provided from each smoke compartment created by smoke barriers without having to return through the smoke compartment from which means of egress originated.

[422.5] 422.4 Automatic sprinkler systems. Automatic sprinkler systems shall be provided for ambulatory care facilities in accordance with Section 903.2.2.

[422.6] 422.5 Fire alarm systems. A fire alarm system shall be provided for ambulatory care facilities in accordance with Section [907.2.2.1] 907.2.2.

SECTION BC 423
STORM SHELTERS

423.1 General. In addition to other applicable requirements in this code, storm shelters shall be constructed in accordance with [ICC-500] ICC 500.

423.1.1 Scope. This section applies to the construction of storm shelters constructed as separate detached buildings or constructed as safe rooms within buildings for the purpose of providing safe refuge from storms that produce high winds, such as tornados and hurricanes. Such structures shall be designated to be hurricane shelters, tornado shelters, or combined hurricane and tornado shelters.

423.2 Definitions specific to this section. The following [words and] terms shall, for the purposes of this [chapter and as used elsewhere in this code] section, have the meanings shown herein[.]:

STORM SHELTER. A building, structure or portion(s) thereof, constructed in accordance with ICC 500 and designated for use during a severe wind storm event, such as a hurricane or tornado.

[COMMUNITY STORM SHELTER] Community storm shelter. A storm shelter not defined as a "Residential [Storm Shelter] storm shelter."

[RESIDENTIAL STORM SHELTER] Residential storm shelter. A storm shelter serving occupants of dwelling units and having an occupant load not exceeding 16 persons.

§ xx.  Section 424 of Chapter 4 of the New York city building code is added to read as follows:

SECTION 424
CHILDREN’S PLAY STRUCTURES

424.1 Children’s play structures. Children’s play structures installed inside all occupancies covered by this code that exceed 10 feet (3048 mm) in height and 150 square feet (14 m2) in area shall comply with Sections 424.2 through 424.5.

424.2 Materials. Children’s play structures shall be constructed of noncombustible materials or of combustible materials that comply with the following:

1.	Fire-retardant-treated wood complying with Section 2303.2.

2.	Light-transmitting plastics complying with Section 2606.

3.	Foam plastics (including the pipe foam used in soft-contained play equipment structures) having a maximum heat-release rate not greater than 100 kilowatts when tested in accordance with UL 1975 or when tested in accordance with NFPA 289, using the 20 kW ignition source.

4.	Aluminum composite material (ACM) meeting the requirements of Class A interior finish in accordance with Chapter 8 when tested as an assembly in the maximum thickness intended for use.

5.	Textiles and films complying with the fire propagation performance criteria contained in Test Method 1 or Test Method 2, as appropriate, of NFPA 701.

6.	Plastic materials used to construct rigid components of soft-contained play equipment structures (such as tubes, windows, panels, junction boxes, pipes, slides and decks) exhibiting a peak rate of heat release not exceeding 400 kW/m2 when tested in accordance with ASTM E 1354 at an incident heat flux of 50 kW/m2 in the horizontal orientation at a thickness of 6 mm.

7.	Ball pool balls, used in soft-contained play equipment structures, having a maximum heat-release rate not greater than 100 kilowatts when tested in accordance with UL 1975 or when tested in accordance with NFPA 289, using the 20 kW ignition source. The minimum specimen test size shall be 36 inches by 36 inches (914 mm by 914 mm) by an average of 21 inches (533 mm) deep, and the balls shall be held in a box constructed of galvanized steel poultry netting wire mesh.

8.	Foam plastics shall be covered by a fabric, coating or film meeting the fire propagation performance criteria contained in Test Method 1 or Test Method 2, as appropriate, of NFPA 701.

9.	The floor covering placed under the children’s play structure shall exhibit a Class I interior floor finish classification, as described in Section 804, when tested in accordance with NFPA 253.

424.3 Fire protection. Children’s play structures shall be provided with the same level of approved fire protection system required for other structures in the same occupancy.

424.4 Separation. Children’s play structures shall have a horizontal separation from building walls, partitions and from elements of the means of egress of not less than 5 feet (1524 mm). Children’s playground structures shall have a horizontal separation from other children’s play structures of not less than 20 feet (6090 mm).

424.5 Area limits. Children’s play structures shall be not greater than 300 square feet (28 m2) in area.

§ xx.  Section 425 of Chapter 4 of the New York city building code is added to read as follows:

SECTION BC 425
HYPERBARIC FACILITIES

425.1 Hyperbaric facilities. Hyperbaric facilities shall meet the requirements contained in Chapter 14 of NFPA 99.

§ xx.  Section 426 of Chapter 4 of the New York city building code is added to read as follows:

SECTION 426
COMBUSTIBLE DUSTS, GRAIN PROCESSING AND STORAGE

426.1 Combustible dusts, grain processing and storage. The provisions of Sections 426.1.1 through 426.1.7 shall apply to buildings in which materials that produce combustible dusts are stored or handled. Buildings that store or handle combustible dusts shall comply with the applicable provisions of NFPA 61, NFPA 69, NFPA 85, NFPA 120, NFPA 484, NFPA 654, NFPA 655 and NFPA 664 and the New York City Fire Code.

426.1.1 Type of construction and height exceptions. Buildings shall be constructed in compliance with the height, number of stories and area limitations specified in Sections 504 and 506; except that where erected of Type I or II construction, the heights and areas of grain elevators and similar structures shall be unlimited, and where of Type IV construction, the maximum building height shall be 65 feet (19 812 mm) and except further that, in isolated areas, the maximum building height of Type IV structures shall be increased to 85 feet (25 908 mm).

426.1.2 Grinding rooms. Every room or space occupied for grinding or other operations that produce combustible dusts in such a manner that the room or space is classified as a Group H-2 occupancy shall be enclosed with fire barriers constructed in accordance with Section 707 or horizontal assemblies constructed in accordance with Section 711, or both. The fire-resistance rating of the enclosure shall be not less than 2 hours where the area is not more than 3,000 square feet (279 m2), and not less than 4 hours where the area is greater than 3,000 square feet (279 m2).

426.1.3 Conveyors. Conveyors, chutes, piping and similar equipment passing through the enclosures of rooms or spaces shall be constructed dirt tight and vapor tight, and be of approved noncombustible materials complying with Chapter 30.

426.1.4 Explosion control. Explosion control shall be provided as specified in the New York City Fire Code, or spaces shall be equipped with the equivalent mechanical ventilation complying with the New York City Mechanical Code.

426.1.5 Grain elevators. Grain elevators, malt houses and buildings for similar occupancies shall not be located within 30 feet (9144 mm) of interior lot lines or structures on the same lot, except where erected along a railroad right-of-way.

426.1.6 Coal pockets. Coal pockets located less than 30 feet (9144 mm) from interior lot lines or from structures on the same lot shall be constructed of not less than Type IB construction. Where more than 30 feet (9144 mm) from interior lot lines, or where erected along a railroad right-of-way, the minimum type of construction of such structures not more than 65 feet (19 812 mm) in building height shall be Type IV.

426.1.7 Tire rebuilding. Buffing operations shall be located in a room separated from the remainder of the building housing the tire rebuilding or tire recapping operation by a 1-hour fire barrier.

Exception: Buffing operations are not required to be separated where all of the following conditions are met:

1.	Buffing operations are equipped with an approved continuous automatic water-spray system directed at the point of cutting action;

2.	Buffing machines are connected to particle-collecting systems providing a minimum air movement of 1,500 cubic feet per minute (cfm) (0.71 m3/5 ) in volume and 4,500 feet per minute (fpm) (23 m/s) in-line velocity; and

3.	The collecting system shall discharge the rubber particles to an approved outdoor noncombustible or fire-resistant container, which is emptied at frequent intervals to prevent overflow.

§ xx.  Section 424 of Chapter 4 of the New York city building code, as renumbered and amended by local law number 141 for the year 2013, is renumbered and amended to read as follows:

SECTION BC [424] 427
NONPRODUCTION CHEMICAL LABORATORIES

[424.1] 427.1 General. The provisions of this section shall govern the design, construction and chemical quantity limitations of buildings and portions thereof occupied or designed to be occupied as a nonproduction laboratory. Nonproduction laboratories shall be classified into occupancy groups in accordance with Section [424.5] 427.5. The provisions of this section shall not apply to production laboratories classified in Occupancy Group F or H.

[424.2] 427.2 Standards. Except as otherwise provided in this section, nonproduction laboratories shall meet the design, construction and chemical quantity limitation requirements for laboratory unit fire hazard Class D, as set forth in NFPA 45 as modified by the New York City Fire Code, and the New York City Mechanical Code. The storage arrangement, handling and use of chemicals within nonproduction laboratories and accessory storage rooms, and the operation and maintenance of nonproduction laboratories shall comply with the requirements of the New York City Fire Code, and the rules of the [fire commissioner] Fire Commissioner.

[424.3] 427.3 Prohibitions. It shall be unlawful in any nonproduction laboratory to:

- Store or use any explosive.

- Store or use any unclassified detonable organic peroxide, detonable pyrophoric material, detonable unstable (reactive) material or detonable water-reactive material.

- Store or use any Class 4 unstable (reactive) material.

- Store or use any Class 4 oxidizing material.

- Store or use any flammable gas below grade.

[424.4] 427.4 Definitions specific to this section. The following [words and] terms shall, for the purposes of this section,[and as used elsewhere in this code,] have the meanings shown herein[.]:

LABORATORY BUILDING. A structure consisting wholly or principally of one or more laboratory units.

LABORATORY CHEMICAL. A material with a health, flammability, or instability hazard rating of 2, 3, or 4 as defined in NFPA 704.

LABORATORY, NONPRODUCTION. A building or portion thereof wherein chemicals or gases are used or synthesized on a nonproduction basis for testing, research, experimental, instructional or educational purposes.

LABORATORY UNIT. An enclosed space of a minimum 1-hour fire-rated construction, designed or used as a nonproduction laboratory. Laboratory units may include one or more separate laboratory work areas, and accessory storage rooms or spaces within or contiguous with the laboratory unit, such as offices and lavatories.

STORAGE CABINET. A cabinet designed and constructed in accordance with UL 1275, and used for the storage of not more than 60 gallons (227 L) of flammable and combustible liquids.

STORAGE ROOM. A room where laboratory chemicals or gases are stored and not otherwise used or synthesized.

[424.5] 427.5 Classification. Buildings or portions thereof occupied as a nonproduction laboratory may be classified as a Group B occupancy provided they comply with the provisions of Section [424] 427. Nonproduction laboratories not in compliance with the provisions of Section [424.7] 427.7 for laboratory chemical quantity limitations shall be classified as Group H occupancy.

[424.5.1] 427.5.1 Accessory use nonproduction laboratories. Accessory use nonproduction laboratories occupying an area not more than 10 percent of the area of the story in which such laboratories are located and not exceeding the tabular values in [Table 503] Sections 504 and 506, for the allowable height or area for such use shall be classified according to the main occupancy. Such accessory nonproduction laboratories shall comply with the provisions of Section [424] 427.

[424.6] 427.6 Fire protection. Fire protection systems in nonproduction laboratories shall be provided in accordance  with Section 427.6.1 through 427.6.3.

[424.6.1] 427.6.1 Sprinkler system. Laboratory units shall be provided throughout with an automatic sprinkler system in accordance with Section 903.3.1.1. The entire building shall be provided throughout with an automatic sprinkler system when the aggregate floor area of all laboratory units within any building exceeds 20,000 square feet (1858 m2).

[424.6.2] 427.6.2 Standpipe and hose system. In all nonproduction laboratory buildings that are two or more stories above or below the grade level (level of exit discharge), standpipes shall be installed in accordance with Section 905.2.

[424.6.3] 427.6.3 Fire alarm system. A manual fire alarm system shall be installed in accordance with Section 907.2.2, 907.2.3, or 907.2.6, as applicable.

[424.7] 427.7 Quantity limitations. Quantity limitations in nonproduction laboratories shall be provided in accordance  with Section 427.7.1 through 427.7.10.

[424.7.1] 427.7.1 Flammable and combustible liquids. The density and total quantity of flammable and combustible liquids allowed within a laboratory unit, outside of storage rooms, shall comply with Table [10.1.1] 9.1.1(A) of NFPA 45, as modified by the New York City Fire Code, for laboratory unit fire hazard Class D.

Exceptions: The following exceptions apply to other than educational or instructional laboratories:

- The density of flammable and combustible liquids allowed within a laboratory unit may be increased to those set forth in Table [10.1.1] 9.1.1(A) of NFPA 45 as modified by the New York City Fire Code, for laboratory unit fire hazard Class B provided the total quantity of flammable and combustible liquid, including any in storage cabinets or safety cans, does not exceed 25 gallons (95 L).

- The density of flammable and combustible liquids allowed within a laboratory unit may be increased to those set forth in Table [10.1.1] 9.1.1(A) of NFPA 45 as modified by the New York City Fire Code, for laboratory unit fire hazard Class B provided the total quantity of flammable and combustible liquid, including any in storage cabinets or safety cans, does not exceed 30 gallons (114 L) and the walls, floors and ceilings of the laboratory unit are separated from all adjoining areas by 2-hour fire-rated construction.

- Based on a density of 1 gallon per 100 square feet (3.785 L per 9.3 m2) of area, the quantity of flammable and combustible liquid allowed within a laboratory unit, excluding quantities in storage cabinets or safety cans, may be increased to 100 gallons (379 L), and the total quantities of flammable and combustible liquids, including quantities in storage cabinets or safety cans, may be increased to 200 gallons [(775 L)] (757 L) provided the walls, floors and ceilings of the laboratory unit are separated from all adjoining areas by 2-hour fire-rated construction.

[424.7.2] 427.7.2 Flammable solids. The total quantity of flammable solids allowed within a laboratory unit, excluding any quantities in a storage room, shall not exceed 10 pounds (4.5 kg).

Exception: The total quantity of flammable solids allowed within a laboratory unit that is provided with walls, floors and ceilings that separate the laboratory unit from all adjoining areas by 2-hour fire-rated construction shall not exceed 15 pounds (6.8 kg).

[424.7.3] 427.7.3 Oxidizers and organic peroxides. The total quantity of solid and liquid oxidizers and organic peroxides combined allowed within a laboratory unit, excluding any quantities in a storage room, shall not exceed 40 pounds (18 kg), provided not more than 2 pounds (0.908 kg) of which are Class 3 oxidizers and 1 pound (0.454 kg) of which is Class I organic peroxides.

Exception: The total quantity of solid and liquid oxidizers and organic peroxides combined allowed within a laboratory unit that is provided with walls, floors and ceilings that separate the laboratory unit from all adjoining areas by 2-hour fire rated construction shall not exceed 50 pounds (23 kg), provided not more than 2 pounds (0.908 kg) of which is Class 3 oxidizers and 1 pound (0.454 kg) of which are Class I organic peroxides.

[424.7.4] 427.7.4 Unstable (reactive). The total quantity of unstable (reactive) material allowed within a laboratory unit, excluding any quantities in a storage room, shall not exceed 6 pounds (2.7 kg), provided not more than 1 pound (0.454 kg) of which is Class 3 unstable (reactive).

Exception: The total quantity of unstable (reactive) material allowed within a laboratory unit that is provided with walls, floors and ceilings that separate the laboratory unit from all adjoining areas by 2-hour fire-rated construction shall not exceed 12 pounds (5.4 kg), provided not more than 1 pound (0.454 kg) of which is Class 3 unstable (reactive).

[424.7.5] 427.7.5 Water reactive material. The total quantity of water reactive material allowed within a laboratory unit, excluding any quantities in a storage room, shall not exceed 2.5 pounds (1.1 kg).

Exception: The total quantity of water-reactive material allowed within a laboratory unit that is provided with walls, floors and ceilings that separate the laboratory unit from all adjoining areas by 2-hour fire-rated construction shall not exceed 5 pounds (2.3 kg).

[424.7.6] 427.7.6 Pyrophoric material. The total quantity of solid or liquid pyrophoric material allowed within a laboratory unit, excluding any quantities in a storage room, shall not exceed 0.5 pounds (0.227 kg).

Exception: The total quantity of pyrophoric material allowed within a laboratory unit that is provided with walls, floors and ceilings that separate the laboratory unit from all adjoining areas by 2-hour fire rated construction shall not exceed 1 pound (0.454 kg).

[424.7.7] 427.7.7 Highly toxic material. The total quantity of solid or liquid highly toxic material allowed within a laboratory unit, excluding any quantities in a storage room, shall not exceed 5 pounds [(0.227 kg)] (2.27 kg).

[424.7.8] 427.7.8 Toxic material. The total quantity of solid or liquid toxic material allowed within a laboratory unit, excluding any quantities in a storage room, shall not exceed 250 pounds [(946 L)] (113.4 kg).

[424.7.9] 427.7.9 Corrosive material. The total quantity of solid or liquid corrosive material allowed within a laboratory unit, excluding any quantity in a storage room, shall not exceed 250 gallons (946 L).

[424.7.10] 427.7.10 [Highly toxic and toxic] Hazardous gases. [In educational and instructional laboratories, the total quantity] The storage, handling and use of hazardous gases, including highly toxic, toxic, corrosive, and [toxic] asphyxiant gases [combined allowed], within a laboratory unit [, excluding any] shall be in accordance the New York City Fire Code, including quantities [in a storage room, shall not exceed 20 standard cubic feet (0.56 standard cubic m)] permitted and oxygen sensors.

[424.8] 427.8 Storage room classification. Storage rooms for laboratory chemicals accessory to a laboratory unit shall be classified as Occupancy Group S-1 provided they comply with the provisions of Section [424.9] 427.9. Storage rooms not in compliance with the provisions of Section [424.9] 427.9 for laboratory chemical quantity limitations shall be classified as a Group H occupancy.

[424.9] 427.9 Storage rooms. In addition to the quantities allowed within a laboratory unit by Section 427.7, laboratory chemicals that are accessory to a laboratory unit may be stored, whether outside of or entirely within a laboratory unit, in dedicated storage rooms complying with all of the following:

- Storage room capacity shall be limited to a maximum of 300 gallons (1136 L) of laboratory chemicals, not to exceed 5 gallons per square foot (0.125 L/m2) of floor area.

- Flammable gas storage rooms shall be limited to 2,500 standard cubic feet (71 standard cubic m) of flammable gas.

- Storage rooms shall be enclosed by a minimum of 2-hour rated fire barriers.

- Storage rooms shall be equipped with a continuously operated ventilation system that provides at least 6 changes of air per hour and vents to the outdoors.

- Each entrance to the storage room shall be provided with a minimum 11/2-hour rated self-closing fire door.

- Each entrance to the storage room shall be provided with a sill at the doorway, except that no sill shall be required in storage rooms containing only flammable gases.

- Storage rooms shall be equipped with an automatic sprinkler system providing at least one sprinkler for each 90 square feet (8.4 m2) or portion thereof.

- Laboratory chemicals that are incompatible with each other shall not be stored in the same storage room unless in compliance with the New York City Fire Code for separation of incompatible materials.

- Storage rooms shall not open directly to an exit or any enclosed exit access component.

- The floor of any storage room storing flammable gases shall be located at or above grade.

[424.10] 427.10 Ventilation. Nonproduction laboratories shall be ventilated in accordance with Section [407] 408 of the New York City Mechanical Code.

§ xx.  Section 425 of Chapter 4 of the New York city building code, as renumbered and amended by local law number 141 for the year 2013, is renumbered and amended to read as follows:

SECTION BC [425] 428
USES AND OCCUPANCIES INVOLVING RADIOACTIVE MATERIALS AND RADIATION-PRODUCING EQUIPMENT

[425.1] 428.1 Scope. This section shall apply to the construction, alteration, and use of buildings or spaces for radioactive materials and radiation-producing equipment.

[425.2] 428.2 City, state and federal regulations. In addition to the requirements of this section, occupancies involving radioactive materials and radiation-producing equipment shall also comply with applicable requirements of the [city health code] New York City Health Code, and applicable state and federal regulations.

[425.3] 428.3 Laboratories. All laboratories utilizing radioactive materials or radiation-producing equipment required to register under the requirements of the New York City Health Code shall comply with the requirements of Sections [425.3.1] 428.3.1 through [425.3.7] 428.3.7.

[425.3.1] 428.3.1 Construction. All buildings in which such laboratories occur shall be of [Group] Type I or II construction.

[425.3.2] 428.3.2 Floors. All floors shall comply with the fire resistance requirements for the class of construction, and provide the degree of radioactive resistance required by applicable city, state, and federal regulations. A finished material shall be applied to provide a continuous nonporous surface, which may be readily removed.

[425.3.3] 428.3.3 Interior finish. All insulation of acoustical treatments and interior partitions shall be of noncombustible material. Walls and ceilings shall have nonporous finishes of Class A rating.

[425.3.4] 428.3.4 Sprinkler protection. Automatic sprinkler protection complying with the construction provisions of Chapter 9 of the New York City Building Code shall be provided, and such protection shall be designed for the type of combustible materials wherever such material is used, and for the radioactive material that may be expected to melt, vaporize, or oxidize under fire conditions. Laboratory equipment susceptible to damage from water or other materials used in the sprinkler system may be shielded by hoods except when the equipment provides a source of combustion. Where sprinkler protection uses water, or small water-spray installations are used to fight small isolated fires, floors shall be provided with drainage so that water may be carried to retention tanks for later disposal as required by the New York City Health Code when contamination of the water is to be anticipated.

[425.3.5] 428.3.5 Electrical controls. Electrical controls and equipment shall be installed in accordance with the requirements of the New York City Electrical Code.

[425.3.6] 428.3.6 Ventilation. Exhaust air from areas in which radioactive materials are used or stored shall be exhausted to the outdoors in such manner as not to create a health hazard, and shall not be recirculated to other areas of the building. Air pressure in rooms in which radioactive materials are used or stored shall be maintained below the air pressure of adjoining rooms, so that there is no flow of radioactive gases or dusts into adjoining rooms.

[425.3.6.1] 428.3.6.1 Ducts. Ducts shall be of sheet steel of not less than No. 16 manufacturers’ standard gauge or of other equivalent noncombustible material having a melting point above 1800°F (982°C). Exhaust ducts within the building, on the discharge side of the fan, shall be welded airtight. Exhaust ducts within the building, on the suction side of the fan, shall have laps in the direction of airflow with smoke-tight joints, and shall be subjected to a smoke test in accordance with the requirements for chimneys in the New York City Mechanical Code. Access hatches with tight-closing covers shall be provided for cleaning and for fire-fighting in the exhaust system ducts.

[425.3.6.2] 428.3.6.2 Fume hoods. Fume hoods shall be exhausted to the outdoors. Controls for hood fans shall be interlocked so that contaminated air cannot be drawn into any space from a hood where the exhaust fan is not in operation.

[425.3.6.3] 428.3.6.3 Fans. Fan equipment other than the impeller and impeller housing shall be located outside the exhaust stream.

[425.3.6.4] 428.3.6.4 Exhaust. When the degree of contamination of the exhaust stream exceeds the concentration limits permitted by the health code, the duct system shall be equipped with devices to decontaminate the air to a safe level before discharging to the outdoor air.

[425.3.7] 428.3.7 Plumbing. Drainage lines from sinks used for radioactive wastes shall be without traps, and shall lead to retention tanks when required by the provisions of the New York City Health Code.

[425.4] 428.4 Radiation machines. Radiation machines or particle accelerators, linear accelerators, cyclotrons, synchrotons, betatrons, or bevatrons shall be located only in buildings of [Group] Type I or II construction; however, this requirement shall not apply to conventional medical, dental, research, or industrial x-ray machines of less than one million-volt capacity.

[425.5] 428.5 Storage. Radioactive materials shall be stored in sealed containers. When required by the commissioner to avoid too concentrated an exposure within any one space, radioactive materials shall be stored in vaults designed in accordance with the radiation shielding or other requirements for the materials to be stored, and with the requirements of Sections [425.5.1] 428.5.1 through [425.5.3] 428.5.3.

[425.5.1] 428.5.1 Fire protection. When any materials are subject to melting, vaporization, or oxidation under fire conditions, the storage vaults shall be constructed of walls having a fire-resistance rating of at least 4 hours, and the vaults shall be equipped with automatic sprinklers complying with the construction requirements of Chapter 9 and shall be vented through devices to decontaminate the air to a safe level.

[425.5.2] 428.5.2 Doors. Doors opening into storage vaults shall meet shielding requirements and have a fire-protection rating of not less than 3 hours.

[425.5.3] 428.5.3 Bins, shelving, partitions and pallets. All bins, shelving, partitions, and pallets in storage vaults shall be of noncombustible materials. Other methods of storage permitted by the health department or applicable state and federal regulations, such as storage under water, may be used.

§ 6. Chapter 5 of the New York city building code, as added by local law number 33 for the year 2007, table 503 as amended by local law number 8 for the rear 2008, sections 501, 502, 503, 504, 505, 506, 507 and 510, as amended by, and sections 508 and 509, as added by, local law number 141 for the year 2013, is amended to read as follows:

CHAPTER 5
GENERAL BUILDING HEIGHTS AND AREAS;
SEPARATION OF OCCUPANCIES

SECTION BC 501
GENERAL

501.1 Scope. The provisions of this chapter control the height and area of structures hereafter erected and additions to existing structures, including separation of occupancies.

501.2 Address identification. Buildings shall be provided with address numbers or letters in accordance with Section 3-505 of the Administrative Code and the rules issued thereunder by the borough president of the borough in which the property is located. Except as otherwise provided by the rules of the borough president in which the property is located, characters shall be a minimum 4 inches (102 mm) high and a minimum of 0.5 inch (12.7 mm) wide. They shall be installed on a contrasting background and be plainly visible from the street or road fronting the property. Where access is by means of a private road and the building address cannot be viewed from the public way, an appropriately placed monument, pole or sign or any other means authorized by the borough president of the borough in which the property is located shall be used to identify the structure.

501.3 Fire Department access. Access shall be provided to the Fire Department in accordance with Sections 501.3.1 and 501.3.2.

501.3.1 Frontage. Every building, exclusive of accessory buildings, shall have at least 8 percent of the total perimeter of the building adjoining a street or frontage space. For the purposes of this section, building perimeter shall be measured at that story having the maximum enclosed floor area; and buildings provided with a front yard or front setback no deeper than 30 feet (9144 mm) in compliance with the New York City Zoning Resolution shall be considered as adjoining the street or frontage space.

501.3.2 Building access. Provisions shall be made for access by the Fire Department to every building in accordance with [Section 903.2.11.1 of this code and Chapter 5 of] the New York City Fire Code and Section 903.2.11.1 of this code. In addition, multiple dwellings shall comply with Section 54 of the New York State Multiple Dwelling Law, as applicable.

SECTION BC 502
DEFINITIONS

502.1 Definitions. The following [words and] terms [shall, for the purposes of this chapter and as used elsewhere in this code, have the meanings shown herein.] are defined in Chapter 2:

AREA, BUILDING. [The area included within surrounding exterior walls (or exterior walls and firewalls) exclusive of vent shafts and courts. Areas of the building not provided with surrounding walls shall be included in the building area if such areas are included within the horizontal projection of the roof or floor above.]

BASEMENT. [A story partly below the grade plane and having less than one-half its clear height (measured from finished floor to finished ceiling) below the grade plane (see “Story” in Section 202 and “Story above grade plane” in this section). A basement shall be considered a story above grade plane.]

CELLAR. [That portion of a building that is partly or wholly underground, and having one-half or more of its clear height (measured from finished floor to finished ceiling) below the grade plane. Cellars shall not be counted as stories in measuring the height of the buildings.]

COMBINED HEAT AND POWER SYSTEMS. [Equipment that simultaneously produces electricity and heat from a single fuel source.]

EQUIPMENT PLATFORM. [An unoccupied, elevated platform used exclusively for mechanical systems or industrial process equipment, including the associated elevated walkways, stairs, alternating tread devices  and ladders necessary to access the platform (see Section 505.5).]

FIRE LANE.

FRONTAGE SPACE. [A street or an open space adjoining a building not less than 30 feet (9144 mm) in any dimension. Such open space shall be accessible from a street by a driveway, lane, private road or alley at least 20 feet (6096 mm) in width. Such open space including accessways shall be permanently maintained free of all obstructions that might interfere with its use by the Fire Department.]

GRADE PLANE. [A reference plane representing the level of the curb as established by the city engineer in the Borough President’s office, measured at the center of the front of a building. Where a building faces on more than one street, the grade plane shall be the average of the levels of the curbs at the center of each front.]

[Exception: The grade plane shall not be referenced to the level of the curb, but shall be considered the average elevation of the final grade adjoining all exterior walls of a building, calculated from final grade elevations taken at intervals of 10 feet (3048 mm) around the perimeter of the building where:]

[1.	No curb elevation has been legally established on the city map; or]

[2.	Every part of the building is setback more than 25 feet (7620 mm) from a street line.]

HEIGHT, BUILDING.[The vertical distance from the grade plane to the average height of the highest roof surfaces.]

MEZZANINE. [An intermediate level or levels between the floor and ceiling of any story in accordance with Section 505.]

STORY.

STORY ABOVE GRADE PLANE. [Any story having its finished floor surface entirely above grade plane, except that a basement shall also be considered a story above grade plane (also see definitions of “Story” in Section BC 202 and “Basement” in this section).]

SECTION BC 503
GENERAL BUILDING HEIGHT AND
AREA LIMITATIONS

503.1 General. [The building height and] Unless otherwise specifically modified in Chapter 4, building height, number of stories and building area shall not exceed the limits specified in [Table 503] Sections 504 and 506, based on the type of construction as determined by Section 602, and the occupancies as determined by Section 302, except as modified hereafter in this chapter. Building height, number of stories and building area provisions shall be applied independently. Each portion of a building separated by one or more fire walls complying with Section 706 shall be considered to be a separate building.

| [TABLE 503 ALLOWABLE BUILDING HEIGHTS AND AREASa Building height limitations shown in feet above grade plane. Story limitations shown as stories above grade plane. Building area limitations shown in square feet, as determined by the definition of “Area, building,” per story. |
| --- |
| GROUP | HEIGHT (feet) HEIGHT (S) | TYPE OF CONSTRUCTION |
|  |  | TYPE I | TYPE II | TYPE III | TYPE IV | TYPE V |
|  |  | A | B | A | B | A | B | HT | A | B |
|  |  | UL | 160e | 65 | 55 | 65 | 55 | 65 | 50 | 40 |
| A-1 | S A | UL UL | UL UL | 6 17,500 | 3 10,500 | 6 14,700 | 3 5,600 | 6 15,000 | 3 8,400 | 2 5,500 |
| A-2 | S A | UL UL | UL UL | 6 17,500 | 3 9,500 | 6 14,000 | 3 5,600 | 6 15,000 | 3 8,400 | 2 5,500 |
| A-3 | S A | UL UL | UL UL | 6 17,500 | 3 9,500 | 6 14,000 | 3 5,600 | 6 15,000 | 3 8,400 | 2 5,500 |
| A-4 | S A | UL UL | UL UL | 6 17,500 | 3 9,500 | 6 14,000 | 3 5,600 | 6 15,000 | 3 8,400 | 2 5,500 |
| A-5 | S A | UL UL | UL UL | UL UL | UL UL | UL UL | UL UL | 6 UL | UL UL | UL UL |
| B | S A | UL UL | UL UL | 6 37,500 | 3 10,500 | 6 28,500 | 3 5,600 | 6 36,000 | 3 8,400 | 2 5,500 |
| E | S A | UL UL | UL UL | 4 26,000 | 3 10,500 | 4 23,500 | 3 5,600 | 6 25,500 | 3 8,400 | 2 5,500 |
| F- 1 | S A | UL UL | 6 UL | 5 12,500 | 3 7,500 | 5 7,500 | 2 3,000 | 5 10,000 | 3 3,000 | 2 1,000 |
| F- 2 | S A | UL UL | UL UL | 6 37,500 | 3 10,500 | 6 28,500 | 3 5,600 | 6 30,000 | 3 8,400 | 2 5,500 |
| H-1 | S A | 1 21,000 | 1 16,500 | 1 11,000 | 1 7,500 | 1 9,500 | 1 7,000 | 1 10,500 | 1 7,500 | NP NP |
| H-2d | S A | UL 21,000 | 3 16,500 | 2 11,000 | 1 7,500 | 2 9,500 | 1 7,000 | 2 10,500 | 1 7,500 | 1 3,000 |
| H-3d | S A | UL UL | 6 60,000 | 4 26,500 | 2 14,000 | 4 17,500 | 2 13,000 | 4 25,000 | 2 10,000 | 1 5,000 |
| H-4 | S A | UL UL | 7 UL | 5 37,500 | 3 17,500 | 5 28,500 | 3 17,500 | 5 36,000 | 3 18,000 | 2 6,500 |
| H-5 | S A | 3 UL | 3 UL | 3 37,500 | 3 23,000 | 3 28,500 | 3 19,000 | 3 36,000 | 3 18,000 | 2 9,000 |
| I-1 | S A | UL UL | UL UL | 6 19,000 | NP NP | 4 16,500 | 3 5,600 | 4 18,000 | NP NP | NP NP |
| I-2 | S A | UL UL | 6 UL | 4 7,000 | 4 3,500 | 5 5,000 | 3 1,200 | 5 6,500 | 3 2,000 | NP NP |
| I-3 | S A | UL UL | 4 UL | 4 7,000 | 3 3,500 | 4 5,000 | 2 1,200 | 4 6,500 | 3 2,000 | NP NP |
| I-4 | S A | UL UL | UL UL | 3 26,500 | 3 9,500 | 3¦ 23,500 | 3 5,600 | 3 25,500 | 2 8,400 | 2 5,500 |
| M | S A | UL UL | UL UL | 6 21,500 | 3 7,500 | 6 18,500 | 3 5,600 | 6 14,000 | 3 8,400 | 2 5,500 |
| R-1 | S A | UL UL | UL UL | 6 UL | NP NP | 6 24,000 | NP NP | 6 20,500 | NP NP | NP NP |
| R-2 | S A | UL UL | UL UL | 6 UL | NP NP | 6 24,000 | 3 5,600 | 6 20,500 | NP NP | NP NP |
| R-3 | S A | UL UL | UL UL | 6 17,500 | 3 10,500 | 6 14,700 | 3 5,600 | 6 30,000 | 3 8,400 | 3 5,500 |
| S-1 | S A | UL UL | 6 48,000 | 5 12,000 | 3 7,500 | 4 7,500 | 3 7,500 | 4 7,500 | 3 5,000 | 2 1,000 |
| S-2b,c | S A | UL UL | UL UL | 6 15,000 | 3 10,000 | 6 10,000 | 4 8,500 | 6 10,000 | 3 8,400 | 2 5,500 |
| Uc | S | UL | 5 | 4 | 2 | 3 | 2 | 4 | 2 | 1 |
|  | A | UL | 35,000 | 19,000 | 8,500 | 14,000 | 8,500 | 18,000 | 9,000 | 5,500 |
| Not permitted in Fire District. |  | Not permitted in Fire District without sprinklers. |  |  |  |  |  |  |

For SI: 1 foot = 304.8 mm, 1 square foot = 0.0929 m2.

A = building area per story, S = stories above grade plane,

UL = Unlimited, NP = Not permitted.

a.	See the following sections for general exceptions to Table 503:

- Section 504.2, Allowable height increase due to automatic sprinkler system installation.

- Section 506.2, Allowable area increase due to frontage.

- Section 506.3, Allowable area increase due to automatic sprinkler system installation.

- Section 507, Unlimited area building.

b.	For open parking structures, see Section 406.3.

c.	For private garages, see Section 406.1.

d.	See Section 415.5 for limitations.

e.	Except for Occupancy Groups F-1, H-1 through H-5,I-2,I-3, S-1 and U, buildings equipped throughout with an approved automatic sprinkler system in accordance with Section 903.3.1.1 shall be unlimited in height.]

503.1.1 Special industrial occupancies. Buildings and structures of Type I and II construction designed to house special industrial processes that require large areas and unusual building heights to accommodate craneways or special machinery and equipment, including, among others, rolling mills; structural metal fabrication shops and foundries; or the production and distribution of electric, gas or steam power, shall be exempt from the building height, number of stories and building area limitations [of Table 503.] specified in Sections 504 and 506. Mezzanines within such buildings or structures shall comply with Section 505.2. Documents and plans describing the special industrial processes shall be submitted to the commissioner for approval.

503.1.2 Buildings on the same tax lot. Two or more buildings on the same tax lot and under the same ownership and control shall be regulated as separate buildings, or, at the option of the owner, shall be considered as portions of one building [if] where the building height, number of stories of each building and the aggregate building area of the combined buildings are within the limitations [of Table 503 as modified by] specified in Sections 504 and 506. The provisions of this code applicable to the aggregate building shall be applicable to each building.

503.1.3 Type I construction. Buildings of Type I construction permitted to be of unlimited tabular building heights and areas [in accordance with Table 503] are not [required] subject to [comply with] the special requirements that allow unlimited area buildings in Section 507 or unlimited building height in Sections 503.1.1 and 504.3 or increased building heights and areas for other types of construction.

[503.2 Reserved.]

SECTION BC 504
BUILDING HEIGHT [MODIFICATIONS] AND NUMBER OF STORIES

504.1 General. [The heights permitted by Table 503 shall only be increased in accordance with this section.] The height, in feet, and the number of stories of a building shall be determined based on the type of construction, occupancy classification and whether there is an automatic sprinkler system installed throughout the building.

Exception: The building height of one-story aircraft hangars, aircraft paint hangars and buildings used for the manufacturing of aircraft shall not be limited [if] where the building is provided with an automatic sprinkler system or automatic fire-extinguishing system in accordance with Chapter 9 and is entirely surrounded by public ways or yards not less in width than one and one-half times the building height.

[504.2 Automatic sprinkler system increase. Where a building is equipped throughout with an approved automatic sprinkler system in accordance with Section 903.3.1.1, the value specified in Table 503 for maximum building height is increased by 20 feet (6096 mm) and the maximum number of stories is increased by one story. These increases are permitted in addition to the building area increase in accordance with Sections 506.2 and 506.3. For Group R buildings equipped throughout with an approved automatic sprinkler system in accordance with Section 903.3.1.2, the value specified in Table 503 for maximum building height is increased by 20 feet (6096 mm) and the maximum number of stories is increased by one story, but shall not exceed 60 feet (18 288 mm) or six stories, respectively.]

[Exceptions:]

[1.	Buildings, or portions of buildings, classified as a Group I-2 occupancy of Type IIB, III, IV or V construction.]

[2.	Buildings, or portions of buildings, classified as a Group H-1, H-2, H-3 or H-5 occupancy.]

[3.	Fire-resistance-rating substitution in accordance with Table 601, Note d.]

504.1.1 Unlimited area buildings. The height of unlimited area buildings shall be designed in accordance with Section 507.

504.1.2 Special provisions. The special provisions of Section 510 permit the use of special conditions that are exempt from, or modify, the specific requirements of this chapter regarding the allowable heights of buildings based on the occupancy classification and type of construction, provided the special condition complies with the provisions specified in Section 510.

504.2 Mixed occupancy. In a building containing mixed occupancies in accordance with Section 508, no individual occupancy shall exceed the height and number of story limits specified in Section 504 for the applicable occupancies.

504.3 [Rooftop structures.] Height in feet and number of stories. The maximum height, in feet, of a building shall not exceed the limits specified in Table 504.3. The maximum number of stories of a building shall not exceed the limits specified in Table 504.4.

Exceptions:

1.	Rooftop structures including but not limited to roof tanks and their supports, ventilating, air conditioning, combined heat and power systems and similar building service equipment, bulkheads, penthouses, greenhouses, chimneys, and parapet walls 4 feet (1219 mm) or less in height shall not be included in the building height of the building or considered an additional story unless the aggregate area of all such structures, exclusive of any solar thermal and solar (photovoltaic) collectors and/or panels and their supporting equipment, exceeds 331/3 percent of the area of the roof of the building upon which they are erected. Rooftop structures shall be constructed in accordance with Section [1509]  1510.

2.	[Exception:] Solar thermal and solar electric (photovoltaic) collectors and/or panels and their supporting equipment that exceed 331/3 percent of the area of the roof of the building upon which they are erected shall not be included in the height of a building or considered an additional story.

3.	Noncombustible steeples, minarets, spires, domes, cupolas and other similar architectural elements, not used for occupancy or storage, shall not be included in the building height of the building or considered an extra story, and may be unlimited in height.

| TABLE 504.3a ALLOWABLE BUILDING HEIGHT IN FEET ABOVE GRADE PLANE |
| --- |
| OCCUPANCY CLASSIFICATION | TYPE OF CONSTRUCTION |
|  | SEE FOOTNOTES | TYPE I | TYPE II | TYPE III | TYPE IVj | TYPE V |
|  |  | A | Bi | A | B | A | B | HT | A | B |
| A-1 | NSb,c | UL | 160 | 65 | 55 | 65 | 55 | 65 | 50 | 40 |
|  | S | UL | 420 | 85 | 75 | 85 | 75 | 85 | 70 | 60 |
| A-2 | NSb,c | UL | 160 | 65 | 55 | 65 | 55 | 65 | 50 | 40 |
|  | S | UL | 420 | 85 | 75 | 85 | 75 | 85 | 70 | 60 |
| A-3 | NSb,c | UL | 160 | 65 | 55 | 65 | 55 | 65 | 50 | 40 |
|  | S | UL | 420 | 85 | 75 | 85 | 75 | 85 | 70 | 60 |
| A-4 | NSb,c | UL | 160 | 65 | 55 | 65 | 55 | 65 | 50 | 40 |
|  | S | UL | 420 | 85 | 75 | 85 | 75 | 85 | 70 | 60 |
| A-5 | NSb,c | UL | 160 | 65 | 55 | 65 | 55 | 65 | 50 | 40 |
|  | S | UL | 420 | 85 | 75 | 85 | 75 | 85 | 70 | 60 |
| B | NSb,c | UL | 160 | 65 | 55 | 65 | 55 | 65 | 50 | 40 |
|  | S | UL | 420 | 85 | 75 | 85 | 75 | 85 | 70 | 60 |
| E | NSb,c | UL | 160 | 65 | 55 | 65 | 55 | 65 | 50 | 40 |
|  | S | UL | 420 | 85 | 75 | 85 | 75 | 85 | 70 | 60 |
| F-1 | NSb,c | UL | 160 | 65 | 55 | 65 | 55 | 65 | 50 | 40 |
|  | S | UL | 180 | 85 | 75 | 85 | 75 | 85 | 70 | 60 |
| F-2 | NSb,c | UL | 160 | 65 | 55 | 65 | 55 | 65 | 50 | 40 |
|  | S | UL | 420 | 85 | 75 | 85 | 75 | 85 | 70 | 60 |
| H-1 | S | UL | 160 | 65 | 55 | 65 | 55 | 65 | 50 | NP |
| H-2f | S | UL | 160 | 65 | 55 | 65 | 55 | 65 | 50 | 40 |
| H-3f | S | UL | 160 | 65 | 55 | 65 | 55 | 65 | 50 | 40 |
| H-4 | S | UL | 180 | 85 | 75 | 85 | 75 | 85 | 70 | 60 |
| H-5 | S | UL | 160 | 65 | 55 | 65 | 55 | 65 | 50 | 40 |
| I-1 | S13D | 60 | 60 | 60 | NP | 60 | 55 | 60 | NP | NP |
|  | S13R |  |  |  |  |  |  |  |  |  |
|  | S | UL | 420 | 85 |  | 85 | 75 | 85 | NP | NP |
| I-2 | S | UL | 180 | 85 | 55 | 65 | 55 | 65 | 50 | NP |
| I-3 | S | UL | 180 | 85 | 75 | 85 | 75 | 85 | 70 | NP |
| I-4 | NSb,c | UL | 160 | 65 | 55 | 65 | 55 | 65 | 50 | 40 |
|  | S | UL | 420 | 85 | 75 | 85 | 75 | 85 | 70 | 60 |
| M | NSb,c | UL | 160 | 65 | 55 | 65 | 55 | 65 | 50 | 40 |
|  | S | UL | 420 | 85 | 75 | 85 | 75 | 85 | 70 | 60 |
| R-1 | S13R | 60 | 60 | 60 | NP | 60 | NP | 60 | NP | NP |
|  | S | UL | 420 | 85 |  | 85 |  | 85 |  |  |
| R-2 | S13R | 60 | 60 | 60 | NP | 60 | 60 | 60 | NP | NP |
|  | S | UL | 420 | 85 |  | 85 | 75 | 85 |  |  |
| R-3 | NSb,c | UL | 160 | 65 | 55 | 65 | 55 | 65 | 50g,h | 40g |
|  | S13D | 60 | 60 | 60 | 60 | 60 | 55 | 60 |  |  |
|  | S13R |  |  |  |  |  | 60 |  | 60g,h | 60g |
|  | S | UL | 420 | 85 | 75 | 85 | 75 | 85 | 70g,h |  |
| S-1 | NSb,c | UL | 160 | 65 | 55 | 65 | 55 | 65 | 50 | 40 |
|  | S | UL | 180 | 85 | 75 | 85 | 75 | 85 | 70 | 60 |
| S-2d,e | NSb,c | UL | 160 | 65 | 55 | 65 | 55 | 65 | 50 | 40 |
|  | S | UL | 420 | 85 | 75 | 85 | 75 | 85 | 70 | 60 |
| Ue | NSb,c | UL | 160 | 65 | 55 | 65 | 55 | 65 | 50 | 40 |
|  | S | UL | 180 | 85 | 75 | 85 | 75 | 85 | 70 | 60 |
|  | = Not permitted in Fire District |  | = Not permitted in Fire District without sprinklers |

For SI: 1 foot = 304.8 mm.

Note: UL = Unlimited; NP = Not permitted; NS = Buildings not equipped throughout with an automatic sprinkler system; S = Buildings equipped throughout with an automatic sprinkler system installed in accordance with Section 903.3.1.1; S13R = Buildings equipped throughout with an automatic sprinkler system installed in accordance with Section 903.3.1.2; S13D = Buildings equipped throughout with an automatic sprinkler system installed in accordance with Section 903.3.1.3.

a.	See the following sections for general exceptions to Table 504.3:

1.	See Chapters 4 and 5 for specific exceptions to the allowable height in this chapter.

2.	Section 506.3, Allowable area increase due to frontage.

3.	Section 507, Unlimited area building.

b.	See Section 903.2 for the minimum thresholds for protection by an automatic sprinkler system for specific occupancies.

c.	The NS value is only for use in buildings not required by this code to be equipped throughout with an automatic sprinkler system.

d.	For open parking structures, see Section 406.5.

e.	For private garages, see Section 406.3.

f.	See Section 415.8 for limitations.

g.	See Exception 9 of Section D105.1 for allowances of Type VA and VB construction for R-3 occupancies.

h.	See Exception 12 of Section D105.1 for allowances of Type VA construction and height limitations for R-3 occupancies in Lower Density Growth Management Areas.

i.	See Section 403.2.1 for additional requirements for high-rise buildings.

j.	Type IV construction utilizing cross-laminated timber or structural composite lumber shall be sprinklered where required by Section 903.2.13.

504.4 Number of stories. The maximum number of stories of a building shall not exceed the limits specified in Table 504.4.

| TABLE 504.4a,b ALLOWABLE NUMBER OF STORIES ABOVE GRADE PLANE |
| --- |
| OCCUPANCY CLASSIFICATION | TYPE OF CONSTRUCTION |
|  | SEE FOOTNOTES | TYPE I | TYPE II | TYPE III | TYPE IVi | TYPE V |
|  |  | A | B | A | B | A | B | HT | A | B |
| A-1 | NSb,c | UL | UL | 6 | 3 | 6 | 3 | 6 | 3 | 2 |
|  | S | UL | UL | 7 | 4 | 7 | 4 | 7 | 4 | 3 |
| A-2 | NSb,c | UL | UL | 6 | 3 | 6 | 3 | 6 | 3 | 2 |
|  | S | UL | UL | 7 | 4 | 7 | 4 | 7 | 4 | 3 |
| A-3 | NSb,c | UL | UL | 6 | 3 | 6 | 3 | 6 | 3 | 2 |
|  | S | UL | UL | 7 | 4 | 7 | 4 | 7 | 4 | 3 |
| A-4 | NSb,c | UL | UL | 6 | 3 | 6 | 3 | 6 | 3 | 2 |
|  | S | UL | UL | 7 | 4 | 7 | 4 | 7 | 4 | 3 |
| A-5 | NSb,c | UL | UL | UL | UL | UL | UL | 6 | UL | UL |
|  | S | UL | UL | UL | UL | UL | UL | 7 | UL | UL |
| B | NSb,c | UL | UL | 6 | 3 | 6 | 3 | 6 | 3 | 2 |
|  | S | UL | UL | 7 | 4 | 7 | 4 | 7 | 4 | 3 |
| E | NSb,c | UL | UL | 4 | 3 | 4 | 3 | 6 | 3 | 2 |
|  | S | UL | UL | 5 | 4 | 5 | 4 | 7 | 4 | 3 |
| F-1 | NSb,c | UL | 6 | 5 | 3 | 5 | 2 | 5 | 3 | 2 |
|  | S | UL | 7 | 6 | 4 | 6 | 3 | 6 | 4 | 3 |
| F-2 | NSb,c | UL | UL | 6 | 3 | 6 | 3 | 6 | 3 | 2 |
|  | S | UL | UL | 7 | 4 | 7 | 4 | 7 | 4 | 3 |
| H-1 | S | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | NP |
| H-2f | S | UL | 3 | 2 | 1 | 2 | 1 | 2 | 1 | 1 |
| H-3f | S | UL | 6 | 4 | 2 | 4 | 2 | 4 | 2 | 1 |
| H-4 | S | UL | 8 | 6 | 4 | 6 | 4 | 6 | 4 | 3 |
| H-5 | S | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 2 |
| I-1 | S13D | 6 | 6 | 6 | NP | 4 | 3 | 4 | NP | NP |
|  | S13R | UL | UL |  |  | 5 | 4 | 5 |  |  |
|  | S | UL | UL | 7 | NP |  |  |  |  |  |
| I-2 | S | UL | 7 | 5 | 4 | 5 | 3 | 5 | 3 | NP |
| I-3 | S | UL | 5 | 5 | 4 | 5 | 3 | 5 | 4 | NP |
| I-4 | NSb,c | UL | UL | 3 | 3 | 3 | 3 | 3 | 2 | 2 |
|  | S | UL | UL | 4 | 4 | 4 | 4 | 4 | 3 | 3 |
| M | NSb,c | UL | UL | 6 | 3 | 6 | 3 | 6 | 3 | 2 |
|  | S | UL | UL | 7 | 4 | 7 | 4 | 7 | 4 | 3 |
| R-1 | S13R | 6 | 6 | 6 | NP | 6 | NP | 6 | NP | NP |
|  | S | UL | UL | 7 | NP | 7 | NP | 7 | NP | NP |
| R-2 | S13R | 6 | 6 | 6 | NP | 6 | 4 | 6 | NP | NP |
|  | S | UL | UL | 7 | NP | 7 |  | 7 | NP | NP |
| R-3 | NSb,c |  |  |  |  |  |  |  | 3g,h | 3g |
|  | S13D | 6 | 6 | 6 | 3 | 6 | 3 | 6 |  |  |
|  | S13R |  |  |  | 4 |  | 4 |  | 4g,h | 4g |
|  | S | UL | UL | 7 |  | 7 |  | 7 |  |  |
| S-1 | NSb,c | UL | 6 | 5 | 3 | 4 | 3 | 4 | 3 | 2 |
|  | S | UL | 7 | 6 | 4 | 5 | 4 | 5 | 4 | 3 |
| S-2d,e | NSb,c | UL | UL | 6 | 3 | 6 | 4 | 6 | 3 | 2 |
|  | S | UL | UL | 7 | 4 | 7 | 5 | 7 | 4 | 3 |
| Ue | NSb,c | UL | 5 | 4 | 2 | 3 | 2 | 4 | 2 | 1 |
|  | S | UL | 6 | 5 | 3 | 4 | 3 | 5 | 3 | 2 |

|  | = Not permitted in Fire District |  | = Not permitted in Fire District without sprinklers |
| --- | --- | --- | --- |
|  | = Number of stories in nonsprinklered 1- & 2-family buildings shall be limited by Section 903.2.8 |

Note: UL = Unlimited; NP = Not Permitted; NS = Buildings not equipped throughout with an automatic sprinkler system; S = Buildings equipped throughout with an automatic sprinkler system installed in accordance with Section 903.3.1.1; S13R = Buildings equipped throughout with an automatic sprinkler system installed in accordance with Section 903.3.1.2; S13D = Buildings equipped throughout with an automatic sprinkler system installed in accordance with Section 903.3.1.3.

a.	See the following sections for general exceptions to Table 504.4.

1.	See Chapters 4 and 5 for specific exceptions to the allowable height in this chapter.

2.	Section 506.3, Allowable area increase due to frontage.

3.	Section 507, Unlimited area building.

b.	See Section 903.2 for the minimum thresholds for protection by an automatic sprinkler system for specific occupancies.

c.	The NS value is only for use in buildings not required by this code to be equipped throughout with an automatic sprinkler system.

d.	For open parking structures, see Section 406.5.

e.	For private garages, see Section 406.3.

f.	See Section 415.8 for limitations.

g.	See Exception 9 of Section D105.1 for allowances of Type VA and VB construction for R-3 occupancies.

h.	See Exception 12 of Section D105.1 for allowances of Type VA construction and height limitations for R-3 occupancies in Lower Density Growth Management Areas.

i.	Type IV construction utilizing cross-laminated timber or structural composite lumber shall be sprinklered where required by Section 903.2.13.

SECTION BC 505
MEZZANINES AND EQUIPMENT PLATFORMS

505.1 General. Mezzanines shall comply with Section 505.2. Equipment platforms shall comply with Section 505.3.

505.2 Mezzanines. A mezzanine or mezzanines in compliance with Section [505] 505.2 shall be considered a portion of the story [in which it is contained] below. Such mezzanines shall not contribute to either the building area or number of stories as regulated by Section 503.1. The area of the mezzanine shall be included in determining the fire area [defined in Section 902]. The clear height above and below the mezzanine floor construction shall be not [be] less than 7 feet (2134 mm).

Exception: The clear height of habitable spaces above or below mezzanines within dwelling units shall be not [be] less than 8 feet (2438 mm).

[505.2] 505.2.1 Area limitation. The aggregate area of a mezzanine or mezzanines within a room or space shall be not [exceed] greater than one-third of the floor area of that room or space in which they are located. The enclosed portions of a room or space shall not be included in determining the permissible floor area of the mezzanine. In determining the allowable mezzanine area, the area of the mezzanine shall not be included in the floor area of the room in which it is contained.

Where a room contains both a mezzanine and an equipment platform, the aggregate area of the two raised floor levels shall be not greater than two-thirds of the floor area of that room or space in which they are located.

Exceptions:

1.	The aggregate area of mezzanines in buildings and structures of Type I or II construction for special industrial occupancies in accordance with Section 503.1.1 shall be not [exceed] greater than two-thirds of the area of the room in which the mezzanines are located.

2.	The aggregate area of a mezzanine or mezzanines within a dwelling unit shall not exceed one-third of the net floor area of such dwelling unit, whether or not portions of such dwelling unit are enclosed. The area of the mezzanine shall not contribute to the determination of the floor area of the dwelling unit in which it is contained.

[505.3 Egress] 505.2.2 Means of egress. Each occupant of a mezzanine shall have access to at least two independent means of egress where the common path of egress travel exceeds the limitations of Section [1014.3]  1006.2. Where a stairway provides a means of exit access from a mezzanine, the maximum travel distance includes the distance traveled on the stairway measured in the plane of the tread nosing. Accessible means of egress shall be provided in accordance with Section [1007]  1009.

Exception: A single means of egress shall be permitted in accordance with Section [1015.1]  1006.2.

[505.4] 505.2.3 Openness. A mezzanine shall be open and unobstructed to the room in which such mezzanine is located except for walls or railings not more than 42 inches (1067 mm) [high] in height, columns and posts.

Exceptions:

1.	Mezzanines or portions thereof are not required to be open to the room in which the mezzanines are located, provided that the occupant load of the aggregate area of the enclosed space [does] is not [exceed] greater than 10.

2.	A mezzanine having two or more means of egress is not required to be open to the room in which the mezzanine is located, if at least one of the means of egress provides direct access to an exit [from] located on the mezzanine level.

3.	Mezzanines or portions thereof are not required to be open to the room in which the mezzanines are located, provided that the aggregate floor area of the enclosed space [does] Is not [exceed] greater than 10 percent of the mezzanine area.

4.	In industrial facilities, mezzanines used for control equipment are permitted to be glazed on all sides.

5.	A mezzanine having two or more means of egress shall not be required to be open to the room in which the mezzanine is located in occupancies, other than Groups H and I, that comply with [items] Items 5.1 through 5.4.

5.1.	Such occupancy is no more than two stories above grade plane,

5.2.	Such occupancy is equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1,

5.3.	An approved fire alarm system is installed throughout the entire building or structure in which such occupancy is located, and

5.4.	Notification appliances are installed throughout the mezzanine in accordance with NFPA 72.

[505.5] 505.3 Equipment platforms. Equipment platforms in buildings shall not be considered as a portion of the floor below. Such equipment platforms shall not contribute to either the building area or the number of stories as regulated by Section 503.1. The area of the equipment platform shall not be included in determining the fire area in accordance with Section 903. Equipment platforms shall not be a part of any mezzanine[,] and such platforms and the walkways, [stairs] stairways, alternating tread devices and ladders providing access to an equipment platform shall not serve as a part of the means of egress from the building.

[505.5.1] 505.3.1 Area [limitations] limitation. The aggregate area of all industrial equipment platforms within a room shall be not [exceed] greater than two-thirds of the area of the room in which they occur. Where an equipment platform is located in the same room as a mezzanine, the area of the mezzanine shall be determined by Section [505.2] 505.2.1 and the combined aggregate area of the equipment platforms and mezzanines shall be not [exceed] greater than two-thirds of the room in which they are located.

[505.5.2] 505.3.2 Fire suppression. Where located in a building that is required to be protected by an automatic sprinkler system, industrial equipment platforms shall be fully protected by sprinklers above and below the platform, where required by the standards referenced in Section 903.3.

[505.5.3] 505.3.3 Guards. Equipment platforms shall have guards where required by Section [1013.1]  1015.2.

SECTION BC 506
BUILDING AREA MODIFICATIONS

506.1 General. The floor area of a building [areas limited by Table 503] shall be [permitted to be increased due to frontage (If) and] determined based on the type of construction, occupancy classification, whether there is an automatic sprinkler system [protection (Is) in accordance with] installed throughout the [following:] building and the amount of building frontage on public way or open space.

[(Equation 5-1)]

[where:]

Allowable building area per story (square feet).]

Tabular building area per story in accordance with Table 503 (square feet).]

[	Area increase factor due to frontage as calculated in accordance with Section 506.2]

Area increase factor due to sprinkler protection as calculated in accordance with Section 506.3.]

[506.2 Frontage increase. Where a building has more than 25 percent of its perimeter adjoining a public way or open space having a minimum width of 20 feet (6096 mm), the frontage increase shall be determined in accordance with the following:]

[(Equation 5-2)]

[where:]

Area increase factor due to frontage.]

Building perimeter that fronts on a public way or open space having 20 feet (6096 mm) open minimum width (feet).]

Perimeter of entire building (feet).]

Width of public way or open space (feet) in accordance with Section 506.2.1.]

506.1.1 Unlimited area buildings. Unlimited area buildings shall be designed in accordance with Section 507.

506.1.2 Special provisions. The special provisions of Section 510 permit the use of special conditions that are exempt from, or modify, the specific requirements of this chapter regarding the allowable areas of buildings based on the occupancy classification and type of construction, provided the special condition complies with the provisions specified in Section 510.

506.1.3 Basement and cellar. A single basement or cellar need not be included in the total allowable building area, provided such basement or cellar does not exceed the area permitted for a building with no more than one story above grade plane.

506.2 Allowable area determination. The allowable area of a building shall be determined in accordance with the applicable provisions of Sections 506.2.1 through 506.2.4, and Section 506.3.

| TABLE 506.2a ALLOWABLE AREA FACTOR (At = NS, S1, S13D, S13R, or SM, as applicable) IN SQUARE FEET |
| --- |
| OCCUPANCY CLASSIFICATION | SEE FOOTNOTES | TYPE OF CONSTRUCTION |
|  |  | TYPE I | TYPE II | TYPE III | TYPE IVi | TYPE V |
|  |  | A | B | A | B | A | B | HT | A | B |
| A-1 | NSb,c | UL | UL | 17,500 | 10,500 | 14,700 | 5,600 | 15,000 | 8,400 | 5,500 |
|  | S1 | UL | UL | 52,500 | 31,500 | 44,100 | 16,800 | 45,000 | 25,200 | 16,500 |
|  | SM | UL | UL | 35,000 | 21,000 | 29,400 | 11,200 | 30,000 | 16,800 | 11,000 |
| A-2 | NSb,c | UL | UL | 17,500 | 9,500 | 14,000 | 5,600 | 15,000 | 8,400 | 5,500 |
|  | S1 | UL | UL | 52,500 | 28,500 | 42,000 | 16,800 | 45,000 | 25,200 | 16,500 |
|  | SM | UL | UL | 35,000 | 19,000 | 28,000 | 11,200 | 30,000 | 16,800 | 11,000 |
| A-3 | NSb,c | UL | UL | 17,500 | 9,500 | 14,000 | 5,600 | 15,000 | 8,400 | 5,500 |
|  | S1 | UL | UL | 52,500 | 28,500 | 42,000 | 16,800 | 45,000 | 25,200 | 16,500 |
|  | SM | UL | UL | 35,000 | 19,000 | 28,000 | 11,200 | 30,000 | 16,800 | 11,000 |
| A-4 | NSb,c | UL | UL | 17,500 | 9,500 | 14,000 | 5,600 | 15,000 | 8,400 | 5,500 |
|  | S1 | UL | UL | 52,500 | 28,500 | 42,000 | 16,800 | 45000 | 25,200 | 16,500 |
|  | SM | UL | UL | 35,000 | 19,000 | 28,000 | 11,200 | 30,000 | 16,800 | 11,000 |
| A-5 | NSb,c | UL | UL | UL | UL | UL | UL | UL | UL | UL |
|  | S1 |  |  |  |  |  |  |  |  |  |
|  | SM |  |  |  |  |  |  |  |  |  |
| B | NSb,c | UL | UL | 37,500 | 10,500 | 28,500 | 5,600 | 36,000 | 8,400 | 5,500 |
|  | S1 | UL | UL | 112,500 | 31,500 | 85,500 | 16,800 | 108,000 | 25,200 | 16,500 |
|  | SM | UL | UL | 75,000 | 21,000 | 57,000 | 11,200 | 72,000 | 16,800 | 11,000 |
| E | NSb,c | UL | UL | 26,000 | 10,500 | 23,500 | 5,600 | 25,500 | 8,400 | 5,500 |
|  | S1 | UL | UL | 78,000 | 31,500 | 70,500 | 16,800 | 76,500 | 25,200 | 16,500 |
|  | SM | UL | UL | 52,000 | 21,000 | 47,000 | 11,200 | 51,000 | 16,800 | 11,000 |
| F-1 | NSb,c | UL | UL | 12,500 | 7,500 | 7,500 | 3,000 | 10,000 | 3,000 | 1,000 |
|  | S1 | UL | UL | 37,500 | 22,500 | 22,500 | 9,000 | 30,000 | 9,000 | 3,000 |
|  | SM | UL | UL | 25,000 | 15,000 | 15,000 | 6,000 | 20,000 | 6,000 | 2,000 |
| F-2 | NSb,c | UL | UL | 37,500 | 10,500 | 28,500 | 5,600 | 30,000 | 8,400 | 5,500 |
|  | S1 | UL | UL | 112,500 | 31,500 | 85,500 | 16,800 | 90,000 | 25,200 | 16,500 |
|  | SM | UL | UL | 75,000 | 21,000 | 57,000 | 11,200 | 60,000 | 16,800 | 11,000 |
| H-1 | NSb,c | 21,000 | 16,500 | 11,000 | 7,500 | 9,500 | 7,000 | 10,500 | 7,500 | NP |
|  | S1 |  |  |  |  |  |  |  |  |  |
| H-2f | NSb,c | 21,000 | 16,500 | 11,000 | 7,500 | 9,500 | 7,000 | 10,500 | 7,500 | 3,000 |
|  | S1 |  |  |  |  |  |  |  |  |  |
|  | SM |  |  |  |  |  |  |  |  |  |
| H-3f | NSb,c | UL | 60,000 | 26,500 | 14,000 | 17,500 | 13,000 | 25,000 | 10,000 | 5,000 |
|  | S1 |  |  |  |  |  |  |  |  |  |
|  | SM |  |  |  |  |  |  |  |  |  |
| H-4 | NSb,c | UL | UL | 37,500 | 17,500 | 28,500 | 17,500 | 36,000 | 18,000 | 6,500 |
|  | S1 | UL | UL | 112,500 | 52,500 | 85,500 | 52,500 | 108,000 | 54,000 | 19,500 |
|  | SM | UL | UL | 75,000 | 35,000 | 57,000 | 35,000 | 72,000 | 36,000 | 13,000 |
| H-5 | NSb,c | UL | UL | 37,500 | 23,000 | 28,500 | 19,000 | 36,000 | 18,000 | 9,000 |
|  | S1 | UL | UL | 112,500 | 69,000 | 85,500 | 57,000 | 108,000 | 54,000 | 27,000 |
|  | SM | UL | UL | 75,000 | 46,000 | 57,000 | 38,000 | 72,000 | 36,000 | 18,000 |
| I-1 | NSb,c | UL | UL | 19,000 | NP | 16,500 | 5,600 | 18,000 | NP | NP |
|  | S13D | UL | UL | 19,000 | NP | 16,500 | 5,600 | 18,000 | NP | NP |
|  | S1 | UL | UL | 57,000 |  | 49,500 | 16,800 | 54,000 | NP | NP |
|  | SM | UL | UL | 38,000 | NP | 33,000 | 11,200 | 36,000 | NP | NP |
| I-2 | NSb,c | UL | UL | 7,000 | 3,500 | 5,000 | 1,200 | 6,500 | 2,000 | NP |
|  | S1 | UL | UL | 21,000 | 10,500 | 15,000 | 3,600 | 19,500 | 6,000 | NP |
|  | SM | UL | UL | 14,000 | 7,000 | 10,000 | 2,400 | 13,000 | 4,000 | NP |
| I-3 | NSb,c | UL | UL | 7,000 | 3,500 | 5,000 | 1,200 | 6,500 | 2,000 | NP |
|  | S1 | UL | UL | 21,000 | 10,500 | 15,000 | 3,600 | 19,500 | 6,000 | NP |
|  | SM | UL | UL | 14,000 | 7,000 | 10,000 | 2,400 | 13,000 | 4,000 | NP |
| I-4 | NSb,c | UL | UL | 26,500 | 9,500 | 23,500 | 5,600 | 25,500 | 8,400 | 5,500 |
|  | S1 | UL | UL | 79,500 | 28,500 | 70,500 | 16,800 | 76,500 | 25,200 | 16,500 |
|  | SM | UL | UL | 53,000 | 19,000 | 47,000 | 11,200 | 51,000 | 16,800 | 11,000 |
| M | NSb,c | UL | UL | 21,500 | 7,500 | 18,500 | 5,600 | 14,000 | 8,400 | 5,500 |
|  | S1 | UL | UL | 64,500 | 22,500 | 55,500 | 16,800 | 42,000 | 25,200 | 16,500 |
|  | SM | UL | UL | 43,000 | 15,000 | 37,000 | 11,200 | 28,000 | 16,800 | 11,000 |
| R-1 | NSb,c | UL | UL | UL | NP | 24,000 | NP | 20,500 | NP | NP |
|  | S13R |  |  |  |  |  |  |  |  |  |
|  | S1 | UL | UL | UL | NP | 72,000 | NP | 61,500 | NP | NP |
|  | SM | UL | UL | UL | NP | 48,000 | NP | 41,000 | NP | NP |
| R-2 | NSb,c | UL | UL | UL | NP | 24,000 | 5,600 | 20,500 | NP | NP |
|  | S13R |  |  |  |  |  |  |  |  |  |
|  | S1 | UL | UL | UL | NP | 72,000 | 16,800 | 61,500 | NP | NP |
|  | SM | UL | UL | UL | NP | 48,000 | 11,200 | 41,000 | NP | NP |
| R-3 | NSb,c | UL | UL | 17,500 | 10,500 | 14,700 | 5,600 | 30,000 | 8,400g,h | 5,500g |
|  | S13D |  |  |  |  |  | 5,600 |  |  |  |
|  | S13R |  |  |  |  |  |  |  |  |  |
|  | S1 | UL | UL | 52,500 | 31,500 | 44,100 | 16,800 | 90,000 | 8,400g,h | 5,500g |
|  | SM | UL | UL | 35,000 | 21,000 | 29,400 | 11,200 | 60,000 |  |  |
| S-1 | NSb,c | UL | 48,000 | 12,000 | 7,500 | 7,500 | 7,500 | 7,500 | 5,000 | 1,000 |
|  | S1 | UL | 144,000 | 36,000 | 22,500 | 22,500 | 22,500 | 22,500 | 15,000 | 3,000 |
|  | SM | UL | 96,000 | 24,000 | 15,000 | 15,000 | 15,000 | 15,000 | 10,000 | 2,000 |
| S-2d,e | NSb,c | UL | UL | 15,000 | 10,000 | 10,000 | 8,500 | 10,000 | 8,400 | 5,500 |
|  | S1 | UL | UL | 45,000 | 30,000 | 30,000 | 25,500 | 30,000 | 25,200 | 16,500 |
|  | SM | UL | UL | 30,000 | 20,000 | 20,000 | 17,000 | 20,000 | 16,800 | 11,000 |
| Ue | NSb,c | UL | 35,000 | 19,000 | 8,500 | 14,000 | 8,500 | 18,000 | 9,000 | 5,500 |
|  | S1 | UL | 105,000 | 57,000 | 25,500 | 42,000 | 25,500 | 54,000 | 27,000 | 16,500 |
|  | SM | UL | 70,000 | 38,000 | 17,000 | 28,000 | 17,000 | 36,000 | 18,000 | 11,000 |
|  | = Not permitted in Fire District |  | = Not permitted in Fire District without sprinklers |

Note: UL = Unlimited; NP = Not permitted;

For SI: 1 square foot = 0.0929 m2.

NS = Buildings not equipped throughout with an automatic sprinkler system; S1 = Buildings a maximum of one story above grade plane equipped throughout with an automatic sprinkler system installed in accordance with Section 903.3.1.1; SM = Buildings two or more stories above grade plane equipped throughout with an automatic sprinkler system installed in accordance with Section 903.3.1.1; S13R = Buildings equipped throughout with an automatic sprinkler system installed in accordance with Section 903.3.1.2; S13D = Buildings equipped throughout with an automatic sprinkler system installed in accordance with Section 903.3.1.3.

a.	See the following sections for general exceptions to Table 506.2.

1.	See Chapters 4 and 5 for specific exceptions to the allowable height in this chapter.

2.	Section 506.3, Allowable area increase due to frontage.

3.	Section 507, Unlimited area building.

b.	See Section 903.2 for the minimum thresholds for protection by an automatic sprinkler system for specific occupancies.

c.	The NS value is only for use in buildings not required by this code to be equipped throughout with an automatic sprinkler system.

d. 	For open parking structures, see Section 406.5.

e. 	For private garages, see Section 406.3.

f. 	See Section 415.8 for limitations.

g.	See Exception 9 of Section D105.1 for allowances of Type VA and VB construction for R-3 occupancies.

h.	See Exception 12 of Section D105.1 for allowances of Type VA construction for R-3 occupancies in Lower Density Growth Management Areas.

i.	Type IV construction utilizing cross-laminated timber or structural composite lumber shall be sprinklered where required by Section 903.2.13.

506.2.1 Single-occupancy, one-story buildings. The allowable area of a single-occupancy building with no more than one story above grade plane shall be determined in accordance with Equation 5-1:

(Equation 5-1)

where:

Allowable area (square feet).

Tabular allowable area factor (NS, S1, S13D or S13R value, as applicable) in accordance with Table 506.2.

Tabular allowable area factor in accordance with Table 506.2 for nonsprinklered building (regardless of whether the building is sprinklered).

Area increase factor due to frontage (percent) as calculated in accordance with Section 506.3.

506.2.2 Mixed-occupancy, one-story buildings. The allowable area of a mixed-occupancy building with no more than one story above grade plane shall be determined in accordance with the applicable provisions of Section 508.1 based on Equation 5-1 for each applicable occupancy.

[506.2.1 Width limits. The value of “W” shall be at least 20 feet (6096 mm). Where the value of W varies along the perimeter of the building, the calculation performed in accordance with Equation 5-2 shall be based on the weighted average of each portion of exterior wall and open space where the value of W is greater than or equal to 20 feet (6096 mm). Where W exceeds 30 feet (9144 mm), a value of 30 feet (9144 mm) shall be used in calculating the weighted average, regardless of the actual width of the open space. Where two or more buildings are on the same tax lot, W shall be measured from the exterior face of a building to the exterior face of an opposing building, as applicable.]

[Exception: The value of W divided by 30 shall be permitted to be a maximum of 2 when the building meets all requirements of Section 507 except for compliance with the 60-foot (18 288 mm) public way or yard requirement, as applicable.]

[506.2.2 Open space limits. Such open space shall be either on the same zoning lot or dedicated for public use and shall be accessed from a street or approved fire lane.]

[506.3 Automatic sprinkler system increase. Where a building is equipped throughout with an approved automatic sprinkler system in accordance with Section 903.3.1.1, the building area limitation in Table 503 is permitted to be increased by an additional 200 percent (Is = 2) for buildings with more than one story above grade plane and an additional 300 percent (Is = 3) for buildings with no more than one story above grade plane. These increases are permitted in addition to the height and story increases in accordance with Section 504.2.]

[Exceptions: The building area limitation increases shall not be permitted for the following conditions:]

[1.	The automatic sprinkler system increase shall not apply to buildings with an occupancy in Group H-1.]

[2.	The automatic sprinkler system increase shall not apply to the building area of an occupancy in Group H-2 or H-3.]

506.2.2.1 Group H-2 or H-3 mixed occupancies. For [buildings] a building containing [such] Group H-2 or H-3 occupancies, the allowable [building] area shall be determined in accordance with Section 508.4.2, with the sprinkler system increase applicable only to the portions of the building not classified as Group H-2 or H-3.

[3.	Fire-resistance rating substitution in accordance with Table 601, Note d.]

[506.4 Single occupancy buildings with more than one story. The total allowable building area of a single occupancy building with more than one story above grade plane shall be determined in accordance with this section.  The actual aggregate building area at all stories in the building shall not exceed the total allowable building area.]

[Exception: A single basement need not be included in the total allowable building area, provided such basement does not exceed the area permitted for a building with no more than one story above grade plane and the finished surface of the floor above the basement does not exceed 6 feet (1829 mm) above grade plane.]

[506.4.1 Area determination. The total allowable building area with more than one story above grade plane shall be determined by multiplying the allowable area per story (Aa), as determined in Section 506.1, by the number of stories above grade plane as listed below.]

[1.	For buildings with two stories above grade plane, multiply by 2;]

[2.	For buildings with three or more stories above grade plane, multiply by 3; and]

[3.	No story shall exceed the allowable area per story (Aa), as determined in Section 506.1 for the occupancies on that story.]

[Exceptions:]

[1.	Unlimited area buildings in accordance with Section 507.]

[2.	In Group R occupancies 6 stories or less in height, the maximum area of a building equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.2 shall be determined by multiplying the allowable area per story (Aa), as determined in Section 506.1, by the number of stories above grade plane.]

[506.5 Mixed occupancy area determination. The total allowable building area for buildings containing mixed occupancies shall be determined in accordance with the applicable provisions of this section.]

[Exception: A single basement need not be included in the total allowable building area, provided such basement does not exceed the area permitted for a building with no more than one story above grade plane and the finished surface of the floor above the basement does not exceed 6 feet (1829 mm) above grade plane.]

[506.5.1 No more than one story above grade plane. For buildings with no more than one story above grade plane and containing mixed occupancies, the total building area shall be determined in accordance with the applicable provisions of Section 508.1.]

506.2.3 Single-occupancy, multistory buildings. The allowable area of a single-occupancy building with more than one story above grade plane shall be determined in accordance with Equation 5-2:

(Equation 5-2)

where:

Allowable area (square feet).

Tabular allowable area factor (NS, S13D, S13R or SM value, as applicable) in accordance with Table 506.2.

Tabular allowable area factor in accordance with Table 506.2 for a nonsprinklered building (regardless of whether the building is sprinklered).

Area factor increase due to frontage (percent) as calculated in accordance with Section 506.3.

Actual number of building stories above grade plane, not to exceed three. For buildings equipped throughout with an automatic sprinkler system installed in accordance with Section 903.3.1.2, use the actual number of building stories above grade plane, not to exceed four.

No individual story shall exceed the allowable area (Aa) as determined by Equation 5-2 using the value of Sa = 1.

[506.5.2 No more than one story above grade plane. For buildings with no more than one story above grade plane and containing mixed occupancies, each story] 506.2.4 Mixed-occupancy, multistory buildings. Each story of a mixed-occupancy building with more than one story above grade plane shall individually comply with the applicable requirements of Section 508.1. For buildings with more than three stories above grade plane, the total building area shall be such that the aggregate sum of the ratios of the actual area of each story divided by the allowable area of such stories, determined in accordance with Equation 5-3 based on the applicable provisions of Section 508.1, shall not exceed [3] three.

(Equation 5-3)

where:

Allowable area (square feet).

Tabular allowable area factor (NS, S13D, S13R or SM value, as applicable) in accordance with Table 506.2.

Tabular allowable area factor in accordance with Table 506.2 for a nonsprinklered building (regardless of whether the building is sprinklered).

Area factor increase due to frontage (percent) as calculated in accordance with Section 506.3.

Exception: For buildings designed as separated occupancies under Section 508.4 and equipped throughout with an automatic sprinkler system installed in accordance with Section 903.3.1.2, the total building area shall be such that the aggregate sum of the ratios of the actual area of each story divided by the allowable area of such stories determined in accordance with Equation 5-3 based on the applicable provisions of Section 508.1, shall not exceed four.

506.2.4.1 Group H-2 or H-3 mixed occupancies. For a building containing Group H-2 or H-3 occupancies, the allowable area shall be determined in accordance with Section 508.4.2, with the sprinkler system increase applicable only to the portions of the building not classified as Group H-2 or H-3.

506.3 Frontage increase. Area factor increase shall be determined in accordance with Sections 506.3.1 through 506.3.3.

506.3.1 Minimum percentage of perimeter. To qualify for an area factor increase based on frontage, a building shall have not less than 25 percent of its perimeter on a public way or open space. Such open space shall be either on the same zoning lot or dedicated for public use and shall be accessed from a street or approved fire lane.

506.3.2 Minimum frontage distance. To qualify for an area factor increase based on frontage, the public way or open space adjacent to the building perimeter shall have a minimum distance (W) of 20 feet (6096 mm) measured at right angles from the building face to any of the following:

1.	The closest interior tax lot line.

2.	The entire width of a street, alley or public way.

3.	The exterior face of an adjacent building on the same tax lot.

Where the value of W is greater than 30 feet (9144 mm), a value of 30 feet (9144 mm) shall be used in calculating the building area increase based on frontage, regardless of the actual width of the public way or open space. Where the value of W varies along the perimeter of the building, the calculation performed in accordance with Equation 5-5 shall be based on the weighted average calculated in accordance with Equation 5-4.

(Equation 5-4)

where:

(Width: weighted average) = Calculated width of public way or open space (feet).

Length of a portion of the exterior perimeter wall.

Width ( 20 feet) of a public way or open space associated with that portion of the exterior perimeter wall.

Building perimeter that fronts on a public way or open space having a width of 20 feet (6096 mm) or more.

Exception: Where a building meets the requirements of Section 507, as applicable, except for compliance with the minimum 60-foot (18 288 mm) public way or yard requirement, and the value of W is greater than 30 feet (9144 mm), the value of W shall not exceed 60 feet (18 288 mm).

506.3.3 Amount of increase. The area factor increase based on frontage shall be determined in accordance with Equation 5-5:

(Equation 5-5)

where:

Area increase factor due to frontage.

Building perimeter that fronts on a public way or open space having minimum distance of 20 feet (6096 mm).

Perimeter of entire building (feet).

Width of public way or open space (feet) in accordance with Section 506.3.2.

SECTION BC 507
UNLIMITED AREA BUILDINGS

507.1 General. The area of buildings of the occupancies and configurations specified in [Section] Sections [507] 507.1 through 507.18 shall not be limited, except that only one cellar or one basement shall be permissible.

507.1.1 Accessory occupancies. Accessory occupancies shall be permitted in unlimited area buildings in accordance with the provisions of Section 508.2, otherwise the requirements of Sections 507.3 through 507.18 shall be applied, where applicable.

507.2 Measurement of open spaces. Where Sections 507.3 through 507.18 require buildings to be surrounded and adjoined by public ways and yards, those open spaces shall be determined as follows:

1.	Yards shall be measured from the building perimeter in all directions to the closest interior lot lines or to the exterior face of an opposing building located on the same tax lot, as applicable.

2.	Where the building fronts on a public way, the entire width of the public way shall be used.

507.2.1 Reduced open space. The public ways or yards of 60 feet (18 288 mm) in width required in Sections 507.3, 507.4, 507.5 and 507.6 shall be permitted to be reduced to not less than 40 feet (12 192 mm) in width provided all of the following requirements are met:

1.	The reduced width shall not be allowed for more than 75 percent of the perimeter of the building.

2.	The exterior walls facing the reduced width shall have a fire-resistance rating of not less than 3 hours.

3.	Openings in the exterior walls facing the reduced width shall have opening protectives with a fire protection rating of not less than 3 hours.

[507.2] 507.3 Nonsprinklered, [one story] one-story buildings. The area of a Group F-2 or S-2 building no more than one story in height, of other than Type V construction, shall not be limited when the building is surrounded and adjoined on all sides by public ways or yards not less than 60 feet (18 288 mm) in width.

[507.3] 507.4 Sprinklered, [one story] one-story buildings. The area of a Group A-4 building no more than one story in height above grade plane of other than Type V construction, or the area of a Group B, F, M or S building no more than one story [in height or a Group A-4 building no more than one story in height of other than Type V construction] in height of any construction type, shall not be limited [when] where the building is provided with an automatic sprinkler system throughout in accordance with Section 903.3.1.1[,] and is surrounded and adjoined on all sides by public ways or yards not less than 60 feet (18 288 mm) in width.

Exceptions:

- In Group F-2 and S-2 occupancies, one-story rack storage facilities of Type II construction that are not accessible to the public shall not be limited in height provided that such buildings conform to the requirements of the New York City Fire Code, and Sections [507.3,] 507.4 and 903.3.1.1 of this code [and the New York City Fire Code].

2.	The automatic sprinkler system shall not be required in areas occupied for indoor participant sports, such as tennis, skating, swimming and equestrian activities, in occupancies in Group A-4, provided that both of the following criteria are met:

2.1.	Exit doors directly to the outside are provided for occupants of the participant sports areas[; and].

2.2.	The building is equipped with a fire alarm system with manual fire alarm boxes installed in accordance with Section 907.

[507.3.1] 507.4.1 Mixed occupancy buildings with Groups A-1 and A-2. Group A-1 and A-2 occupancies of other than Type V construction shall be permitted within mixed occupancy buildings of unlimited area complying with Section [507.3] 507.4, provided all of the following criteria are met:

1.	Group A-1 and A-2 occupancies are separated from other occupancies as required for separated occupancies in Section 508.4.4 with no reduction allowed in the fire-resistance rating of the separation based upon the installation of an automatic sprinkler system[;].

2.	Each area of the portions of the building used for Group A-1 or A-2 occupancies shall not exceed the maximum allowable area permitted for such occupancies in Section 503.1[; and].

3.	[All exit] Exit doors from Group A-1 and A-2 occupancies shall discharge directly to the exterior of the building.

[507.4] 507.5 Sprinklered, [two story] two-story buildings. The area of a Group B, F, M or S building no more than two stories in height shall not be limited when the building is provided with an automatic sprinkler system in accordance with Section 903.3.1.1 throughout, and is surrounded and adjoined on all sides by public ways or yards not less than 60 feet (18 288 mm) in width.

[507.5 Reduced open space. The public ways or yards of 60 feet (18 288 mm) required in Sections 507.2, 507.3, 507.4 and 507.6 shall be permitted to be reduced to not less than 40 feet (12 192 mm) in width provided all of the following requirements are met:]

[1.	The reduced width shall not be allowed for more than 75 percent of the perimeter of the building.]

[2.	The exterior wall facing the reduced width shall have a minimum fire-resistance rating of 3 hours.]

[3.	Openings in the exterior wall, facing the reduced open space, shall have opening protectives with a minimum fire-resistance rating of 3 hours.]

507.6 Group A buildings. The area of a Group A-1, A-2, A-3, or A-4 building of Type IIA, IIIA or IV construction shall not be limited where the building is equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1. The area of a one-story, Group A-3 building used as a house of worship, community hall, dance hall, exhibition hall, gymnasium, lecture hall, indoor swimming pool or tennis court of Type IIB construction shall not be limited when all of the following criteria are met:

- The building shall not have a stage other than a platform.

- The building shall be equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1.

- The assembly floor shall be located at or within 21 inches (533 mm) of street or grade level and all exits are provided with ramps complying with Section [1010.1]  1012.1 to the street or grade level.

- The building shall be surrounded and adjoined on all sides by public ways or yards not less than 60 feet (18 288 mm) in width.

507.7 Reserved.

507.8 Group H occupancies. Group H-2, H-3 and H-4 fire occupancies shall be permitted in unlimited area buildings containing [Groups] Group F [and] or S occupancies[,] in accordance with Sections [507.3] 507.4 and [507.4] 507.5 and the [limitations of this section] provisions of Sections 507.8.1 through 507.8.4.

507.8.1 Allowable area. The aggregate floor area of [the] Group H occupancies located [at the perimeter of the] in an unlimited area building shall not exceed 10 percent of the area of the building[, nor] and shall not exceed the area limitations for the Group H occupancies as specified in [Table 503 as modified by Section 506.2,] Section 506 based [upon] on [the percentage of] the perimeter of [the] each Group H floor area that fronts on a [street] public way or [other unoccupied] open space.

507.8.1.1 Located within the building. The aggregate floor area of Group H occupancies not located at the perimeter of the building [as allowed by Section 415.3] shall not exceed 25 percent of the area limitations for the Group H occupancies as specified in [Table 503] Section 506.

507.8.1.1.1 Liquid use, dispensing and mixing rooms. Liquid use, dispensing and mixing rooms having a floor area of not more than 500 square feet (46.5 m2) need not be located on the outer perimeter of the building where they are in accordance with the New York City Fire Code and NFPA 30.

507.8.1.1.2 Liquid storage rooms. Liquid storage rooms having a floor area of not more than 1,000 square feet (93 m2) need not be located on the outer perimeter where they are in accordance with the New York City Fire Code and NFPA 30.

507.8.1.1.3 Spray paint booths. Spray paint booths that comply with the New York City Fire Code need not be located on the outer perimeter.

507.8.2 Located on building perimeter. Except as provided for in Section 507.8.1.1, Group H occupancies shall be located on the perimeter of the building. In Group H-2 and H-3 occupancies, not less than 25 percent of the perimeter of such occupancies shall be an exterior wall.

507.8.3 Occupancy separations. Group H occupancies shall be separated from the [rest] remainder of the unlimited area [buildings] building and from each other in accordance with Table 508.4.

507.8.4 Height limitations. For two-story, unlimited area buildings, [the] Group H occupancies shall not be located more than one story above grade plane unless permitted [by] based on the allowable height [in] and number of stories and feet as set forth in [Table 503] Section 504 based on the type of construction of the unlimited area building.

507.9 Unlimited mixed occupancy buildings with Group H-5. The area of a Group B, F, H-5, M or S building no more than two stories above grade plane shall not be limited where the building is equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1, and is surrounded and adjoined by public ways or yards not less than 60 feet (18 288 mm) in width, provided all of the following criteria are met:

1.	Buildings containing Group H-5 occupancy shall be of Type I or II construction.

2.	Each area used for Group H-5 occupancy shall be separated from other occupancies as required in Sections 415.11 and 508.4.

3.	Each area used for Group H-5 occupancy shall not exceed the maximum allowable area permitted for such occupancies in Section 503.1 including modifications of Section 506.

Exception: Where the Group H-5 occupancy exceeds the maximum allowable area, the Group H-5 shall be subdivided into areas that are separated by 2-hour fire barriers.

[507.9] 507.10 Aircraft paint hangar. The area of a Group H-2 aircraft paint hangar no more than one story above grade plane shall not be limited where such aircraft paint hangar complies with the provisions of Section 412.6 and is surrounded and adjoined by public ways or yards not less in width than one and one-half times the building height.

[507.10] 507.11 Group E buildings. The area of a Group E building of Type IIA, IIIA or IV construction shall not be limited where the building is protected throughout with an approved automatic sprinkler system in accordance with Section 903.3.1.1. The area of a one-story Group E building of Type IIB construction shall not be limited when the following criteria are met:

1.	Each classroom shall have not less than two means of egress, with one of the means of egress being a direct exit to the outside of the building complying with Section [1020]  1022.

2.	The building is equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1.

3.	The building is surrounded and adjoined on all sides by public ways or yards not less than 60 feet (18 288 mm) in width.

[507.11] 507.12 Motion picture theaters. In buildings of Type II, IIIA and IV construction, the area of a motion picture theater located on the first story above grade plane shall not be limited when the building is provided with an automatic sprinkler system throughout in accordance with Section 903.3.1.1 and is surrounded and adjoined on all sides by public ways or yards not less than 60 feet (18 288 mm) in width.

[507.12] 507.13 Covered and open mall buildings and anchor [stores] buildings. The area of covered and open mall buildings and anchor [stores] buildings not exceeding three stories in height that comply with Section [402.6] 402 shall not be limited.

[507.13] 507.14 Group B buildings. Notwithstanding the provisions of Sections [507.2] 507.3 and [507.3] 507.4, the area of a Group B building of Type IIA, IIIA or IV construction shall not be limited where the building is protected throughout with an approved automatic sprinkler system in accordance with Section 903.3.1.1.

[507.14] 507.15 Group F-2 buildings. Notwithstanding the provisions of Sections [507.2] 507.3 and [507.3] 507.4, the area of a Group F-2 building of Type IIA, IIIA or IV construction shall not be limited where the building is protected throughout with an approved automatic sprinkler system in accordance with Section 903.3.1.1.

[507.15] 507.16 Group M buildings. Notwithstanding the provisions of Sections [507.2] 507.3 and [507.3] 507.4, the area of a Group M building of Type IIA, IIIA or IV construction shall not be limited where the building is protected throughout with an approved automatic sprinkler system in accordance with Section 903.3.1.1.

[507.16] 507.17 Group R buildings. The area of Group R-1 and R-2 buildings of Type IIA, IIIA or IV construction shall not be limited where the building is protected throughout with an approved automatic sprinkler system in accordance with Section 903.3.1.1 or 903.3.1.2, as applicable.

[507.17] 507.18 Group S-2 buildings. Notwithstanding the provisions of Sections [507.2] 507.3 and [507.3] 507.4, the area of a Group S-2 building of Type IB, IIA, IIIA or IV construction shall not be limited where the building is protected throughout with an approved automatic sprinkler system in accordance with Section 903.3.1.1.

SECTION BC 508
MIXED USE AND OCCUPANCY

508.1 General. Each portion of a building shall be individually classified in accordance with Section 302.1. Where a building contains more than one occupancy group, the building or portion thereof shall comply with the applicable provisions of Section 508.2, 508.3 or 508.4, or a combination of these sections.

Exceptions:

1.	Occupancies separated in accordance with Section 510.

2.	Where required by Table [415.5.2] 415.6.2, areas of Group H-1, H-2 and H-3 occupancies shall be located in a detached building or structure.

3.	Where identified in Table 509, rooms or spaces shall be treated as incidental uses.

4.	Where not identified in Table 509, mechanical and/or electrical equipment rooms shall be permitted to be classified as the occupancy within which they are located, or at the option of the applicant, classified as Group F-2 occupancy in accordance with Section 306.3.

5.	Commercial kitchens classified as Group F-2 need not be separated by fire separations from adjoining dining spaces, provided that the conditions of Items 5.1, 5.2, and 5.3 are met:

5.1.	The cooking equipment is vented directly to the outdoors;

5.2.	A draft curtain of noncombustible material, at least 24 inches (609 mm) down from the ceiling, is provided to separate the opening between the cooking facilities and the dining spaces; and

5.3.	A fire protection system is installed and located as set forth in Item 5.3.1 or 5.3.2.

5.3.1.	A fire protection system in accordance with Sections 903 and 904 is installed within the cooking facilities. Additionally, sprinkler heads protecting the opening between the cooking facilities and the dining spaces shall be located within 24 inches (609 mm) of the curtain on the cooking facilities side; or

5.3.2.	A fire protection system in accordance with Section 903 is located along any opening between the cooking facilities and the dining space on the cooking facilities side, with sprinkler heads located within 24 inches (609 mm) of the opening and, if the opening is more than 60 inches (1524 mm) wide, the sprinkler heads are spaced not more than 48 inches (1219 mm) on center.

Where the conditions of Items 5.1, 5.2, and 5.3 cannot be satisfied, such commercial kitchen shall be separated from adjoining dining spaces in accordance with Table 508.4, footnote f.

508.2 Accessory occupancies. Accessory occupancies are those occupancies that are ancillary to the main occupancy of the building or portion thereof. Accessory occupancies shall comply with the provisions of Sections 508.2.1 through 508.2.4.

[508.2.1 Area limitations. Aggregate accessory occupancies shall not occupy more than 10 percent of the building area of the story in which they are located and shall not exceed the tabular values in Table 503, without building area increases in accordance with Section 506 for such accessory occupancies.]

[Exceptions:]

[1.	The following accessory occupancies are permitted to occupy more than 10 percent of the floor area of the story in which they are located:]

[1.1. Accessory assembly areas having a floor area less than 750 square feet (69.7 m2).]

[1.2. Assembly areas that are accessory to Group E occupancies.]

[1.3. Accessory religious educational rooms and religious auditoriums with occupant loads of less than 100.]

[2.	Rooms or spaces within Group H-2, H-3, H-4 or H-5 occupancy shall not be considered accessory occupancies and shall be treated as separated occupancies.]

[508.2.2] 508.2.1 Occupancy classification. Accessory occupancies shall be individually classified in accordance with Section 302.1. The requirements of this code shall apply to each portion of the building based on the occupancy classification of that space.

508.2.2 Allowable building height. The allowable height and number of stories of the building containing accessory occupancies shall be in accordance with Section 504 for the main occupancy of the building.

508.2.3 Allowable building area [and height]. [The allowable building area and height of the building shall be based on the allowable building area and height for the main occupancy in accordance with Section 503.1.  The height of each accessory occupancy shall not exceed the tabular values in Table 503, without increases in accordance with Section 504 for such accessory occupancies. The building area of the accessory occupancies shall be in accordance with Section 508.2.1.] The allowable area of the building shall be based on the applicable provisions of Section 506 for the main occupancy of the building. Aggregate accessory occupancies shall not occupy more than 10 percent of the building area of the story in which they are located and shall not exceed the tabular values for nonsprinklered buildings in Table 506.2 for each such accessory occupancy.

Exceptions:

1.	The following accessory occupancies are permitted to occupy more than 10 percent of the floor area of the story in which they are located:

1.1.	Accessory assembly areas having a floor area less than 750 square feet (69.7 m2).

1.2.	Assembly areas that are accessory to Group E occupancies.

1.3.	Accessory religious educational rooms and religious auditoriums with occupant loads of less than 100.

2.	Rooms or spaces within Group H-2, H-3, H-4 or H-5 occupancy shall not be considered accessory occupancies and shall be treated as separated occupancies.

508.2.4 Separation of occupancies. No separation is required between accessory occupancies and the main occupancy.

Exceptions:

1.	Group H-2, H-3, H-4 and H-5 occupancies shall be separated from all other occupancies in accordance with Section 508.4.

2.	Separated tenancies in accordance with the requirements of Section 510.

508.3 Nonseparated occupancies. Buildings or portions of buildings that comply with the provisions of this section shall be considered as nonseparated occupancies.

508.3.1 Occupancy [Classification] classification. Nonseparated occupancies shall be individually classified in accordance with Section 302.1. The requirements of this code shall apply to each portion of the building based on the occupancy classification of that space. In addition, the most restrictive provisions of Chapter 9 [which] that apply to the nonseparated occupancies shall apply to the total nonseparated occupancy area. Where nonseparated occupancies occur in a high-rise building, the most restrictive requirements of Section 403 [which] that apply to the nonseparated occupancies shall apply throughout the high-rise building.

508.3.2 Allowable building area and height. The allowable building area and height of the building or portion thereof shall be based on the most restrictive allowances for the occupancy groups under consideration for the type of construction of the building in accordance with Section 503.1.

508.3.3 Separation. No separation is required between nonseparated occupancies.

Exceptions:

- Group H-2, H-3, H-4 and H-5 occupancies shall be separated from all other occupancies in accordance with Section 508.4.

2.	Separated tenancies in accordance with Section 510.10.

3.	 [Kitchens] Commercial kitchens shall be separated in accordance with Section [508.4.4] 508.1, Exception 5.

508.4 Separated occupancies. Buildings or portions of buildings that comply with the provisions of this section shall be considered as separated occupancies.

| TABLE 508.4 REQUIRED SEPARATION OF OCCUPANCIES (HOURS) |
| --- |
| OCCUPANCY | A, E | I-1a, I-3, I-4 | I-2 | Ra | F-2, S-2b, U | Be | F-1 | M | S-1 | H-1 | H-2 | H-3, H-4 | H-5 |
|  | S | NS | S | NS | S | NS | S | NS | S | NS | S | NS | S | NS | S | NS | S | NS | S | NS | S | NS | S | NS | S | NS |
| A, E | N | N | 1 | 2 | 2 | NP | 1 | 2 | Nf | 1f | 1 | 2 | 1 | 2 | 1 | 2 | 1 | 2 | NP | NP | 3 | 4 | 2 | 3 | 2 | NP |
| I-1a, I-3, I-4 | -- | -- | N | N | 2 | NP | 1 | NP | 1 | 2 | 1 | 2 | 1 | 2 | 1 | 2 | 1 | 2 | NP | NP | 3 | NP | 2 | NP | 2 | NP |
| I-2 | -- | -- | -- | -- | N | N | 2 | NP | 2 | NP | 2 | NP | 2 | NP | 2 | NP | 2 | NP | NP | NP | 3 | NP | 2 | NP | 2 | NP |
| Ra | -- | -- | -- | -- | -- | -- | N | N | 1c | 2c | 1 | 2 | 1 | 2 | 1 | 2 | 1 | 2 | NP | NP | 3 | NP | 2 | NP | 2 | NP |
| F-2, S-2b, U | -- | -- | -- | -- | -- | -- | -- | -- | N | N | 1 | 2 | 1 | 2 | 1 | 2 | 1 | 2 | NP | NP | 3 | 4 | 2 | 3 | 2 | NP |
| Be | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | N | N | 2 | 3 | 1 | 2 | 2 | 3 | NP | NP | 2 | 3 | 1 | 2 | 1 | NP |
| F-1 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | N | N | 2 | 3 | 2 | 3 | NP | NP | 2 | 3 | 1 | 2 | 1 | NP |
| M | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | N | N | 2 | 3 | NP | NP | 2 | 3 | 1 | 2 | 1 | NP |
| S-1 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | N | N | NP | NP | 2 | 3 | 1 | 2 | 1 | NP |
| H-1 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | N | NP | NP | NP | NP | NP | NP | NP |
| H-2 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | N | NP | 1 | NP | 1 | NP |
| H-3, H-4 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | 1d | NP | 1 | NP |
| H-5 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- | N | NP |

S = Buildings equipped throughout with an automatic sprinkler system installed in accordance with Section 903.3.1.1.

NS = Buildings not equipped throughout with an automatic sprinkler system installed in accordance with Section 903.3.1.1.

N = No separation requirement.

NP = Not permitted.

a.	See Section 420.

b.	The required separation from areas used only for private or pleasure vehicles shall be reduced by 1 hour but to not less than 1 hour.

c.	See Section [406.1.4] 406.3.4.

d.	Separation is not required between occupancies of the same classification.

e.	See Section 422.2 for ambulatory care facilities.

f.	A commercial kitchen in Group F-2 that does not comply with Section 508.1, Exception 5 shall be separated from adjoining dining spaces with 1-hour fire separation where the dining spaces are equipped throughout with an automatic sprinkler system installed in accordance with Section 903.3.1.1, and separated with 2-hour fire separation where the dining spaces is not equipped throughout with an automatic sprinkler system.

508.4.1 Occupancy classification. Separated occupancies shall be individually classified in accordance with Section 302.1. Each separated space shall comply with this code based on the occupancy classification of that portion of the building.

508.4.2 Allowable building area. In each story, the building area shall be such that the sum of the ratios of the actual building area of each separated occupancy divided by the allowable building area of each separated occupancy shall not exceed 1.

508.4.3 Allowable height. Each separated occupancy shall comply with the building height limitations based on the type of construction of the building in accordance with Section 503.1.

Exception: Special provisions [permitted by] of Section 510 shall permit occupancies at building heights other than provided in Section 503.1.

508.4.4 Separation. Individual occupancies shall be separated from adjacent occupancies in accordance with Table 508.4.

[Exceptions] Exception:

[1.	] Fire separations of Group H and I-2 occupancies shall not be permitted any reductions in fire-resistance ratings.

[2.	Nonresidential kitchens need not be separated by fire separations from adjoining dining spaces, provided that all of the following conditions are satisfied:]

[2.1.	The cooking equipment is vented directly to the outdoors; and]

[2.2.	A draft curtain of noncombustible material, at least 24 inches (609 mm) down from the ceiling, is provided to separate the cooking facilities from dining spaces; and]

[2.3.	Fire protection systems in accordance with the provisions of Section 903 and 904 are provided on the cooking facilities side of the curtain, or any opening between the kitchen and dining space, located within 24 inches (609 mm) of the curtain or opening, and spaced not more than 48 inches (1219 mm) on center if the opening is more than 60 inches (1524 mm) wide.]

508.4.4.1 Construction. Required separations shall be fire barriers constructed in accordance with Section 707 or horizontal assemblies constructed in accordance with Section [712] 711, or both, so as to completely separate adjacent occupancies.

SECTION BC 509
INCIDENTAL USES

509.1 General. Incidental uses listed in Table 509 and located within single occupancy or mixed occupancy buildings shall comply with the provisions of this section. Incidental uses are ancillary functions associated with a given occupancy that generally pose a greater level of risk to that occupancy and are limited to those uses listed in Table 509.

Exception: Incidental uses within and serving a dwelling unit are not required to comply with this section.

| TABLE 509c INCIDENTAL USES |
| --- |
| ROOM OR AREA | SEPARATION AND/OR PROTECTION |
| Furnace room where any piece of equipment is over 350,000 Btu per hour input | 2 hour; or 1 hour and provide automatic sprinkler systema |
| Furnace room where any piece of equipment is 350,000 Btu per hour input or less, except in R-3 occupancy | 1 hour or provide automatic sprinkler systema |
| Rooms with a high pressure steam or water boiler that exceeds 350,000 Btu per hour input | 2 hour; or 1 hour and provide automatic fire-extinguishing systema |
| Rooms with a high pressure steam or water boiler that is 350,000 Btu per hour input or less | 1 hour or provide automatic sprinkler systema |
| Rooms that contain a low pressure steam or water boiler regardless of Btu per hour input | 1 hour or provide automatic sprinkler systema, b |
| Refrigerant machinery room | 1 hour or provide automatic sprinkler system |
| Hydrogen fuel gas rooms, not classified as Group H | 2 hours in all occupancies |
| Incinerator rooms | 2 hours and provide automatic sprinkler system |
| Paint shops, not classified a Group H, located in occupancies other than Group F | 2 hours; or 1 hour and provide automatic sprinkler system |
| In Group E occupancies, laboratories [Laboratories] and vocational shops[,] not classified as Group H[, located in a Group E or I-2 occupancy] | 1 hour or provide automatic sprinkler system |
| In Group I-2 occupancies, laboratories not classified as Group H | 1 hour and provide automatic sprinkler system |
| In ambulatory care facilities, laboratories not classified as Group H | 1 hour or provide automatic sprinkler system |
| Laundry rooms over 100 square feet | 1 hour or provide automatic sprinkler system |
| In Group I-2, laundry rooms over 100 square feet | 1 hour |
| Group I-3 cells and Group I-2 patient rooms equipped with padded surfaces | 1 hour |
| In Group I-2, physical plant maintenance shops | 1 hour |
| In ambulatory care facilities or Group I-2 occupancies, waste [Waste] and linen collection rooms with containers that have an aggregate volume of 10 cubic feet or greater[located in either Group I-2 occupancies or ambulatory care facilities] | 1 hour |
| In other than ambulatory care facilities and Group I-2 occupancies, waste [Waste] and linen collection rooms over 100 square feet | 1 hour or provide automatic sprinkler system |
| In ambulatory care facilities or Group I-2 occupancies, storage rooms greater than 100 square feet | 1 hour |
| Stationary storage battery systems having [a liquid electrolyte capacity of more than 50 gallons for flooded lead-acid, nickel cadmium or VRLA, or more than 1,000 pounds for lithium-ion and lithium metal polymer used for facility standby power, emergency power or uninterruptable power supplies] an energy capacity greater than the threshold quantity specified in Table 608.9.1.1 of the New York City Fire Code | 1 hour in group B, F, M, S and U occupancies; 2 hours in Group A, E, I and R occupancies |
| Rooms containing fire pumps in non-high-rise buildings | 2 hours; or 1 hour and provide automatic sprinkler system throughout the building |
| Rooms containing fire pumps in high-rise buildings | 2 hours |

a.	Boilers servicing more than one dwelling unit in multiple dwellings shall also comply with Section 65 of the New York State Multiple Dwelling Law.

b.	Sealed combustion direct vent boilers shall comply with Section 303 of the New York City Mechanical Code and Section 303 of the New York City Fuel Gas Code, as applicable.

c.	For mechanical and/or electrical equipment rooms not identified in this Table, see Section 508.1.

For SI: 1 square foot = 0.0929 m2, 1 pound per square inch (psi) = 6.9 kPa, 1 British thermal unit (Btu) per hour = 0.293 watts, 1 horsepower = 746 watts, 1 gallon = 3.785 L, 1 cubic foot = 0.0283m3.

509.2 Occupancy classification. Incidental uses shall not be individually classified in accordance with Section 302.1. Incidental uses shall be included in the building occupancies within which they are located.

509.3 Area limitations. Incidental uses shall not occupy more than 10 percent of the building in which they are located.

509.4 Separation and protection. The incidental uses listed in Table 509 shall be separated from the remainder of the building or equipped with an automatic sprinkler system, or both, in accordance with the provisions of that table.

509.4.1 Separation. Where Table 509 specifies a fire-resistance-rated separation, the incidental uses shall be separated from the remainder of the building by a fire barrier constructed in accordance with Section 707 or a horizontal assembly constructed in accordance with Section [712] 711, or both. Construction supporting 1-hour fire barriers or horizontal assemblies used for incidental use separations in buildings of Type IIB, IIIB and VB construction is not required to be fire-resistance rated unless required by other sections of this code.

509.4.2 Protection. Where Table 509 permits an automatic sprinkler system without a fire barrier, the incidental uses shall be separated from the remainder of the building by construction capable of resisting the passage of smoke. The walls shall extend from the top of the foundation or floor assembly below to the underside of the ceiling that is a component of a fire-resistance-rated floor assembly or roof assembly above or to the underside of the floor or roof sheathing, [desk] deck or slab above. Doors shall be self- or automatic-closing upon detection of smoke in accordance with Section [715.4.8.3] 716.5.9.3. Doors shall not have air transfer openings and shall not be undercut in excess of the clearance permitted in accordance with NFPA 80. Walls surrounding the incidental use shall not have air transfer openings unless provided with smoke dampers in accordance with Section [710.7] 710.8.

509.4.2.1 Protection limitation. Except as specified in Table 509 for certain incidental uses, where an automatic sprinkler system is provided in accordance with Table 509, only the space occupied by the incidental use need be equipped with such a system.

SECTION BC 510
SPECIAL PROVISIONS

510.1 General. The provisions in [this section] Sections 510.2 through 510.10 shall permit the use of special conditions that are exempt from, or modify, the specific requirements of this chapter regarding the allowable building heights and areas of buildings based on the occupancy classification and type of construction, provided the special condition complies with the provisions specified in this section for such condition and other applicable requirements of this code. The provisions of Sections 510.2 through 510.8 are to be considered independent and separate from each other.

510.2 Horizontal building separation allowance. Buildings shall be considered as separate and distinct from each other for the purpose of determining area limitations, continuity of fire walls, limitation of number of stories and type of construction, where all of the following conditions are met:

1.	The buildings are separated with a horizontal floor assembly having a [minimum 3-hour] fire-resistance rating of not less than 3 hours.

2.	[The building below the horizontal assembly is no more than one story above grade plane.]

[3.	] The building below the horizontal assembly is of Type IA construction.

[4.	] 3. Shaft, stairway, ramp or escalator enclosures through the horizontal floor assembly shall have [a minimum of] not less than a 2-hour fire-resistance rating with opening protectives in accordance with Section [715.4] 716.5.

Exception: Where the enclosure walls below the horizontal floor assembly have [a minimum of] not less than a 3-hour fire-resistance rating with opening protectives in accordance with Section [715.4] 716.5, the enclosure walls extending above the horizontal floor assembly shall be permitted to have a 1-hour fire-resistance rating, provided:

[4.1.]  1.	The building above the horizontal floor assembly is not required to be of Type I construction;

[4.2.] 2.	The enclosure connects [less] fewer than four stories[,]; and

[4.3.] 3.	The enclosure opening protectives above the horizontal floor assembly have a [minimum 1-hour] fire protection rating of not less than 1 hour.

[5.] 4.	The building or buildings above the horizontal assembly shall be permitted to have multiple Group A occupancy uses, each with an occupant load of less than 300, or Group B, M, R[,] or S occupancies.

[6.] 5.	The building below the horizontal assembly shall be protected throughout by an approved automatic sprinkler system in accordance with Section 903.3.1.1, and shall be permitted to be any [of the following occupancies:]

[6.1.	Group S-2 parking garage used for the parking and storage of private motor vehicles.]

[6.2.	Uses incidental to the operation of the building (including entry lobbies, mechanical rooms, storage areas and similar uses).] occupancy allowed by this code except Group H.

[7.] 6.	The maximum building height in feet (mm) as measured from the grade plane shall not exceed the limits set forth in Section [503] 504.3 for the building having the smaller allowable height as measured from the grade plane.

510.3 Group S-2 enclosed parking garage with Group S-2 open parking garage above. A Group S-2 enclosed parking garage with [no] not more than one story above grade plane and located below a Group S-2 open parking garage shall be classified as a separate and distinct building for the purpose of determining the type of construction where all of the following conditions are met:

1.	The allowable area of the building shall be such that the sum of the ratios of the actual area divided by the allowable area for each separate occupancy shall not exceed 1.

2.	The Group S-2 enclosed parking garage is of Type I or II construction and is at least equal to the fire-resistance requirements of the Group S-2 open parking garage.

3.	The height and the number of the tiers of the Group S-2 open parking garage shall be limited as specified in Table [406.3.5] 406.5.4.

4.	The floor assembly separating the Group S-2 enclosed parking garage and Group S-2 open parking garage shall be protected as required for the floor assembly of the Group S-2 enclosed parking garage. Openings between the Group S-2 enclosed parking garage and Group S-2 open parking garage, except exit openings, shall not be required to be protected.

5.	The Group S-2 enclosed parking garage is used exclusively for the parking or storage of private motor vehicles, but shall be permitted to contain an accessory office, waiting room and toilet room having a total area of not more than 1,000 square feet (93 m2)[,] and mechanical equipment rooms incidental to the operation of the building.

510.4 Parking beneath Group R. Where a maximum [one-story] one story above grade plane Group S-2 parking garage, enclosed or open, or combination thereof, of Type I construction or open of Type IV construction, with grade entrance, is provided under a building of Group R, the number of stories to be used in determining the minimum type of construction shall be measured from the floor above such a parking area. The horizontal floor assembly between the parking garage and the Group R above shall comply with the type of construction required for the parking garage and shall also provide a fire-resistance rating not less than the mixed occupancy separation required in Section 508.4.

510.5 Reserved.

510.6 Group R-2 buildings of Type IIA construction. The height limitation for buildings of Type IIA construction in Group R-2 shall be increased to nine stories and 100 feet (30 480 mm) where the building is separated by not less than 50 feet (15 240 mm) from any other building on the lot and from lot lines, the exits are segregated in an area enclosed by a 2-hour fire-resistance-rated fire wall and the [first-floor] first floor assembly has a fire-resistance rating of not less than 11/2 hours.

510.7 Open parking garage beneath Groups A, I, B, M and R. Open parking garages constructed under Groups A, I, B, M and R shall not exceed the height and area limitations permitted under Section [406.3] 406.5. The height and area of the portion of the building above the open parking garage shall not exceed the limitations in Section 503 for the upper occupancy. The height, in both feet and stories, of the portion of the building above the open parking garage shall be measured from grade plane and shall include both the open parking garage and the portion of the building above the parking garage.

510.7.1 Fire separation. Fire barriers constructed in accordance with Section 707 or horizontal assemblies constructed in accordance with Section [712] 711 between the parking occupancy and the upper occupancy shall correspond to the required fire-resistance rating prescribed in Table 508.4 for the occupancies involved. The type of construction shall apply to each occupancy individually, except that structural members, including main bracing within the open parking structure, which is necessary to support the upper occupancy, shall be protected with the more restrictive fire-resistance-rated assemblies of the groups involved as shown in Table 601. Means of egress for the upper occupancy shall conform to Chapter 10 and shall be separated from the parking occupancy by fire barriers having [at least] not less than a 2-hour fire-resistance rating as required by Section 707, with self-closing doors complying with Section [715] 716 or horizontal assemblies having [at least] not less than a 2-hour fire-resistance rating as required by Section [712] 711, with self-closing doors complying with Section [715] 716. Means of egress from the open parking garage shall comply with Section [406.3] 406.5.

510.8 Industrial uses in buildings containing Group R. No space classified as Factory Industrial Group F shall be located above the second story of any building of Type III, IV or V construction containing a space classified as Residential Group R-1 or R-2.

510.9 Multiple buildings above Group S-2 parking garages. Where two or more buildings are provided above the horizontal assembly separating a Group S-2 open or closed parking garage from the buildings above in accordance with the special provisions in Section 510.2, 510.3 or 510.8, the buildings above the horizontal assembly shall be regarded as separate and distinct buildings from each other and shall comply with all other provisions of this code as applicable to each separate and distinct building.

510.10 Separation of different tenancies. Spaces or dwelling units occupied by different tenants shall be separated by fire barriers having at least 1-hour fire-resistance ratings.

Exceptions:

- Nonresidential spaces occupied by different tenants located in buildings that are sprinklered throughout.

- Tenant spaces in covered mall buildings complying with Section 402.

§ 7. Chapter 6 of the New York city building code, as amended by local law number 141 for the year 2013, is amended to read as follows:

CHAPTER 6
TYPES OF CONSTRUCTION

SECTION BC 601
GENERAL

601.1 Scope. The provisions of this chapter shall control the classification of buildings as to type of construction.

| TABLE 601 FIRE-RESISTANCE RATING REQUIREMENTS FOR BUILDING ELEMENTS ([hours] HOURS) |
| --- |
| BUILDING ELEMENT | TYPE I | TYPE II | TYPE III | TYPE IV | TYPE V[j]i |
|  | A | B | A[d] | B | A[d] | B | HT | A[d] | B |
| Primary structural frame [g,k]f (see Section 202) | 3a | 2a, j | 1j | 0 | 1 | 0 | HT | 1 | 0 |
| Bearing walls Exteriore,f,g [,h] Interior | 3 3a | 2 2a | 1 1 | 0 0 | 2 1 | 2 0 | 2 1/HT | 1 1 | 0 0 |
| Nonbearing walls and partitions Exterior | See Table 602 |
| Nonbearing walls and partitions Interior[e]d | 0 | 0 | 0 | 0 | 0 | 0 | See Section 602.4.6 | 0 | 0 |
| Floor construction[i,]h and associated secondary members (see Section 202) | 2 | 2 | 1 | 0 | 1 | 0 | HT | 1 | 0 |
| Roof construction [Including supporting beams and joists] and associated secondary [member] members (see Section 202) | 1½b,c | 1b,c | 1b,c | 0[b,]c | 1b,c | 0 | HT | 1b,c | 0 |

For SI: 1 foot = 304.8 mm.

a.	Roof supports: Fire-resistance ratings of primary structural frame and bearing walls are permitted to be reduced by 1 hour where supporting a roof only.

b.	1. Except in Group F-1, H, M and S-1 occupancies, fire protection of structural members in roof construction shall not be required, including protection of primary structural frame members within any portion of the roof, roof framing and decking where every part of the roof construction is 20 feet or more above any floor immediately below. Fire-retardant-treated wood members shall be allowed to be used for such unprotected members.

2. Except in Group F occupancies subject to regulation under Sections 264(1) and 264(2) of the New York State Labor Law, and in Group I-1, R-1, and R-2 occupancies, in Types I and II construction, fire-retardant–treated wood shall be allowed in buildings including girders and trusses as part of the roof construction when the building is:

- Type II construction of any height; or

ii.	Type I construction two stories or less; or when over two stories, the vertical distance from the upper floor to the roof is 20 feet or more.

c.	Except in Group F occupancies subject to regulation under Sections 264(1) and 264(2) of the New York State Labor Law, and in Group I-1, R-1 and R-2 occupancies, heavy timber shall be allowed where a 1-hour or less fire-resistance rating is required.

d.	[An approved automatic sprinkler system in accordance with Section 903.3.1.1 shall be allowed to be substituted for 1-hour fire-resistance-rated construction, provided such system is not otherwise required by other provisions of the code or used for an allowable area increase in accordance with Section 506.3 or an allowable height increase in accordance with Section 504.2. The 1-hour substitution for the fire resistance of exterior walls shall not be permitted.]

[e.]	Not less than the fire-resistance rating required by other sections of this code.

[f.]e.	Not less than the fire-resistance rating based on fire separation distance (see Table 602).

[g.]f.	Not less than the fire-resistance rating as referenced in Section 704.10.

[h.]g.	See note g of Table 602.

[i.]h.	See Section 711.2.4 for additional requirements.

[j.]i.	Type V construction is not permitted inside fire districts except as provided for in Section D105.1 of Appendix D.

[k.]j.	See Section [BC] 403.2.1 for additional requirements for high-rise buildings and fire-resistance rating of columns in such buildings.

| TABLE 602 FIRE-RESISTANCE RATING REQUIREMENTS FOR EXTERIOR WALLS BASED ON FIRE SEPARATION DISTANCEa,e,g,h,j |
| --- |
| FIRE SEPARATION DISTANCE = X (feet) | TYPE OF CONSTRUCTION | OCCUPANCY GROUP Hf | OCCUPANCY GROUP F-1, M, S-1g,i | OCCUPANCY GROUP A, B, E, F-2, I, R, S-2, Ub |
| X < 5c | All | 3 | 2 | 1 |
| 5 ≤ X < 10 | IA Others | 3 2 | 2 1 | 1 1 |
| 10 ≤ X < 30 | IA, IB IIB, VB Others | 2 1 1 | 1 0 1 | 1d 0 1d |
| X ≥ 30 | All | 0 | 0 | 0 |

For SI: 1 foot = 304.8 mm.

a.	Load-bearing exterior walls shall also comply with the fire-resistance rating requirements of Table 601.

b.	Group U when used as accessory to Group R-3 shall not be required to have a fire-resistance rating where the fire separation distance is 5 feet or more for free standing private garages in compliance with Section 406.1, and when the separation distance is 3 feet or more for other freestanding Group U buildings.  For free standing private garages where the fire separation distance is less than 5 feet, refer to Section [406.1] 406.3.4 for required fire-resistance rating for exterior walls.

c.	See Section 706.1.1 for party walls.

d.	Open parking garages complying with Section 406 shall not be required to have a fire-resistance rating.

e.	The fire-resistance rating of an exterior wall is determined based upon the fire separation distance of the exterior wall and the story in which the wall is located.

f.	For special requirements for Group H occupancies, see Section [415.3] 415.6.

g.	Inside the fire district, exterior load-bearing walls of Type II buildings shall have a fire-resistance rating not less than prescribed below:

X < 5		2 hours

5 ≤ X < 10		2 hours

10 ≤ X < 30		1 hour

X ≥ 30		As per [table] Table 602.

h.	Inside the fire district, exterior nonload-bearing walls of Type II buildings shall have a fire-resistance rating not less than prescribed below:

X < 5		As per Table 602

5 ≤ X<10		As per Table 602

10 ≤ X < 30		1 hour

X ≥ 30		As per Table 602.

i.	For special requirements for Group S aircraft hangars, see Section 412.4.1.

j.	Where Table 705.8 permits nonbearing exterior walls with unlimited area of unprotected openings, the required fire-resistance rating for the exterior walls is 0 hours.

602.1.1 Minimum requirements. A building or portion thereof shall not be required to conform to the details of a type of construction higher than that type which meets the minimum requirements based on occupancy even though certain features of such a building actually conform to a higher type of construction. Classification shall be that of the minimum requirement unless all of the requirements for the higher type of construction are met.

Exception: Portions of buildings that cantilever over an adjacent building or tax lot shall also comply with the fire-resistance ratings of Section 705.12.

602.2 Types I and II. Types I and II construction are those types of construction in which the building elements listed in Table 601 are of noncombustible materials, except as permitted in Section 603 and elsewhere in this code.

602.3 Type III. Type III construction is that type of construction in which the exterior walls are of noncombustible materials and the interior building elements are of any material permitted by this code. Fire-retardant-treated wood framing complying with Section 2303.2 shall be permitted within exterior wall assemblies of a 2-hour rating or less.

Exceptions:

- In Group I-1, R-1, and R-2 occupancies, all exterior walls, fire walls, exit passageways, and shaft enclosures shall be noncombustible.

- In Group F occupancies subject to Section 270(1) of the New York State Labor Law, all exterior wall assemblies and all structural elements shall meet the requirements for a “fireproof building” as such term is defined in Section 264 of such law.

- Inside the fire district, exterior load-bearing walls shall be constructed of noncombustible material.

- Inside the fire district, exterior nonload-bearing walls may be constructed with fire-retardant-treated wood complying with Section 2303.2 where the building is equipped throughout with an automatic sprinkler system in accordance with Sections 903.3.1.1 through 903.3.1.3, unless otherwise prohibited by Exception 1 or 2 above.

602.4 Type IV. Type IV construction [(Heavy Timber, HT)] is that type of construction in which the exterior walls are of noncombustible materials or other materials permitted by Section 602.4.1 or 602.4.2, and the interior building elements are of solid [or] wood, glue-laminated [wood] timber, heavy timber (HT), structural composite lumber (SCL), or cross-laminated timber (CLT) without concealed spaces. The minimum dimensions for permitted materials including solid timber, glued-laminated timber, structural composite lumber (SCL), and cross-laminated timber and details of Type IV construction shall comply with the provisions of Section 2304.11 and this section. [Fire-retardant-treated-wood framing complying with Section 2303.2 shall be permitted within exterior wall assemblies with a 2-hour rating or less. Minimum solid sawn nominal dimensions are required for structures built using Type IV construction (HT). For glued-laminated members the equivalent net finished width and depths corresponding to the minimum nominal width and depths of solid sawn lumber are required as specified in Table 602.4.] Interior walls and partitions not less than 1-hour fire-resistance rating or heavy timber complying with Section 2304.11.2.2 shall be permitted. Buildings of Type IV construction utilizing structural composite lumber (SCL) or cross-laminated timber (CLT) shall be equipped throughout with an automatic sprinkler system where required by Section 903.2.13. In buildings of Type IV construction utilizing structural composite lumber (SCL) or cross-laminated timber (CLT), a fire watch shall be maintained in accordance with Section 901.7.2 of the New York City Fire Code and Section 3303.3 of this code.

Exceptions:

1.	In Group I-1, R-1, and R-2 occupancies, all exterior walls, fire walls, exit passageways, and shaft enclosures shall be noncombustible.

2.	In Group F occupancies subject to Section 270(1) of the New York State Labor Law, all exterior wall assemblies and all structural elements shall meet the requirements for a "fireproof building" as defined in Section 264 of such law.

3.	Inside the fire district, exterior load-bearing walls shall be constructed of noncombustible material.

4.	Inside the fire district, exterior non-bearing walls may be constructed with fire-retardant-treated wood complying with Section 2303.2 where the building is equipped throughout with an automatic sprinkler system in accordance with Sections 903.3.1.1 through 903.3.1.3, unless otherwise prohibited by Exception 1 or 2 above.

5.	Inside the fire district, exterior non-bearing walls are permitted to be constructed with cross-laminated timber (CLT) complying with Section 602.4.2, unless otherwise prohibited by Exception 1 or 2 above.

602.4.1 Fire-retardant-treated wood in exterior walls. Fire-retardant-treated wood framing and sheathing complying with Section 2303.2 shall be permitted within exterior wall assemblies not less than 6 inches (152 mm) in thickness with a 2-hour rating or less.

602.4.2 Cross-laminated timber in exterior walls. Cross-laminated timber (CLT) complying with Section 2303.1.4 shall be permitted within exterior wall assemblies not less than 6 inches (152 mm) in thickness with a 2-hour rating or less, provided the exterior surface of the cross-laminated timber (CLT) is protected by one of the following:

1.	Fire-retardant-treated wood sheathing complying with Section 2303.2 and not less than 15/32 inch (12 mm) thick;

2.	Type X gypsum board not less than ⅝ inch (15.9 mm) thick; or

3.	A noncombustible material.

| [TABLE 602.4 WOOD MEMBER SIZE |
| --- |
| MINIMUM NOMINAL SOLID SAWN SIZE | MINIMUM GLUED-LAMINATED NET SIZE |
| Width, inch | Depth, inch | Width, inch | Depth, inch |
| 8 | 8 | 6¾ | 8¼ |
| 6 | 10 | 5 | 10½ |
| 6 | 8 | 5 | 8¼ |
| 6 | 6 | 5 | 6 |
| 4 | 6 | 3 | 6 ⅞ |

For SI: 1 inch = 25.4 mm.]

[602.4.1 Columns. Wood columns shall be sawn or glued laminated and shall not be less than 8 inches (203 mm) nominal in any dimension where supporting floor loads and not less than 6 inches (152 mm) nominal in width and not less than 8 inches (203 mm) nominal in depth where supporting roof and ceiling loads only. Columns shall be continuous or superimposed and connected in an approved manner.]

[602.4.2 Floor framing. Wood beams and girders shall be of sawn or glued-laminated timber and shall be not less than 6 inches (152 mm) nominal in width and not less than 10 inches (254 mm) nominal in depth. Framed sawn or glued-laminated timber arches, which spring from the floor line and support floor loads, shall be not less than 8 inches (203 mm) nominal in any dimension. Framed timber trusses supporting floor loads shall have members of not less than 8 inches (203 mm) nominal in any dimension.]

[602.4.3 Roof framing. Wood-frame or glued-laminated arches for roof construction, which spring from the floor line or from grade and do not support floor loads, shall have members not less than 6 inches (152 mm) nominal in width and have less than 8 inches (203 mm) nominal in depth for the lower half of the height and not less than 6 inches (152 mm) nominal in depth for the upper half. Framed or glued laminated arches for roof construction that spring from the top of walls or wall abutments, framed timber trusses and other roof framing, which do not support floor loads, shall have members not less than 4 inches (102 mm) nominal in width and not less than 6 inches (152 mm) nominal in depth. Spaced members shall be permitted to be composed of two or more pieces not less than 3 inches (76 mm) nominal in thickness where blocked solidly throughout their intervening spaces or where spaces are tightly closed by a continuous wood cover plate of not less than 2 inches (51 mm) nominal in thickness secured to the underside of the members. Splice plates shall be not less than 3 inches (76 mm) nominal in thickness. Where protected by approved automatic sprinklers under the roof deck, framing members shall be not less than 3 inches (76 mm) nominal in width.]

[602.4.4 Floors. Floors shall be without concealed spaces. Wood floors shall be of sawn or glued-laminated planks, splined or tongue-and-groove, of not less than 3 inches (76 mm) nominal in thickness covered with 1-inch (25 mm) nominal dimension tongue-and-groove flooring, laid crosswise or diagonally, or 0.5-inch (12.7 mm) particleboard or planks not less than 4 inches (102 mm) nominal in width set on edge close together and well spiked and covered with 1-inch (25 mm) nominal dimension flooring or 15/32-inch (12 mm) wood structural panel or 0.5-inch  (12.7 mm) particleboard. The lumber shall be laid so that no continuous line of joints will occur except at points of support. Floors shall not extend closer than 0.5 inch (12.7 mm) to walls. Such 0.5-inch (12.7 mm) space shall be covered by a molding fastened to the wall and so arranged that it will not obstruct the swelling or shrinkage movements of the floor. Corbeling of masonry walls under the floor shall be permitted to be used in place of molding.]

[602.4.5 Roofs. Roofs shall be without concealed spaces and wood roof decks shall be sawn or glued laminated, splined or tongue-and-groove plank, not less than 2 inches (51 mm) nominal in thickness, 1⅛-inch-thick (32 mm) wood structural panel (exterior glue), or of planks not less than 3 inches (76 mm) nominal in width, set on edge close together and laid as required for floors. Other types of decking shall be permitted to be used if providing equivalent fire resistance and structural properties.]

[602.4.6 Partitions. Partitions shall be of solid wood construction formed by not less than two layers of 1-inch (25 mm) matched boards or laminated construction 4 inches (102 mm) thick, or of 1-hour fire-resistance-rated construction.]

[602.4.7] 602.4.3 Exterior structural members. Where a horizontal separation of 20 feet (6096 mm) or more is provided, wood columns and arches conforming to heavy timber sizes in accordance with Section 2304.11 shall be permitted to be used externally[, except as prohibited by Section 602.4 for Occupancy Groups F, I-1, R-1 and R-2].

Exception:  Where prohibited by Exceptions 1, 2 or 3 of Section 602.4.

602.5 Type V. Type V construction is that type of construction in which the structural elements, exterior walls and interior walls are of any materials permitted by this code. Type V construction shall not be permitted inside the fire district unless otherwise permitted by Section D105.1.

Exception: In Group F occupancies subject to Section 270(1) of the New York State Labor Law, all exterior wall assemblies and all structural elements shall meet the requirements for a “fireproof building” as defined in Section 264 of such law.

SECTION BC 603
COMBUSTIBLE MATERIAL IN [TYPE] TYPES I AND II CONSTRUCTION

603.1 Allowable materials. Combustible materials shall be permitted in buildings of Type I or II construction in the following applications and in accordance with Sections 603.1.1 through 603.1.3[.]:

1.	Fire-retardant-treated wood, complying with Section 2303.2, shall be permitted in:

1.1.	Nonbearing interior partitions where the required fire-resistance rating is 1 hour or less.

Exception: Public corridors and exits shall be constructed of noncombustible materials.

1.2.	Roof construction as permitted in Table 601, Note b.

2.	Thermal and acoustical insulation, other than foam plastics, having a flame spread index of not more than 25.

Exceptions:

1.	Insulation placed between two layers of noncombustible materials without an intervening airspace shall be allowed to have a flame spread index of not more than 100.

2.	Insulation installed between a finished floor and solid decking without intervening airspace shall be allowed to have a flame spread index of not more than 200.

3.	Foam plastics in accordance with Chapter 26.

4.	Roof coverings that have an A or B classification as defined in Section 1505.

5.	Interior floor finish and floor covering materials installed in accordance with Section 804.

6.	Millwork such as doors, door frames, window sashes and frames [Millwork such as doors, door frames, window sashes and frames as permitted by Chapter 8].

7.	Interior wall and ceiling finishes installed in accordance with Sections 801 and 803.

8.	Trim installed in accordance with Section 806.

9.	Where not installed [over] greater than 15 feet (4572 mm) above grade, show windows, nailing or furring strips and wooden bulkheads below show windows, including their frames, aprons and show cases.

10.	Finish flooring installed in accordance with Section 805.

11.	Partitions dividing portions of stores, offices or similar places occupied by one tenant only and [which] that do not establish a corridor serving an occupant load of 30 or more shall be permitted to be constructed of fire-retardant-treated wood, 1-hour fire-resistance-rated construction or of wood panels or similar light construction up to 6 feet (1829 mm) in height.

12.	Stages and platforms constructed in accordance with Sections 410.3 and 410.4, respectively.

13.	Combustible exterior wall coverings, balconies and similar projections and bay or oriel windows in accordance [in accordance] with Chapter 14.

14.	Blocking such as for handrails, millwork, cabinets and window and door frames.

15.	Light-transmitting plastics as permitted by Chapter 26.

16.	Mastics and caulking materials applied to provide flexible seals between components of exterior wall construction.

17.	Exterior plastic veneer installed in accordance with Section 2605.2.

18.	Nailing or furring strips as permitted by Section [803.4] 803.13.

19.	Heavy timber as permitted by Note c to Table 601 and Section [602.4.7] 602.4.3.

20.	Aggregates, component materials and admixtures as permitted by Section 703.2.2.

21.	Sprayed fire-resistant materials and intumescent and mastic fire-resistant coatings, determined on the basis of [fire-resistance] fire resistance tests in accordance with Section 703.2 and installed in accordance with Sections [1704.11]  1705.14 and [1704.12]  1705.15, respectively.[.]

22.	Materials used to protect penetrations in fire-resistance-rated assemblies in accordance with Section [713] 714.

23.	Materials used to protect joints in fire-resistance-rated assemblies in accordance with Section [714] 715.

24.	Materials allowed in the concealed spaces of buildings of Types I and II construction in accordance with Section [717.5] 718.5.

25.	Materials exposed within plenums complying with Section 602 of the New York City Mechanical Code.

26.	Bleachers, grandstands, and folding and telescopic seating within an assembly space in accordance with Section 1029.1.1.

603.1.1 Ducts. The use of nonmetallic ducts shall be permitted [when] where installed in accordance with the limitations of the New York City Mechanical Code.

603.1.2 Piping. The use of combustible piping materials shall be permitted [when] where installed in accordance with the limitations of the New York City Mechanical Code and the New York City Plumbing Code.

603.1.3 Electrical. The use of electrical wiring methods with combustible insulation, tubing, raceways and related components shall be permitted [when] where installed in accordance with the limitations of the New York City Electrical Code.

§ 8. Chapter 7 of the New York city building code, as amended by and section 704 as added by local law number 141 for the year 2013, section 708.7 as amended by and item 12 of section 715.4.8.3 as added by local law number 17 for the year 2014, and sections 704.11, 708.12.1.3.2 and 708.13.3 and item 1 of section 716.3.3.2 as amended by local law number 51 for the year 2014, is amended to read as follows:

CHAPTER 7
FIRE AND SMOKE PROTECTION FEATURES

SECTION BC 701
GENERAL

701.1 Scope. The provisions of this chapter shall govern the materials and assemblies used for structural fire resistance and fire-resistance-rated construction separation of adjacent spaces to safeguard against the spread of fire and smoke within a building and the spread of fire to or from buildings.

701.2 Multiple use fire assemblies. Fire assemblies that serve multiple purposes in a building shall comply with all of the requirements that are applicable for each of the individual fire assemblies.

SECTION BC 702
DEFINITIONS

702.1 Definitions. The following [words and] terms [shall, for the purposes of this chapter, and as used elsewhere in this code, have the meanings shown herein.] are defined in Chapter 2:

ANNULAR SPACE. [The opening around the penetrating item.]

BUILDING ELEMENT. [A fundamental component of building construction, listed in Table 601, which may or may not be of fire-resistance-rated construction and is constructed of materials based on the building type of construction.]

CEILING RADIATION DAMPER. [A listed device installed in a ceiling membrane of a fire-resistance-rated floor/ceiling or roof/ceiling assembly to limit automatically the radiative heat transfer through an air inlet/outlet opening.]

COMBINATION FIRE/SMOKE DAMPER. [A listed device installed in ducts and air transfer openings designed to close automatically upon the detection of heat and resist the passage of flame and smoke. The device is installed to operate automatically, controlled by a smoke detection system, and where required, is capable of being positioned from a fire command center.]

CONCEALED SPACES.  [Enclosed spaces within partitions, walls, floors, roofs, stairs, furring, pipe chases and column enclosures and other similar spaces.]

DAMPER. [See “Ceiling radiation damper,” “Combination fire/smoke damper,” “Fire damper” and “Smoke damper.”]

[DRAFT STOP.  A material, device or construction installed to restrict the movement of air within open spaces of concealed areas of building components such as crawl spaces, floor/ceiling assemblies, roof/ceiling assemblies and attics.] DRAFTSTOP.

F RATING. [The time period that the through-penetration firestop system limits the spread of fire through the penetration when tested in accordance with ASTM E 814.]

FIRE BARRIER. [A fire-resistance-rated wall assembly of materials complying with Section 707 designed to restrict the spread of fire in which continuity of the fire-resistance rating is maintained.]

FIRE DAMPER. [A listed device, installed in ducts and air transfer openings designed to close automatically upon detection of heat and restrict the passage of flame. Fire dampers are classified for use in either static systems that will automatically shut down in the event of a fire, or in dynamic systems that continues to operate during a fire. A dynamic fire damper is tested and rated for closure under elevated temperature airflow.]

FIRE DOOR. [The door component of a fire door assembly.]

FIRE DOOR ASSEMBLY. [Any combination of a fire door, frame, hardware, and other accessories that together, as an opening protective, provide a specific degree of fire protection to the opening.]

FIRE PARTITION. [A vertical assembly of materials complying with Section 709, designed to restrict the spread of fire in which openings are protected.]

FIRE PROTECTION RATING. [The period of time that an opening protective assembly will maintain the ability to confine a fire as determined by tests prescribed in Section 715. Ratings are stated in hours or minutes.]

FIRE-RATED GLAZING.

FIRE RESISTANCE. [That property of materials or their assemblies that prevents or retards the passage of excessive heat, hot gases or flames under conditions of use.]

FIRE-RESISTANCE RATING. [The period of time a building element, component or assembly maintains the ability to withstand fire exposure, continues to perform a given structural function, or both, as determined by the tests, or the methods based on tests, prescribed in Section 703.]

FIRE-RESISTANT JOINT SYSTEM. [An assemblage of specific materials or products that are designed, tested, and fire-resistance rated in accordance with either ASTM E 1966 or UL 2079 to resist for a prescribed period of time the passage of fire through joints made in or between fire-resistance-rated assemblies.]

FIRE SEPARATION DISTANCE. [The distance measured from the building face to one of the following:]

[1.	The closest interior tax lot line;]

[2.	To the centerline of a street, an alley or public space; or]

[3.	To an imaginary line between two buildings on the same tax lot.]

[The distance shall be measured at right angles from the face of the wall.]

FIRE WALL. [A fire-resistance-rated smoke-tight wall having protected openings, which restricts the spread of fire and extends continuously from the foundation to or through the roof, with sufficient structural stability under fire conditions to allow collapse of construction on either side without collapse of the wall.]

FIRE WINDOW ASSEMBLY. [A window, as an opening protective, constructed and glazed to give protection against the passage of fire, smoke and hot gases.]

FIREBLOCKING. [A building material or materials approved for use as fireblocking to resist the free passage of flame or hot gases to other areas of the building through concealed spaces.]

FIRESTOPPING. [A through-penetration firestop or a membrane penetration firestop.]

FLOOR FIRE DOOR ASSEMBLY. [A combination of a fire door, a frame, hardware and other accessories installed, as an opening protective, in a horizontal plane, which together provide a specific degree of fire protection to a through opening in a fire-resistance-rated floor (see Section 712.8).]

HORIZONTAL ASSEMBLY. [A fire-resistance-rated floor or roof assembly of materials designed to restrict the spread of fire in which continuity of the fire-resistance rating is maintained.]

JOINT.

L RATING.

MEMBRANE PENETRATION. [An opening made through one side (wall, floor or ceiling membrane) of an assembly.]

MEMBRANE PENETRATION FIRESTOP. [A material, device, or assemblage of specific materials or products that is designed, tested and fire-resistance rated to resist for a prescribed time period the passage of flame and heat through openings in a protective membrane in order to accommodate cables, cable trays, conduit, tubing, pipes or similar items.]

MEMBRANE-PENETRATION FIRESTOP SYSTEM.

MINERAL FIBER. [Insulation composed principally of fibers manufactured from rock, slag or glass, with or without binders.]

MINERAL WOOL. [Synthetic vitreous fiber insulation made by melting predominantly igneous rock or furnace slag, and other inorganic materials, and then physically forming the melt into fibers.]

PENETRATION FIRESTOP. [A through-penetration firestop or a membrane penetration firestop.]

SELF-CLOSING. [As applied to a fire door or other opening, means equipped with an approved device that will ensure closing after having been opened.]

SHAFT. [An enclosed space extending through one or more stories of a building, connecting vertical openings in successive floors, or floors and roof.]

SHAFT ENCLOSURE. [The walls or construction forming the boundaries of a shaft.]

SMOKE BARRIER. [A continuous membrane, either vertical or horizontal, such as a wall, floor, or ceiling assembly, that is designed and constructed in accordance with Section 710 to restrict the movement of smoke.]

SMOKE COMPARTMENT. [A space within a building enclosed by smoke barriers on all sides, including the top and bottom.]

SMOKE DAMPER. [A listed device installed in ducts and air transfer openings that is designed to resist the passage of air and smoke. The device is installed to operate automatically, controlled by a smoke detection system, and where required, is capable of being positioned from a fire command center.]

SMOKE PARTITION. [A continuous vertical assembly that is designed and constructed to restrict the movement of smoke and is not generally required to have a fire-resistance rating in accordance with Section 711.]

SPLICE.

T RATING. [The time period that the penetration firestop system, including the penetrating item, limits the maximum temperature rise to 325°F (163°C) above its initial temperature through the penetration on the nonfire side when tested in accordance with ASTM E 814.]

[THROUGH PENETRATION. An opening that passes through an entire assembly.]

THROUGH-PENETRATION.

THROUGH-PENETRATION FIRESTOP SYSTEM. [An assemblage of specific materials or products that are designed, tested and fire-resistance rated to resist for a prescribed period of time the spread of fire through penetrations. The F and T rating criteria for penetration firestop systems shall be in accordance with ASTM E 814 or UL 1479. See definitions of “F rating” and “T rating.”]

SECTION BC 703
FIRE-RESISTANCE RATINGS AND FIRE TESTS

703.1 Scope. Materials prescribed herein for fire resistance shall conform to the requirements of this chapter.

703.2 Fire-resistance ratings. The fire-resistance rating of building elements, components or assemblies shall be determined in accordance with the test procedures set forth in ASTM E 119 or UL 263 or in accordance with Section 703.3. [Where materials, systems or devices that have not been tested as part of a fire-resistance-rated assembly are incorporated into the building element component or assembly, sufficient data shall be made available to the commissioner to show that the required fire-resistance rating is not reduced. Materials and methods of construction used to protect joints and penetrations in fire-resistance- rated building elements, components or assemblies shall not reduce the required fire-resistance rating.] The fire-resistance rating of penetrations and fire-resistant joint systems shall be determined in accordance with Sections 714 and 715, respectively.

[Exception: In determining the fire-resistance rating of exterior bearing walls, compliance with the ASTM E 119 or UL 263 criteria for unexposed surface temperature rise and ignition of cotton waste due to passage of flame or gases is required only for a period of time corresponding to the required fire-resistance rating of an exterior nonbearing wall with the same fire separation distance, and in a building of the same group. When the fire-resistance rating determined in accordance with this exception exceeds the fire-resistance rating determined in accordance with ASTM E 119 or UL 263, the fire exposure time period, water pressure, and application duration criteria for the hose stream test of ASTM E 119 or UL 263 shall be based upon the fire-resistance rating determined in accordance with this exception.]

703.2.1 Nonsymmetrical wall construction. Interior walls and partitions of nonsymmetrical construction shall be tested with both faces exposed to the furnace, and the assigned fire-resistance rating shall be the shortest duration obtained from the two tests conducted in compliance with ASTM E 119 or UL 263. Where evidence is furnished to show that the wall was tested with the least fire-resistant side exposed to the furnace, subject to acceptance of the commissioner, the wall need not be subjected to tests from the opposite side (see Section 705.5 for exterior walls).

703.2.2 Combustible components. Combustible aggregates may be integrated with other materials to form a noncombustible material provided that the entire mixture, in the form in which it is to be used in construction, meets the requirement of this code for noncombustible construction.

703.2.3 Restrained classification. Fire-resistance-rated assemblies tested under ASTM E 119 or UL 263 shall not be considered to be restrained unless evidence satisfactory to the commissioner is furnished by the registered design professional showing that the construction qualifies for a restrained classification in accordance with ASTM E 119 or UL 263. Restrained construction shall be identified on the [plans] construction documents.

703.2.4 Supplemental features. Where materials, systems or devices that have not been tested as part of a fire-resistance-rated assembly are incorporated into the building element component or assembly, sufficient data shall be made available to the commissioner to show that the required fire-resistance rating is not reduced. Materials and methods of construction used to protect joints and penetrations in fire-resistance-rated building elements, components or assemblies shall not reduce the required fire-resistance rating.

703.2.5 Exterior bearing walls. In determining the fire-resistance rating of exterior bearing walls, compliance with the ASTM E 119 or UL 263 criteria for unexposed surface temperature rise and ignition of cotton waste due to passage of flame or gases is required only for a period of time corresponding to the required fire-resistance rating of an exterior nonbearing wall with the same fire separation distance, and in a building of the same group. Where the fire-resistance rating, determined in accordance with this section, exceeds the fire-resistance rating determined in accordance with ASTM E 119 or UL 263, the fire exposure time period, water pressure and application duration criteria for the hose stream test of ASTM E 119 or UL 263 shall be based on the fire-resistance rating determined in accordance with this section.

703.3 [Alternative methods] Methods for determining fire resistance. The application of any of the [alternative] methods listed in this section shall be based on the fire exposure and acceptance criteria specified in ASTM E 119 or UL 263. The required fire resistance of a building element, component or assembly shall be permitted to be established by any of the following methods or procedures:

1.	Fire-resistance designs documented in approved sources.

2.	Prescriptive designs of fire-resistance-rated building elements, components or assemblies as prescribed in Section [720] 721.

3.	Calculations in accordance with Section [721] 722.

4.	Engineering analysis based on a comparison of building element, component or assemblies designs having fire-resistance ratings as determined by the test procedures set forth in ASTM E 119 or UL 263.

5.	Alternative protection methods as allowed by rules of the department.

703.4 [Noncombustibility tests.] Automatic sprinklers. Under the prescriptive fire-resistance requirements of this code, the fire-resistance rating of a building element, component or assembly shall be established without the use of automatic sprinklers or any other fire suppression system being incorporated as part of the assembly tested in accordance with the fire exposure, procedures and acceptance criteria specified in ASTM E 119 or UL 263. However, this section shall not prohibit or limit the duties and powers of the commissioner as allowed by Sections 28-103.1.3 and 28-103.3 of the New York City Administrative Code.

703.5 Noncombustibility tests. The tests indicated in Sections [703.4.1 and 703.4.2] 703.5.1 and 703.5.2 shall serve as criteria for acceptance of building materials as set forth in Sections 602.2, 602.3 and 602.4 in Type I, II, III and IV construction. The term “noncombustible” does not apply to the flame spread characteristics of interior finish or trim materials. A material shall not be classified as a noncombustible building construction material if it is subject to an increase in combustibility or flame spread beyond the limitations herein established through the effects of age, fabrication or erection techniques, moisture or other atmospheric conditions.

[703.4.1] 703.5.1 Elementary materials. Materials required to be noncombustible shall be tested in accordance with ASTM E 136.

[703.4.2] 703.5.2 Composite materials. Materials having a structural base of noncombustible material as determined in accordance with Section [703.4.1] 703.5.1 with a surfacing not more than 0.125 inch (3.18 mm) thick that has a flame spread index not greater than 50 when tested in accordance with ASTM E 84 or UL 723 shall be acceptable as noncombustible materials.

[703.5] 703.6 Fire-resistance-rated glazing. Fire-resistance-rated glazing, when tested in accordance with ASTM E 119 or UL 263 and complying with the requirements of Section 707, shall be permitted. Fire-resistance-rated glazing shall bear a label [or other identification showing the name of the manufacturer, the test standard and the identifier “W-XXX,” where the “XXX” is the fire-resistance rating in minutes. Such label or identification shall be] marked in accordance with Table 716.3 and issued by an approved agency [and] that shall be permanently [affixed to] identified on the glazing.

[703.6] 703.7 Marking and identification. [Fire] Where there is a concealed floor, floor-ceiling or attic space, fire walls, fire barriers, fire partitions, smoke barriers and smoke partitions or any other wall required to have protected openings or penetrations shall be effectively and permanently identified with signs or stenciling in the concealed space. Such identification shall [be located in accessible concealed floor, floor-ceiling or attic spaces; and]:

1.	Be [repeated] located within 15 feet (4572 mm) of the end of each wall and at intervals not exceeding 30 feet [(914 mm)] (9144 mm) measured horizontally along the wall or partition[; and].

2.	 Include lettering not less than [0.5 inch (12.7 mm)] 3 inches (76 mm) in height[,] with a minimum 3/8-inch (9.5 mm) stroke in a contrasting color incorporating the suggested wording[:], “FIRE AND/OR SMOKE BARRIER—PROTECT ALL OPENINGS.”

[Exception: Walls in Group R-2 occupancies that do not have a removable decorative ceiling allowing access to the concealed space.]

SECTION BC 704
FIRE-RESISTANCE RATING OF
STRUCTURAL MEMBERS

704.1 Requirements. The fire-resistance ratings of structural members and assemblies shall comply with this section and the requirements for the type of construction as specified in Table 601. The fire-resistance ratings shall be not [be] less than the ratings required for the fire-resistance-rated assemblies supported by the structural members.

Exception: Fire barriers, fire partitions, smoke barriers and horizontal assemblies as provided in Sections 707.5, [709.4, 710.4] 708.4 and [712.4] 711.2, respectively.

704.2 Column protection. Where columns are required to [be] have protection to achieve a fire-resistance [rated] rating, the entire column shall be provided individual encasement protection by protecting it on all sides for the full column [length] height, including connections to other structural members, with materials having the required fire-resistance rating. Where the column extends through a ceiling, the encasement protection shall be continuous from the top of the foundation or floor/ceiling assembly below through the ceiling space to the top of the column.

704.3 Protection of the primary structural frame other than columns. Members of the primary structural frame other than columns that are required to have protection to achieve a fire-resistance rating and support more than one floor or one floor and roof, or support a load-bearing wall or a nonload-bearing wall more than one story high, shall be provided individual encasement protection by protecting them on all sides for [their] the full length, including connections to other structural members, with materials having the required fire-resistance rating.

Exception: Individual encasement protection may be omitted on those exposed sides where the extent of protection is in accordance with the required fire-resistance rating, as determined in Section 703.

704.4 Protection of secondary members. Secondary members that are required to have protection to achieve a fire-resistance rating shall be protected by individual encasement protection[, by the membrane or ceiling of a horizontal assembly in accordance with Section 712, or by a combination of both].

704.4.1 Light-frame construction. [King studs] Studs and boundary elements that are integral elements in load-bearing walls of light-frame construction shall be permitted to have required fire-resistance ratings provided by the membrane protection provided for the load-bearing wall.

704.4.2 Horizontal assemblies. Horizontal assemblies are permitted to be protected with a membrane or ceiling where the membrane or ceiling provides the required fire-resistance rating and is installed in accordance with Section 711.

704.5 Truss protection. The required thickness and construction of fire-resistance-rated assemblies enclosing trusses shall be based on the results of full-scale tests or combinations of tests on truss components or on approved calculations based on such tests that satisfactorily demonstrate that the assembly has the required fire resistance.

704.6 Attachments to structural members. The edges of lugs, brackets, rivets and bolt heads attached to structural members shall be protected to the highest required fire-resistance rating of the members connected.

704.7 Reinforcing. Thickness of protection for concrete or masonry reinforcement shall be measured to the outside of the reinforcement, including stirrups, ties and spiral reinforcing ties.

704.8 Embedments and enclosures. Pipes, wires, conduits, ducts or other service facilities shall not be embedded in the required fire [protection] protective covering of a structural member that is required to be individually encased.

Exception: Pipes, wires, and conduits may be installed in the space between the required fire protection and the structural member protected, provided that where such facilities pierce the required fire protection:

1.	[the] The area of the penetration does not exceed two percent of the area of the fire protection on any one face,

2.	[the] The penetrations are closed off with close-fitting metal escutcheons or plates, and

3.	[the] The concealed space is firestopped at each story.

704.9 Impact protection. Where the fire protective covering of a structural member is subject to impact damage from moving vehicles, the handling of merchandise or other activity, the fire protective covering shall be protected by corner guards or by a substantial jacket of metal or other noncombustible material to a height adequate to provide full protection, but not less than 5 feet (1524 mm) from the finished floor.

Exception: Corner protection is not required on concrete columns in open or enclosed parking garages.

704.10 Exterior structural members. Load-bearing structural members located within the exterior walls, or exposed to the outside of a building or structure shall be provided with the highest fire-resistance rating as determined in accordance with the following:

1.	As required by Table 601 for the type of building element based on the type of construction of the building;

2.	As required by Table 601 for exterior bearing walls based on the type of construction; and

3.	As required by Table 602 for exterior walls based on the fire separation distance.

704.11 [Lintel protection. Lintels over openings wider than 4 feet (1219 mm) in masonry walls, other than in walls of masonry veneer on wood frame structures, shall be fire protected as required by Section 704.3 when the full load over the opening is not relieved by a masonry arch of required strength.]

[Exceptions:]

[1.	The members of an assembled metal lintel that support only outer face masonry that is securely bonded or anchored to backing need not be fire protected, provided that the inner members of the assembly support the full load imposed.]

[2.	The use of stone lintels in spans exceeding 4 feet (1219 mm) shall not be permitted unless supplemented by fire-protected structural members or masonry arches of the required strength to support the superimposed loads.]

Bottom flange protection. Fire protection is not required at the bottom flange of lintels, shelf angles and plates spanning not more than 6 feet 4 inches (1931 mm), whether part of the primary structural frame or not, and from the bottom flange of lintels, shelf angles and plates not part of the structural frame, regardless of span.

704.12 Seismic isolation systems. Fire-resistance ratings for the isolation system shall meet the fire-resistance rating required for the columns, walls or other structural elements in which the isolation system is installed in accordance with Table 601. Isolation systems required to have a fire-resistance rating shall be protected with approved materials or construction assemblies designed to provide the same degree of fire resistance as the structural element in which [it ] the system is installed when tested in accordance with ASTM E 119 or UL 263 (see Section 703.2).

Such isolation system protection applied to isolator units shall be capable of retarding the transfer of heat to the isolator unit in such a manner that the required gravity load-carrying capacity of the isolator unit will not be impaired after exposure to the standard time-temperature curve fire test prescribed in ASTM E 119 or UL 263 for a duration not less than that required for the fire-resistance rating of the structure element in which [it] the system is installed.

Such isolation system protection applied to isolator units shall be suitably designed and securely installed so as not to dislodge, loosen, sustain damage or otherwise impair its ability to accommodate the seismic movements for which the isolator unit is designed and to maintain its integrity for the purpose of providing the required fire-resistance protection.

704.13 Sprayed fire-resistant materials (SFRM). Sprayed fire-resistant materials (SFRM) shall comply with Sections 704.13.1 through 704.13.5.

704.13.1 Fire-resistance rating. The application of SFRM shall be consistent with the fire-resistance rating and the listing, including, but not limited to, minimum thickness and dry density of the applied SFRM, method of application, substrate surface conditions and the use of bonding adhesives, sealants, reinforcing or other materials.

704.13.2 Manufacturer’s installation instructions. The application of SFRM shall be in accordance with the manufacturer’s installation instructions. The instructions shall include, but are not limited to, substrate temperatures and surface conditions and SFRM handling, storage, mixing, conveyance, method of application, curing and ventilation.

704.13.3 Substrate condition. The SFRM shall be applied to a substrate in compliance with Sections 704.13.3.1 through 704.13.3.2.

704.13.3.1 Surface conditions. Substrates to receive SFRM shall be free of dirt, oil, grease, release agents, loose scale and any other condition that prevents adhesion. The substrates shall [also] be free of primers, paints and encapsulants other than those fire tested and listed by a nationally recognized testing agency. Primed, painted or encapsulated steel shall be allowed, provided that testing has demonstrated that required adhesion is maintained.

704.13.3.2 Primers, paints and encapsulants. Where the SFRM is to be applied over primers, paints or encapsulants other than those specified in the listing, the material shall be field tested in accordance with ASTM E 736. Where testing of the SFRM with primers, paints or encapsulants demonstrates that required adhesion is maintained, SFRM shall be permitted to be applied to primed, painted or encapsulated wide flange steel shapes subject to the following conditions:

1.	The beam flange width of such shape may not exceed 12 inches (305 mm);

2.	The column flange width of such shape may not exceed 16 inches (400 mm);

3.	The beam or column web depth of such shape may not exceed 16 inches (400 mm); and

4.	The average and minimum bond strength values shall be determined based on a minimum of five bond tests conducted in accordance with ASTM E 736. Bond tests conducted in accordance with ASTM E 736 shall indicate [a minimum] an average bond strength of not less than 80 percent and [a minimum] an individual bond strength of not less than 50 percent, when compared to the bond strength of the SFRM as applied to clean uncoated 1/8-inch-thick [(3-mm)] (3.2 mm) steel plate.

704.13.4 Temperature. A minimum ambient and substrate temperature of 40°F (4.44°C) shall be maintained during and for [a minimum of] not fewer than 24 hours after the application of the SFRM, unless the manufacturer’s [installation] instructions allow otherwise.

704.13.5 Finished condition. The finished condition of SFRM applied to structural members or assemblies shall not, upon complete drying or curing, exhibit cracks, voids, spalls, delamination or any exposure of the substrate. Surface irregularities of SFRM shall be deemed acceptable.

704.14 Fire retardant or intumescent coatings on mass timber. Fire retardant or intumescent coatings shall not be used to achieve the required fire-resistance rating on structural elements composed of heavy timber members including, but not limited to, glued-laminated members, cross laminated timber (CLT) or structural composite lumber (SCL).

SECTION BC 705
EXTERIOR WALLS

705.1 General. Exterior walls shall comply with this section. Exterior wall construction shall comply with the provisions of Chapter 14 and Appendix D where applicable.

705.2 Projections. Cornices, eave overhangs, exterior balconies and similar projections, including but not limited to, fascias, belt courses, pilasters, surrounds, gutters, leaders, half-timber work, shutters, and trellises, [which extend] extending beyond the exterior wall shall conform to the requirements of this section and Section 1406, provided that any such projection, if removed, altered or destroyed, will not reduce the structural stability of the building enclosure, and that such projection is installed so as not to reduce the required fire-resistance rating of the building enclosure. Exterior egress balconies and exterior exit stairways and ramps shall comply with the requirements of this section and Sections [1019] 1021 and [1026] 1027, respectively. Projections shall not extend [beyond the] any closer to the line used to determine the fire separation distance [determined by the following three methods, whichever results] than shown in [the lesser projection:] Table 705.2. Exterior wall coverings and cladding at exterior balconies and similar projections shall comply with Section 1406.3.

[1.	A point one-third the distance from the exterior face of the wall to the tax lot line where protected openings or a combination of protected and unprotected openings are required in.]

[2.	A point one-half the distance from the exterior face of the wall to the tax lot line where all openings in the exterior wall are permitted to be unprotected or the building is equipped throughout with an automatic sprinkler system installed under the provisions of Section 705.8.2.]

[3.	More than 12 inches (305 mm) into areas where openings are prohibited.]

Exception[.]: Buildings on the same tax lot and considered as portions of one building in accordance with Section 705.3 are not required to comply with this section.

| TABLE 705.2 MINIMUM SETBACK DISTANCE OF PROJECTION |
| --- |
| FIRE SEPARATION DISTANCE (FSD)a | MINIMUM DISTANCE FROM LINE USED TO DETERMINE FSD |
| 0 feet to 2 feet | Projections not permitted |
| Greater than 2 feet to less than or equal to 3 feet | 24 inches |
| Greater than 3 feet to less than 30 feet | 24 inches plus 8 inches for every foot of FSD beyond 3 feet or fraction thereof |
| 30 feet or greater | 20 feet |

For SI: 1 foot = 304.8 mm; 1 inch = 25.4 mm.

a.	Distance to be measured from the lot line, or lot line equivalent to the exterior wall.

705.2.1 Type I and II construction. Projections from walls, including balconies on the exterior of buildings of Type I or II construction shall be of noncombustible materials.

705.2.2 Type III, IV or V construction. Projections from walls of Type III, IV or V construction shall be of any approved material. Projections located where openings are not permitted or where protection of openings is required shall be constructed of the following:

[705.2.2 Combustible projections. Combustible projections located where openings are not permitted or where protection of openings is required shall be of at least 1-hour fire-resistance-rated construction, Type IV construction, fire-retardant-treated wood or as required by Section 1406.3.]

1.	Noncombustible materials.

2.	Combustible materials of not less than 1 hour fire resistant-rated construction.

3.	Heavy timber construction complying with Section 2304.11.

4.	Fire-retardant treated wood.

5.	As permitted by Section 705.2.2.1.

705.2.2.1 Exterior balconies and similar projections. Exterior balconies and similar projections shall be permitted to be constructed of combustible materials provided that the exterior balcony or similar projection affords the fire-resistance rating required by Table 601 for floor construction.

Exceptions: Balconies or similar projections serving as a required exit shall not be constructed of combustible materials.

705.3 Buildings on the same tax lot. For the purposes of determining the required wall and opening protection, projections and roof-covering requirements, buildings on the same tax lot shall be assumed to have an imaginary line between them.

[Exception:]  Exceptions:

1.	Two or more buildings on the same tax lot shall be either [be] regulated as separate buildings or shall be considered as portions of one building if the aggregate area of such buildings is within the limits specified in Chapter 5 for a single building. Where the buildings contain different occupancy groups or are of different types of construction, the area shall be that allowed for the most restrictive occupancy or construction.

2.	Where an S-2 parking garage of Construction Type I or IIA is erected on the same lot as a Group R-2 building, and there is no fire separation distance between these buildings, then the adjoining exterior walls between the buildings are permitted to have occupant use openings in accordance with Section 706.8. However, opening protectives in such openings shall only be required in the exterior wall of the S-2 parking garage, not in the exterior wall openings in the R-2 building, and these opening protectives in the exterior wall of the S-2 parking garage shall be not less than 11/2-hour fire protection rating.

705.4 Materials. Exterior walls shall be of materials permitted by the building type of construction.

705.5 Fire-resistance ratings. Exterior walls shall be fire-resistance rated in accordance with Tables 601[,] and 602[,] and Appendix D where applicable. The required fire-resistance rating of exterior walls with a [fire-separation] fire separation distance of greater than 10 feet (3048 mm) shall be rated for exposure to fire from the inside. The required fire-resistance rating of exterior walls with a fire separation distance of less than or equal to 10 feet (3048 mm) shall be rated for exposure to fire from both sides.

705.6 Structural stability. [The wall shall extend to the height required by Section 705.11 and shall have sufficient structural stability such that it will remain in place for the duration of time indicated by the required fire-resistance rating.] Exterior walls shall extend to the height required by Section 705.11. Interior structural elements that brace the exterior wall but that are not located within the plane of the exterior wall shall have the minimum fire-resistance rating required in Table 601 for that structural element. Structural elements that brace the exterior wall but are located outside of the exterior wall or wholly or partly within the plane of the exterior wall shall have the minimum fire-resistance rating required in Tables 601 and 602 for the exterior wall.

705.7 Unexposed surface temperature. Where protected openings are not limited by Section 705.8, the limitation on the rise of temperature on the unexposed surface of exterior walls as required by ASTM E 119 or UL 263 shall not apply. Where protected openings are limited by Section 705.8, the limitation on the rise of temperature on the unexposed surface of exterior walls as required by ASTM E 119 or UL 263 shall not apply provided that a correction is made for radiation from the unexposed exterior wall surface in accordance with the following formula:

(Equation 7-1)

where:

Ae =	Equivalent area of protected openings.

A =	Actual area of protected openings.

Af =	Area of exterior wall surface in the story under consideration exclusive of openings, on which the temperature limitations of ASTM E 119 or UL 263 for walls are exceeded.

Feo =	An “equivalent opening factor” derived from Figure 705.7 based on the average temperature of the unexposed wall surface and the fire-resistance rating of the wall.

For SI: °C = [(°F) - 32] / 1.8.

FIGURE 705.7
EQUIVALENT OPENING FACTOR

705.8 Openings. Openings in exterior walls shall comply with Sections 705.8.1 through [705.8.7] 705.8.6.

| TABLE 705.8 MAXIMUM AREA OF EXTERIOR WALL OPENINGS BASED ON FIRE SEPARATION DISTANCE AND DEGREE OF OPENING PROTECTIONm |
| --- |
| FIRE SEPARATION DISTANCE (feet) | DEGREE OF OPENING PROTECTION | ALLOWABLE AREAa |
| 0 to less than 3b,c | Unprotected, Nonsprinklered (UP, NS) | Not Permitted |
|  | Unprotected, Sprinklered (UP, S)i | Not Permitted |
|  | Protected (P) | Not Permittedj,k |
| 3 to less than 5d,e | Unprotected, Nonsprinklered (UP, NS) | Not Permitted |
|  | Unprotected, Sprinklered (UP, S)i | 15% |
|  | Protected (P) | 15%l |
| 5 to less than 10e,f,n | Unprotected, Nonsprinklered (UP, NS) | 10%h |
|  | Unprotected, Sprinklered (UP, S)i | 25% |
|  | Protected (P) | 25%l |
| 10 to less than 15e,f,g,n | Unprotected, Nonsprinklered (UP, NS) | 15%h |
|  | Unprotected, Sprinklered (UP, S)i | 45% |
|  | Protected (P) | 45%l |
| 15 to less than 20f,g,n | Unprotected, Nonsprinklered (UP, NS) | 25% |
|  | Unprotected, Sprinklered (UP, S)i | 75% |
|  | Protected (P) | 75%l |
| 20 to less than 25f,g,n | Unprotected, Nonsprinklered (UP, NS) | 45% |
|  | Unprotected, Sprinklered (UP, S)i | No Limit |
|  | Protected (P) | No Limitl |
| 25 to less than 30f,g,n | Unprotected, Nonsprinklered (UP, NS) | 70% |
|  | Unprotected, Sprinklered (UP, S)i | No Limit |
|  | Protected (P) | No Limitl |
| 30 or greater | Unprotected, Nonsprinklered (UP, NS) | No Limit |
|  | Unprotected, Sprinklered (UP, S)i | [Not Required] No Limit |
|  | Protected (P) | [Not Required] No Limit |

For SI: 1 foot = 304.8 mm.

UP, NS = Unprotected openings in buildings not equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1.

UP, S = Unprotected openings in buildings equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1.

P = Openings protected with an opening protective assembly in accordance with Section 705.8.2.

a.	Values indicated are the percentage of the area of the exterior wall, per story.

b.	For the requirements for fire walls of buildings with differing heights, see Section 706.6.

c.	For openings in a fire wall for buildings on the same tax lot, see Section 706.8.

d.	The maximum percentage of unprotected and protected openings shall be 25 percent for Group R-3 occupancies.

e.	Unprotected openings shall not be permitted for openings with a fire separation distance of less than 15 feet for Group H-2 and H-3 occupancies.

f.	The area of unprotected and protected openings for Group R-3 occupancies shall [not be limited for Group R-3 occupancies, as applicable in Section 101.2,] have no limit, if provided with a fire separation distance of 5 feet or [more] greater.

g.	The area of openings in an open parking structure, with a fire separation distance of 10 feet or greater, shall [not be limited] have no limit.

h.	Includes buildings accessory to Group R-3.

i.	Not applicable to Group H-1, H-2 and H-3 occupancies.

j.	Protected openings through a wall or walls between buildings shall comply with Section 705.8.

k.	Protected openings within a fire separation distance of 3 feet or less are permitted for Occupancy Groups R-2 and R-3 provided such openings do not exceed 10 percent of the area of the façade of the story in which they are located. These openings shall not be credited towards meeting any mandatory natural light or ventilation requirements unless they also comply with applicable provisions of Chapter 12 and the Zoning Resolution.

l.	In Group R-2 and R-3 occupancies with an exterior separation distance greater than 3 feet, openings shall be in accordance with percentages indicated as “Protected Classification of Opening” in Table 705.8. However, such openings shall not be required to be protected.

m.	Upon special application, the commissioner may permit exterior wall openings to be constructed in excess of the permitted area established by Table 705.8 provided that such openings are protected and provided that at the time of their construction they are located at least 60 feet in a direct line, measured at any angle, including vertically and horizontally, from any neighboring building, unless otherwise permitted by Section 705.3 for buildings on the same tax lot. The construction [class] type of the neighboring building shall not be factored into the measurement of the distance between the openings and adjoining building. If any neighboring building is later altered or constructed to come within the above distance limitation, the affected exterior openings shall immediately be closed with construction meeting the fire-resistance-rating requirements for exterior wall construction of the building in which they are located. Such additional openings shall not be credited toward meeting any of the mandatory natural light or ventilation requirements unless they also comply with applicable provisions of [Chapter 12 and] the New York City Zoning Resolution and Chapter 12 of this code.

n.	The area of openings in a building containing only a Group U occupancy private garage or carport, with a fire separation distance of 5 feet (1524 mm) or greater, shall have no limit.

705.8.1 Allowable area of openings. The maximum area of unprotected and protected openings permitted in an exterior wall in any story of a building shall not exceed the percentages specified in Table 705.8.

Exceptions:

- In other than Group H occupancies, unlimited unprotected openings are permitted in the first story above grade plane either:

1.1.	Where the wall faces a street and has a fire separation distance of more than 15 feet (4572 mm); or

1.2.	Where the wall faces an unoccupied space, the unoccupied space shall be on the same tax lot or dedicated for public use, shall be not [be] less than 30 feet (9144 mm) in width and shall have access from a street by a posted fire lane in accordance with the New York City Fire Code.

2.	Buildings whose exterior bearing walls, exterior nonbearing walls and exterior primary structural frame are not required to be fire-resistance rated shall be permitted to have unlimited unprotected openings.

705.8.2 Protected openings. Where openings are required to be protected, fire doors and fire shutters shall comply with Section [715.4] 716.5 and fire window assemblies shall comply with Section [715.5] 716.6.

Exception: Opening protectives are not required where the building is equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1 and the exterior openings are protected by a water curtain using automatic sprinklers approved for that use. The sprinklers and the water curtain shall be installed in accordance with NFPA 13, as modified in Appendix Q.

705.8.3 Unprotected openings. Where unprotected openings are permitted, windows and doors shall be constructed of any approved materials. Glazing shall conform to the requirements of Chapters 24 and 26.

705.8.4 Mixed openings. Where both unprotected and protected openings are located in the exterior wall in any story of a building, the total area of the openings shall be determined in accordance with the following formula:

[

(Equation 7-2)

where:

Ap= Actual area of protected openings, or the equivalent area of protected openings, Ae (see Section 705.7).

ap = Allowable area of protected openings.

Au=  Actual area of unprotected openings.

au= Allowable area of unprotected openings.

705.8.5 Vertical separation of openings. Openings in exterior walls in adjacent stories shall be separated vertically to protect against fire spread on the exterior of the buildings where the openings are within 5 feet (1524 mm) of each other horizontally. Such openings shall be separated vertically [at least] not less than 3 feet (914 mm) by spandrel girders, exterior walls or other similar assemblies that have a fire-resistance rating of [at least] not less than 1 hour, rated for exposure to fire from both sides, or by flame barriers that extend horizontally [at least] not less than 30 inches (762 mm) beyond the exterior wall and that are at least as wide as the opening. Flame barriers shall [also] have a fire-resistance rating of [at least] not less than 1 hour. The unexposed surface temperature limitations specified in ASTM E 119 or UL 263 shall not apply to the flame barriers or vertical separation unless otherwise required by the provisions of this code. Where a curtain wall assembly is used on the exterior wall, the intersection between the floor assembly and curtain wall assembly shall be protected in accordance with Section 713.4.

Exceptions:

1.	This section shall not apply to buildings that are three stories or less above grade plane.

- This section shall not apply to buildings equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1 or 903.3.1.2.

- This section shall not apply to open parking garages.

4.	This section shall not apply to Occupancy Group A, E, I or R.

5.	This section shall not apply where the opening in the lower story is a protected opening with a fire protection rating of at least ¾ hour.

705.8.6 Vertical exposure. For buildings on the same tax lot, opening protectives shall be provided in every opening that is less than 15 feet (4572 mm) vertically above the roof of an adjacent building or structure based on assuming an imaginary line between them. The opening [protective] protectives are required where the fire separation distance between the imaginary line and the adjacent building or structure is less than 15 feet (4572 mm).

Exceptions:

1.	Opening protectives are not required where the roof assembly of the adjacent building or structure has a fire-resistance rating of not less than 1 hour for a minimum distance of 10 feet (3048 mm) from the exterior wall facing the imaginary line and the entire length and span of the supporting elements for the fire-resistance-rated roof assembly has a fire-resistance rating of not less than 1 hour.

2.	Buildings on the same tax lot and considered as portions of one building in accordance with Section 705.3 are not required to comply with Section 705.8.6.

705.9 Joints. Joints made in or between exterior walls required by this section to have a fire-resistance rating shall comply with Section [714] 715.

Exception: Joints in exterior walls that are permitted to have unprotected openings.

705.9.1 Voids. The void created at the intersection of a floor/ceiling assembly and an exterior curtain wall assembly shall be protected in accordance with Section [714.4] 715.4.

705.10 Ducts and air transfer openings. Penetrations by air ducts and air transfer openings in fire-resistance-rated exterior walls required to have protected openings shall comply with Section [716] 717.

Exception: Foundation vents installed in accordance with this code are permitted.

705.11 Parapets. Parapets shall be provided on exterior walls of buildings.

Exceptions: A parapet need not be provided on an exterior wall where any of the following conditions exist:

1.	The wall is not required to be fire-resistance rated in accordance with Table 602 because of fire separation distance.

2.	The building has an area of not more than 1,000 square feet (93 m²) on any floor.

3.	Walls that terminate at roofs of not less than 2-hour fire-resistance-rated construction.

4.	One-hour fire-resistance-rated exterior walls that terminate at the underside of the roof sheathing, deck or slab, provided that the entire building is covered with a Class A roof covering. Such roof shall not have openings located within 10 feet (3048 mm) of the 1-hour fire-resistance-rated exterior wall and not within 5 feet (1524 mm) for Groups R and U.

4.1.	Where the roof/ceiling framing elements are parallel to the walls, such framing and elements supporting such framing shall not be of less than 1-hour fire- resistance-rated construction for a width of 4 feet [(1219 mm) measured from the interior side of the wall] (1220 mm) for Groups R and U and 10 feet (3048 mm) for other occupancies[; or], measured from the interior side of the wall.

4.2.	Where roof/ceiling framing elements are not parallel to the wall, the entire span of such framing and elements supporting such framing shall not be of less than 1-hour fire-resistance-rated construction.

5.	In occupancies of Groups R-2 and R-3, where both are provided with a Class A or B roof covering, the exterior wall shall be permitted to terminate at the underside of the roof sheathing or deck in Type III, IV and V construction, provided one or both of the following criteria is met:

5.1.	The roof sheathing or deck is constructed of approved noncombustible materials or of fire-retardant-treated wood[,] for a distance of 4 feet [(1219 mm)] (1220 mm) from the perimeter; or

5.2.	The roof is protected with 0.625-inch (16 mm) Type X gypsum board directly beneath the underside of the roof sheathing or deck, supported by [a minimum of] not less than nominal 2-inch (51 mm) ledgers attached to the sides of the roof framing members[,] for a minimum distance of 4 feet [(1219 mm)] (1220 mm).

6.	Where the wall is permitted to have [at least] not less than 25 percent of the exterior wall areas containing unprotected openings based on fire separation distance as determined in accordance with Section 705.8.

705.11.1 Parapet construction. Parapets shall have the same fire-resistance rating as that required for the supporting wall, and on any side adjacent to a roof surface, shall have noncombustible faces for the uppermost 18 inches (457 mm), including counterflashing and coping materials. The height of the parapet shall be not [be] less than 30 inches (762 mm) above the point where the roof surface and the wall intersect. Where the roof slopes toward a parapet at a slope greater than two units vertical in 12 units horizontal (16.7-percent slope), the parapet shall extend to the same height as any portion of the roof within a fire separation distance where protection of wall openings is required, but in no case shall the height be less than 30 inches (762 mm).

705.12 Portions of a building cantilevered over existing buildings. Where a portion of a building is cantilevered over an adjacent building or tax lot by a horizontal distance greater than 1 foot (305 mm), the cantilevered portions shall be protected with construction that conforms to a fire engineering analysis acceptable to the commissioner that conforms to Section 705.12.1. In no case shall the protection for structural elements and horizontal assemblies be less than that required [for] by the [construction class of the] building type of construction. In no case shall the fire-resistance rating of exterior walls or any other cantilevered exterior surfaces be less than that required by the building type of construction, and in no case shall the limitations for openings on such exterior surfaces be less than that required for a lot line condition pursuant to Table 705.8, including footnote “m.”

705.12.1 Analysis. The analysis shall [demonstrates] demonstrate that all portions of the building that cantilever will withstand the anticipated effects of a design fire in accordance with generally accepted fire engineering principles with respect to at least all of the following building elements:

1.	The structural supports and frame of the cantilevered portion of the building;

2.	The underside projecting assemblies of the cantilevered portion of the building; and

3.	The exterior walls and openings on all sides of the cantilevered portion of the building.

705.12.1.1 Criteria. With respect to the design fire within the existing building over which the proposed building is cantilevered, the analysis shall include a scenario to burn-out, where any active fire suppression systems do not operate, the fire department does not intervene, all interior vertical compartmentation, including at the entrances to the stairways, has been removed, and the fuel loading exceeds what is normally expected for the current occupancy by a factor of safety acceptable to the commissioner. Where there is no existing building below the cantilever, or where the existing building below the cantilever is significantly underbuilt, the commissioner may require additional data and analysis.

705.12.2 Fire Department access to buildings and roofs. The applicant shall submit to the department an approval from the Fire Department that the proposed cantilever complies with applicable provisions of the New York City Fire Code with respect to access to buildings and roofs.

705.12.3 Fire protection peer review. A fire protection peer review of the analysis required by Sections 705.12.1 and 705.12.1.1 shall be submitted to the department for each such analysis.

705.12.3.1. Fire protection peer reviewer. The fire protection peer review shall be performed by a qualified independent fire protection engineer who has been retained by or on behalf of the owner. A fire protection peer reviewer shall meet the requirements of the rules of the department.

705.12.3.2 Extent of fire protection peer review. The fire protection peer reviewer shall review the fire engineering analysis and construction documents relevant to the analysis for general compliance with the applicable provisions of this code.

705.12.3.3 Fire protection peer review report. The fire protection peer reviewer shall submit a report to the department stating that the fire engineering analysis conforms to the requirements of this code without exception.

705.12.3.4 Responsibility. The responsibility for the fire engineering analysis shall comply with Sections 705.12.3.4.1 and 705.12.3.4.2.

705.12.3.4.1 Applicant of record. The architect or engineer submitting the fire engineering analysis shall retain responsibility for the fire engineering analysis. The activities and reports of the fire protection peer reviewer shall not relieve the applicant of record of this responsibility.

705.12.3.4.2 Fire protection peer reviewer. The fire protection peer reviewer’s report shall state his or her opinion regarding the fire engineering analysis by the applicant of record.

SECTION BC 706
FIRE WALLS

706.1 General. Each portion of a building separated by one or more fire walls that comply with the provisions of this section shall be considered a separate building. The extent and location of such fire walls shall provide a complete separation. Where a fire wall also separates occupancies that are required to be separated by a fire barrier wall, the most restrictive requirements of each separation shall apply. Concealed spaces in cornices and eaves shall comply with the provisions of Section 705.2.2.

706.1.1 Party walls. Any wall located on a property line between adjacent buildings, which is used or adapted for joint service between the two buildings, shall be constructed as a fire wall in accordance with Section 706, and shall create separate buildings.

Exception: Openings in a party wall separating an anchor building and a mall shall be in accordance with Section [402.7.3] 402.4.2.2.

706.1.2 Walls separating attached one- and two-family dwellings. Attached one- and two-family dwellings shall be separated by walls constructed in accordance with Section 706 or Appendix M.

706.2 Structural stability. Fire walls shall [have sufficient structural stability under fire conditions] be designed and constructed to allow collapse of [construction] the structure on either side without collapse of the wall [for the duration of time indicated by the required fire-resistance rating] under fire conditions. Fire walls designed and constructed in accordance with NFPA 221 shall be deemed to comply with this section.

706.3 Materials. Fire walls shall be constructed of any approved noncombustible materials.

706.4 Fire-resistance rating. Fire walls shall have a fire-resistance rating of not less than that required by Table 706.4.

| TABLE 706.4 FIRE WALL FIRE-RESISTANCE RATINGS |
| --- |
| GROUP | FIRE-RESISTANCE RATING (hours) |
| A, B, E, H-4, I, R-1, R-2, U | 3a |
| F-1, H-3b, H-5, M, S-1 | 3 |
| H-1, H-2 | 4b |
| F-2, S-2, R-3 | 2 |

- Walls shall be not less than 2-hour fire-resistance rated where separating buildings of Type II or V construction

- For Group H-1, H-2 or H-3 buildings, also see Sections [415.4] 415.7 and [415.5] 415.8.

706.5 Horizontal continuity. Fire walls shall be continuous from exterior wall to exterior wall and shall extend [at least] not less than 18 inches (457 mm) beyond the exterior surface of exterior walls.

Exceptions:

1.	Fire walls shall be permitted to terminate at the interior surface of combustible exterior sheathing or siding provided the exterior wall has a fire-resistance rating of [at least] not less than 1 hour for a horizontal distance of [at least] not less than 4 feet [(1219 mm)] (1220 mm) on both sides of the fire wall. Openings within such exterior walls shall be protected by opening protectives having a fire protection rating of not less than 3/4 hour.

2.	Fire walls shall be permitted to terminate at the interior surface of noncombustible exterior sheathing, exterior siding or other noncombustible exterior finishes provided the sheathing, siding[,] or other exterior noncombustible finish extends a horizontal distance of [at least] not less than 4 feet [(1219 mm)] (1220 mm) on both sides of the fire wall.

3.	Fire walls shall be permitted to terminate at the interior surface of noncombustible exterior sheathing where the building on each side of the fire wall is protected by an automatic sprinkler system installed in accordance with Section 903.3.1.1 or 903.3.1.2.

706.5.1 Exterior walls. Where the fire wall intersects [the] exterior walls, the fire-resistance rating and opening protection of the exterior walls shall comply with one of the following:

- The exterior walls on both sides of the fire wall shall have a 1-hour fire-resistance rating with 3/4-hour protection where opening protection is required by Section 705.8[.]. The fire-resistance rating of the exterior wall shall extend [a minimum of] not less than 4 feet [(1219 mm)] (1220 mm) on each side of the intersection of the fire wall to exterior wall. Exterior wall intersections at fire walls that form an angle equal to or greater than 180 degrees (3.14 rad) do not need exterior wall protection.

2.	Buildings or spaces on both sides of the intersecting fire wall shall assume to have an imaginary lot line at the fire wall and extending beyond the exterior of the fire wall. The location of the assumed line in relation to the exterior walls and the fire wall shall be such that the exterior wall and opening protection meet the requirements set forth in Sections 705.5 and 705.8. Such protection is not required for exterior walls terminating at fire walls that form an angle equal to or greater than 180 degrees (3.14 rad).

706.5.2 Horizontal projecting elements. Fire walls shall extend to the outer edge of horizontal projecting elements such as balconies, roof overhangs, canopies, marquees and [architectural] similar projections that are within 4 feet [(1219 mm)] (1220 mm) of the fire wall.

Exceptions:

1.	Horizontal projecting elements without concealed spaces, provided the exterior wall behind and below the projecting element has not less than 1-hour fire-resistance-rated construction for a distance not less than the depth of the projecting element on both sides of the fire wall. Openings within such exterior walls shall be protected by opening protectives having a fire protection rating of not less than 3/4 hour.

2.	Noncombustible horizontal projecting elements with concealed spaces, provided a minimum 1-hour fire-resistance-rated wall extends through the concealed space. The projecting element shall be separated from the building by [a minimum of] not less than 1-hour fire-resistance-rated construction for a distance on each side of the fire wall equal to the depth of the projecting element. The wall is not required to extend under the projecting element where the building exterior wall is not less than 1-hour fire-resistance rated for a distance on each side of the fire wall equal to the depth of the projecting element. Openings within such exterior walls shall be protected by opening protectives having a fire protection rating of not less than 3/4 hour.

3.	For combustible horizontal projecting elements with concealed spaces, the fire wall need only extend through the concealed space to the outer edges of the projecting elements. The exterior wall behind and below the projecting element shall be of not less than 1-hour fire-resistance-rated construction for a distance not less than the depth of the projecting elements on both sides of the fire wall. Openings within such exterior walls shall be protected by opening protectives having a fire-protection rating of not less than 3/4 hour.

706.6 Vertical continuity. Fire walls shall extend from the foundation through the roof, to form a parapet [at least] not less than 30 inches (762 mm) in height. [Such parapet shall in no event extend to a point less than 4 inches (102 mm) above the highest point of peaked or gabled roof.]

Exceptions:

- Where a [two-hour] 2-hour fire wall is permitted in accordance with Table 706.4, such wall shall be permitted to terminate at the underside of the roof sheathing, deck or slab provided:

  - The lower roof assembly within 4 feet [(1219 mm)] (1220 mm) of the wall has not less than a 1-hour fire-resistance rating and the entire length and span of supporting elements for the rated roof assembly has a fire-resistance rating of not less than 1 hour; and

  - Openings in the roof shall not be located within 4 feet (1219 mm) of the fire wall; and

  - Each building shall be provided with not less than a Class A roof covering.

- In buildings of Type I or II construction, fire walls shall be permitted to terminate at the underside of noncombustible roof sheathing, deck, or slabs where both buildings are provided with not less than a Class A roof covering. Openings in the roof shall not be located within 4 feet (1219 mm) of the fire wall.

- In buildings of Type III, IV and V construction, fire walls shall be permitted to terminate at the underside of noncombustible roof sheathing or decks provided:

3.1.	There are no openings in the roof within 4 feet (1219mm) of the fire wall; and

3.2.	The roof is covered with a minimum Class A roof covering.

- [Buildings located above a parking garage] In buildings designed in accordance with Section 510.2[shall be permitted to have the], fire walls [for the buildings] located above the [parking garage extend from the horizontal separation between the parking garage and the buildings] 3-hour horizontal assembly required by Section 510.2, Item 1 shall be permitted to extend from the top of this horizontal assembly.

5.	Where a fire wall serves as an interior wall for a building, and the roof on one side or both sides of the fire wall slopes toward the fire wall at a slope greater than two units vertical in 12 units horizontal (2:12), the fire wall shall extend to a height equal to the height of the roof located 4 feet (1220 mm) from the fire wall plus 30 inches (762 mm). In no case shall the extension of the fire wall be less than 30 inches (762 mm).

706.6.1 Stepped buildings. Where a fire wall serves as an exterior wall for a building and separates buildings having different roof levels, such wall shall terminate at a point not less than 30 inches (762 mm) above the lower roof level, provided the exterior wall for a height of 60 feet (18 288 mm) above the lower roof is not less than 1-hour fire-resistance-rated construction from both sides with openings protected by fire assemblies having a fire protection rating of not less than ¾ hour.

Exception: Where the fire wall terminates at the underside of the roof sheathing, deck or slab of the lower roof, provided:

1.	The lower roof assembly within 10 feet (3048 mm) of the wall has not less than a 1-hour fire-resistance rating and the entire length and span of supporting elements for the rated roof assembly has a fire-resistance rating of not less than 1 hour.

2.	Openings in the lower roof shall not be located within 10 feet (3048 mm) of the fire wall.

706.7 Combustible framing in fire walls. Adjacent combustible members entering into a concrete or masonry fire wall from opposite sides shall not have less than a 4-inch (102 mm) distance between embedded ends. Where combustible members frame into hollow walls or walls of hollow units, hollow spaces shall be solidly filled for the full thickness of the wall and for a distance not less than 4 inches (102 mm) above, below and between the structural members, with noncombustible materials approved for fireblocking.

706.8 Openings. Each opening through a fire wall[,] or a party wall[, or a through wall between two buildings] shall be protected in accordance with Section [715.4] 716.5 and shall not exceed 156 square feet (15 m²)[, with no dimension greater than 12 feet (3658 mm)]. The aggregate width of openings at any floor level shall not exceed 25 percent of the length of the wall.

Exception: Openings shall not be limited to 156 square feet (15 m²) where both buildings are equipped throughout with an automatic sprinkler system installed in accordance with Section 903.3.1.1. However, the aggregate width of all openings at any one floor level shall not exceed 25 percent of the length of the wall.

706.9 Penetrations. Penetrations [through] of fire walls shall comply with Section [713] 714.

706.10 Joints. Joints made in or between fire walls shall comply with Section [714] 715.

706.11 Ducts and air transfer openings. Ducts and air transfer openings shall not penetrate fire walls.

Exception: Penetrations by ducts and air transfer openings of fire walls that are not on a [tax] lot line shall be allowed provided the penetrations comply with Section [716] 717. The size and aggregate width of all openings shall not exceed the limitations of Section 706.8.

SECTION BC 707
FIRE BARRIERS

707.1 General. Fire barriers installed as required elsewhere in this code or the New York City Fire Code, shall comply with this section.

707.2 Materials. Fire barriers shall be of materials permitted by the building type of construction.

707.3 Fire-resistance rating. The fire-resistance rating of fire barriers shall comply with this section.

707.3.1 Shaft enclosures. The fire-resistance rating of the fire barrier separating building areas from a shaft shall comply with Section [708.4] 713.4.

707.3.2 [Exit enclosures] Interior exit stairway and ramp construction. The fire-resistance rating of the fire barrier separating building areas from an interior exit stairway or ramp shall comply with Section [1022.1]  1023.1.

707.3.3 Enclosures for exit access stairways. The fire-resistance rating of the fire barrier separating building areas from an exit access stairway or ramp shall comply with Section 713.4.

707.3.4 Exit passageway. The fire-resistance rating of the fire barrier separating building areas from an exit passageway shall comply with Section [1023.1]  1024.3.

[707.3.4] 707.3.5 Horizontal exit. The fire-resistance rating of the separation between building areas connected by a horizontal exit shall comply with Section [1025.1] 1026.1.

[707.3.5] 707.3.6 Atriums. The fire-resistance rating of the fire barrier separating atriums shall comply with Section 404.6.

[707.3.6] 707.3.7 Incidental uses. The fire barrier separating incidental uses from other spaces in the building shall have a fire-resistance rating of not less than that indicated in Table 509.

[707.3.7] 707.3.8 Control areas. Fire barriers separating control areas shall have a fire-resistance rating of not less than that required in Section 414.2.4.

[707.3.8] 707.3.9 Separated occupancies. Where the provisions of Section 508.4 are applicable, the fire barrier separating mixed occupancies shall have a fire-resistance rating of not less than that indicated in [Section] Table 508.4 based on the occupancies being separated.

[707.3.9] 707.3.10 Fire areas. The fire barriers or horizontal assemblies, or both, separating a single occupancy into different fire areas shall have a fire-resistance rating of not less than that indicated in Table [707.3.9] 707.3.10. The fire barriers or horizontal assemblies, or both, separating fire areas of mixed occupancies shall have a fire-resistance rating of not less than the highest value indicated in Table [707.3.9] 707.3.10 for the occupancies under consideration.

Exception: For fire-resistance ratings of public corridors, see Section 707.3.11.

| TABLE [707.3.9] 707.3.10 FIRE-RESISTANCE RATING REQUIREMENTS FOR FIRE BARRIER ASSEMBLIES OR HORIZONTAL ASSEMBLIES BETWEEN FIRE AREAS |
| --- |
| OCCUPANCY GROUP | FIRE-RESISTANCE RATING (hours) |
| H-1, H-2 | 4 |
| F-1, H-3, S-1 | 3 |
| A, B, E, F-2, H-4, H-5, I, M, R, S-2 | 2 |
| U | 1 |

707.3.11 Public corridors. The fire-resistance rating of public corridor walls shall comply with Table 1020.1.2.

707.4 Exterior walls. Where exterior walls serve as a part of a required fire-resistance-rated shaft [or exit], stairway or ramp enclosure, or separation, such walls shall comply with the requirements of Section 705 for exterior walls[,] and the fire-resistance-rated enclosure or separation requirements shall not apply.

Exception: Exterior walls required to be fire-resistance rated in accordance with Section [1019.2] 1021 for exterior egress balconies, Section [1022.6] 1023.7 for interior exit [enclosures] stairways and ramps and Section [1026.6] 1027.6 for exterior exit [ramps and] stairways and ramps.

707.5 Continuity. Fire barriers shall extend from the top of the floor/ceiling assembly below[,] to the underside of the floor or roof sheathing, slab or deck above and shall be securely attached thereto. Such fire barriers shall be continuous through concealed spaces, such as the space above a suspended ceiling. Joints and voids at intersections shall comply with Sections 707.8 and 707.9.

Exceptions:

1.	Shaft enclosures shall be permitted to terminate at a top enclosure complying with Section 713.12.

2.	Interior exit stairway and ramp enclosures required by Section 1023 and exit access stairway and ramp enclosures required by Section 1019 shall be permitted to terminate at a top enclosure complying with Section 713.12.

707.5.1 Supporting construction. The supporting construction for a fire barrier shall be protected to afford the required fire-resistance rating of the fire barrier supported. Hollow vertical spaces within a fire barrier shall be fireblocked in accordance with Section [717.2] 718.2 at every floor level.

Exceptions:

1.	The maximum required fire-resistance rating for assemblies supporting fire barriers separating tank storage as provided for in Section [415.6.2.1] 415.9.1.2 shall be 2 hours, but not less than required by Table 601 for the building construction type.

[2.	Shaft enclosures shall be permitted to terminate at a top enclosure complying with Section 708.12.]

[3.] 2.Supporting construction for 1-hour fire barriers required by Table 509 in buildings of Type IIB, IIIB and VB construction is not required to be fire-resistance rated unless required by other sections of this code.

707.6 Openings. Openings in a fire barrier shall be protected in accordance with Section [715] 716. Openings shall be limited to a maximum aggregate width of 25 percent of the length of the wall, and the maximum area of any single opening shall not exceed 156 square feet (15 m2). Openings in [vertical exit] enclosures for exit access stairways and ramps, interior exit stairways and ramps and exit passageways shall also comply with Sections [1022.3 and 1023.5] 1019, 1023.4 and 1024.5, respectively.

Exceptions:

1.	Openings shall not be limited to 156 square feet (15 m²) where adjoining floor areas are equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1.

2.	Openings [for fire doors serving an exit enclosure] shall not be limited to 156 square feet (15 m²) or an aggregate width of 25 percent of the length of the wall where the opening protective is a fire door serving enclosures for exit access stairways and ramps, and/or interior exit stairways and ramps.

3.	Openings shall not be limited to 156 square feet (15 m²) or an aggregate width of 25 percent of the length of the wall where the opening protective has been tested in accordance with ASTM E 119 or UL 263 and has a minimum fire-resistance rating not less than the fire-resistance rating of the wall.

4.	Fire window assemblies permitted in atrium separation walls shall not be limited to a maximum aggregate width of 25 percent of the length of the wall.

5.	Openings shall not be limited to 156 square feet (15 m²) or an aggregate width of 25 percent of the length of the wall where the opening protective is a fire door assembly in a fire barrier separating an [exit] enclosure for exit access stairways and ramps, and/or interior exit stairways and ramps from an exit passageway in accordance with Section [1022.2.1] 1023.3.1.

6.	Openings permitted in atrium enclosures shall comply with the provisions of Section 404.5.

707.7 Penetrations. Penetrations of fire barriers shall comply with Section [713] 714.

707.7.1 Prohibited penetrations. [Penetrations into an exit enclosure or an exit passageway shall be allowed when permitted by Sections 1022.4 or 1023.6, respectively.] Penetrations into enclosures for exit access stairways and ramps, interior exit stairways and ramps, and exit passageways shall be allowed only where permitted by Sections 1019, 1023.5 and 1024.6, respectively.

707.8 Joints. Joints made in or between fire barriers, and joints made at the intersection of fire barriers with underside of [the] a fire-resistance-rated floor or roof sheathing, slab or deck above, and the exterior vertical wall intersection shall comply with Section [714] 715.

707.9 Voids at intersections. The voids created at the intersection of a fire barrier and a nonfire-resistance-rated roof assembly or a nonfire-resistance-rated exterior wall assembly shall be filled. An approved material or system, or a material consistent with the construction requirements of the fire barrier, shall be used to fill the void, and shall be securely installed in or on the intersection for its entire length so as not to dislodge, loosen or otherwise impair its ability to accommodate expected building movements and to retard the passage of fire and hot gases.

707.10 Ducts and air transfer openings. Penetrations in a fire barrier by ducts and air transfer openings shall comply with Section [716] 717.

[707.9.1] 707.10.1 Prohibited ducts and air transfer openings. Penetrations by ducts and air transfer openings into an [exit] enclosure for exit access stairways and ramps shall only be allowed when permitted by Sections [1022.4 and 1023.6] 1023.4 and 1023.6.

[SECTION BC 708
SHAFT ENCLOSURES]

[708.1 General. The provisions of this section shall apply to shafts required to protect openings and penetrations through floor/ceiling and roof/ceiling assemblies. Shaft enclosures shall be constructed as fire barriers in accordance with Section 707 or horizontal assemblies in accordance with Section 712, or both.]

[708.2 Shaft enclosure required. Openings through a floor/ceiling assembly shall be protected by a shaft enclosure complying with this section.]

[Exceptions:]

[1.	A shaft enclosure is not required for openings totally within an individual residential dwelling unit and connecting four stories or less where such dwelling unit is fully sprinklered in accordance with Section 903.3.1.1, 903.3.1.2 or 903.3.1.3.]

[2.	A shaft enclosure is not required in a building equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1 for an escalator opening or stairway which is not a portion of the means of egress protected according to Item 2.1 or 2.2:]

[2.1.	Where the area of the floor opening between stories does not exceed twice the horizontal projected area of the escalator or stairway and the opening is protected by a draft curtain and closely spaced sprinklers in accordance with NFPA 13, as modified in Appendix Q. In other than Groups B and M, this application is limited to openings that do not connect more than four stories.]

[2.2.	Where the opening is protected by approved power-operated automatic shutters at every penetrated floor. The shutters shall be of noncombustible construction and have a fire-resistance rating of not less than 1.5 hours. The shutter shall be so constructed as to close immediately upon the actuation of a smoke detector installed in accordance with Section 907.3 and shall completely shut off the well opening. Escalators shall cease operation when the shutter begins to close. The shutter shall operate at a speed of not more than 30 feet per minute (152.4 mm/s) and shall be equipped with a sensitive leading edge to arrest its progress where in contact with any obstacle, and to continue its progress on release therefrom.]

[3.	A shaft enclosure is not required for penetrations by pipe, tube, conduit, wire, cable, and vents protected in accordance with Section 713.4.]

[4.	A shaft enclosure is not required for penetrations by ducts protected in accordance with Section 716.6. Grease ducts shall be protected in accordance with the New York City Mechanical Code.]

[5.	In other than Group H occupancies, a shaft enclosure is not required for floor openings complying with the provisions for atriums in Section 404.]

[6.	A shaft enclosure is not required for approved masonry chimneys, where annular space is fireblocked at each floor level in accordance with Section 717.2.5.]

[7.	In other than Groups I-2 and I-3, a shaft enclosure is not required for a floor opening or an air transfer opening that complies with all of the following:]

[7.1.	Does not connect more than two stories.]

[7.2.	Is not part of the required means of egress system.]

[7.3.	Is not concealed within the building construction of a wall or floor/ceiling assembly.]

[7.4.	Is not open to a corridor in Group I and R occupancies where such corridor is required to be fire-resistance rated in accordance with Tables 1018.1.1 and 1018.1.2.]

[7.5.	Is not open to a corridor on nonsprinklered floors in any occupancy where such corridor is required to be fire-resistance rated in accordance with Tables 1018.1.1 and 1018.1.2.]

[7.6.	Is separated from floor openings and air transfer openings serving other floors by construction conforming to required shaft enclosures.]

[7.7.	Is limited to the same smoke compartment.]

[8.	A shaft enclosure is not required for automobile ramps in open and enclosed parking garages constructed in accordance with Sections 406.3 and 406.4, respectively.]

[9.	A shaft enclosure is not required for floor openings between a mezzanine and the floor below.]

[10.	A shaft enclosure is not required for joints protected by a fire-resistant joint system in accordance with Section 714.]

[11.	A shaft enclosure shall not be required for floor openings created by unenclosed stairs or ramps in accordance with Exception 3 or 4 in Section 1016.1.]

[12.	Floor openings protected by floor fire doors in accordance with Section 712.8.]

[13.	In Group I-3 occupancies, a shaft enclosure is not required for floor openings in accordance with Section 408.5.]

[14.	A shaft enclosure is not required for elevator hoistways in open or enclosed parking garages that serve only the parking garage.]

[15.	In open or enclosed parking garages, a shaft enclosure is not required to enclose mechanical exhaust or supply duct systems when such duct system is contained within and serves only the parking garage.]

[16.	Where permitted by other sections of this code.]

[708.3 Materials. The shaft enclosure shall be of materials permitted by the building type of construction.]

[Exception: Noncombustible materials shall be used for shaft enclosures in Group I-1, R- 1 and R-2 buildings irrespective of the building type of construction.]

[708.4 Fire-resistance rating. Shaft enclosures shall have a fire-resistance rating of not less than 2 hours where penetrating three stories or more and not less than 1 hour where penetrating fewer than three stories. The number of stories connected by the shaft enclosure shall include any basements or cellars, but not any mezzanines. Shaft enclosures shall have a fire-resistance rating not less than the floor assembly penetrated, but need not exceed 2 hours. Shaft enclosures shall meet the requirements of Section 703.2.]

[708.5 Continuity. Shaft enclosures shall be constructed as fire barriers in accordance with Section 707 or horizontal assemblies constructed in accordance with Section 712 or both. Where the roof construction is of combustible materials, shaft enclosure walls shall extend through the roof construction at least 30 inches (762 mm) above the roof. Where the roof construction is of noncombustible materials, shaft enclosure walls shall extend from the top of the floor/ceiling assembly below to the underside of the floor or roof slab or deck above and shall be securely attached thereto. These walls shall be continuous through concealed spaces such as the space above a suspended ceiling. The supporting construction shall be protected to afford the required fire-resistance rating of the element supported. Hollow vertical spaces within the shaft enclosure construction wall shall be firestopped at every floor level.]

[Exception: A shaft enclosure of a refuse or laundry chute shall extend through combustible or noncombustible roof construction at least 6 feet (1829 mm) above the roof.]

[708.6 Exterior walls. Where exterior walls serve as a part of a required shaft enclosure, such walls shall comply with the requirements of Section 705 for exterior walls and the fire-resistance-rated enclosure requirements of Section 707.4 shall not apply.]

[Exception: Exterior walls required to be fire-resistance rated in accordance with Section 1019.2 for exterior egress balconies, Section 1022.6 for exit enclosures and Section 1026.6 for exterior exit ramps and stairways.]

[708.7 Openings. Openings in a shaft enclosure shall be protected in accordance with Section 715 as required for fire barriers. Doors shall be self-closing or automatic-closing by smoke detection in accordance with Section 715.4.8.3. Automatic-closing by smoke detection is not permitted for doors serving vertical exit enclosures.]

[Exception: For no more than one vertical exit enclosure in a building, doors serving such enclosure may be automatic-closing by smoke detection provided that the following conditions are satisfied:]

[1.	The building contains no Group H space and:]

[1.1.	Is not a high-rise building pursuant to Section 403.1 of this code, or for 	the purposes of prior code buildings, Section 27-232 of the Administrative Code, and is equipped with a fire alarm system; or]

[1.2.	Is equipped with fire alarm systems and automatic sprinkler systems throughout; or]

[1.3.	Is a high-rise office building, as such term is defined in Section 27-232 of the Administrative Code, that is 100 feet (30 480 mm) or more in height, equipped with a fire alarm system and subdivided into compartments pursuant to subdivision c of Section 27-339 of the Administrative Code.]

[2.	Such doors serve no more than three levels within such vertical exit enclosure, which must be consecutive levels.]

[3.	All levels served by such doors are served by at least one other exit.]

[4.	Such doors are connected to a fire alarm system and installed in accordance with Section 715.4.8.3 and NFPA 80.]

[5.	The hold-open devices of such doors:]

[5.1.	Are capable of manual release at the fire command center or, if a fire command center is not required, at a fire alarm control panel that is near the main building entrance; and]

[5.2.	Are capable of manual release by pulling the doors to the closed position.]

[708.7.1 Prohibited openings. Openings other than those necessary for the purpose of the shaft shall not be permitted in shaft enclosures.]

[708.8 Penetrations. Penetrations in a shaft enclosure shall be protected in accordance with Section 713 as required for fire barriers.]

[708.8.1 Prohibited penetrations. Penetrations other than those necessary for the purpose of the shaft shall not be permitted in shaft enclosures.]

[708.9 Joints. Joints in a shaft enclosure shall comply with Section 714.]

[708.10 Ducts and air transfer openings. Penetrations of a shaft enclosure by ducts and air transfer openings shall comply with Section 716.]

[708.11 Enclosure at the bottom. Shafts that do not extend to the bottom of the building or structure shall comply with one of the following:]

[1.	They shall be enclosed at the lowest level with construction of the same fire-resistance rating as the lowest floor through which the shaft passes, but not less than the rating required for the shaft enclosure; or]

[2.	They shall terminate in a room having a use related to the purpose of the shaft. The room shall be separated from the remainder of the building by fire barriers constructed in accordance with Section 707 or horizontal assemblies constructed in accordance with Section 712, or both. The fire-resistance rating and opening protectives shall be at least equal to the protection required for the shaft enclosure.]

[Exceptions:]

[1.	The fire-resistance-rated room separation is not required provided there are no openings in or penetrations of the shaft enclosure to the interior of the building except at the bottom. The bottom of the shaft shall be closed off around the penetrating items with materials permitted by Section 717.3.1 for draftstopping, or the room shall be provided with an approved automatic fire suppression system.]

[2.	A shaft enclosure containing a refuse chute or laundry chute shall not be used for any other purpose and shall terminate in a room protected in accordance with Section 708.13.4.]

[3.	The fire-resistance-rated room separation and the protection at the bottom of the shaft are not required provided there are no combustibles in the shaft and there are no openings or other penetrations through the shaft enclosure to the interior of the building.]

[708.12 Enclosure at the top. Shafts that do not extend to the top of the building or structure shall:]

[1.	Be enclosed at the highest level with construction of the same fire-resistance rating as the highest floor through which the shaft passes, but not less than the rating required for the shaft enclosure; or]

[2.	Terminate in a room having a use related to the purpose of the shaft. The room shall be separated from the remainder of the building by construction having a fire-resistance rating and opening protective at least equal to the protection required for the shaft enclosure.]

[708.12.1 Smoke venting of stair and other closed shafts. All closed shafts, including vertical exit enclosures, having a floor area exceeding 4 square feet (0.37 m2) shall be provided with a smoke vent in accordance with Sections 708.12.1.1 through 708.12.1.3.]

[Exception: Elevator and dumbwaiter shafts in accordance with Chapter 30.]

[708.12.1.1 Smoke vent construction. Smoke vents may be constructed as windows, louvers, skylights, vent ducts, or similar devices. Where a vent duct is installed, such vent ducts shall be enclosed by construction having the same fire-resistance rating as required for the shaft enclosure.]

[708.12.1.2 Smoke vent dimensions. The effective venting area shall not be less than 3½ percent of the maximum shaft area at any floor, but in no event less than 72 square inches (0.05 m2).]

[708.12.1.3 Smoke vent location. Smoke vents shall be located in accordance with Section 708.12.1.3.1 or 708.12.1.3.2, as applicable.]

[708.12.1.3.1 Smoke vents located above the roof line. Where a closed shaft or smoke vent duct penetrates through the roof of the building, the vent shall be located as follows:]

[1.	The vent shall be located at least 8 inches (203 mm) above a noncombustible roof assembly or at least 36 inches (914 mm) above a combustible roof assembly.]

[2.	The vent shall be located at least 10 feet (3048 mm) from any window, door, exterior stairway, or interior lot line. The vent may be located no less than 5 feet (1524 mm) from any window or door provided that the vent is located at a point higher than the top of such window or door.]

[3.	Where the vent is constructed as a window or louver, the sill of the window or louver shall be located at least 36 inches (914 mm)(above the roof assembly).]

[708.12.1.3.2 Smoke vents located in an exterior wall. Where the exterior wall serves as part of a shaft enclosure or where a smoke vent duct penetrates the exterior wall of the building, no openings shall be located in the wall within a distance of 30 feet (9144 mm) vertically above the vent opening, nor within 5 feet (1524 mm) on either side of the vent opening.]

[708.13 Refuse and laundry chutes. Refuse and laundry chutes, access and termination rooms and incinerator rooms shall meet the requirements of Sections 708.13.1 through 708.13.6.]

[Exception: Chutes serving and contained within a single dwelling unit.]

[708.13.1 Refuse and laundry chute enclosures. A shaft enclosure containing a refuse or laundry chute shall not be used for any other purpose and shall have a fire-resistance rating of 2 hours. Openings into the shaft, including those from access rooms and termination rooms, shall be protected in accordance with this section and Section 715. Openings into chutes shall not be located in corridors. Doors shall be self-closing.]

[708.13.2 Materials. A shaft enclosure containing a refuse or laundry chute shall be constructed of noncombustible materials.]

[708.13.3 Refuse and laundry chute access rooms. Access openings for refuse and laundry chutes shall be located in dedicated rooms or compartments enclosed by not less than 2-hour fire barriers constructed in accordance with Section 707 or horizontal assemblies constructed in accordance with Section 712, or both. Openings into the access rooms shall be protected by opening protectives having a fire protection rating of not less than 11/2 hour. Doors shall be self closing except that where the storage of refuse, including recyclables, or laundry is not permitted in such access rooms doors may be automatic closing upon the detection of smoke in accordance with Section 715.4.8.3.]

[Exception: Access openings for refuse or laundry chutes located within a dwelling unit need not be located within a separate room or compartment.]

[708.13.4 Termination room. Refuse and laundry chutes shall discharge into an enclosed room separated from the remainder of the building by not less than 3-hour fire barriers constructed in accordance with Section 707 or horizontal assemblies constructed in accordance with Section 712, or both. Openings into the termination room shall be protected by opening protectives having a fire protection rating of not less than 11/2 hours. Doors shall be self-closing.]

[Exception: Opening protectives shall not be required at a refuse or laundry chute opening to a termination room.]

[708.13.5 Incinerator room. Incinerator rooms shall comply with Table 509.]

[708.13.6 Automatic fire sprinkler system. An approved automatic fire sprinkler system shall be installed in accordance with Section 903.2.11.6.]

[708.14 Elevator, dumbwaiter and other hoistways. Elevator, dumbwaiter, and other hoistway enclosures shall be constructed in accordance with Section 708 and Chapter 30.]

[708.14.1 Elevator lobby. Except as provided by Sections 403.6.1 and 403.6.2, an enclosed elevator lobby shall be provided in high rise buildings at the following locations:]

[1.	Elevators opening onto a fire-resistance-rated corridor, in all occupancy groups.]

[2.	Elevators serving Group B occupancies. Elevators that serve four or more stories that contain space classified in occupancy Group B, inclusive of any lobby or entrance level, shall provide elevator lobbies at every level served by such elevator.]

[The lobby enclosure shall separate the elevator shaft enclosure doors from each floor by smoke partitions. In addition to the requirements in Section 709 for fire partitions, doors protecting openings in the elevator lobby enclosure walls shall also comply with Section 711.5.3 and penetrations of the elevator lobby enclosure by ducts and air transfer openings shall be protected in accordance with Section 711.7. Elevator lobbies shall have at least one means of egress complying with Chapter 10 and other provisions within this code. Access to an exit on any story through an elevator lobby shall be permitted provided that access to at least one other required exit does not require passing through the elevator lobby.]

[Exceptions:]

[1.	Enclosed elevator lobbies are not required at the street floor, provided the entire street floor is equipped with an automatic sprinkler system in accordance with Section 903.3.1.1.]

[2.	Elevators not required to be located in a shaft in accordance with Section 708.2 are not required to have enclosed elevator lobbies.]

[3.	Enclosed elevator lobbies are not required where zero-clearance doors are provided at the hoistway opening in accordance with Section 3002.6. Such doors shall be tested in accordance with UL 1784 without an artificial bottom seal.]

[4.	Enclosed elevator lobbies are not required on floors with less than 2,500 square feet (232 m2), provided that the commissioner accepts an alternative design or construction method that accomplishes the purposes of this section, or provided that the commissioner determines that compliance with this section is impracticable in whole or in part, whereby the commissioner may authorize an exemption from the requirements of this section.]

[5.	Enclosed elevator lobbies are not required on Group R-2 occupied floors.]

[6.	Enclosed elevator lobbies are not required where the elevator hoistway is pressurized in accordance with Section 708.14.2.]

[7.	Enclosed elevator lobbies are not required where the elevator serves only open parking garages in accordance with Section 406.3.]

[708.14.1.1 Areas of rescue assistance. Areas of rescue assistance shall be provided as required in Section 1007.6.]

[708.14.2 Enclosed elevator lobby. Where elevator hoistway pressurization is provided in lieu of required enclosed elevator lobbies, the pressurization system shall comply with this section except as provided by Sections 403.6.1 and 403.6.2.]

[708.14.2.1 Pressurization requirements. Elevator hoistways shall be pressurized to maintain a minimum positive pressure of 0.10 inches of water (25 Pa) and a maximum positive pressure of 0.25 inches of water (67 Pa) with respect to adjacent occupied space on all floors. This pressure shall be measured at the midpoint of each hoistway door, with all elevator cars at the floor of recall and all hoistway doors on the floor of recall open and all other hoistway doors closed. The opening and closing of hoistway doors at each level must be demonstrated during this test. The supply air intake shall be from an outside, uncontaminated source located a minimum distance of 20 feet (6096 mm) from any air exhaust system or outlet.]

[708.14.2.2 Rational analysis. A rational analysis complying with Section 909.4 shall be submitted with the construction documents.]

[708.14.2.3 Ducts for system. Any duct system that is part of the pressurization system shall be protected with the same fire-resistance rating as required for the elevator shaft enclosure.]

[708.14.2.4 Fan system. The fan system provided for the pressurization system shall be as required by this section.]

[708.14.2.4.1 Fire resistance. When located within the building, the fan system that provides the pressurization shall be protected with the same fire-resistance rating required for the elevator shaft enclosure.]

[708.14.2.4.2 Smoke detection. The fan system shall be equipped with a smoke detector that will automatically shut down the fan system when smoke is detected within the system.]

[708.14.2.4.3 Separate systems. A separate fan system shall be used for each elevator hoistway.]

[708.14.2.4.4 Fan capacity. The supply fan shall either be adjustable with a capacity of at least 1,000 cfm (0.4719 m3/s) per door, or that specified by a registered design professional to meet the requirements of a designed pressurization system.]

[708.14.2.5 Standby power. The pressurization system shall be provided with standby power from the same source as other required emergency systems for the building.]

[708.14.2.6 Activation of pressurization system. The elevator pressurization system shall be activated upon activation of the building fire alarm system or upon activation of the elevator lobby smoke detectors. Where both a building fire alarm system and elevator lobby smoke detectors are present, each shall be independently capable of activating the pressurization system.]

[708.14.2.7 Special inspection. Special inspection for performance shall be required in accordance with Section 909.18.8. System acceptance shall be in accordance with Section 909.19.]

[708.14.2.8 Marking and identification. Detection and control systems shall be marked in accordance with Section 909.14.]

[708.14.2.9 Control diagrams. Control diagrams shall be provided in accordance with Section 909.15.]

[708.14.2.10 Control panel. A control panel complying with Section 909.16 shall be provided.]

[708.14.2.11 System response time. Hoistway pressurization systems shall comply with the requirements for smoke control system response time in Section 909.17.]

SECTION BC [709] 708
FIRE PARTITIONS

[709.1] 708.1 General. The following wall assemblies shall comply with this section.

1.	Separation walls as required by Section 420.2 for Groups I-1, R-1, R-2 and R-3.

2.	Walls separating tenant spaces in covered and open mall buildings as required by Section [402.7.2] 402.4.2.1.

[2.] 3.	Corridor walls as required by Section [1018.1] 1020.1.

4.	Egress balconies as required by Section 1021.2.

[709.2] 708.2 Materials. The walls shall be of materials permitted by the building type of construction.

[709.3] 708.3 Fire-resistance rating. Fire partitions shall have a fire-resistance rating of not less than 1 hour.

Exception: Interior corridor walls as permitted by Table [1018.1.1] 1020.1.

[709.4] 708.4 Continuity. Fire partitions shall extend from the top of the foundation or [floorr/ceiling] floor/ceiling assembly below to the underside of the floor or roof sheathing, slab or deck above or to the fire-resistance-rated floor/ceiling or roof/ceiling assembly above, and shall be securely attached thereto. If the fire partitions are not continuous to the sheathing, deck[,] or slab, the space between the ceiling and the sheathing, deck or slab above shall be fire blocked or draft stopped in accordance with Sections [717.2.1] 718.2 and [717.3.1] 718.3 at the partition line. The supporting construction shall be protected to afford the required fire-resistance rating of the wall supported.

Exceptions:

1.	The fire [partition] partitions separating tenant spaces in a covered or open mall building, complying with Section [402.7.2] 402.4.2.1, [is] are not required to extend beyond the underside of a ceiling that is not part of a fire-resistance-rated assembly. A wall is not required in attic or ceiling spaces above tenant separation walls. However, fireblocking or draftstopping shall be provided in accordance with Section 718.

2.	[Fireblocking] Attic fireblocking or draftstopping is not required at the partition line in Group R-2 buildings that do not exceed four stories above grade plane, provided the attic space is subdivided by draftstopping into areas not exceeding 3,000 square feet (279 m2) or above every two dwelling units, whichever is smaller.

3.	Fireblocking or draftstopping is not required at the partition line in buildings equipped with an automatic sprinkler system installed throughout in accordance with Section 903.3.1.1 or 903.3.1.2, provided that automatic sprinklers are installed in combustible floor/ceiling and roof/ceiling spaces.

[709.5] 708.5 Exterior walls. Where exterior walls serve as a part of a required fire-resistance-rated separation, such walls shall comply with the requirements of Section 705 for exterior walls, and the fire-resistance-rated separation requirements shall not apply.

Exception: Exterior walls required to be fire-resistance rated in accordance with Section [1019.2] 1021.2 for exterior egress balconies, Section [1022.6] 1023.7 for [exit enclosures] interior exit stairways and ramps and Section [1026.6] 1027.6 for exterior exit [ramps and] stairways and ramps.

[709.6] 708.6 Openings. Openings in a fire partition shall be protected in accordance with Section [715] 716.

[709.7] 708.7 Penetrations. Penetrations through fire partitions shall comply with Section [713] 714.

[709.8] 708.8 Joints. Joints made in or between fire partitions shall comply with Section [714] 715.

[709.9] 708.9 Ducts and air transfer openings. Penetrations in a fire partition by ducts and air transfer openings shall comply with Section [716] 717.

SECTION BC [710] 709
SMOKE BARRIERS

[710.1] 709.1 General. [Smoke] Vertical and horizontal smoke barriers shall comply with this section.

[710.2] 709.2 Materials. Smoke barriers shall be of materials permitted by the building type of construction.

[710.3] 709.3 Fire-resistance rating. A 1-hour fire-resistance rating is required for smoke barriers.

Exception: Smoke barriers constructed of minimum 0.10-inch-thick (2.5 mm) steel in Group I-3 buildings.

[710.4] 709.4 Continuity. Smoke barriers shall form an effective membrane continuous from [outside wall to outside wall and from] the top of the foundation or floor/ceiling assembly below to the underside of the floor or roof sheathing, deck[,] or slab above, including continuity through concealed spaces, such as those found above suspended ceilings, and interstitial structural and mechanical spaces. The supporting construction shall be protected to afford the required fire-resistance rating of the wall or floor supported in buildings of other than Type IIB, IIIB or VB construction. Smoke barrier walls used to separate smoke compartments shall comply with Section 709.4.1. Smoke-barrier walls used to enclose areas of refuge in accordance with Section 1009.6.4 or to enclose elevator lobbies in accordance with Section 405.4.3, 3007.6.2, or 3008.7.2 shall also comply with Section 709.4.2.

Exception: Smoke barrier walls are not required in interstitial spaces where such spaces are designed and constructed with ceilings or exterior walls that provide resistance to the passage of fire and smoke equivalent to that provided by the smoke barrier walls.

709.4.1 Smoke-barrier walls separating smoke compartments. Smoke-barrier walls used to separate smoke compartments shall form an effective membrane continuous from outside wall to outside wall.

709.4.2 Smoke-barrier walls enclosing areas of refuge or elevator lobbies. Smoke-barrier walls used to enclose areas of refuge in accordance with Section 1009.6.4, or to enclose elevator lobbies in accordance with Section 405.4.3, 3007.6.2, or 3008.7.2, shall form an effective membrane enclosure that terminates at a fire barrier wall, provided such fire barrier wall has a level of fire protection rating not less than 1 hour, or that terminates at another smoke barrier wall or an outside wall. A smoke and draft control door assembly as specified in Section 716.5.3.1 shall not be required at each elevator hoistway door opening or at each exit doorway between an area of refuge and the enclosure of interior exit stairways or ramps or exit passageways.

[710.5] 709.5 Openings. Openings in a smoke barrier shall be protected in accordance with Section [715] 716.

Exceptions:

1.	In Group I-1, Group I-2 and Group B ambulatory care facilities, where [doors are installed across corridors,] a pair of opposite-swinging doors [without a center mullion shall be installed having vision panels with fire-protection-rated glazing materials in approved fire-resistance-rated frames, the area of which shall not exceed that tested] are installed across a corridor in accordance with Section 709.5.1, the doors shall not be required to be protected in accordance with Section 716. The doors shall be close fitting within operational tolerances, and shall not have a center mullion or undercuts in excess of ¾-inch (19.1 mm), louvers or grilles. The doors shall have head and jamb stops, and astragals or rabbets at meeting edges [and shall be automatic-closing by smoke detection in accordance with Section 715.4.8.3]. Where permitted by the door manufacturer’s listing, [positive latching] positive-latching devices are not required.

2.	In Group I-1, Group I-2 and Group B and ambulatory care facilities, horizontal sliding doors installed in accordance with Section [1008.1.4.3] 1010.1.4.3 and protected in accordance with Section [715] 716.

709.5.1 Group I-2 and ambulatory care facilities. In Group I-2 and Group B ambulatory care facilities, where doors are installed across a corridor, the doors shall be automatic-closing by smoke detection in accordance with Section 716.5.9.3 and shall have a vision panel with fire-protection-rated glazing materials in fire-protection-rated frames, the area of which shall not exceed that tested.

[710.6] 709.6 Penetrations. Penetrations through smoke barriers shall comply with Section [713] 714.

[710.7] 709.7 Joints. Joints made in or between smoke barriers shall comply with Section [714] 715.

[710.8] 709.8 Duct and air transfer openings. Penetrations by duct and air transfer openings shall comply with Section [716] 717.

SECTION BC [711] 710
SMOKE PARTITIONS

[711.1] 710.1 General. Smoke partitions installed as required elsewhere in the code shall comply with this section.

[711.2] 710.2 Materials. Smoke partitions shall be constructed of noncombustible materials. Glazing may be used provided it is heat-strengthened or tempered glazing complying and shall otherwise comply with Chapter 24, and shall be protected by sprinkler heads installed in a maximum of 6 feet (1829 mm) on center on each side of the smoke partition.

[711.3] 710.3 Fire-resistance rating. Unless required elsewhere in the code, smoke partitions are not required to have a fire-resistance rating.

[711.4] 710.4 Continuity. Smoke partitions shall extend from the top of the foundation or floor below to the underside of the floor or roof sheathing, deck[,] or slab above or to the underside of the ceiling above where the ceiling membrane is constructed to limit the transfer of smoke.

[711.5] 710.5 Openings. [Windows shall be sealed to resist the free passage of smoke or be automatic-closing upon detection of smoke. Doors in smoke partitions shall comply with this section.] Openings in smoke partitions shall comply with Sections 710.5.1 and 710.5.2.

710.5.1 Windows. Windows in smoke partitions shall be sealed to resist the free passage of smoke or be automatic-closing upon detection of smoke.

710.5.2 Doors. Doors in smoke partitions shall comply with Sections 710.5.2.1 through 710.5.2.3.

[711.5.1] 710.5.2.1 Louvers. Doors in smoke partitions shall not include louvers.

[711.5.2] 710.5.2.2 Smoke and draft-control doors. Where required elsewhere in the code, doors in smoke partitions shall meet the requirements for a smoke and draft control door assembly tested in accordance with UL 1784. The air leakage rate of the door assembly shall not exceed 3.0 cubic feet per minute per square foot (0.015424 m3/s m2) of door opening at 0.10 inch (24.9 Pa) of water for both the ambient temperature test and the elevated temperature exposure test. Installation of smoke doors shall be in accordance with NFPA 105.

710.5.2.2.1 Smoke and draft control door labeling. Smoke and draft control doors complying only with UL 1784 shall be permitted to show the letter “S” on the manufacturer’s labeling.

[711.5.3] 710.5.2.3 Self-closing or automatic-closing doors. Where required elsewhere in the code, doors in smoke partitions shall be [self-closing] self- or automatic-closing by smoke detection in accordance with Section [715.4.8.3] 716.5.9.3.

[711.6] 710.6 Penetrations [and joints]. The space around penetrating items [and in joints] shall be filled with an approved material to limit the free passage of smoke.

710.7 Joints. Joints shall be filled with an approved material to limit the free passage of smoke.

[711.7] 710.8 Ducts and air transfer openings. The space around a duct penetrating a smoke partition shall be filled with an approved material to limit the free passage of smoke. Air transfer openings in smoke partitions shall be provided with a smoke damper complying with Section [716.3.2] 717.3.2.2.

Exception: Where the installation of a smoke damper will interfere with the operation of a required smoke control system in accordance with Section 909, approved alternative protection shall be utilized.

SECTION BC [712] 711
HORIZONTAL ASSEMBLIES

[712.1 General. Floor and roof assemblies required to have a fire-resistance rating shall comply with this section.] 711.1 General. Horizontal assemblies shall comply with Section 711.2. Nonfire-resistance-rated floor and roof assemblies shall comply with Section 711.3.

711.2 Horizontal assemblies. Horizontal assemblies shall comply with Sections 711.2.1 through 711.2.6.

[712.2] 711.2.1 Materials. [The floor and roof assemblies] Horizontal assemblies shall be of materials permitted by the building type of construction.

[Exception:]

711.2.1.1 Noncombustible materials. Horizontal floor or roof assemblies shall be of noncombustible materials when such assemblies serve as [a] horizontal [offset] offsets to [a] fire [wall] walls or fire [barrier that is] barriers required to be noncombustible.

[712.3 Fire-resistance rating. The fire-resistance rating of floor and roof assemblies shall not be less than that required by the building type of construction. Where the floor assembly separates mixed occupancies, the assembly shall have a fire-resistance rating of not less than that required by Section 508.4 based on the occupancies being separated. Where the floor assembly separates a single occupancy into different fire areas, the assembly shall have a fire-resistance rating of not less than that required by Section 707.3.9. Horizontal assemblies separating dwelling units in Group I-1 or R occupancies shall be a minimum of 1-hour fire-resistance-rated construction.]

[712.3.1 Ceiling panels. Where the weight of lay-in ceiling panels, used as part of fire-resistance-rated floor/ceiling or roof/ceiling assemblies, is not adequate to resist an upward force of 1 pound per square foot (48 Pa), wire or other approved devices shall be installed above the panels to prevent vertical displacement under such upward force.]

[712.3.2 Access doors. Access doors shall be permitted in ceilings of fire-resistance-rated floor/ceiling and roof/ceiling assemblies provided such doors are tested in accordance with ASTM E 119 or UL 263 as horizontal assemblies and labeled by an approved agency for such purpose.]

[712.3.3 Unusable space. In 1-hour fire-resistance-rated floor assemblies, the ceiling membrane is not required to be installed over unusable crawl spaces not intended for occupancy or storage, less than 24 inches (610 mm) in height. In 1-hour fire-resistance-rated roof assemblies, the floor membrane is not required to be installed where the unusable attic space above is not intended for occupancy or storage.]

[712.4 Continuity. Assemblies shall be continuous without openings, penetrations or joints except as permitted by this section and Sections 708.2, 713.4, 714, and 1022.1. Skylights and other penetrations through a fire-resistance-rated roof deck or slab are permitted to be unprotected, provided that the structural integrity of the fire-resistance-rated roof assemblies is maintained. Unprotected skylights shall not be permitted in roof construction required to be fire-resistance rated in accordance with Section 705.8.6. The supporting construction shall be protected to afford the required fire-resistance rating of the horizontal assembly supported.]

[Exception: In buildings of Type IIB, IIIB, or VB construction, the construction supporting the horizontal assembly is not required to be fire-resistance-rated at the following:]

[1.	Horizontal assemblies at the separations of incidental uses as specified by Table 509, provided the required fire-resistance rating does not exceed 1 hour.]

[2.	Horizontal assemblies at the separations of dwelling units and sleeping units as required by Section 420.3.]

[3.	Horizontal assemblies at smoke barriers constructed in accordance with Section 710.]

[712.5 Penetrations. Penetrations of horizontal assemblies shall comply with Section 713.]

[712.6 Joints. Joints made in or between fire-resistance-rated horizontal assemblies shall comply with Section 714. The void created at the intersection of a floor/ceiling assembly and an exterior curtain wall assembly shall be protected in accordance with Section 714.4.]

[712.7 Ducts and air transfer openings. Penetrations in horizontal assemblies by ducts and air transfer openings shall comply with Section 716.]

[712.8 Floor fire door assemblies. Floor fire door assemblies used to protect openings in fire-resistance-rated floors shall be tested in accordance with NFPA 288, and shall achieve a fire-resistance rating not less than the assembly being penetrated. Floor fire door assemblies shall be labeled by an approved agency. The label shall be permanently affixed and shall specify the manufacturer, the test standard and the fire-resistance rating.]

[712.9 Smoke barrier. Where horizontal assemblies are required to resist the movement of smoke by other sections of this code in accordance with the definition of smoke barrier, penetrations and joints in such horizontal assemblies shall be protected as required for smoke barriers in accordance with Sections 713.5 and 714.6. Openings through horizontal assemblies shall be protected by shaft enclosures complying with Section 708. Horizontal assemblies shall not be allowed to have unprotected vertical openings.]

711.2.2 Continuity. Assemblies shall be continuous without vertical openings, except as permitted by this section and Section 712.

711.2.3 Supporting construction. The supporting construction shall be protected to afford the required fire-resistance rating of the horizontal assembly supported.

Exception: In buildings of Type IIB, IIIB or VB construction, the construction supporting the horizontal assembly is not required to be fire-resistance rated at the following:

1.	Horizontal assemblies at the separations of incidental uses as specified by Table 509 provided the required fire-resistance rating does not exceed 1 hour.

2.	Horizontal assemblies at the separations of dwelling units and sleeping units as required by Section 420.3.

3.	Horizontal assemblies at smoke barriers constructed in accordance with Section 709.

711.2.4 Fire-resistance rating. The fire-resistance rating of horizontal assemblies shall comply with Sections 711.2.4.1 through 711.2.4.6 but shall be not less than that required by the building type of construction.

711.2.4.1 Separating mixed occupancies. Where the horizontal assembly separates mixed occupancies, the assembly shall have a fire-resistance rating of not less than that required by Section 508.4 based on the occupancies being separated.

711.2.4.2 Separating fire areas. Where the horizontal assembly separates a single occupancy into different fire areas, the assembly shall have a fire-resistance rating of not less than that required by Section 707.3.10.

711.2.4.3 Dwelling units and sleeping units. Horizontal assemblies serving as dwelling or sleeping unit separations in accordance with Section 420.3, located in Group I-1 and R occupancies, shall be not less than 1-hour fire-resistance-rated construction.

711.2.4.4 Separating smoke compartments. Where the horizontal assembly is required to be a smoke barrier, the assembly shall comply with Section 709.

711.2.4.5 Separating incidental uses. Where the horizontal assembly separates incidental uses from the remainder of the building, the assembly shall have a fire-resistance rating of not less than that required by Section 509.

711.2.4.6 Other separations. Where a horizontal assembly is required by other sections of this code, the most restrictive fire-resistance rating shall govern.

711.2.5 Ceiling panels. Where the weight of lay-in ceiling panels, used as part of fire-resistance-rated floor/ceiling or roof/ceiling assemblies, is not adequate to resist an upward force of 1 pound per square foot (48 Pa), wire or other approved devices shall be installed above the panels to prevent vertical displacement under such upward force.

711.2.6 Crawl spaces. In 1-hour fire-resistance-rated floor/ceiling assemblies, the ceiling membrane is not required to be installed over crawl spaces that are not intended for occupancy or storage and that are less than 24 inches (610 mm) in height. Where the ceiling membrane is not provided, occupancy or storage is not permitted in the crawl space.

711.2.7 Attic spaces. In 1-hour fire-resistance-rated roof assemblies, the floor membrane is not required to be installed where the attic space above the floor membrane is not intended for occupancy or storage. Where the floor membrane is not provided, occupancy or storage is not permitted in the attic space.

711.3 Nonfire-resistance-rated floor and roof assemblies. Nonfire-resistance-rated floor, floor/ceiling, roof and roof/ceiling assemblies shall comply with Sections 711.3.1 and 711.3.2.

711.3.1 Materials. Assemblies shall be of materials permitted by the building type of construction.

711.3.2 Continuity. Assemblies shall be continuous without vertical openings, except as permitted by Section 712.

SECTION BC 712
VERTICAL OPENINGS

712.1 General. Each vertical opening shall comply in accordance with one of the protection methods in Sections 712.1.1 through 712.1.16.

712.1.1 Shaft enclosures. Vertical openings contained entirely within a shaft enclosure complying with Section 713 shall be permitted.

712.1.2 Individual dwelling unit. Unconcealed vertical openings totally within an individual residential dwelling unit and connecting four stories or less, where such dwelling unit is fully sprinklered in accordance with Sections 903.3.1.1, 903.3.1.2 or 903.3.1.3, shall be permitted.

712.1.3 Escalator openings. Where a building is equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1, vertical openings for escalators shall be permitted where protected in accordance with Section 712.1.3.1 or 712.1.3.2.

712.1.3.1 Opening size. Protection by a draft curtain and closely spaced sprinklers in accordance with NFPA 13, as modified by Appendix Q, shall be permitted where the area of the vertical opening between stories does not exceed twice the horizontal projected area of the escalator or stairway. In other than Groups B and M, this application is limited to openings that do not connect more than four stories.

712.1.3.2 Automatic shutters. Protection of the vertical opening by approved shutters at every penetrated floor shall be permitted in accordance with this section. The shutters shall be of noncombustible construction and have a fire-resistance rating of not less than 1.5 hours. The shutter shall be so constructed as to close immediately upon the actuation of a smoke detector installed in accordance with Section 907.3.1 and shall completely shut off the well opening. Escalators shall cease operation when the shutter begins to close. The shutter shall operate at a speed of not more than 30 feet per minute (152.4 mm/s) and shall be equipped with a sensitive leading edge to arrest its progress where in contact with any obstacle, and to continue its progress on release there from.

712.1.4 Penetrations. Penetrations, concealed and unconcealed, shall be permitted where protected in accordance with Section 714.

712.1.5 Joints. Joints shall be permitted where complying with Section 712.1.5.1 or 712.1.5.2, as applicable.

712.1.5.1 Joints in or between horizontal assemblies. Joints made in or between horizontal assemblies shall comply with Section 715. The void created at the intersection of a floor/ceiling assembly and an exterior curtain wall assembly shall be permitted where protected in accordance with Section 715.4.

712.1.5.2 Joints in or between nonfire-resistance-rated floor assemblies. Joints in or between floor assemblies without a required fire-resistance rating shall be permitted where they comply with one of the following:

1.	The joint shall be concealed within the cavity of a wall.

2.	The joint shall be located above a ceiling.

3.	The joint shall be sealed, treated or covered with an approved material or system to resist the free passage of flame and the products of combustion.

Exception: Joints meeting one of the exceptions listed in Section 715.1.

712.1.6 Ducts and air transfer openings. Penetrations by ducts and air transfer openings shall be protected in accordance with Section 717. Grease ducts shall be protected in accordance with the New York City Mechanical Code.

712.1.7 Atriums. In other than Group H occupancies, atriums complying with Section 404 shall be permitted.

712.1.8 Masonry chimney. Approved vertical openings for masonry chimneys shall be permitted where the annular space is fireblocked at each floor level in accordance with Section 718.2.5.

712.1.9 Two-story openings. In other than Groups I-2 and I-3, a vertical opening that is not used as one of the applications listed in this section shall be permitted if the opening complies with all of the items below:

1.	Does not connect more than two stories.

2.	Does not penetrate a horizontal assembly that separates fire areas or smoke barriers that separate smoke compartments.

3.	Is not concealed within the construction of a wall or a floor/ceiling assembly.

4.	Is not open to a corridor in Group I and R occupancies, where such corridor is required to be fire-resistance rated in accordance with Table 1020.1.

5.	Is not open to a corridor on nonsprinklered floors, where such corridor is required to be fire-resistance rated in accordance with Table 1020.1.

6.	Is separated from floor openings and air transfer openings serving other floors by construction conforming to required shaft enclosures.

712.1.10 Parking garages. Vertical openings in parking garages for automobile ramps, elevators and duct systems shall comply with Section 712.1.10.1, 712.1.10.2 or 712.1.10.3, as applicable.

712.1.10.1 Automobile ramps. Vertical openings for automobile ramps in open and enclosed parking garages shall be permitted where constructed in accordance with Sections 406.5 and 406.6, respectively.

712.1.10.2 Elevators. Vertical openings for elevator hoistways in open and enclosed parking garages that serve only the parking garage, and complying with Sections 406.5 and 406.6, respectively, shall be permitted.

712.1.10.3 Duct systems. Vertical openings for mechanical exhaust or supply duct systems in open or enclosed parking garages complying with Sections 406.5 and 406.6, respectively, shall be permitted to be unenclosed where such duct system is contained within and serves only the parking garage.

712.1.11 Mezzanine. Vertical openings between a mezzanine complying with Section 505 and the floor below shall be permitted.

712.1.12 Exit access stairways and ramps. Vertical openings containing exit access stairways or ramps in accordance with Section 1019 shall be permitted.

712.1.13 Openings. Vertical openings for floor fire doors and access doors shall be permitted where protected by Section 712.1.13.1 or 712.1.13.2.

712.1.13.1 Horizontal fire door assemblies. Horizontal fire door assemblies used to protect openings in fire-resistance-rated horizontal assemblies shall be tested in accordance with NFPA 288, and shall achieve a fire-resistance rating not less than the assembly being penetrated. Horizontal fire door assemblies shall be labeled by an approved agency. The label shall be permanently affixed and shall specify the manufacturer, the test standard and the fire-resistance rating.

712.1.13.2 Access doors. Access doors shall be permitted in ceilings of fire-resistance-rated floor/ceiling and roof/ceiling assemblies, provided such doors are tested in accordance with ASTM E 119 or UL 263 as horizontal assemblies and labeled by an approved agency for such purpose.

712.1.14 Group I-3. In Group I-3 occupancies, vertical openings shall be permitted in accordance with Section 408.5.

712.1.15 Skylights. Skylights and other penetrations through a fire-resistance-rated roof deck or slab are permitted to be unprotected, provided that the structural integrity of the fire-resistance-rated roof assembly is maintained. Unprotected skylights shall not be permitted in roof assemblies required to be fire-resistance rated in accordance with Section 705.8.6. The supporting construction shall be protected to afford the required fire-resistance rating of the horizontal assembly supported.

712.1.16 Openings otherwise permitted. Vertical openings shall be permitted where allowed by other sections of this code.

SECTION BC 713
SHAFT ENCLOSURES

713.1 General. The provisions of this section shall apply to shafts required to protect openings and penetrations through floor/ceiling and roof/ceiling assemblies. Interior exit stairways and ramps shall be enclosed in accordance with Section 1023.

713.2 Construction. Shaft enclosures shall be constructed as fire barriers in accordance with Section 707 or horizontal assemblies in accordance with Section 711, or both.

713.3 Materials. The shaft enclosure shall be of materials permitted by the building type of construction.

Exception: Noncombustible materials shall be used for shaft enclosures in Group I-1, R-1 and R-2 buildings irrespective of the building type of construction.

713.4 Fire-resistance rating. Shaft enclosures shall have a fire-resistance rating of not less than 2 hours where penetrating three stories or more, and not less than 1 hour where penetrating fewer than three stories. The number of stories connected by the shaft enclosure shall include any basements or cellars, but not any mezzanines. Shaft enclosures shall have a fire-resistance rating not less than the floor assembly penetrated, but need not exceed 2 hours. Shaft enclosures shall meet the requirements of Section 703.2.1.

713.5 Continuity. Shaft enclosures shall be constructed as fire barriers in accordance with Section 707 or horizontal assemblies constructed in accordance with Section 711, or both. Where the roof construction is of combustible materials, shaft enclosure walls shall extend through the roof construction not less than 30 inches (762 mm) above the roof. Where the roof construction is of noncombustible materials, shaft enclosure walls shall extend from the top of the floor/ceiling assembly below to the underside of the floor or roof slab or deck above and shall be securely attached thereto. These walls shall be continuous through concealed spaces such as the space above a suspended ceiling. The supporting construction shall be protected to afford the required fire-resistance rating of the element supported. Hollow vertical spaces within the shaft enclosure construction wall shall be firestopped at every floor level.

Exception: A shaft enclosure of a refuse or laundry chute shall extend through combustible or noncombustible roof construction not less than 6 feet (1829 mm) above the roof.

713.6 Exterior walls. Where exterior walls serve as a part of a required shaft enclosure, such walls shall comply with the requirements of Section 705 for exterior walls and the fire-resistance-rated enclosure requirements of Section 713.4 shall not apply.

Exception: Exterior walls required to be fire-resistance rated in accordance with Section 1021.2 for exterior egress balconies, Section 1023.7 for interior exit stairways and ramps and Section 1027.6 for exterior exit stairways and ramps.

713.7 Openings. Openings in a shaft enclosure shall be protected in accordance with Section 716 as required for fire barriers. Doors shall be self-closing or automatic-closing by smoke detection in accordance with Section 716.5.9.3. Automatic-closing by smoke detection is not permitted for doors serving interior exit stairways or ramps.

Exception: For no more than one interior exit stairway or ramp in a building, doors serving such enclosure may be automatic-closing by smoke detection provided that all the following conditions are satisfied:

1.	The building contains no Group H space and:

1.1.	Is not a high-rise building pursuant to Section 403.1 of this code, or for the purposes of prior code buildings, Section 27-232 of the Administrative Code, and is equipped with a fire alarm system; or

1.2.	Is equipped with fire alarm systems and automatic sprinkler systems throughout; or

1.3.	Is a high-rise office building, as such term is defined in Section 27-232 of the Administrative Code, that is 100 feet (30 480 mm) or more in height, equipped with a fire alarm system and subdivided into compartments pursuant to subdivision c of Section 27-339 of the Administrative Code.

2.	Such doors serve no more than three levels within such vertical exit enclosure, which must be consecutive levels.

3.	All levels served by such doors are served by not less than one other exit.

4.	Such doors are connected to a fire alarm system and installed in accordance with NFPA 80 and Section 716.5.9.3 of this code.

5.	The hold-open devices of such doors:

5.1.	Are capable of manual release at the fire command center, or if a fire command center is not required, at a fire alarm control panel that is near the main building entrance; and

5.2.	Are capable of manual release by pulling the doors to the closed position.

713.7.1 Prohibited openings. Openings other than those necessary for the purpose of the shaft shall not be permitted in shaft enclosures.

713.8 Penetrations. Penetrations in a shaft enclosure shall be protected in accordance with Section 714 as required for fire barriers. Structural elements, such as beams or joists, where protected in accordance with Section 714 shall be permitted to penetrate a shaft enclosure.

713.8.1 Prohibited penetrations. Penetrations other than those necessary for the purpose of the shaft shall not be permitted in shaft enclosures.

713.9 Joints. Joints in a shaft enclosure shall comply with Section 715.

713.10 Duct and air transfer openings. Penetrations of a shaft enclosure by ducts and air transfer openings shall comply with Section 717.

713.11 Enclosure at the bottom. Shafts that do not extend to the bottom of the building or structure shall comply with one of the following:

1.	They shall be enclosed at the lowest level with construction of the same fire-resistance rating as the lowest floor through which the shaft passes, but not less than the rating required for the shaft enclosure.

2.	They shall terminate in a room having a use related to the purpose of the shaft. The room shall be separated from the remainder of the building by fire barriers constructed in accordance with Section 707 or horizontal assemblies constructed in accordance with Section 711, or both. The fire-resistance rating and opening protectives shall be not less than the protection required for the shaft enclosure.

Exceptions:

1.	The fire-resistance-rated room separation is not required, provided there are no openings in or penetrations of the shaft enclosure to the interior of the building except at the bottom. The bottom of the shaft shall be closed off around the penetrating items with materials permitted by Section 718.3.1 for draftstopping, or the room shall be provided with an approved automatic sprinkler system.

2.	A shaft enclosure containing a waste or linen chute shall not be used for any other purpose and shall discharge into a room protected in accordance with Section 713.13.4.

3.	The fire-resistance-rated room separation and the protection at the bottom of the shaft are not required provided there are no combustibles in the shaft and there are no openings or other penetrations through the shaft enclosure to the interior of the building.

713.12 Enclosure at the top. Shafts that do not extend to the top of the building or structure shall comply with one of the following:

1.	They shall be enclosed at the highest level with construction of the same fire-resistance rating as the highest floor through which the shaft passes, but not less than the rating required for the shaft enclosure.

2.	They shall terminate in a room having a use related to the purpose of the shaft. The room shall be separated from the remainder of the building by construction having a fire-resistance rating and opening protective not less than the protection required for the shaft enclosure.

713.12.1 Smoke venting of stair and other closed shafts. All closed shafts, including vertical exit enclosures, having a floor area exceeding 4 square feet (0.37 m2) shall be provided with a smoke vent in accordance with Sections 713.12.1.1 through 713.12.1.3. Interior vertical exit shaft enclosures shall also comply with Chapter 10.

Exceptions:

1.	Elevator and dumbwaiter shafts in accordance with Chapter 30.

2.	Interior exit stairways and ramps constructed as smokeproof enclosures in accordance with Section 1023.11.

713.12.1.1 Smoke vent construction. Smoke vents may be constructed as windows, louvers, skylights, vent ducts, or similar devices, and shall be approved for such use. Where a vent duct is installed, such vent duct shall be enclosed by construction having the same fire-resistance rating as required for the shaft enclosure.

713.12.1.2 Smoke vent dimensions. The effective venting area shall be not less than 3½ percent of the maximum shaft area at any floor, but in no event less than 72 square inches (46 454 mm2).

713.12.1.3 Smoke vent location. Smoke vents shall be located in accordance with Section 713.12.1.3.1 or 713.12.1.3.2, as applicable.

713.12.1.3.1 Smoke vents located above the roof line. Where a closed shaft or smoke vent duct penetrates through the roof of the building, the vent shall be approved for such use and located as follows:

1.	The vent shall be located not less than 8 inches (203 mm) above a noncombustible roof assembly or not less than 36 inches (914 mm) above a combustible roof assembly.

2.	The vent shall be located not less than 10 feet (3048 mm) from any window, door, exterior stairway, or interior lot line. The vent may be located not less than 5 feet (1524 mm) from any window or door provided that the vent is located at a point higher than the top of such window or door.

3.	Where the vent is constructed as a window or louver, the sill of the window or louver shall be located not less than 36 inches (914 mm) above the roof assembly.

713.12.1.3.2 Smoke vents located in an exterior wall. Where a smoke vent is located in an exterior wall, openings in the wall are prohibited within an area 30 feet (9144 mm) vertically above the vent opening and 5 feet (1524 mm) horizontally on either side of the vent opening.

713.13 Waste and linen chutes, including discharge rooms, and incinerator rooms. Waste and linen chutes, and discharge rooms for such chutes, shall comply with the provisions of NFPA 82, Chapter 6 and shall meet the requirements of Sections 713.13.1 through 713.13.6 of this code. Incinerator rooms shall meet the provisions of Sections 713.13.4 through 713.13.5.

Exception: Chutes serving and contained within a single dwelling unit.

713.13.1 Waste and linen. A shaft enclosure containing a recycling, or waste or linen chute, and any associated discharge room, shall not be used for any other purpose and shall have a fire-resistance rating of 2 hours. Openings into the shaft, including those from access rooms and discharge rooms, shall be protected in accordance with this section and Section 716. Openings into chutes shall not be located in corridors. Doors into chutes shall be self-closing. Discharge doors shall be self-closing or automatic-closing upon the actuation of a smoke detector in accordance with Section 716.5.9.3, except that heat-activated closing devices shall be permitted between the shaft and the discharge room.

713.13.2 Materials. A shaft enclosure containing a waste, recycling, or linen chute shall be constructed of noncombustible materials.

713.13.3 Waste and linen chute access rooms. Access openings for waste and linen chutes shall be located in dedicated rooms or compartments enclosed by not less than 2-hour fire barriers constructed in accordance with Section 707 or horizontal assemblies constructed in accordance with Section 711 or both. Openings into the access rooms shall be protected by opening protectives having a fire protection rating of not less than 11/2 hours. Doors to access rooms shall be self-closing, except where the storage of waste, including recyclables, or linen and other laundry, is not permitted in such access room, doors may be automatic-closing upon the detection of smoke in accordance with Section 716.5.9.3.

Exception: Access openings for waste or linen chutes located within a dwelling unit need not be located within a separate room or compartment.

713.13.4 Chute discharge room. Waste or linen chutes shall discharge into an enclosed room separated by not less than 3-hour fire barriers constructed in accordance with Section 707 or by horizontal assemblies constructed in accordance with Section 711, or both. Openings into the discharge room from the remainder of the building shall be protected by opening protectives having a fire protection rating equal to the protection required for the shaft enclosure. Doors shall be self- or automatic-closing upon the detection of smoke in accordance with Section 716.5.9.3. Waste chutes shall not terminate in an incinerator room. Waste and linen rooms that are not provided with chutes need only comply with Table 509.

Exception: Opening protectives shall not be required at a waste or linen chute opening to a discharge room.

713.13.5 Incinerator room. Incinerator rooms shall comply with Table 509.

713.13.6 Automatic sprinkler system. An approved automatic sprinkler system shall be installed in accordance with Section 903.2.11.6.

713.14 Elevator, dumbwaiter and other hoistways. Elevator, dumbwaiter and other hoistway enclosures shall be constructed in accordance with Chapter 30 and this section.

SECTION BC [713] 714
PENETRATIONS

[713.1] 714.1 Scope. The provisions of this section shall govern the materials and methods of construction used to protect [through penetrations] through-penetrations and [membrane penetrations] membrane-penetrations of horizontal assemblies and fire-resistance-rated wall assemblies.

[713.1.1] 714.1.1 Ducts and air transfer openings. Penetrations of fire-resistance-rated walls by ducts that are not protected with dampers shall comply with Sections [713.2] 714.2 through [713.3.3] 714.3.3. Penetrations of horizontal assemblies not protected with a shaft as permitted by [Exception 4 of] Section [708.2] 717.6, and not required to be protected with fire dampers by other sections of this code, shall comply with Sections [713.4] 714.4 through [713.4.2.2] 714.5.2. Ducts and air transfer openings that are protected with dampers shall comply with Section [716] 717.

[713.1.2] 714.1.2 Special inspection. All through-penetration and membrane-penetration firestop systems shall comply with the special inspection requirements of Chapter 17.

[713.2] 714.2 Installation details. Where sleeves are used, they shall be securely fastened to the assembly penetrated. The space between the item contained in the sleeve and the sleeve itself and any space between the sleeve and the assembly penetrated shall be protected in accordance with this section. Insulation and coverings on or in the penetrating item shall not penetrate the assembly unless the specific material used has been tested as part of the assembly in accordance with this section.

[713.3] 714.3 Fire-resistance-rated walls. Penetrations into or through fire walls, fire barriers, smoke barrier walls[,] and fire partitions shall comply with Sections [713.3.1] 714.3.1 through [713.3.3] 714.3.3. Penetrations in smoke barrier walls shall also comply with Section [713.5] 714.4.3.

[713.3.1 Through penetrations. Through penetrations] 714.3.1 Through-penetrations. Through-penetrations of fire-resistance-rated walls shall comply with Section [713.3.1.1] 714.3.1.1 or [713.3.1.2] 714.3.1.2.

Exception: Where the penetrating items are steel, ferrous or copper pipes, tubes or conduits, the annular space between the penetrating item and the fire-resistance-rated wall is permitted to be protected [as follows:] by either of the following measures:

1.	In concrete or masonry walls where the penetrating item is a maximum 6-inch (152 mm) nominal diameter and the area of the opening through the wall does not exceed 144 square inches [(0.0929 m²)] (92 903 mm2), concrete, grout or mortar is permitted where installed the full thickness of the wall or the thickness required to maintain the fire-resistance rating[; or].

2.	The material used to fill the annular space shall prevent the passage of flame and hot gases sufficient to ignite cotton waste where subjected to ASTM E 119 or UL 263 time-temperature fire conditions under a minimum positive pressure differential of 0.01 inch (2.49 Pa) of water at the location of the penetration for the time period equivalent to the fire-resistance rating of the construction penetrated.

[713.3.1.1] 714.3.1.1 Fire-resistance-rated assemblies. Penetrations shall be installed as tested in an approved fire-resistance-rated assembly.

[713.3.1.2] 714.3.1.2 Through-penetration firestop system. [Through penetrations] Through-penetrations shall be protected by an approved penetration [fire stop] firestop system installed as tested in accordance with ASTM E 814 or UL 1479, with a minimum positive pressure differential of 0.01 inch (2.49 Pa) of water and shall have an F rating of not less than the required fire-resistance rating of the wall penetrated.

[713.3.2] 714.3.2 Membrane penetrations. Membrane penetrations shall be protected by a membrane penetration firestop installed in accordance with Section [713.3.1] 714.3.1. Where walls or partitions are required to have a fire-resistance rating, recessed fixtures shall be installed such that the required fire resistance will not be reduced.

Exceptions:

1.	Membrane penetrations of maximum 2-hour fire-resistance-rated walls and partitions by steel electrical boxes that do not exceed 16 square inches (0.0103 m²) in area, provided the aggregate area of the openings does not exceed 100 square inches (0.0645 m²) for any 100 square feet (9.29 m²) [in] of wall area. The annular space between the wall membrane and the box shall not exceed 1/8 inch [(3.1 mm)] (3.2 mm). Such boxes on opposite sides of the wall or [partitions] partition shall be separated by one of the following:

1.1.	By a horizontal distance of not less than 24 inches (610 mm) where the wall or partition is constructed with individual noncommunicating stud cavities;

1.2.	By a horizontal distance of not less than the depth of the wall cavity where the wall cavity is filled with cellulose loose-fill, rock wool or slag mineral wool insulation;

1.3.	By solid fireblocking in accordance with Section [717.2.1] 718.2.1;

1.4.	By protecting both outlet boxes with listed putty pads; or

1.5.	By other listed materials and methods.

2.	Membrane penetrations by listed electrical boxes of any material, provided such boxes have been tested for use in fire-resistance-rated assemblies and are installed in accordance with the instructions included in the listing. The annular space between the wall membrane and the box shall not exceed 1/8 inch [(3.1 mm)] (3.2 mm) unless listed otherwise. Such boxes on opposite sides of the wall or partition shall be separated by one of the following:

2.1.	By the horizontal distance specified in the listing of the electrical boxes;

2.2.	By solid fireblocking in accordance with Section [717.2.1] 718.2.1;

2.3.	By protecting both boxes with listed putty pads; or

2.4.	By other listed materials and methods.

3.	Membrane penetrations by electrical boxes of any size or type[, which] that have been listed as part of a wall opening protective material system for use in fire-resistance-rated assemblies and are installed in accordance with the instructions included in the listing.

4.	Membrane penetrations by boxes other than electrical boxes, provided such penetrating items and the annular space between the wall membrane and the box, are protected by an approved [membrane penetration] membrane-penetration firestop system installed as tested in accordance with ASTM E 814 or UL 1479, with a minimum positive pressure differential of 0.01 inch (2.49 Pa) of water, and shall have an F and T rating of not less than the required fire-resistance rating of the wall penetrated and be installed in accordance with their listing.

5.	The annular space created by the penetration of an automatic sprinkler, provided it is covered by a metal escutcheon plate.

6.	Membrane penetrations of maximum 2-hour fire resistance-rated walls and partitions by steel electrical boxes that exceed 16 square inches (0.0103 m²) in area, or steel electrical boxes of any size having an aggregate area through the membrane exceeding 100 square inches (0.0645 m²) in any 100 square feet (9.29 m²) of wall area, provided such penetrating items are protected by listed putty pads or other listed materials and methods, and installed in accordance with the listing.

[713.3.3] 714.3.3 Dissimilar materials. Noncombustible penetrating items shall not connect to combustible items beyond the point of fire stopping unless it can be demonstrated to the commissioner that the fire-resistance integrity of the wall is maintained.

[713.4] 714.4 Horizontal assemblies. Penetrations of a fire-resistance-rated floor, floor/ceiling assembly or the ceiling membrane of a roof/ceiling assembly not required to be enclosed in a shaft by Section [708.2] 711.1 shall be protected in accordance with Sections [713.4.1] 714.4.1 through [713.4.2.2] 714.4.2.2.

[713.4.1 Fire-resistance-rated assemblies. Penetrations of the fire-resistance-rated floor, floor/ceiling assembly or the ceiling membrane of a roof/ceiling assembly shall comply with Sections 713.4.1.1 through 713.4.1.4. Penetrations in horizontal smoke barriers shall also comply with Section 713.5.]

[713.4.1.1 Through penetrations. Through penetrations] 714.4.1 Through-penetrations. Through-penetrations of [fire-resistance-rated] horizontal assemblies shall comply with Section [713.4.1.1.1] 714.4.1.1 or [713.4.1.1.2] 714.4.1.2.

Exceptions:

1.	Penetrations by steel, ferrous or copper conduits, pipes, tubes or vents or concrete[,] or masonry items through a single fire-resistance-rated floor assembly where the annular space is protected with materials that prevent the passage of flame and hot gases sufficient to ignite cotton waste where subjected to ASTM E 119 or UL 263 time-temperature fire conditions under a minimum positive pressure differential of 0.01 inch (2.49 Pa) of water at the location of the penetration for the time period equivalent to the fire-resistance rating of the construction penetrated. Penetrating items with a maximum 6-inch (152 mm) nominal diameter shall not be limited to the penetration of a single fire-resistance-rated floor assembly, provided the aggregate area of the [penetration] penetrations does not exceed 144 square inches (92 900 mm²) in any 100 square feet (9.3 m²) of floor area.

2.	Penetrations in a single concrete floor by steel, ferrous or copper conduits, pipes, tubes or vents with a maximum 6-inch (152 mm) nominal diameter, provided that the concrete, grout or mortar is installed the full thickness of the floor or the thickness required to maintain the fire-resistance rating. The penetrating items shall not be limited to the penetration of a single concrete floor, provided [that] the area of the opening through each floor does not exceed 144 square inches (92 900 mm²).

3.	Penetrations by listed electrical boxes of any material, provided that such boxes have been tested for use in fire-resistance-rated assemblies and installed in accordance with the instructions included in the listing.

[713.4.1.1.1] 714.4.1.1 Installation. [Through penetrations] Through-penetrations shall be installed as tested in the approved fire-resistance-rated assembly.

[713.4.1.1.2] 714.4.1.2 Through-penetration firestop system. [Through penetrations] Through-penetrations shall be protected by an approved through-penetration [fire stop] firestop system installed and tested in accordance with ASTM E 814 or UL 1479, with a minimum positive pressure differential of 0.01 inch (2.49 Pa) of water. The system shall have both, an F rating (flame) and a T rating (temperature) of not less than 1 hour but not less than the required rating of the floor penetrated.

[Exception:]  Exceptions:

1.	Floor penetrations contained and located within the cavity of a wall do not require a T rating.

2.	Floor penetrations by floor drains, tub drains or shower drains contained and located within the concealed space of a horizontal assembly do not require a T rating.

3.	Floor penetrations of maximum 4-inch (102 mm) nominal diameter penetrating directly into metal-enclosed electrical power switchgear do not require a T rating.

[713.4.1.2] 714.4.2 Membrane penetrations. Penetrations of membranes that are part of a [fire-resistance-rated] horizontal assembly shall comply with Section [713.4.1.1.1 or 713.4.1.1] 714.4.1.1 or 714.4.1.2. Where floor/ceiling assemblies are required to have a fire-resistance rating, recessed fixtures shall be installed such that the required fire resistance will not be reduced.

Exceptions:

1.	Membrane penetrations by steel, ferrous or copper conduits, pipes, tubes or vents, or concrete[,] or masonry items where the annular space is protected either in accordance with Section [713.4.1.1] 714.4.1 or to prevent the free passage of flame and the products of combustion. The aggregate area of the openings through the membrane shall not exceed 100 square inches (64 500 mm2) in any 100 square feet (9.3 m2) of ceiling area in assemblies tested without penetrations.

2.	Ceiling membrane penetrations of maximum 2-hour horizontal assemblies by steel electrical boxes that do not exceed 16 square inches (10 323 mm2) in area, provided the aggregate area of such penetrations does not exceed 100 square inches [(44 500 mm2)] (64 500 mm2) in any 100 square feet [(9.29 m2)] (9.3 m2) of ceiling area, and the annular space between the ceiling membrane and the box does not exceed 1/8 inch (3.2 mm).

3.	Membrane penetrations by electrical boxes of any size or type [, which] that have been listed as part of an opening protective material system for use in horizontal assemblies and are installed in accordance with the instructions included in the listing.

4.	Membrane penetrations by listed electrical boxes of any material, provided such boxes have been tested for use in fire-resistance-rated assemblies and are installed in accordance with the instructions included in the listing. The annular space between the ceiling membrane and the box shall not exceed 1/8 inch (3.2 mm) unless listed otherwise.

5.	The annular space created by the penetration of a fire sprinkler, provided it is covered by a metal escutcheon plate.

6.	Noncombustible items that are cast into concrete building elements and that do not penetrate both top and bottom surfaces of the element, provided such items are installed such that the required fire resistance will not be reduced.

7.	The ceiling membrane of 1- and 2-hour fire-resistance-rated horizontal assemblies is permitted to be interrupted with the double wood top plate of a wall assembly that is sheathed with Type X gypsum wallboard, provided that all penetrating items through the double top plates are protected in accordance with Section 714.4.1.1 or 714.4.1.2 and the ceiling membrane is tight to the top plates.

[713.4.1.3 Ducts and air transfer openings. Penetrations of horizontal assemblies by ducts and air transfer openings shall comply with Section 716.]

714.4.3 Penetrations in smoke barriers. Penetrations in smoke barriers shall be protected by an approved through-penetration firestop system installed and tested in accordance with the requirements of UL 1479 for air leakage. The L rating of the system measured at 0.30 inch (7.47 Pa) of water in both the ambient temperature and elevated temperature tests shall not exceed:

1.	5.0 cfm per square foot (0.025 m3/ s · m2) of penetration opening for each through-penetration firestop system; or

2.	A total cumulative leakage of 50 cfm (0.024 m3/s) for any 100 square feet (9.3 m2) of wall area, or floor area.

[713.4.2] 714.5 Nonfire-resistance-rated assemblies. Penetrations of nonfire-resistance-rated floor or floor/ceiling assemblies or the ceiling membrane of a nonfire-resistance-rated roof/ceiling assembly shall meet the requirements of Section [708] 713 or shall comply with [Sections 713.4.2.1 through 713.4.2] Section 714.5.1 or 714.5.2.

[713.4.2.1] 714.5.1 Noncombustible penetrating items. Noncombustible penetrating items that connect not more than three stories are permitted, provided that the annular space is filled with an approved noncombustible material or with a fill, void or cavity material that is tested and classified for use in through-penetration firestop systems.

[713.4.2.2] 714.5.2 Penetrating items. Penetrating items that connect not more than two stories are permitted, provided that the annular space is filled with an approved material to resist the free passage of flame and the products of combustion.

[713.5 Penetrations in smoke barriers. Penetrations in smoke barriers shall be tested in accordance with the requirements of UL 1479 for air leakage. The air leakage rate of the penetration assemblies measured at 0.30 inch (7.47 Pa) of water in both the ambient temperature and elevated temperature tests, shall not exceed:]

[1.	5.0 cfm per square foot (0.025 m3/s m2) of penetration opening for each through-penetration firestop system; or]

[2.	A total cumulative leakage of 50 cfm (0.024 m3/s) for any 100 square feet (9.3 m2) of wall area, or floor area.]

SECTION BC [714] 715
FIRE-RESISTANT JOINT SYSTEMS

[714.1] 715.1 General. Joints installed in or between fire-resistance-rated walls, floor or floor/ceiling assemblies and roofs or roof/ceiling assemblies shall be protected by an approved fire-resistant joint system designed to resist the passage of fire for a time period not less than the required fire-resistance rating of the wall, floor or roof in or between which [it] the system is installed. Fire-resistant joint systems shall be tested in accordance with Section [714.3] 715.3. [The void created at the intersection of a floor/ceiling assembly and an exterior curtain wall assembly shall be protected in accordance with Section 714.4.]

Exception: Fire-resistant joint systems shall not be required for joints in all of the following locations:

1.	Floors within a single dwelling unit.

2.	Floors where the joint is protected by a shaft enclosure in accordance with Section [708] 713.

3.	Floors within atriums where the space adjacent to the atrium is included in the volume of the atrium for smoke control purposes.

4.	[Floors within malls where a tenant space is separated from the mall.] Joints between floors within malls and non-rated assemblies.

5.	Floors and ramps within open and enclosed parking garages or structures constructed in accordance with Sections [406.3] 406.5 and [406.4] 406.6, respectively.

6.	Mezzanine floors.

7.	Walls that are permitted to have unprotected openings.

8.	Roofs where openings are permitted.

9.	Control joints not exceeding a maximum width of 0.625 inch (15.9 mm) and tested in accordance with ASTM E 119 or UL 263.

715.1.1 Curtain wall assembly. The void created at the intersection of a floor/ceiling assembly and an exterior curtain wall assembly shall be protected in accordance with Section 715.4.

[714.2] 715.2 Installation. [Fire-resistant joint systems] A fire-resistant joint system shall be securely installed in accordance with the listing criteria in or on the joint for its entire length so as not to dislodge, loosen or otherwise impair [its] the joint system’s ability to accommodate expected building movements and to resist the passage of fire and hot gases.

[714.3] 715.3 Fire test criteria. Fire-resistant joint systems shall be tested in accordance with the requirements of either ASTM E 1966 or UL 2079. Nonsymmetrical wall joint systems shall be tested with both faces exposed to the furnace, and the assigned fire-resistance rating shall be the shortest duration obtained from the two tests. [When] Where evidence is furnished to show that the wall was tested with the least fire-resistant side exposed to the furnace, subject to acceptance of the commissioner, the wall need not be subjected to tests from the opposite side.

Exception: For exterior walls with a horizontal fire separation distance greater than 5 feet (1524 mm), the joint system shall be required to be tested for interior fire exposure only.

[714.4] 715.4 Exterior curtain wall/floor intersection. Where fire resistance-rated floor or floor/ceiling assemblies are required, voids created at the intersection of the exterior curtain wall assemblies and such floor assemblies shall be sealed with an approved system to prevent the interior spread of fire. Such systems shall be securely installed and tested in accordance with ASTM E 2307 to [prevent the passage of flame] provide an F rating for [the] a time period [at least equal to] not less than the fire-resistance rating of the floor assembly [and prevent the passage of heat and hot gases sufficient to ignite cotton waste]. Height and fire-resistance requirements for curtain wall spandrels shall comply with Section 705.8.5.

Exception: Voids created at the intersection of the exterior curtain wall assemblies and such floor assemblies where the vision glass extends to the finished floor level shall be permitted to be sealed with an approved material to prevent the interior spread of fire. Such material shall be securely installed and capable of preventing the passage of flame and hot gases sufficient to ignite cotton waste where subjected to ASTM E 119 time-temperature fire conditions under a minimum positive pressure differential of 0.01 inch (0.254 mm) of water column (2.5 Pa) for the time period not less than the fire-resistance rating of the floor assembly.

715.4.1 Exterior curtain wall/nonfire-resistance-rated floor assembly intersections. Voids created at the intersection of exterior curtain wall assemblies and nonfire-resistance-rated floor or floor/ceiling assemblies shall be sealed with an approved material or system to retard the interior spread of fire and hot gases between stories.

715.4.2 Exterior curtain wall/vertical fire barrier intersections. Voids created at the intersection of nonfire-resistance-rated exterior curtain wall assemblies and fire barriers shall be filled. An approved material or system shall be used to fill the void and shall be securely installed in or on the intersection for its entire length so as not to dislodge, loosen or otherwise impair its ability to accommodate expected building movements and to retard the passage of fire and hot gases.

[714.5] 715.5 Spandrel wall. Height and fire-resistance requirements for curtain wall spandrels shall comply with Section 705.8.5. Where Section 705.8.5 does not require a fire-resistance-rated spandrel wall, the requirements of Section [714.4] 715.4 shall still apply to the intersection between the spandrel wall and the floor.

[714.6] 715.6 Fire-resistant joint systems in smoke barriers. Fire-resistant joint systems in smoke barriers, and joints at the intersection of a horizontal smoke barrier and an exterior curtain wall, shall be tested in accordance with the requirements of UL 2079 for air leakage. The [air leakage rate] L rating of the joint system shall not exceed 5 cfm per [lineal] linear foot (0.00775 m3/s m) of joint at 0.30 inch (7.47 Pa) of water for both the ambient temperature and elevated temperature tests.

SECTION BC [715] 716
OPENING PROTECTIVES

[715.1] 716.1 General. Opening protectives required by other sections of this code shall comply with the provisions of this section.

[715.2] 716.2 Fire-resistance-rated glazing. Fire-resistance-rated glazing tested as part of a fire-resistance-rated wall or floor/ceiling assembly in accordance with ASTM E 119 or UL 263 and labeled in accordance with Section [703.5] 703.6 shall not otherwise be required to comply with this section where used as part of a wall or floor/ceiling assembly. Fire-resistance-rated glazing shall be permitted in fire [doors] door and fire window assemblies where tested and installed in accordance with their listings and [shall not otherwise be required to comply with] where in compliance with the requirements of this section.

716.3 Marking fire-rated glazing assemblies. Fire-rated glazing assemblies shall be marked in accordance with Tables 716.3, 716.5 and 716.6.

| TABLE 716.3 MARKING FIRE-RATED GLAZING ASSEMBLIES |
| --- |
| FIRE TEST STANDARD | MARKING | DEFINITION OF MARKING |
| ASTM E 119 or UL 263 | W | Meets wall assembly criteria. |
| NFPA 257 or UL 9 | OH | Meets fire window assembly criteria including the hose stream test. |
| NFPA 252 or UL 10B or UL 10C | D H T | Meets fire door assembly criteria. Meets fire door assembly hose stream test. Meets 450ºF temperature rise criteria for 30 minutes. |
|  | XXX | The time in minutes of the fire resistance or fire protection rating of the glazing assembly. |

For SI: ºC = ((ºF) – 32)/1.8.

716.3.1 Fire-rated glazing identification. For fire-rated glazing, the label shall bear the identification required in Tables 716.3 and 716.5. “D” indicates that the glazing is permitted to be used in fire door assemblies and that the glazing meets the fire protection requirements of NFPA 252. “H” shall indicate that the glazing meets the hose stream requirements of NFPA 252. “T” shall indicate that the glazing meets the temperature requirements of Section 716.5.5.1. The placeholder “XXX” represents the fire-rating period, in minutes.

716.3.2 Fire-protection-rated glazing identification. For fire-protection-rated glazing, the label shall bear the following identification required in Tables 716.3 and 716.6: “OH – XXX.” “OH” indicates that the glazing meets both the fire protection and the hose-stream requirements of NFPA 257 or UL 9 and is permitted to be used in fire window openings. The placeholder “XXX” represents the fire-rating period, in minutes.

716.3.3 Fire-rated glazing that exceeds the code requirements. Fire-rated glazing assemblies marked as complying with hose stream requirements (H) shall be permitted in applications that do not require compliance with hose stream requirements. Fire-rated glazing assemblies marked as complying with temperature rise requirements (T) shall be permitted in applications that do not require compliance with temperature rise requirements. Fire-rated glazing assemblies marked with ratings (XXX) that exceed the ratings required by this code shall be permitted.

[715.3] 716.4 Alternative methods for determining fire protection ratings. The application of any of the alternative methods listed in this section shall be based on the fire exposure and acceptance criteria specified in NFPA 252, NFPA 257 or UL 9. The required fire resistance of an opening protective shall be permitted to be established by any of the following methods or procedures:

1.	Designs documented in approved sources.

2.	Calculations performed in an approved manner.

3.	Engineering analysis based on a comparison of opening protective designs having fire protection ratings as determined by the test procedures set forth in NFPA 252, NFPA 257 or UL 9.

4.	Alternative protection methods as allowed by Section 28-113.2 of the Administrative Code.

[715.4] 716.5 Fire door and shutter assemblies. Approved fire door and fire shutter assemblies shall be constructed of any material or assembly of component materials that conforms to the test requirements of Section [715.4.1] 716.5.1, [715.4.2] 716.5.2 or [715.4.3] 716.5.3 and the fire protection rating indicated in Table [715.4] 716.5. Fire door frames with transom lights, sidelights or both shall be permitted in accordance with Section [715.4.5] 716.5.6. Fire door assemblies and shutters shall be installed in accordance with the provisions of this section and NFPA 80.

Exceptions:

1.	Labeled protective assemblies that conform to the requirements of this section or UL 10A, UL 14B and UL 14C for tin-clad fire door assemblies.

2.	Floor fire door assemblies in accordance with Section [712.8] 712.1.13.1.

| [TABLE 715.4 FIRE DOOR AND FIRE SHUTTER FIRE PROTECTION RATINGS] |
| --- |
| [TYPE OF ASSEMBLY] | [REQUIRED ASSEMBLY RATING (hours)] | [MINIMUM FIRE DOOR AND FIRE SHUTTER ASSEMBLY RATING (hours)] |
| [Fire walls and fire barriers having a required fire-resistance rating greater than 1 hour] | [4] | [3] |
|  | [3] | [3a] |
|  | [2] | [11/2] |
|  | [11/2] | [11/2] |
| [Fire barriers having a required fire-resistance rating of 1 hour:] |  |  |
| [Shaft, exit enclosure and exit passageway walls] | [1] | [1] |
| [Other fire barriers] | [1] | [3/4] |
| [Fire partitions:] |  |  |
| [Corridor walls] | [1] | [3/4] |
| [Other partitions] | [1] | [3/4] |
| [Exterior walls] | [3] | [11/2] |
|  | [2] | [11/2] |
|  | [1] | [3/4] |
| [Smoke barriers] | [1] | [1/3] |

[a.	Two doors, each with a fire protection rating of 11/2 hours, installed on opposite sides of the same opening in a fire wall, shall be deemed equivalent in fire protection rating to one 3-hour fire door.]

[b.	For testing requirements, see Section 715.4.3.]

| TABLE 716.5 OPENING FIRE PROTECTION ASSEMBLIES, RATINGS AND MARKINGS |
| --- |
| TYPE OF ASSEMBLY | REQUIRED WALL ASSEMBLY RATING (hours) | MINIMUM FIRE DOOR AND FIRE SHUTTER ASSEMBLY RATING (hours) | DOOR VISION PANEL SIZEb | FIRE-RATED GLAZING MARKING DOOR VISION PANELd | MINIMUM SIDELIGHT/ TRANSOM ASSEMBLY RATING (hours) | FIRE-RATED GLAZING MARKING SIDELIGHT/TRANSOM PANEL |
|  |  |  |  |  | Fire protection | Fire resistance | Fire protection | Fire resistance |
| Fire walls, public corridor walls and fire barriers having a required fire-resistance rating greater than 1 hour | 4 | 3 | See Note b | D-H-W-240 | Not Permitted | 4 | Not Permitted | W-240 |
|  | 3 | 3a | See Note b | D-H-W-180 | Not Permitted | 3 | Not Permitted | W-180 |
|  | 2 | 11/2 | 100 sq. in. | 100 sq. in. = D-H-90 >100 sq. in.= D-H-W-90 | Not Permitted | 2 | Not Permitted | W-120 |
|  | 11/2 | 11/2 | 100 sq. in. | 100 sq. in. = D-H-90 >100 sq. in.= D-H-W-90 | Not Permitted | 11/2 | Not Permitted | W-90 |
| Enclosures for shafts, interior exit stairways and interior exit ramps | 2 | 11/2 | 100 sq. in. | 100 sq. in. = D-H-90 > 100 sq. in.= D-H-T-W-90 | Not Permitted | 2 | Not Permitted | W-120 |
| Horizontal exits in fire wallse | 4 | 3 | 100 sq. in. | 100 sq. in. = D-H-180 > 100 sq. in.= D-H-W-240 | Not Permitted | 4 | Not Permitted | W-240 |
|  | 3 | 3a | 100 sq. in. | 100 sq. in. = D-H-180 > 100 sq. in.= D-H-W-180 | Not Permitted | 3 | Not Permitted | W-180 |
| Fire barriers having a required fire-resistance rating of 1 hour: Enclosures for shafts, exit access stairways, exit access ramps, interior exit stairways and interior exit ramps; and exit passageway walls | 1 | 1 | 100 sq. in.c | 100 sq. in. = D-H-60 >100 sq. in.= D-H-T-W-60 | Not Permitted | 1 | Not Permitted | W-60 |
|  | Fire protection |  |
| Other fire barriers; and public corridor walls | 1 | 3/4 | Maximum size tested | D-H | 3/4 | D-H |
| Fire partitions: Interior corridor walls | 1 | 3/4 | Maximum size tested | D-20 | 3/4b | D-H-OH-45 |
| Other fire partitions | 1 | 3/4 | Maximum size tested | D-H-45 | 3/4 | D-H-45 |
| Exterior walls | 3 | 11/2 | 100 sq. in.b | 100 sq. in. = D-H-90 >100 sq. in = D-H-W-90 | Not Permitted | 3 | Not Permitted | W-180 |
|  | 2 | 11/2 | 100 sq. in.b | 100 sq. in. = D-H-90 >100 sq. in.= D-H-W-90 | Not Permitted | 2 | Not Permitted | W-120 |
|  |  | Fire protection |  |
|  | 1 | 3/4 | Maximum size tested | D-H-45 | 3/4 | D-H-45 |
| Smoke barriers |  | Fire protection |  |
|  | 1 | 1/3 | Maximum size tested | D-20 | 3/4 | D-H-OH-45 |

For SI: 1 square inch = 645.2 mm.

a.	Two doors, each with a fire protection rating of 11/2 hours, installed on opposite sides of the same opening in a fire wall, shall be deemed equivalent in fire protection rating to one 3-hour fire door.

b.	Fire-resistance-rated glazing tested to ASTM E 119 in accordance with Section 716.2 shall be permitted, in the maximum size tested.

c.	Except where the building is equipped throughout with an automatic sprinkler and the fire-rated glazing meets the criteria established in Section 716.5.5.

d.	Under the column heading “Fire-rated glazing marking door vision panel,” W refers to the fire-resistance rating of the glazing, not the frame.

e.	See Section 716.5.8.1.2.1.

[715.4.1] 716.5.1 Side-hinged or pivoted swinging doors. Fire door assemblies with side-hinged and pivoted swinging doors shall be tested in accordance with NFPA 252 or UL 10C. After 5 minutes into the NFPA 252 test, the neutral pressure level in the furnace shall be established at 40 inches (1016 mm) or less above the sill.

[715.4.2] 716.5.2 Other types of assemblies. Fire door assemblies with other types of doors, including swinging elevator doors, horizontal sliding fire door assemblies, and fire shutter assemblies, bottom and side-hinged chute intake doors, and top-hinged chute discharge doors, shall be tested in accordance with NFPA 252 or UL 10B. The pressure in the furnace shall be maintained as nearly equal to the atmospheric pressure as possible. Once established, the pressure shall be maintained during the entire test period.

[715.4.3] 716.5.3 Door assemblies in corridors and smoke barriers. Fire door assemblies located in corridor walls or smoke barrier walls having a fire-resistance rating in accordance with Table [715.4] 716.5 shall be tested in accordance with NFPA 252 or UL 10C.

Exceptions:

1.	Viewports that require a hole not larger than 1 inch (25 mm) in diameter through the door, have [at least an] not less than a 0.25-inch-thick (6.4 mm) glass disc and the holder is of metal that will not melt out where subject to temperatures of 1,700°F (927°C).

2.	Corridor door assemblies in occupancies of Group I-2 shall be in accordance with Section 407.3.1.

3.	Horizontal sliding doors in smoke barriers that comply with Sections [408.3] 408.6 and 408.8.4 in occupancies in Group I-3.

[715.4.3.1] 716.5.3.1 Smoke and draft control. Fire door assemblies shall [also] meet the requirements for a smoke and draft control door assembly tested in accordance with UL 1784. The air leakage rate of the door assembly shall not exceed 3.0 cubic feet per minute per square foot (0.01524 m3/s • m2) of door opening at 0.10 inch (24.9 Pa) of water for both the ambient temperature and elevated temperature tests. Louvers shall be prohibited. Installation of smoke doors shall be in accordance with NFPA 105.

[715.4.3.2] 716.5.3.2 Glazing in door assemblies. Glazing material in any other part of the door assembly, including transom lights and sidelights, shall be tested in accordance with NFPA 257 or UL 9, including the hose stream test, in accordance with Section [715.5] 716.6.

716.5.4 Reserved.

[715.4.4] 716.5.5 Doors in interior exit [enclosures] stairways and ramps and exit passageways. Fire door assemblies in interior exit [enclosures] stairways and ramps and exit passageways shall have a maximum transmitted temperature [end point] rise of not more than 450°F (232°C) above ambient at the end of 30 minutes of standard fire test exposure.

Exception: The maximum transmitted temperature is not required in buildings equipped throughout with an automatic sprinkler system installed in accordance with Section 903.3.1.1 or 903.3.1.2.

[715.4.4.1] 716.5.5.1 Glazing in doors. Fire-protection-rated glazing in excess of 100 square inches (0.065 m2) [shall be permitted in fire door assemblies when tested as components of the door assemblies and not as glass lights, and shall have a maximum transmitted temperature rise of 450F (232C) in accordance with Section 715.4.4.] is not permitted.  Fire-resistance-rated glazing in excess of 100 square inches (64 516 mm2) shall be permitted in fire doors. Listed fire-resistance-rated glazing in a fire door shall have a maximum transmitted temperature rise in accordance with Section 716.5.5 when the fire door is tested in accordance with NFPA 252, UL 10B or UL 10C.

[Exception: The maximum transmitted temperature rise is not required in buildings equipped throughout with an automatic sprinkler system installed in accordance with Section 903.3.1.1 or 903.3.1.2.]

[715.4.5] 716.5.6 Fire door frames with transom lights and sidelights. Door frames with transom lights, sidelights[,] or both, shall be permitted where a 3/4-hour fire protection rating or less is required in accordance with Table [715.4] 716.5. [Where a fire protection rating exceeding ¾-hour is required in accordance with Table 715.4, fire door] Fire door frames with transom lights, sidelights, or both, [shall be permitted where] installed with fire-resistance-rated glazing tested as an assembly in accordance with ASTM E 119 or UL 263 shall be permitted where a fire protection rating exceeding 3/4 hour is required in accordance with Table 716.5.

[715.4.6] 716.5.7 Labeled protective assemblies. Fire door assemblies shall be labeled by an approved agency. The labels shall comply with NFPA 80, and shall be permanently affixed to the door or frame.

[715.4.6.1] 716.5.7.1 Fire door labeling requirements. Fire doors shall be labeled showing the name of the manufacturer or other identification readily traceable back to the manufacturer, the name or trademark of the third-party inspection agency, the fire protection rating and, where required for fire doors in interior exit [enclosures] stairways and ramps and exit passageways by Section [715.4.4] 716.5.5, the maximum transmitted temperature end point. Smoke and draft control doors complying with UL 1784 shall be labeled as such and shall [also] comply with Section [715.4.6] 716.5.7. Labels shall be approved and permanently affixed. The label shall be applied at the factory or location where fabrication and assembly are performed.

716.5.7.1.1 Vision light kits, louvers and components. Listed vision light kits and louvers and their required preparations shall be considered as part of the labeled door where such installations are listed and where quality assurance testing is done under the listing program of the third-party testing agency. Fire doors and door assemblies shall be permitted to consist of components, including glazing, vision light kits and hardware that are listed or classified and labeled for such use by different third-party agencies.

[715.4.6.2] 716.5.7.2 Oversized doors. Oversized fire doors shall bear an oversized fire door label by an approved agency or shall be provided with a certificate of inspection furnished by an approved testing agency. [When] Where a certificate of inspection is furnished by an approved testing agency, the certificate shall state that the door conforms to the requirements of design, materials and construction, but has not been subjected to the fire test.

[715.4.6.3] 716.5.7.3 Smoke and draft control door labeling requirements. Smoke and draft control doors complying with UL 1784 shall be labeled in accordance with Section [715.4.6.1] 716.5.7.1 and shall show the letter “S” on the fire rating label of the door. This marking shall indicate that the door and frame assembly are in compliance [when] where listed or labeled gasketing is [also] installed.

[715.4.6.4] 716.5.7.4 Fire door frame labeling requirements. Fire door frames shall be labeled showing the names of the manufacturer and the third-party inspection agency.

716.5.7.5 Fire door operator labeling requirements. Fire door operators for horizontal sliding doors shall be labeled and listed for use with the assembly.

[715.4.7] 716.5.8 Glazing material. [Fire-protection-rated] Fire-rated glazing and fire-resistance-rated glazing conforming to the opening protection requirements in Section [715.4] 716.5 shall be permitted in fire door assemblies.

[715.4.7.1 Size limitations. Fire-protection-rated glazing used in fire doors shall comply with the size limitations of NFPA 80.]

[Exceptions:]

[1.	Fire-protection-rated glazing in fire doors located in fire walls shall be prohibited except that where serving in a fire door in a horizontal exit, a self-closing swinging door shall be permitted to have a vision panel of not more than 100 square inches (0.065 m2) without a dimension exceeding 10 inches (254 mm).]

[2.	Fire-protection-rated lazing shall not be installed in  fire doors having a 11/2-hour fire protection rating intended for installation in fire barriers, unless the glazing is not more than 100 square inches (0.065 m2) in area.]

716.5.8.1 Size limitations. Fire-resistance-rated glazing shall comply with the size limitations in Section 716.5.8.1.1. Fire-protection-rated glazing shall comply with the size limitations of NFPA 80, and as provided in Section 716.5.8.1.2.

716.5.8.1.1 Fire-rated glazing in door assemblies in fire walls and fire barriers rated greater than 1 hour. Fire-rated glazing tested to ASTM E 119 or UL 263 and NFPA 252, UL 10B or UL 10C shall be permitted in fire door assemblies located in fire walls and in fire barriers in accordance with Table 716.5 to the maximum size tested and in accordance with their listings.

716.5.8.1.2 Fire-protection-rated glazing in door assemblies in fire walls and fire barriers rated greater than 1 hour. Fire-rated glazing shall be prohibited in fire walls and fire barriers except as provided in Sections 716.5.8.1.2.1 and 716.5.8.1.2.2.

716.5.8.1.2.1 Horizontal exits. Fire-protection-rated glazing shall be permitted as vision panels in self-closing swinging fire door assemblies serving as horizontal exits in fire walls where limited to 100 square inches (64 516 mm2) with no dimension exceeding 10 inches (254 mm).

716.5.8.1.2.2 Fire barriers. Fire-rated glazing shall be permitted in fire doors having a 11/2-hour fire protection rating intended for installation in fire barriers, where limited to 100 square inches (64 516 mm2).

[715.4.7.2 Exit] 716.5.8.2 Elevator, stairway and [elevator] ramp protectives. Approved [fire-protection-rated] fire-rated glazing used in fire door assemblies in elevator, stairway and [exit] ramp enclosures shall be so located as to furnish clear vision of the passageway or approach to the elevator, [ramp or] stairway or ramp.

[715.4.7.3] 716.5.8.3 Labeling. [Fire-protection-rated] Fire-rated glazing shall bear a label or other identification showing the name of the manufacturer, the test standard and information required in [Section 715.5.9.1] Table 716.3 that shall be issued by an approved agency and shall be permanently [affixed to] identified on the glazing.

[715.4.7.3.1 Identification. For fire protection-rated glazing, the label shall bear the following four-part identification: “D, H or NH, T or NT, XXX.” “D” indicates that the glazing shall “NH” shall indicate that the glazing does not meet the hose stream requirements of the test. “T” shall indicate that the glazing meets the temperature requirements of Section 715.4.4.1. “NT” shall indicate that the glazing does not meet the temperature requirements of Section 715.4.4.1. The placeholder “XXX” shall specify the fire-protection-rating period, in minutes.]

[715.4.7.4] 716.5.8.4 Safety glazing. [Fire-protection-rated] Fire-rated glazing installed in fire [doors in areas subject to human impact in hazardous locations] door assemblies shall comply with the safety glazing requirements of Chapter 24 where applicable.

[715.4.8] 716.5.9 Door closing. Fire doors shall be latching and self-closing or automatic-closing in accordance with this section.

Exceptions:

1.	Fire doors located in common walls separating sleeping units in Group R-1 shall be permitted without automatic- or self-closing devices.

2.	The elevator car doors and the associated hoistway enclosure doors at the floor level designated for recall in accordance with Section 3003.2 shall be permitted to remain open during Phase I emergency recall operation.

[715.4.8.1] 716.5.9.1 Latch required. Unless otherwise specifically permitted, single fire doors and both leaves of pairs of side-hinged swinging fire doors shall be provided with an active latch bolt that will secure the door when it is closed.

716.5.9.1.1 Chute intake door latching. Chute intake doors shall be positive latching, remaining latched and closed in the event of latch spring failure during a fire emergency.

[715.4.8.2] 716.5.9.2 Automatic-closing fire door assemblies. Automatic-closing fire door assemblies shall be self-closing in accordance with NFPA 80.

[715.4.8.3] 716.5.9.3 Smoke-activated doors. Automatic-closing fire doors installed in the following locations shall be automatic-closing by the actuation of smoke detectors installed in accordance with Section 907.3 or by loss of power to the smoke detector where such detector is powered by the building’s normal electrical service or by loss of power to the hold-open device. Doors that are automatic-closing by smoke detection shall not have more than a 10-second delay before the door starts to close after the smoke detector is actuated.

1.	Doors installed across a corridor.

2.	Doors installed in the enclosures of exit access stairways and ramps in accordance with Sections 1019 and 1023, respectively.

[2.] 3.	Doors that protect openings in exits or corridors required to be of fire-resistance-rated construction.

[3.] 4.	Doors that protect openings in walls that are capable of resisting the passage of smoke in accordance with Section 509.4.

[4.] 5.	Doors installed in smoke barriers in accordance with Section [710.5] 709.5.

[5.] 6.	Doors installed in fire partitions in accordance with Section [709.6] 708.6.

[6.] 7.	Doors installed in a fire wall in accordance with Section 706.8.

[7.] 8.	Doors installed in shaft enclosures in accordance with Section [708.7] 713.7.

[8.] 9.	Doors installed in [refuse] waste and [laundry] linen chutes, discharge openings and access and [termination] discharge rooms in accordance with Section [708.13] 713.13. Loading doors installed in waste and linen chutes shall meet the requirements of Sections 716.5.9 and 716.5.9.1.1.

[9.] 10.	Doors installed in the walls for compartmentation of underground buildings in accordance with Section 405.4.2.

[10.] 11.	Doors installed in the elevator lobby walls of underground buildings in accordance with Section 405.4.3.

[11.] 12.	Doors installed in smoke partitions in accordance with Section [711.5.3] 710.5.2.3.

[12.] 13. Doors serving [vertical] interior exit [enclosures] stairways or ramps in accordance with the exception to Section [708.7] 713.7.

[715.4.8.4] 716.5.9.4 Doors in pedestrian ways. Vertical sliding or vertical rolling steel fire doors in openings through which pedestrian’s travel shall be heat activated or activated by smoke detectors with alarm verification.

[715.4.9] 716.5.10 Swinging fire shutters. Where fire shutters of the swinging type are installed in exterior openings, not less than one row in every three vertical rows shall be arranged to be readily opened from the outside, and shall be identified by distinguishing marks or letters not less than 6 inches (152 mm) high.

[715.4.10] 716.5.11 Rolling fire shutters. Where fire shutters of the rolling type are installed, such shutters shall include approved automatic-closing devices.

[715.5] 716.6 [Fire-protection rated] Fire-protection-rated glazing. Glazing in fire window assemblies shall be fire protection rated in accordance with this section and Table [715.5] 716.6. Glazing in fire door assemblies shall comply with Section [715.4.7] 716.5.8. Fire-protection-rated glazing in fire window assemblies shall be tested in accordance with and shall meet the acceptance criteria of NFPA 257 or UL 9. Fire-protection-rated glazing shall [also] comply with NFPA 80. Openings in nonfire-resistance-rated exterior wall assemblies that require protection in accordance with Section 705.3, 705.8, 705.8.5 or 705.8.6 shall have a fire protection rating of not less than ¾ hour.

[Exception: Wired glass in accordance with Section 715.5.4.]

| [TABLE 715.5 FIRE WINDOW ASSEMBLY FIRE PROTECTION RATINGS] |
| --- |
| [TYPE OF ASSEMBLY] | [REQUIRED ASSEMBLY RATING (hours)] | [MINIMUM FIRE WINDOW ASSEMBLY RATING (hours)] |
| [Interior walls:] | [Fire walls] | [All] | [NPa] |
|  | [Fire barriers] | [>1] [1] | [NPa] [¾] |
|  | [Smoke barriers] | [1] | [¾] |
|  | [Fire partitions] | [1] | [¾] |
| [Exterior walls] | [>1] [1] | [1½] [¾] |
| [Party walls] | [All] | [NPa] |

[a. Not permitted except as specified in Section 715.2.]

| TABLE 716.6 FIRE WINDOW ASSEMBLY FIRE PROTECTION RATINGS |
| --- |
| TYPE OF WALL ASSEMBLY | REQUIRED WALL ASSEMBLY RATING (hours) | MINIMUM FIRE WINDOW ASSEMBLY RATING (hours) | FIRE-RATED GLAZING MARKING |
| Interior walls: |
| Fire walls | All | NPa | W-XXXb |
| Fire barriers | >1 1 | NPa NPa | W-XXXb W-XXXb |
| Incidental use areas (Section 707.3.7), Mixed occupancy separations (Section 707.3.9) | 1 | 3/4 | OH-45 or W-60 |
| Fire partitions | 1 | 3/4 | OH-45 or W-60 |
| Smoke barriers | 1 | 3/4 | OH-45 or W-60 |
| Exterior walls | >1 1 | 11/2 3/4 | OH-90 or W-XXXb OH-45 or W-60 |
| Party wall | All | NP | Not Applicable |

NP = Not Permitted.

a.	Not permitted except fire-resistance-rated glazing assemblies tested to ASTM E 119 or UL 263, as specified in Section 716.2.

b.	XXX = The fire rating duration period in minutes, which shall be equal to the fire-resistance-rating required for the wall assembly.

[715.5.1] 716.6.1 Testing under positive pressure. NFPA 257 or UL 9 shall evaluate fire-protection-rated glazing under positive pressure. Within the first 10 minutes of a test, the pressure in the furnace shall be adjusted so [at least] not less than two-thirds of the test specimen is above the neutral pressure plane, and the neutral pressure plane shall be maintained at that height for the balance of the test.

[715.5.2] 716.6.2 Nonsymmetrical glazing systems. Nonsymmetrical fire-protection-rated glazing systems in fire partitions, fire barriers or in exterior walls with a fire separation distance of 5 feet (1524 mm) or less pursuant to Section [704] 705 shall be tested with both faces exposed to the furnace, and the assigned fire protection rating shall be the shortest duration obtained from the two tests conducted in compliance with NFPA 257 or UL 9.

[715.5.3] 716.6.3 Safety glazing. Fire-protection-rated glazing and fire-resistance-rated glazing installed in fire window assemblies [in areas subject to human impact in hazardous locations] shall comply with the safety glazing requirements of Chapter 24 where applicable.

[715.5.4 Wired glass. Steel window frame assemblies of 0.125-inch (3.2 mm) minimum solid section or of not less than nominal 0.048-inch-thick (1.2 mm) formed sheet steel members fabricated by pressing, mitering, riveting, interlocking or welding and having provision for glazing with 1/4-inch (6.4 mm) wired glass where securely installed in the building construction and glazed with 1/4-inch (6.4 mm) labeled wired glass shall be deemed to meet the requirements for a 3/4-hour fire window assembly. Wired glass panels shall conform to the size limitations set forth in Table 715.5.4.]

| [TABLE 715.5.4 FIRE DOOR AND FIRE SHUTTER FIRE PROTECTION RATINGS] |
| --- |
| [OPENING FIRE PROTECTION RATING] | [MAXIMUM AREA (square inches)] | [MAXIMUM HEIGHT (inches)] | [MAXIMUM WIDTH (inches)] |
| [3 hours] | [0] | [0] | [0] |
| [11/2-hour doors in exterior walls] | [0] | [0] | [0] |
| [1 and 11/2 hours] | [100] | [33] | [10] |
| [3/4 hour] | [1,296] | [54] | [54] |
| [Fire window assemblies] | [1 ,296] | [54] | [54] |

[For SI: 1 inch = 25.4 mm, 1 square inch = 645.2 mm2.]

[715.5.5 Nonwired glass.] 716.6.4 Glass and glazing. Glazing [other than wired glass] in fire window assemblies shall be fire-protection-rated glazing installed in accordance with and complying with the size limitations set forth in NFPA 80.

[715.5.6] 716.6.5 Installation. Fire-protection-rated glazing shall be in the fixed position or be automatic-closing and shall be installed in approved frames.

[715.5.7] 716.6.6 Window mullions. Metal mullions that exceed a nominal height of 12 feet (3658 mm) shall be protected with materials to afford the same fire-resistance rating as required for the wall construction in which the protective is located.

[715.5.8] 716.6.7 Interior fire window assemblies. Fire-protection-rated glazing used in fire window assemblies located in fire partitions and fire barriers shall be limited to use in assemblies with a maximum fire-resistance rating of 1 hour in accordance with this section.

[715.5.8.1] 716.6.7.1 Where 3/4-hour fire protection window assemblies permitted. Fire-protection-rated glazing requiring 45-minute opening protection in accordance with Table [715.5] 716.6 shall be limited to fire partitions designed in accordance with Section [709] 708 and fire barriers utilized in the applications set forth in Sections 707.3.6, 707.3.7 and [707.3.8] 707.3.9 where the fire-resistance rating does not exceed 1 hour. Fire-resistance-rated glazing assemblies tested in accordance with ASTM E 119 or UL 263 shall not be subject to the limitations of this section.

[715.5.8.2] 716.6.7.2 [Size] Area limitations. The total area of [windows] the glazing in fire-protection-rated window assemblies shall not exceed 25 percent of the area of a common wall with any room.

[715.5.9] 716.6.8 Labeling requirements. Fire-protection-rated glazing shall bear a label or other identification showing the name of the manufacturer, the test standard[,] and information required in Section [715.5.9.1] 716.3.2 and Table 716.6 that shall be issued by an approved agency and [shall be] permanently [affixed to the glazing] identified on the glazing.

[715.5.9.1 Identification. For fire-protection-rated glazing, the label shall bear the following two-part identification: “OH – XXX.” “OH” indicates that the glazing meets both the fire protection and the hose-stream requirements of NFPA 257 or UL 9 and is permitted to be used in openings. “XXX” represents the fire-protection rating period, in minutes, that was tested.]

SECTION [716] 717
DUCTS AND AIR TRANSFER OPENINGS

[716.1] 717.1 General. The provisions of this section shall govern the protection of duct penetrations and air transfer openings in assemblies required to be protected and duct penetrations in nonfire-resistance-rated floor assemblies.

717.1.1 Ducts and air transfer openings. Ducts transitioning horizontally between shafts shall not require a shaft enclosure provided that the duct penetration into each associated shaft is protected with dampers complying with this section.

[716.1.1] 717.1.2 Ducts that penetrate fire-resistance-rated assemblies without dampers. Ducts that penetrate fire-resistance-rated assemblies and are not required by this section to have dampers shall comply with the requirements of Sections [713.2] 714.2 through [713.3.3] 714.3.3. Ducts that penetrate horizontal assemblies not required to be contained within a shaft and not required by this section to have dampers shall comply with the requirements of [Section 713.4] Sections 714.4 through [713.4.2.2] 714.5.2.

[716.1.1.1] 717.1.2.1 Ducts that penetrate nonfire-resistance-rated assemblies. The space around a duct penetrating a nonfire-resistance-rated floor assembly shall comply with Section [716.6.3] 717.6.3.

[716.2] 717.2 Installation. Fire dampers, smoke dampers, combination fire/smoke dampers and ceiling radiation dampers located within air distribution and smoke control systems shall be installed in accordance with the requirements of this section, the New York City Mechanical Code, the manufacturer’s [installation] instructions and damper’s listing.

[716.2.1] 717.2.1 Smoke control system. Where the installation of a fire damper will interfere with the operation of a required smoke control system in accordance with Section 909, approved alternative protection shall be utilized. Where mechanical systems including ducts and dampers utilized for normal building ventilation serve as part of the smoke control system, the expected performance of these systems in smoke control mode shall be addressed in the rational analysis required by Section 909.4.

[716.2.1.1] 717.2.1.1 Remote control. Provisions for operation by remote control of combination fire/smoke dampers shall be in accordance with Section 607.2.1.1 of the New York City Mechanical Code.

[716.2.2] 717.2.2 Hazardous exhaust ducts. Fire dampers for hazardous exhaust duct systems shall comply with the New York City Mechanical Code.

[716.2.3] 717.2.3 Supply air systems. Smoke dampers in supply airhandling systems having a capacity equal to or greater than 15,000 cfm (7.1 m3/s) shall be installed in accordance with Section 607.2.3 of the New York City Mechanical Code.

[716.3] 717.3 Damper testing, ratings and actuation. Damper testing, ratings and actuation shall be in accordance with Sections [716.3.1] 717.3.1 through [716.3.3] 717.3.3.

[716.3.1] 717.3.1 Damper testing. Dampers shall be listed and [bear the label of an approved testing agency indicating compliance with] labeled in accordance with the standards in this section.

1.	Fire dampers shall comply with the requirements of UL 555. Only fire dampers and ceiling radiation dampers labeled for use in dynamic systems shall be installed in heating, ventilation and air-conditioning systems designed to operate with fans on during a fire.[Smoke dampers shall comply with the requirements of UL 555S. Combination fire/smoke dampers shall comply with the requirements of both UL 555 and UL 555S. Ceiling radiation dampers shall comply with the requirements of UL 555C.]

2.	Smoke dampers shall comply with the requirements of UL 555S.

3.	Combination fire/smoke dampers shall comply with the requirements of both UL 555 and UL 555S.

4.	Ceiling radiation dampers shall comply with the requirements of UL 555C or shall be tested as part of a fire-resistance-rated floor/ceiling or roof/ceiling assembly in accordance with ASTM E119 or UL 263.

[716.3.2] 717.3.2 Damper rating. Damper ratings shall be in accordance with Sections [716.3.2.1] 717.3.2.1 through [716.3.2.3] 717.3.2.3.

[716.3.2.1] 717.3.2.1 Fire damper ratings. Fire dampers shall have the minimum fire protection rating specified in Table [716.3.2.1] 717.3.2.1 for the type of penetration.

| TABLE [716.3.2.1] 717.3.2.1 FIRE DAMPER RATING |
| --- |
| TYPE OF PENETRATION | MINIMUM DAMPER RATING (hours) |
| Less than 3-hour fire-resistance-rated assemblies | 1.5 |
| 3-hour or greater fire-resistance-rated assemblies | 3 |

[716.3.2.2] 717.3.2.2 Smoke damper ratings. Smoke damper leakage ratings shall [not] be [less than] Class I or II. Elevated temperature ratings shall be not [be] less than 250°F (121°C).

[716.3.2.3] 717.3.2.3 Combination fire/smoke damper ratings. Combination fire/smoke dampers shall have the minimum fire protection rating specified for fire dampers in Table [716.3.2.1] 717.3.2.1 for the type of penetration and shall [also] have a minimum [Class II leakage rating and a minimum elevated temperature rating of 250°F (121°C)] smoke damper rating as specified in Section 717.3.2.2.

[716.3.3] 717.3.3 Damper actuation. Damper actuation shall be in accordance with Sections [716.3.3.1] 717.3.3.1 through [716.3.3.4] 717.3.3.4 as applicable.

[716.3.3.1] 717.3.3.1 Fire damper actuation device. The fire damper actuation device shall meet one of the following requirements:

1.	The operating temperature shall be approximately 50°F (10°C) above the normal temperature within the duct system, but not less than 160°F (71°C).

2.	The operating temperature shall be not more than [286°F (141°C)] 350°F (177°C) where located in a smoke control system complying with Section 909.

[716.3.3.2] 717.3.3.2 Smoke damper actuation. The smoke damper shall close upon actuation of a listed smoke detector or detectors installed in accordance with Section 907.3 and one of the following methods, as applicable:

1.	Where a smoke damper is installed within a duct, a smoke detector shall be installed [in] inside the duct or outside the duct with sampling tubes protruding into the duct. The detector or tubes within the duct shall be within 5 feet (1524 mm) of the damper [with no air]. Air outlets [or] and inlets shall not be located between the detector or tubes and the damper. The detector shall be listed for the air velocity, temperature and humidity anticipated at the point where it is installed. Other than in mechanical smoke control systems, dampers shall be closed upon fan shutdown where local smoke detectors require a minimum velocity to operate.

Exceptions:

1.	Duct smoke detectors will not be required at each fire smoke damper provided the supply fan shall shut down and all the fire smoke dampers associated with the supply system automatically close upon actuation of any automatic alarm initiating device on the floor(s).

2.	Duct smoke detectors will be required within 5 feet (1.5 m) downstream of any electric duct reheat coil.

3.	Non-ducted return air systems shall have a smoke detector located within 5 feet (1.5 m) upstream of each return air protected opening in a 2-hour fire-rated barrier.

4.	Ducted return air systems shall have a duct smoke detector located within 5 feet (1.5 m) of a smoke damper; additional smoke detectors will not be required at fire smoke dampers located downstream where there are no additional return air inlets.

2.	Where a smoke damper is installed above smoke barrier doors in a smoke barrier, a spot-type detector [listed for releasing service] shall be installed on either side of the smoke barrier door opening. The detector shall be listed for releasing service if used for direct interface with the damper.

3.	Where a smoke damper is installed within an unducted opening in a wall, a spot-type detector [listed for releasing service] shall be installed within 5 feet (1524 mm) horizontally of the damper. The detector shall be listed for releasing service if used for direct interface with the damper.

4.	Where a smoke damper is installed in a corridor wall or ceiling, the damper shall be permitted to be controlled by a smoke detection system installed in the corridor.

5.	Where a [total-coverage] smoke detection system is [provided within] installed in all areas served by [a heating, ventilation and air-conditioning (HVAC) system,]  duct in which the damper will be located, the smoke dampers shall be permitted to be controlled by the smoke detection system.

6.	Smoke dampers that are part of an engineered smoke control system shall be controlled in accordance with Section 607.3.3.2 of the New York City Mechanical Code.

[716.3.3.3] 717.3.3.3 Combination fire/smoke damper actuation. Combination fire/smoke damper actuation shall be in accordance with Sections [716.3.3.1] 717.3.3.1 and [716.3.3.2] 717.3.3.2. Combination fire/smoke dampers installed in smoke control system shaft penetrations shall not be activated by local area smoke detection unless it is secondary to the smoke management system controls.

[716.3.3.4] 717.3.3.4 Ceiling radiation damper actuation. The operating temperature of a ceiling radiation damper actuation device shall be 50°F [(27.8°C)] (10°C) above the normal temperature within the duct system, but not less than 160°F (71°C).

[716.4] 717.4 Access and identification. Fire and smoke dampers shall be provided with an approved means of access[, which] that is large enough to permit inspection and maintenance of the damper and its operating parts. The access shall not affect the integrity of fire-resistance-rated assemblies. The access openings shall not reduce the fire-resistance rating of the assembly. Access points shall be permanently identified on the exterior by a label having letters not less than 1/2 inch (12.7 mm) in height reading: FIRE/SMOKE DAMPER, SMOKE DAMPER or FIRE DAMPER followed by an identification marking that is individual and unique to the damper accessed.

[716.5] 717.5 Where required. Fire dampers, smoke dampers, [and] combination fire/smoke dampers, and ceiling radiation dampers shall be provided as specified in [this section] Sections 717.5.1 through 717.5.7 and 717.6. Where an assembly is required to have both fire dampers and smoke dampers, combination fire/smoke dampers or a fire damper and a smoke damper shall be [required] provided.

Exception: Ducts 20 square inches [(129 cm2)] (12 903 mm2) or less passing through fire-resistance-rated assemblies shall not require fire dampers or fire smoke dampers.

[716.5.1] 717.5.1 Fire walls. Ducts and air transfer openings permitted in fire walls in accordance with Section 706.11 shall be protected with listed fire dampers and smoke dampers installed in accordance with their listing.

Exception: Smoke dampers shall not be required in ducts where the air continues to move and the air-handling system installed is arranged to prevent recirculation of exhaust or return air under fire emergency conditions. The air-handling system shall be continuously monitored to ensure continuous airflow at a constantly attended location and be inspected and maintained in accordance with the system manufacturer’s instructions.

[716.5.1.1] 717.5.1.1 Horizontal exits. A listed smoke damper designed to resist the passage of smoke shall be provided at each point that a duct or air transfer opening penetrates a fire wall that serves as a horizontal exit.

[Exception: Smoke dampers shall not be required in ducts where the air continues to move and the air-handling system installed is arranged to prevent recirculation of exhaust or return air under fire emergency conditions.]

[716.5.2] 717.5.2 Fire barriers. Ducts and air transfer openings that penetrate fire barriers (horizontal and wall assemblies) shall be protected with listed fire dampers installed in accordance with their listing. Ducts and air transfer openings shall not penetrate [exit] enclosures for interior exit stairways and ramps and exit passageways, except as permitted by Sections [1022.4 and 1023.6] 1023.5 and 1024.6, respectively. In addition, smoke dampers shall be installed in penetrations of public corridor and horizontal exit walls in accordance with Sections [716.5.2.1] 717.5.2.1 and [716.5.2.2] 717.5.2.2.

Exception: Fire dampers are not required at penetrations of fire barriers where any of the following apply:

1.	Penetrations are tested in accordance with ASTM E 119 or UL 263 as part of the fire-resistance-rated assembly.

2.	Ducts are used as part of an engineered smoke control system in accordance with Section [716.2.1] 717.2.1 and Section 909 where the use of a fire damper would interfere with the operation of a smoke control system.

3.	Such walls are penetrated by ducted HVAC systems, have a required fire-resistance rating of 1 hour or less, are in areas of other than Group H and are in buildings equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1 or 903.3.1.2. For the purposes of this exception, a ducted HVAC system shall be a duct system for conveying supply, return or exhaust air as part of the structure’s HVAC system. Such a duct system shall be constructed of sheet steel not less than No. 26 gage thickness and shall be continuous from the air-handling appliance or equipment to the air outlet and inlet terminals.

[716.5.2.1] 717.5.2.1 Horizontal exits. A listed smoke damper designed to resist the passage of smoke shall be provided at each point a duct or air transfer opening penetrates a fire barrier that serves as a horizontal exit.

[Exception: Smoke dampers shall not be required in ducts where the air continues to move and the air-handling system installed is arranged to prevent recirculation of exhaust or return air under fire emergency conditions.]

[716.5.2.2] 717.5.2.2 Public corridors. A listed smoke damper designed to resist the passage of smoke shall be provided at each point a duct or air transfer opening penetrates a public corridor wall or floor constructed as a fire barrier.

Exceptions:

1.	Smoke dampers are not required where the building is equipped throughout with an engineered smoke control system in accordance with Section 909, and smoke dampers are not necessary for the operation and control of the system.

2.	Smoke dampers are not required in corridor penetrations where the duct is constructed of steel not less than 0.019-inch (0.48 mm) in thickness and there are no openings serving the corridor.

3.	Smoke dampers are not required in corridor penetrations in Group R-2 buildings and Public Corridors serving R-2 spaces in mixed use buildings.

4.	Smoke dampers shall not be required in ducts where the air continues to move and the air-handling system installed is arranged to prevent recirculation of exhaust or return air under fire emergency conditions. The air-handling system shall be continuously monitored to ensure continuous airflow at a constantly attended location and be inspected and maintained in accordance with the system manufacturer’s instructions.

[716.5.3] 717.5.3 Shaft enclosures. Ducts and air transfer openings shall not penetrate a shaft serving as an exit enclosure except as permitted by Section [1022.4] 1023.5.  Shaft enclosures that are permitted to be penetrated by ducts and air transfer openings shall be protected with approved fire and smoke dampers installed in accordance with their listing.

Exceptions:

1.	Fire dampers are not required at penetrations of shafts where any of the following criteria are met:

1.1.	[Steel] In buildings equipped throughout with an automatic sprinkler system in accordance with Chapter 9, steel exhaust subducts [are extended at least] having minimum thickness of 0.0187 inch (0.4712 mm) (No. 26 gage) extend not less than 22 inches (559 mm) vertically in exhaust shafts provided that there is a continuous airflow upward to the [outside;] outdoors whenever the building is occupied.

1.2.	Penetrations are tested in accordance with ASTM E 119 or UL 263 as part of the fire-resistance-rated assembly[;].

1.3.	Ducts are used as part of an approved smoke control system designed and installed in accordance with Section 909[,] and where the fire damper will interfere with the operation of the smoke control system[; or].

1.4.	The penetrations are in parking garage exhaust or supply shafts that are separated from other building shafts by not less than 2-hour fire-resistance-rated construction.

2.	[In Group B and R occupancies equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1, smoke dampers are not required at penetrations of shafts where kitchen, bathroom and toilet room exhaust openings with steel exhaust subducts, having a minimum thickness of 0.0187 inch (0.4712 mm) (No. 36 gage), extend at least 22 inches (559 mm) vertically and where the exhaust fan at the upper terminus is powered continuously and maintains airflow upward to the outdoors.] Smoke dampers are not required in exhaust ducts or shafts where the exhaust fan is maintained in operation whenever the building is occupied, in bathrooms and toilet room exhausts.

3.	Smoke dampers are not required at [penetration] penetrations of exhaust or supply shafts in parking garages that are separated from other building shafts by not less than 2-hour fire-resistance-rated construction.

4.	Smoke dampers are not required at penetrations of shafts where ducts are used as part of an engineered mechanical smoke control system designed in accordance with Section 909 and where the smoke damper will interfere with the operation of the smoke control system.

5.	Fire dampers and/or smoke dampers are not required at a shaft where the shaft is acting as an extension of the mechanical equipment room that it serves and the shaft and mechanical equipment room maintain fire and smoke separation required by the greater of the two spaces from the occupied portions of the building and meet the requirements of Sections [708.11] 713.11 and [708.12] 713.12.

6.	Smoke dampers are not required to be located within a prescribed distance of a fire-rated enclosure within which the air handling equipment is located and where isolation smoke dampers are used in air-handling equipment in accordance with Section 607.2.3 of the New York City Mechanical Code.

7.	Smoke dampers are not required in ducts where the air continues to move and the air-handling system installed is arranged to prevent recirculation of exhaust or return air during a fire emergency condition. Such fans shall be provided with standby power in accordance with Chapter 27.

[8.	Smoke dampers are not required in exhaust ducts or shafts where the exhaust fan is maintained in operation during occupancy, such as in bathroom and toilet room exhausts.]

[716.5.3.1] 717.5.3.1 Limitations. Shafts that constitute air ducts shall be limited in accordance with Section 607.5.5.2 of the New York City Mechanical Code.

[716.5.4] 717.5.4 Fire partitions. Ducts and air transfer openings that penetrate fire partitions shall be protected with listed fire dampers installed in accordance with their listing.

Exceptions: In occupancies other than Group H, fire dampers are not required where any of the following apply:

1.	The fire partitions are for tenant separation [and] or interior corridor walls in buildings equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1 or 903.3.1.2 and the duct is protected as a [through penetration] through-penetration in accordance with Section [713] 714.

2.	The fire partitions are for tenant partitions in covered mall buildings where the walls are not required by provisions elsewhere in the code to extend to the underside of the floor or roof sheathing, slab or deck above.

3.	The duct system is constructed of approved materials in accordance with the New York City Mechanical Code and the duct penetrating the wall complies with all of the following requirements:

3.1.	The duct shall not exceed 100 square inches [(0.06 m2)] (64 516 mm2).

3.2.	The duct shall be constructed of steel [a minimum of] not less than 0.0217 inch (0.55 mm) in thickness.

3.3.	The duct shall not have openings that communicate the corridor with adjacent spaces or rooms.

3.4.	The duct shall be installed above a ceiling.

3.5.	The duct shall not terminate at a wall register in the fire-resistance-rated wall.

3.6.	A minimum 12-inch-long (305 mm) by 0.060-inch-thick (1.52 mm) steel sleeve shall be centered in each duct opening. The sleeve shall be secured to both sides of the wall and all four sides of the sleeve with minimum 11/2-inch by 11/2-inch by 0.060-inch (38 mm by 38 mm by 1.52 mm) steel retaining angles. The retaining angles shall be secured to the sleeve and the wall with No. 10 (M5) screws. The annular space between the steel sleeve and the wall opening shall be filled with mineral wool batting or approved equivalent on all sides.

4.	Such walls are penetrated by ducted HVAC systems, have a required fire-resistance rating of 1 hour or less, and are in buildings equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1 or 903.3.1.2. For the purposes of this exception, a ducted HVAC system shall be a duct system for conveying supply, return or exhaust air as part of the structure’s HVAC system. Such a duct system shall be constructed of sheet steel not less than No. 26 gage thickness and shall be continuous from the air-handling appliance or equipment to the air outlet and inlet terminals.

[716.5.5] 717.5.5 Smoke barriers. A listed smoke damper designed to resist the passage of smoke shall be provided at each point a duct or air transfer opening penetrates a smoke barrier. Smoke dampers and smoke damper actuation methods shall comply with Section [716.3.3.2] 717.3.3.2.

Exceptions:

1.	Smoke dampers are not required where the openings in ducts are limited to a single smoke compartment and the ducts are constructed of steel.

2.	Smoke dampers are not required in ducts where the air continues to move and the air-handling system installed is arranged to prevent recirculation of exhaust or return air under fire emergency conditions.

3.	Smoke dampers are not required in smoke barriers required by Section 407.5 for Group I-2, Condition 2 where the HVAC system is fully ducted in accordance with Section 603 of the New York City Mechanical Code and where buildings are equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1 and equipped with quick-response sprinklers in accordance with Section 903.3.2.

[716.5.6] 717.5.6 Exterior walls. Ducts and air transfer openings in fire-resistance-rated exterior walls required to have protected openings in accordance with Section 705.10 shall be protected with listed fire dampers installed in accordance with their listing.

[716.5.7] 717.5.7 Smoke partitions. A listed smoke damper designed to resist the passage of smoke shall be provided at each point that an air transfer opening penetrates a smoke partition. Smoke dampers and smoke damper actuation methods shall comply with Section [716.3.3.2] 717.3.3.2.

[Exceptions: 1.] Exception:

Where the installation of a smoke damper will interfere with the operation of a required smoke control system in accordance with Section 909, approved alternative protection shall be utilized.

[2.	Smoke dampers shall not be required in ducts where the air continues to move and the air-handling system installed is arranged to prevent recirculation of exhaust or return air under fire emergency conditions.]

[716.6] 717.6 Horizontal assemblies. Penetrations by ducts and air transfer openings of a floor, floor/ceiling assembly or the ceiling membrane of a roof/ceiling assembly shall be protected by a shaft enclosure that complies with Section [708] 713 or shall comply with Sections [716.6.1] 717.6.1 through [716.6.3] 717.6.3.

[716.6.1 Through penetrations.] 717.6.1 Through-penetrations. In occupancies other than Groups I-2 and I-3, a duct and air transfer opening system constructed of approved materials in accordance with the New York City Mechanical Code that penetrates a fire-resistance-rated floor/ceiling assembly that connects not more than two stories is permitted without shaft enclosure protection, provided a listed fire damper is installed at the floor line [and the penetration is fireblocked in accordance with Section 717.2.5] or the duct is protected in accordance with Section [713.4] 714.4. For air transfer openings, see [Exception 7 to] Section [708.2] 712.1.9.

Exception: A duct serving a dwelling unit is permitted to penetrate three floors or less without a fire damper at each floor, provided such duct meets all of the following requirements:

1.	The duct shall be contained and located within the cavity of a wall and shall be constructed of steel having a minimum wall thickness of [0.187 inches (0.4712 mm)] 0.0187 inches (0.4749 mm) (No. 26 gage).

2.	The duct shall open into only one dwelling or sleeping unit and the duct system shall be continuous from the unit to the exterior of the building.

3.	The duct shall not exceed 5-inch (127 mm) nominal diameter and the total area of such ducts shall not exceed 100 square inches (0.065 m2) in any 100 square feet (9.3 m2) of floor area.

4.	The annular space around the duct is protected with materials that prevent the passage of flame and hot gases sufficient to ignite cotton waste where subjected to ASTM E 119 or UL 263 time-temperature conditions under a minimum positive pressure differential of 0.01 inch (2.49 Pa) of water at the location of the penetration for the time period equivalent to the fire-resistance rating of the construction penetrated.

5.	Grille openings located in a ceiling of a fire-resistance-rated floor/ceiling or roof/ceiling assembly shall be protected with a listed ceiling radiation damper installed in accordance with Section [716.6.2] 717.6.2.1.

[716.6.2] 717.6.2 Membrane penetrations. Ducts and air transfer openings constructed of approved materials in accordance with the New York City Mechanical Code that penetrate the ceiling membrane of a fire-resistance-rated floor/ceiling assembly or roof/ceiling assembly shall be protected with one of the following:

1.	A shaft enclosure in accordance with Section [708] 713.

2.	A listed ceiling radiation damper and firestopping is installed at the ceiling line where a duct penetrates the ceiling of a fire-resistance-rated floor/ceiling assembly or roof/ceiling assembly.

3.	A listed ceiling radiation damper and firestopping is installed at the ceiling line where a diffuser with no duct attached penetrates the ceiling of a fire-resistance-rated floor/ceiling assembly or roof/ceiling assembly.

[716.6.2.1] 717.6.2.1 Ceiling radiation dampers. Ceiling radiation dampers shall be tested [as part of a fire-resistance-rated floor/ceiling or roof/ceiling assembly] in accordance with [ASTM E 119 or UL 263] Section 717.3.1. Ceiling radiation dampers shall be installed in accordance with the details listed in [a] the fire-resistance-rated assembly and the manufacturer’s [installation] instructions and the listing. Ceiling radiation dampers are not required where [either] one of the following applies:

1.	Tests in accordance with ASTM E 119 or UL 263 have shown that ceiling radiation dampers are not necessary in order to maintain the fire-resistance rating of the assembly.

2.	Where exhaust duct penetrations are protected in accordance with Section [713.4.1.2] 714.4.2, are located within the cavity of a wall and do not pass through another dwelling unit or tenant space.

3.	Where duct and air transfer openings are protected with a duct outlet protection system tested as part of a fire-resistance-rated assembly in accordance with ASTM E 119 or UL 263.

[716.6.3] 717.6.3 Nonfire-resistance-rated floor assemblies. Duct systems constructed of approved materials in accordance with the New York City Mechanical Code that penetrate nonfire-resistance-rated floor assemblies shall be protected by any of the following methods:

1.	A shaft enclosure in accordance with Section [708] 713.

2.	The duct connects not more than two stories, and the annular space around the penetrating duct is protected with [an approved] a listed noncombustible material that resists the free passage of flame and the products of combustion.

3.	[The] In floor assemblies composed of noncombustible materials, a shaft shall not be required where the duct connects not more than three stories [and], the annular space around the penetrating duct is protected with an approved noncombustible material that resists the free passage of flame and the products of combustion[,] and a fire damper is installed at each floor line.

Exception: Fire dampers are not required in ducts within individual residential dwelling units.

[716.7] 717.7 Flexible ducts and air connectors. Flexible ducts and air connectors shall not pass through any fire-resistance-rated assembly. Flexible air connectors shall not pass through any wall, floor or ceiling.

SECTION BC [717] 718
CONCEALED SPACES

[717.1] 718.1 General. Fireblocking and draftstopping shall be installed in combustible and noncombustible concealed locations in accordance with this section. Fireblocking shall comply with Section [717.2] 718.2. Draftstopping in floor/ceiling spaces and attic spaces shall comply with Sections [717.3] 718.3 and [717.4] 718.4, respectively. The permitted use of combustible materials in concealed spaces of buildings of Type I or II construction shall be limited to the applications indicated in Section [717.5] 718.5. Installations of fireblocking and draftstopping shall comply with the special inspection requirements of Chapter 17.

Exception: Concealed spaces that are sprinklered in accordance with Chapter 9 or are constructed as a shaft.

[717.2] 718.2 Fireblocking. In combustible and noncombustible construction, fireblocking shall be installed to cut off concealed draft openings (both vertical and horizontal) and shall form an effective barrier between floors, between a top story and a roof or attic space. Fireblocking shall be installed in the locations specified in Sections [717.2.2] 718.2.2 through [717.2.7] 718.2.7.

[717.2.1] 718.2.1 Fireblocking materials. Fireblocking shall consist of the following materials:

1.	Two-inch (51 mm) nominal lumber.

2.	Two thicknesses of 1-inch (25 mm) nominal lumber with broken lap joints.

3.	One thickness of 0.719-inch (18.3 mm) wood structural panels with joints backed by 0.719-inch (18.3 mm) wood structural panels.

4.	One thickness of 0.75-inch [(19 mm)] (19.1 mm) particleboard with joints backed by 0.75-inch [(19 mm)] (19.1 mm) particleboard.

5.	One-half-inch (12.7 mm) gypsum board.

6.	One-fourth-inch (6.4 mm) cement–based millboard.

7.	Batts or blankets of mineral wool[,] and mineral fiber [or other approved materials] installed in such a manner as to be securely retained in place.

8.	Other materials approved by the commissioner.

[717.2.1.1] 718.2.1.1 Batts or blankets of mineral wool or mineral fiber. Batts or blankets of mineral or glass fiber or other [approved] listed nonrigid materials shall be permitted for compliance with the 10-foot (3048 mm) horizontal fireblocking in walls constructed using parallel rows of studs or staggered studs.

[717.2.1.2] 718.2.1.2 Unfaced fiberglass. Unfaced fiberglass batt insulation used as fireblocking shall fill the entire cross section of the wall cavity to a minimum height of 16 inches (406 mm) measured vertically. [When] Where piping, conduit or similar obstructions are encountered, the insulation shall be packed tightly around the obstruction.

[717.2.1.3] 718.2.1.3 Loose-fill insulation material. Loose-fill insulation material, insulating foam sealants and caulk materials shall not be used as a [fire block] fireblock unless specifically tested in the form and manner intended for use to demonstrate its ability to remain in place and to retard the spread of fire and hot gases.

[717.2.1.4] 718.2.1.4 Fireblocking integrity. The integrity of [fire blocks] fireblocks shall be maintained.

[717.2.1.5] 718.2.1.5 Double stud walls. Batts or blankets of mineral or glass fiber or other approved nonrigid materials shall be allowed as fireblocking in walls constructed using parallel rows of studs or staggered studs.

[717.2.2] 718.2.2 Concealed wall spaces. Fireblocking shall be provided in concealed spaces of stud walls and partitions, including furred spaces, and parallel rows of studs or staggered studs, as follows:

1.	Vertically at the ceiling and floor levels.

2.	Horizontally at intervals not exceeding 10 feet (3048 mm).

[717.2.3] 718.2.3 Connections between horizontal and vertical spaces. Fireblocking shall be provided at interconnections between concealed vertical stud wall or partition spaces and concealed horizontal spaces created by an assembly of floor joists or trusses, and between concealed vertical and horizontal spaces such as occur at soffits, drop ceilings, cove ceilings and similar locations.

[717.2.4] 718.2.4 Stairways. Fireblocking shall be provided in concealed spaces between stair stringers at the top and bottom of the run. Enclosed spaces under [stairs] stairways shall also comply with Section [1009.6.3] 1011.7.3.

[717.2.5] 718.2.5 Ceiling and floor openings. Where required by [Exception 6 of] Section [708.2] 712.1.8, Exception 1 of Section [713.4.1.2,] 714.4.2 or Section [713.4.2] 714.5, fireblocking of the annular space around vents, pipes, ducts, chimneys and fireplaces at ceilings and floor levels shall be installed with a material specifically tested in the form and manner intended for use to demonstrate its ability to remain in place and resist the free passage of flame and the products of combustion.

[717.2.5.1] 718.2.5.1 Factory-built chimneys and fireplaces. Factory-built chimneys and fireplaces shall be [fire blocked] fireblocked in accordance with UL 103 and UL 127.

[717.2.6] 718.2.6 Architectural trim. Fireblocking shall be installed within concealed spaces of exterior wall [finish] coverings and other exterior architectural elements where permitted to be of combustible construction as specified in Section 1406 or where erected with combustible frames, at maximum intervals of 20 feet (6096 mm) so that there will be no open space exceeding 100 square feet (9.3 m2). Where wood furring strips are used, they shall be of approved wood of natural decay resistance or preservative-treated wood. If non-continuous, such elements shall have closed ends, with at least 4 inches (102 mm) of separation between sections.

Exceptions:

1.	Fireblocking of cornices is not required in single-family dwellings. Fireblocking of cornices of a two-family dwelling is required only at the line of dwelling unit separation.

2.	Fireblocking shall not be required where the exterior wall covering does not contain plastic or foam plastic insulation, is installed on noncombustible framing and the [face of the exposed to the concealed space is covered by] exterior wall covering is one of the following materials:

2.1.	Aluminum siding having a minimum thickness of 0.019 inch (0.5 mm).

2.2.	Corrosion‐resistant steel [having a base metal thickness] siding not less than 0.016 inch (0.4 mm) at any point.

[2.3.	Other approved noncombustible materials.]

718.2.6.1 Exterior wall coverings containing plastics, MCM or HPL panels. Exterior wall coverings containing plastics complying with Chapter 26, metal composite materials (MCM) or high-pressure decorative exterior-grade compact laminates (HPL), shall be fireblocked.

718.2.6.1.1 Locations. Noncombustible fireblocking materials shall be required at all of the following locations to cut off concealed spaces within the exterior wall covering:

1.	Around wall openings.

2.	In alignment with the slab edge, for a height of not less than 8 inches (203 mm), and at maximum intervals of 20 feet (6096 mm) vertically.

3.	Between different occupancy groups, horizontally or vertically, as applicable.

718.2.6.1.2 Foam plastic insulation. Foam plastic insulation in the exterior wall covering shall be interrupted with noncombustible materials approved for fireblocking at locations specified in Section 718.2.6.1.1.

Exceptions:

1.	One-story buildings complying with Section 2603.4.1.4.

2.	Fireblocking shall not be required at each floor level and interrupt the foam plastic insulation provided the foam plastic insulation has a flame spread index of not more than 25 as determined in accordance with ASTM E 84 or UL 723 and comply with the following conditions:

2.1.	Concrete and masonry veneer. Fireblocking material shall not be required at each floor level for concrete or masonry veneer installed less than 75 feet (22 860 mm) above grade as part of an exterior wall covering containing foam plastic insulation, with or without air space, and installed on masonry or concrete backup walls.

2.2.	Exterior insulation and finish systems (EIFS). Fireblocking material shall not be required at each floor level for EIFS containing foam plastic insulation installed less than 75 feet (22 860 mm) above grade, and installed on masonry or concrete backup walls.

3.	Detached one- and two-family dwellings. Fireblocking of foam plastic insulation shall not be required at each floor level in detached one- and two-family dwellings of Type V construction that do not exceed three stories or 40 feet (12 190 mm) in height above grade plane.

[717.2.7] 718.2.7 Concealed sleeper spaces. Where wood sleepers are used for laying wood flooring on masonry or concrete fire-resistance-rated floors, the space between the floor slab and the underside of the wood flooring shall be filled with an approved material to resist the free passage of flame and products of combustion or [fire blocked] fireblocked in such a manner that there will be no open spaces under the flooring that will exceed 20 square feet (1.86 m2) in area and such space shall be filled solidly under permanent partitions so that there is no communication under the flooring between adjoining rooms.

Exceptions:

1.	Fireblocking is not required for slab-on-grade floors in gymnasiums.

2.	Fireblocking is required only at the juncture of each alternate lane and at the ends of each lane in a bowling facility.

[717.3] 718.3 Draftstopping in floors. In combustible and noncombustible construction, draftstopping shall be installed to subdivide floor/ceiling assemblies in the locations prescribed in Sections [717.3.2] 718.3.2 through [717.3.3] 718.3.3.

[717.3.1] 718.3.1 Draftstopping materials. In noncombustible construction, draftstopping shall be of noncombustible materials. In combustible construction, draftstopping materials shall be not [be] less than 1/2-inch (12.7 mm) gypsum board, 3/8-inch (9.5 mm) wood structural panel, 3/8-inch (9.5 mm) particleboard, 1-inch (25 mm) nominal lumber, cement fiberboard, batts or blankets of mineral wool or glass fiber, or other approved materials adequately supported. The integrity of [draft stops] draftstops shall be maintained.

[717.3.2] 718.3.2 Group R. Draftstopping shall be provided in floor/ceiling spaces in Group R buildings. Draftstopping shall be located above and in line with the dwelling unit separations.

Exceptions:

1.	Draftstopping is not required in buildings equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1.

2.	Draftstopping is not required in buildings equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.2, provided that automatic sprinklers are [also] installed in the combustible concealed spaces where the draftstopping is being omitted.

3.	Where laminated wood I-joist assemblies are used, the space between the ceiling and the floor or roof above shall be divided into approximately equal areas not greater than 500 square feet (46.5 m2).

4.	Draftstopping shall not be required where the structural members within the concealed ceiling space are individually protected on all sides for their full length with materials having the required fire-resistance rating.

[717.3.3] 718.3.3 Other groups. In occupancies other than Group R, [draft stopping] draftstopping shall be installed so that horizontal floor areas do not exceed 3,000 square feet (279 m2).

Exceptions:

1.	Draftstopping is not required in buildings equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1.

2.	Draftstopping shall not be required where the structural members within the concealed ceiling space are individually protected on all sides for their full length with materials having the required fire-resistance rating.

[717.4] 718.4 Draftstopping in attics. In combustible and noncombustible construction, draftstopping shall be installed to subdivide attic spaces and concealed roof spaces in the locations prescribed in Sections [717.4.2] 718.4.2 and [717.4.3] 718.4.3. Ventilation of concealed roof spaces shall be maintained in accordance with Section 1203.2.

[717.4.1] 718.4.1 Draftstopping materials. Materials utilized for draftstopping of attic spaces shall comply with Section [717.3.1] 718.3.1.

[717.4.1.1] 718.4.1.1 Openings. Openings in draftstop partitions provided in accordance with Section 1209.2 shall be protected by self-closing doors with automatic latches constructed as required for the partitions.

[717.4.2] 718.4.2 Groups R-1 and R-2. Draftstopping shall be provided in attics, mansards, overhangs or other concealed roof spaces of Group R-2 buildings with three or more dwelling units and in all Group R-1 buildings. Draftstopping shall be installed above, and in line with dwelling unit separation walls that do not extend to the underside of the roof sheathing above.

Exceptions:

1.	Draftstopping shall not be required where the structural members within the concealed attic space are individually protected on all sides for their full length with materials having the required fire-resistance rating.

2.	Draftstopping is not required in buildings equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1.

3.	In occupancies in Group R-2 that do not exceed four stories above grade plane, the attic space shall be subdivided by [draft stops] draftstops into areas not exceeding 3,000 square feet (279 m2) or above every two dwelling units, whichever is smaller.

4.	Draftstopping is not required in buildings equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.2, provided that automatic sprinklers are [also] installed in the combustible concealed [spaces] space where the draftstopping is being omitted.

5.	Where laminated wood I-joist assemblies are used, the space between the ceiling and the floor or roof above shall be divided into approximately equal areas not greater than 500 square feet (46.5 m2).

[717.4.3] 718.4.3 Other groups. Draftstopping shall be installed in attics and concealed roof spaces, such that any horizontal area does not exceed 3,000 square feet (279 m2).

Exceptions:

- Draftstopping is not required in buildings equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1.

- Draftstopping shall not be required where the structural members within the concealed attic space are individually protected on all sides for their full length with materials having the required fire-resistance rating.

3.	Where laminated wood I-joist assemblies are used, the space between the ceiling and the floor or roof above shall be divided into approximately equal areas not greater than 500 square feet (46.5 m2).

[717.5] 718.5 Combustible materials in concealed spaces in Type I or II construction. Combustible materials shall not be permitted in concealed spaces of buildings of Type I or II construction.

Exceptions:

1.	Combustible materials in accordance with Section 603.

2.	Combustible materials exposed [with] within plenums complying with Section 602 of the New York City Mechanical Code.

3.	Class A interior finish materials classified in accordance with Section 803.

4.	Combustible piping within partitions or shaft enclosures installed in accordance with the provisions of this code.

5.	Combustible piping within concealed ceiling spaces installed in accordance with the New York City Mechanical Code and the New York City Plumbing Code.

6.	Combustible insulation and covering on pipe and tubing, installed in concealed spaces other than plenums, complying with Section [719.7] 720.7.

SECTION BC [718] 719
FIRE-RESISTANCE REQUIREMENTS FOR PLASTER

[718.1] 719.1 Thickness of plaster. The minimum thickness of gypsum plaster or portland cement plaster used in a fire-resistance-rated system shall be determined by the prescribed fire tests. The plaster thickness shall be measured from the face of the lath where applied to gypsum lath or metal lath.

[718.2] 719.2 Plaster equivalents. For fire-resistance purposes, 1/2 inch (12.7 mm) of unsanded gypsum plaster shall be deemed equivalent to 3/4 inch (19.1 mm) of one-to-three gypsum sand plaster or 1 inch (25 mm) of portland cement sand plaster.

[718.3] 719.3 Noncombustible furring. In buildings of Type I and II construction, plaster shall be applied directly on concrete or masonry or on approved noncombustible plastering base and furring.

[718.4] 719.4 Double reinforcement. Plaster protection more than 1 inch (25 mm) in thickness shall be reinforced with an additional layer of approved lath embedded [at least] not less than 3/4 inch (19.1 mm) from the outer surface and fixed securely in place.

Exception: Solid plaster partitions or where otherwise determined by fire tests.

[718.5] 719.5 Plaster alternatives for concrete. In reinforced concrete construction, gypsum plaster or portland cement plaster is permitted to be substituted for 1/2 inch (12.7 mm) of the required poured concrete protection, except that a minimum thickness of 3/8 inch (9.5 mm) of poured concrete shall be provided in reinforced concrete floors and 1 inch (25 mm) in reinforced concrete columns in addition to the plaster finish. The concrete base shall be prepared in accordance with Section 2510.7.

SECTION BC [719] 720
THERMAL- AND SOUND-INSULATING MATERIALS

[719.1] 720.1 General. Insulating materials, including facings such as vapor retarders and vapor-permeable membranes, similar coverings, and all layers of single and multilayer reflective foil insulations, shall comply with the requirements of this section. Where a flame spread index or a smoke-development index is specified in this section, such index shall be determined in accordance with ASTM E 84 or UL 723. Any material that is subject to an increase in flame spread index or smoke-development index beyond the limits herein established through the effects of age, moisture[,] or other atmospheric conditions shall not be permitted.

Exceptions:

1.	Fiberboard insulation shall comply with Chapter 23.

2.	Foam plastic insulation shall comply with Chapter 26.

3.	Duct and pipe insulation and duct and pipe coverings and linings in plenums shall comply with the New York City Mechanical Code.

4.	Exterior insulation finish systems (EIFS) shall comply with Chapters 14 and 26.

[719.1.1] 720.1.1 Noncombustible construction. Insulating materials used in noncombustible construction must either:

1.	Satisfactorily pass a test for determining noncombustibility of elementary materials, based on the test procedures of ASTM E 136; or

2.	Have a flame spread index not greater than 25, a smoke-development index not greater than 50, and be without evidence of continued progressive combustion when tested in accordance with ASTM E 84.

[719.1.2] 720.1.2 Combustible construction. Insulating materials used in combustible construction shall have a flame spread index not greater than 25, a smoke-development index not greater than 450, and be without evidence of continuous progressive combustion when tested in accordance with ASTM E 84.

[719.2] 720.2 Concealed installation. Insulating materials, where concealed as installed in buildings of any type construction, shall comply with Sections [719.1.1] 720.1.1, [719.1] 720.1 and [719.1.2] 720.1.2. Concealed insulation shall be separated from the building interior by a thermal barrier consisting of at least 1/2-inch-thick (12.7 mm) gypsum wallboard or approved equivalent.

Exception: [Cellulose] Cellulosic fiber loose-fill insulation [that is not spray applied,] complying with the requirements of Section [719.6,] 720.6 shall only be required to meet [the] a smoke-development index of not more than 450, when tested in accordance with CAN/ULC S102.2, provided such insulation has a smoke-development index that complies with the requirements of Section 720.2 or 720.3, as applicable, and Section 720.6 of this code.

[719.2.1] 720.2.1 Facings. Where such materials are installed in concealed spaces in buildings of Type III, IV or V construction, the flame spread and smoke-development limits do not apply to facings, coverings, and layers of reflective foil insulation that are installed behind and in substantial contact with the unexposed surface of the ceiling, wall or floor finish.

Exception: All layers of single and multilayer reflective plastic core insulation shall comply with Section [2613] 2614.

[719.3] 720.3 Exposed installation. Insulation materials, where exposed as installed in buildings of any type of construction, shall have a flame spread index of not more than 25 and a smoke-development index of not more than 50.

Exception: [Cellulose] Cellulosic fiber loose-fill insulation [that is not spray applied] complying with the requirements of Section [719.6] 720.6 shall [only] not be required to meet [the] a flame spread index requirement but shall be required to meet a smoke-development index of not more than 50 when tested in accordance with CAN/ULC S102.2.

[719.3.1] 720.3.1 Attic floors. Exposed insulation materials installed on attic floors shall have a critical radiant flux of not less than 0.12 watt per square centimeter when tested in accordance with ASTM E 970.

[719.3.2 Toxicity. Upon exposure to fire, insulating materials used in building interiors, including facings, such as vapor retarders and vapor-permeable membranes, similar coverings, and all layers of single and multilayer reflective foil insulation, shall not produce products of decomposition or combustion that are more toxic in point of concentration than those given off by wood or paper when decomposing or burning under comparable conditions in accordance with test standards approved by the department.]

[719.4] 720.4 Loose-fill insulation. Loose-fill insulation materials that cannot be mounted in the ASTM E 84 apparatus without a screen or artificial supports shall comply with the flame spread and smoke-developed limits of Sections [719.2] 720.2 and [719.3] 720.3 when tested in accordance with CAN/ULC S102.2.

Exception: [Cellulose] Cellulosic fiber loose-fill insulation shall not be required to [be] meet a flame spread index requirement when tested in accordance with CAN/ULC S102.2, provided such insulation has a smoke-development index that complies with the requirements of Section [719.2] 720.2 or [719.3] 720.3, as applicable, and Section [719.6] 720.6.

[719.5] 720.5 Roof insulation. The use of combustible roof insulation not complying with Sections [719.2] 720.2 and [719.3] 720.3 shall be permitted in any type of construction provided it is applied on top of roof decking or slab and that such insulation is covered with approved roof coverings directly applied thereto.

[719.6 Cellulose] 720.6 Cellulosic fiber loose-fill insulation and self-supported spray-applied cellulosic insulation. [Cellulose] Cellulosic fiber loose-fill insulation and self-supported spray-applied cellulosic insulation shall comply with CPSC 16 CFR[, Part] Parts 1209 and [CPSC 16 CFR, Part] 1404. Each package of such insulating material shall be clearly labeled in accordance with CPSC 16 CFR[, Part] 1209 and [CPSC 16 CFR, Part] 1404.

[719.7] 720.7 Insulation and covering on pipe and tubing. Insulation and covering on pipe and tubing shall comply with the requirements of the New York City Mechanical Code, the New York City Plumbing Code, and the New York City Energy Conservation Code.

SECTION BC [720] 721
PRESCRIPTIVE FIRE RESISTANCE

[720.1] 721.1 General. The provisions of this section contain prescriptive details of fire-resistance-rated building elements, components or assemblies. The materials of construction listed in Tables [720.1(1)] 721.1(1), [720.1(2)] 721.1(2), and [720.1(3)] 721.1(3) shall be assumed to have the fire-resistance ratings prescribed therein. Where materials that change the capacity for heat dissipation are incorporated into a fire-resistance-rated assembly, fire test results or other substantiating data shall be made available to the commissioner to show that the required fire-resistance-rating time period is not reduced.

| TABLE [720.1(1)] 721.1(1) MINIMUM PROTECTION OF STRUCTURAL PARTS BASED ON TIME PERIODS FOR VARIOUS NONCOMBUSTIBLE INSULATING MATERIALSm |
| --- |
| STRUCTURAL PARTS TO BE PROTECTED | ITEM NUMBER | INSULATING MATERIAL USED | MINIMUM THICKNESS OF INSULATING MATERIAL FOR THE FOLLOWING FIRE-RESISTANCE PERIODS (inches) |
|  |  |  | 4 [hour] hours | 3 [hour] hours | 2 [hour] hours | 1 hour |
| 1. Steel columns and all of primary trusses | 1-1.1 | Carbonate, lightweight and sand-lightweight aggregate concrete, members 6″ × 6″ or greater (not including sandstone, granite and siliceous gravel).a | 21/2 | 2 | 11/2 | 1 |
|  | 1-1.2 | Carbonate, lightweight and sand-lightweight aggregate concrete, members 8″ × 8″ or greater (not including sandstone, granite and siliceous gravel).a | 2 | 11/2 | 1 | 1 |
|  | 1-1.3 | Carbonate, lightweight and sand-lightweight aggregate concrete, members 12″ × 12″ or greater (not including sandstone, granite and siliceous gravel).a | 11/2 | 1 | 1 | 1 |
|  | 1-1.4 | Siliceous aggregate concrete and concrete excluded in Item 1-1.1, members 6″ × 6″ or greater.a | 3 | 2 | 11/2 | 1 |
|  | 1-1.5 | Siliceous aggregate concrete and concrete excluded in Item 1-1.1, members 8″ × 8″ or greater.a | 21/2 | 2 | 1 | 1 |
|  | 1-1.6 | Siliceous aggregate concrete and concrete excluded in Item 1-1.1, members 12″ × 12″ or greater.a | 2 | 1 | 1 | 1 |
| 1. Steel columns and all of primary trusses | 1-2.1 | Clay or shale brick with brick and mortar fill.a | 33/4 | — | — | 21/4 |
| 1. Steel columns and all of primary trusses | 1-3.1 | 4″ hollow clay tile in two 2″ layers; 1/2″ mortar between tile and column; 3/8″ metal mesh 0.046″ wire diameter in horizontal joints; tile fill.a | 4 | — | — | — |
|  | 1-3.2 | 2″ hollow clay tile; 3/4″ mortar between tile and column; 3/8″ metal mesh 0.046″ wire diameter in horizontal joints; limestone concrete fill;a plastered with 3/4″ gypsum plaster. | 3 | — | — | — |
|  | 1-3.3 | 2″ hollow clay tile with outside wire ties 0.08″ diameter at each course of tile or 3/8″ metal mesh 0.046″ diameter wire in horizontal joints; limestone or trap-rock concrete filla extending 1″ outside column on all sides. | — | — | 3 | — |
|  | 1-3.4 | 2″ hollow clay tile with outside wire ties 0.08″ diameter at each course of tile with or without concrete fill; 3/4″ mortar between tile and column. | — | — | — | 2 |
| 1. Steel columns and all of primary trusses | 1-4.1 | Cement plaster over metal lath wire tied to 3/4″ cold-rolled vertical channels with 0.049″ (Νο. 18 Β.W. gage) wire ties spaced 3″ to 6″ on center. Plaster mixed 1:2 1/2 by volume, cement to sand. | — | — | 21/2b | 7/8 |
| 1. Steel columns and all of primary trusses | 1-5.1 | Vermiculite concrete, 1:4 mix by volume over paperbacked wire fabric lath wrapped directly around column with additional 2″ × 2″ 0.065″/0.065″ (No. 16/16 B.W. gage) wire fabric placed 3/4″ from outer concrete surface. Wire fabric tied with 0.049″ (No. 18 B.W. gage) wire spaced 6″ on center for inner layer and 2″ on center for outer layer. | 2 | — | — | — |
| 1. Steel columns and all of primary trusses | 1-6.1 | Perlite or vermiculite gypsum plaster over metal lath wrapped around column and furred 11/4″ from column flanges. Sheets lapped at ends and tied at 6″ intervals with 0.049″ (No. 18 B.W. gage) tie wire. Plaster pushed through to flanges. | 11/2 | 1 | — | — |
|  | 1-6.2 | Perlite or vermiculite gypsum plaster over self-furring metal lath wrapped directly around column, lapped 1″ and tied at 6″ intervals with 0.049″ (No. 18 B.W. gage) wire. | 13/4 | 13/8 | 1 | — |
|  | 1-6.3 | Perlite or vermiculite gypsum plaster on metal lath applied to 3/4″ cold-rolled channels spaced 24″ apart vertically and wrapped flatwise around column. | 11/2 | — | — | — |
|  | 1-6.4 | Perlite or vermiculite gypsum plaster over two layers of 1/2″ plain full-length gypsum lath applied tight to column flanges. Lath wrapped with 1″ hexagonal mesh of No. 20 gage wire and tied with doubled 0.035″ diameter (No. 18 B.W. gage) wire ties spaced 23″ on center. For three-coat work, the plaster mix for the second coat shall not exceed 100 pounds of gypsum to 21/2 cubic feet of aggregate for the 3-hour system. | 21/2 | 2 | — | — |
|  | 1-6.5 | Perlite or [vermiculate] vermiculite gypsum plaster over one layer of 1/2″ plain full-length gypsum lath applied tight to column flanges. Lath tied with doubled 0.049″ (No. 18 B.W. gage) wire ties spaced 23″ on center and scratch coat wrapped with 1″ hexagonal mesh 0.035″ (No. 20 B.W. gage) wire fabric. For three-coat work, the plaster mix for the second coat shall not exceed 100 pounds of gypsum to 21/2 cubic feet of aggregate. | — | 2 | — | — |
| 1. Steel columns and all of primary trusses | 1-7.1 | Multiple layers of 1/2″ gypsum wallboardc adhesivelyd secured to column flanges and successive layers. Wallboard applied without horizontal joints. Corner edges of each layer staggered. Wallboard layer below outer layer secured to column with doubled 0.049″ (No. 18 B.W. gage) steel wire ties spaced 15″ on center. Exposed corners taped and treated. | — | — | 2 | 1 |
|  | 1-7.2 | Three layers of 5/8″ Type X gypsum wallboard.c First and second layer held in place by 1/8″ diameter by 13/8″ long ring shank nails with 5/16 ″ diameter heads spaced 24″ on center at corners. Middle layer also secured with metal straps at mid-height and 18″ from each end, and by metal corner bead at each corner held by the metal straps. Third layer attached to corner bead with 1″ long gypsum wallboard screws spaced 12″ on center. | — | — | 17/8 | — |
|  | 1-7.3 | Three layers of 5/8″ Type X gypsum wallboard,c each layer screw attached to 15/8″ steel studs 0.018″ thick (No. 25 carbon sheet steel gage) at each corner of column. Middle layer also secured with 0.049″ (No. 18 B.W. gage) double-strand steel wire ties, 24″ on center. Screws are No. 6 by 1″ spaced 24″ on center for inner layer, No. 6 by 15/8″ spaced 12″on center for middle layer and No. 8 by 21/4″ spaced 12″ on center for outer layer. | — | 17/8 | — | — |
| 1. Steel columns and all of primary trusses | 1-8.1 | Wood-fibered gypsum plaster mixed 1:1 by weight gypsum-to-sand aggregate applied over metal lath. Lath lapped 1″ and tied 6″ on center at all end, edges and spacers with 0.049″ (No. 18 B.W. gage) steel tie wires. Lath applied over 1/2″ spacers made of 3/4″ furring channel with 2″ legs bent around each corner. Spacers located 1″ from top and bottom of member and a maximum of 40″ on center and wire tied with a single strand of 0.049″ (No. 18 B.W. gage) steel tie wires. Corner bead tied to the lath at 6″ on center along each corner to provide plaster thickness. | — | — | 15/8 | — |
| 1. Steel columns and all of primary trusses | 1-9.1 | Minimum W 8×35 wide flange steel column (w/d > 0.75) with each web cavity filled even with the flange tip with normal weight carbonate or siliceous aggregate concrete (3,000 psi minimum compressive strength with 145 pcf ± 3 pcf unit weight). Reinforce the concrete in each web cavity with a minimum No. 4 deformed reinforcing bar installed vertically and centered in the cavity, and secured to the column web with a minimum No. 2 horizontal deformed reinforcing bar welded to the web every 18″ on center vertically. As an alternative to the No. 4 rebar, ¾″ diameter by 3″ long headed studs, spaced at 12″ on center vertically, shall be welded on each side of the web midway between the column flanges. | — | — | — | See Note n |
| 2. Webs or flanges of steel beams and girders | 2-1.1 | Carbonate, lightweight and sand-lightweight aggregate concrete (not including sandstone, granite and siliceous gravel) with 3″ or finer metal mesh placed 1″ from the finished surface anchored to the top flange and providing not less than 0.025 square inch of steel area per foot in each direction. | 2 | 11/2 | 1 | 1 |
| 2. Webs or flanges of steel beams and girders | 2-1.2 | Siliceous aggregate concrete and concrete excluded in Item 2-1.1 with 3″ or finer metal mesh placed 1″ from the finished surface anchored to the top flange and providing not less than 0.025 square inch of steel area per foot in each direction. | 21/2 | 2 | 11/2 | 1 |
| 2. Webs or flanges of steel beams and girders | 2-2.1 | Cement plaster on metal lath attached to 3/4″ cold-rolled channels with [0.049] 0.04″ (No. 18 B.W. gage) wire ties spaced 3″ to 6″ on center. Plaster mixed 1:21/2 by volume, cement to sand. | — | — | 21/2b | 7/8 |
| 2. Webs or flanges of steel beams and girders | 2-3.1 | Vermiculite gypsum plaster on a metal lath cage, wire tied to 0.165″ diameter (No. 8 B.W. gage) steel wire hangers wrapped around beam and spaced 16″ on center. Metal lath ties spaced approximately 5″ on center at cage sides and bottom. | — | 7/8 | — | — |
| 2. Webs or flanges of steel beams and girders | 2-4.1 | Two layers of 5/8″ Type X gypsum wallboardc are attached to U-shaped brackets spaced 24″ on center. 0.018″ thick (No. 25 carbon sheet steel gage) 15/8″ deep by 1″ galvanized steel runner channels are first installed parallel to and on each side of the top beam flange to provide a 1/2″ clearance to the flange. The channel runners are attached to steel deck or concrete floor construction with approved fasteners spaced 12″ on center. U-shaped brackets are formed from members identical to the channel runners. At the bent portion of the U-shaped bracket, the flanges of the channel are cut out so that 15/8″ deep corner channels can be inserted without attachment parallel to each side of the lower flange. As an [alternate] alternative, 0.021″ thick (No. 24 carbon sheet steel gage) 1’ × 2″ runner and corner angles [may] shall be used in lieu of channels, and the web cutouts in the U-shaped brackets [may] shall not be [omitted] required. Each angle is attached to the bracket with 1/2″-long No. 8 self-drilling screws. The vertical legs of the U-shaped bracket are attached to the runners with one 1/2″ long No. 8 self-drilling screw. The completed steel framing provides a 21/8″ and 11/2″ space between the inner layer of wallboard and the sides and bottom of the steel beam, respectively. The inner layer of wallboard is attached to the top runners and bottom corner channels or corner angles with 11/4″-long No. 6 self-drilling screws spaced 16″ on center. The outer layer of wallboard is applied with 13/4″-long No. 6 self-drilling screws spaced 8″ on center. The bottom corners are reinforced with metal corner beads. | — | — | 11/4 | — |
| 2. Webs or flanges of steel beams and girders | 2-4.2 | Three layers of 5/8″ Type X gypsum wallboardc attached to a steel suspension system as described immediately above utilizing the 0.018″ thick (No. 25 carbon sheet steel gage) 1″ × 2″ lower corner angles. The framing is located so that a 21/8″ and 2″ space is provided between the inner layer of wallboard and the sides and bottom of the beam, respectively. The first two layers of wallboard are attached as described immediately above. A layer of 0.035″ thick (No. 20 B.W. gage) 1″ hexagonal galvanized wire mesh is applied under the soffit of the middle layer and up the sides approximately 2″. The mesh is held in position with the No. 6 15/8″-long screws installed in the vertical leg of the bottom corner angles. The outer layer of wallboard is attached with No. 6 21/4″-long screws spaced 8″ on center. One screw is also installed at the mid-depth of the bracket in each layer. Bottom corners are finished as described above. | — | 17/8 | — | — |
| 3. Bonded pretensioned reinforcement in prestressed concretee | 3-1.1 | Carbonate, lightweight, sand-lightweight and siliceousf aggregate concrete |  |  |  |  |
|  |  | Beams or girders | 4g | 3g | 21/2 | 11/2 |
|  |  | Solid slabsh |  | 2 | 11/2 | 1 |
| 4. Bonded or unbonded post-tensioned tendons in prestressed concretee, i | 4-1.1 | Carbonate, lightweight, sand-lightweight and siliceousf aggregate concrete Unrestrained members: |  |  |  |  |
|  |  | Solid slabsh | — | 2 | 11/2 | — |
|  |  | Beams and girdersj |  |  |  |  |
|  |  | 8″ wide |  | 41/2 | 21/2 | 13/4 |
|  |  | greater than 12″ wide | 3 | 21/2 | 2 | 11/2 |
| 4. Bonded or unbonded post-tensioned tendons in prestressed concretee, i | 4-1.2 | Carbonate, lightweight, sand-lightweight and siliceous aggregate Restrained members:k |  |  |  |  |
|  |  | Solid slabsh | 11/4 | 1 | 3/4 |  |
|  |  | Beams and girdersj |  |  |  |  |
|  |  | 8″ wide | 21/2 | 2 | 13/4 |  |
|  |  | greater than 12″ wide | 2 | 13/4 | 11/2 | — |
| 5. Reinforcing steel in reinforced concrete columns, beams girders and trusses | 5-1.1 | Carbonate, lightweight and sand-lightweight aggregate concrete, members 12″ or larger, square or round. (Size limit does not apply to beams and girders monolithic with floors.) | 11/2 | 11/2 | 11/2 | 11/2 |
|  |  | Siliceous aggregate concrete, members 12″ or larger, square or round. (Size limit does not apply to beams and girders monolithic with floors.) | 2 | 11/2 | 11/2 | 11/2 |
| 6. Reinforcing steel in reinforced concrete joistsl | 6-1.1 | Carbonate, lightweight and sand-lightweight aggregate concrete. | 11/4 | 11/4 | 1 | 3/4 |
|  | 6-1.2 | Siliceous aggregate concrete. | 13/4 | 11/2 | 1 | 3/4 |
| 7. Reinforcing and tie rods in floor and roof slabsl | 7-1.1 | Carbonate, lightweight and sand-lightweight aggregate concrete. | 1 | 1 | 3/4 | 3/4 |
|  | 7-1.2 | Siliceous aggregate concrete. | 11/4 | 1 | 1 | 3/4 |

For SI: 1 inch = 25.4 mm, 1 square inch = 645.2 mm2, 1 cubic foot = 0.0283 m3.

- Reentrant parts of protected members to be filled solidly.

- Two layers of equal thickness with a 3/4-inch airspace between.

- For all of the construction with gypsum wallboard described in Table [720.1(1)] 721.1(1), gypsum base for veneer plaster of the same size, thickness and core type shall be permitted to be substituted for gypsum wallboard, provided attachment is identical to that specified for the wallboard and the joints on the face layer are reinforced, and the entire surface is covered with [a minimum of] not less than 1/16-inch gypsum veneer plaster.

- An approved adhesive qualified under ASTM E 119 or UL 263.

- Where lightweight or sand-lightweight concrete having an oven-dry weight of 110 pounds per cubic foot or less is used, the tabulated minimum cover shall be permitted to be reduced 25 percent, except that in no case shall the cover be less than 3/4 inch in slabs or 11/2 inches in beams or girders.

- For solid slabs of siliceous aggregate concrete, increase tendon cover 20 percent.

- Adequate provisions against spalling shall be provided by U-shaped or hooped stirrups spaced not to exceed the depth of the member with a clear cover of 1 inch.

- Prestressed slabs shall have a thickness not less than that required in Table [720.1(3)] 721.1(3) for the respective fire resistance time period.

- Fire coverage and end anchorages shall be as follows: Cover to the prestressing steel at the anchor shall be 1/2 inch greater than that required away from the anchor. Minimum cover to steel-bearing plate shall be 1 inch in beams and 3/4 inch in slabs.

- For beam widths between 8 inches and 12 inches, cover thickness shall be permitted to be determined by interpolation.

- Interior spans of continuous slabs, beams and girders shall be permitted to be considered restrained.

- For use with concrete slabs having a comparable fire endurance where members are framed into the structure in such a manner as to provide equivalent performance to that of monolithic concrete construction.

- Generic fire-resistance ratings (those not designated as PROPRIETARY* in the listing) in GA 600 shall be accepted as if herein listed.

- No additional insulating material is required on an exposed outside face of the column flange to achieve a 1-hour fire-resistance rating.

| TABLE [720.1(2)] 721.1(2) RATED FIRE-RESISTANCE PERIODS FOR VARIOUS WALLS AND PARTITIONSa,o,p |
| --- |
| MATERIAL | ITEM NUMBER | CONSTRUCTION | MINIMUM FINISHED THICKNESS FACE-TO-FACEb (inches) |
|  |  |  | 4 [hour] hours | 3 [hour] hours | 2 [hour] hours | 1 hour |
| 1. Brick of clay or shale | 1-1.1 | Solid brick of clay or shalec. | 6 | 4.9 | 3.8 | 2.7 |
|  | 1-1.2 | Hollow brick, not filled. | 5.0 | 4.3 | 3.4 | 2.3 |
|  | 1-1.3 | Hollow brick unit wall, grout or filled with perlite vermiculite or expanded shale aggregate. | 6.6 | 5.5 | 4.4 | 3.0 |
|  | 1-2.1 | 4″ nominal thick units [at least] not less than 75 percent solid backed with a hat-shaped metal furring channel 3/4″ thick formed from 0.021″ sheet metal attached to the brick wall on 24″ centers with approved fasteners, and 1/2″ Type X gypsum wallboard attached to the metal furring strips with 1″-long Type S screws spaced 8″ on center. | — | — | 5d | — |
| 2. Combination of clay brick and load-bearing hollow clay tile | 2-1.1 | 4″ solid brick and 4″ tile ([at least] not less than 40 percent solid). | — | 8 | — | — |
|  | 2-1.2 | 4″ solid brick and 8″ tile [at least] not less than 40 percent solid). | 12 | — | — | — |
| 3. Concrete masonry units | 3-1.1f,g | Expanded slag or pumice. | 4.7 | 4.0 | 3.2 | 2.1 |
|  | 3-1.2f,g | Expanded clay, shale or slate. | 5.1 | 4.4 | 3.6 | 2.6 |
|  | 3-1.3f | Limestone, cinders or air-cooled slag. | 5.9 | 5.0 | 4.0 | 2.7 |
|  | 3-1.4f,g | Calcareous or siliceous gravel. | 6.2 | 5.3 | 4.2 | 2.8 |
| 4. Solid concreteh,i | 4-1.1 | Siliceous aggregate concrete. | 7.0 | 6.2 | 5.0 | 3.5 |
|  |  | Carbonate aggregate concrete. | 6.6 | 5.7 | 4.6 | 3.2 |
|  |  | Sand-lightweight concrete. | 5.4 | 4.6 | 3.8 | 2.7 |
|  |  | Lightweight concrete. | 5.1 | 4.4 | 3.6 | 2.5 |
| 5. Glazed or unglazed facing tile, nonload-bearing | 5-1.1 | One 2″ unit cored 15 percent maximum and one 4″ unit cored 25 percent maximum with 3/4″ mortar-filled collar joint. Unit positions reversed in alternate courses. | — | 63/8 | — | — |
| 5. Glazed or unglazed facing tile, nonload-bearing | 5-1.2 | One 2″ unit cored 15 percent maximum and one 4″ unit cored 40 percent maximum with 3/4″ mortar-filled collar joint. Unit positions side with 3/4″ gypsum plaster. Two wythes tied together every fourth course with No. 22 gage corrugated metal ties. | — | [63/8] 63/4 | — | — |
| 5. Glazed or unglazed facing tile, nonload-bearing | 5-1.3 | One unit with three cells in wall thickness, cored 29 percent maximum. | — | — | 6 | — |
| 5. Glazed or unglazed facing tile, nonload-bearing | 5-1.4 | One 2″ unit cored 22 percent maximum and one 4″ unit cored 41 percent maximum with 1/4″ mortar-filled collar joint. Two wythes tied together every third course with 0.030″ (No. 22 galvanized sheet steel gage) corrugated metal ties. | — | — | 6 | — |
| 5. Glazed or unglazed facing tile, nonload-bearing | 5-1.5 | One 4″ unit cored 25 percent maximum with 3/4″ gypsum plaster on one side. | — | — | 43/4 | — |
| 5. Glazed or unglazed facing tile, nonload-bearing | 5-1.6 | One 4″ unit with two cells in wall thickness, cored 22 percent maximum. | — | — | — | 4 |
| 5. Glazed or unglazed facing tile, nonload-bearing | 5-1.7 | One 4″ unit cored 30 percent maximum with 3/4″ vermiculite gypsum plaster on one side. | — | — | 41/2 | — |
| 5. Glazed or unglazed facing tile, nonload-bearing | 5-1.8 | One 4″ unit cored 39 percent maximum with 3/4″ gypsum plaster on one side. | — | — | — | 41/2 |
| 6. Solid gypsum plaster | 6-1.1 | 3/4″ by 0.055″ (No. 16 carbon sheet steel gage) vertical cold-rolled channels, 16″ on center with 2.6-pound flat metal lath applied to one face and tied with 0.049″ (No. 18 B.W. [Gage] gage) wire at 6″ spacing. Gypsum plaster each side mixed 1:2 by weight, gypsum to sand aggregate. | — | — | — | 2d |
| 6. Solid gypsum plaster | 6-1.2 | 3/4″ by 0.055″ (No. 16 carbon sheet steel gage) cold-rolled channels 16" on center with metal lath applied to one face and tied with 0.049″ (No. 18 B.W. gage) wire at 6″ spacing. Perlite or vermiculite gypsum plaster each side. For three-coat work, the plaster mix for the second coat shall not exceed 100 pounds of gypsum to 21/2 cubic feet of aggregate for the 1-hour system. | — | — | 21/2d | 2d |
| 6. Solid gypsum plaster | 6-1.3 | 3/4″ by 0.055″ (No. 16 carbon sheet steel gage) vertical cold-rolled channels, 16″ on center with 3/8″gypsum lath applied to one face and attached with sheet metal clips. Gypsum plaster each side mixed 1:2 by weight, gypsum to sand aggregate. | — | — | — | 2d |
| 6. Solid gypsum plaster | 6-2.1 | Studless with 1/2″ full-length plain gypsum lath and gypsum plaster each side. Plaster mixed 1:1 for scratch coat and 1:2 for brown coat, by weight, gypsum to sand aggregate. | — | — | — | 2d |
| 6. Solid gypsum plaster | 6- 2.2 | Studless with 1/2″ full-length plain gypsum lath and perlite or vermiculite gypsum plaster each side. | — | — | 21/2d | 2d |
| 6. Solid gypsum plaster | 6-2.3 | Studless partition with 3/8″ rib metal lath installed vertically adjacent edges tied 6″ on center with No. 18 gage wire ties, gypsum plaster each side mixed 1:2 by weight, gypsum to sand aggregate. | — | — | — | 2d |
| 7. Solid perlite and portland cement | 7-1.1 | Perlite mixed in the ratio of 3 cubic feet to 100 pounds of portland cement and machine applied to stud side of 11/2″ mesh by 0.058-inch (No. 17 B.W. gage) paper-backed woven wire fabric lath wire-tied to 4″-deep steel trussed wirej studs 16″ on center. Wire ties of 0.049″ (No. 18 B.W. gage) galvanized steel wire 6″ on center vertically. | — | — | 31/8d | — |
| 8. Solid neat wood fibered gypsum plaster | 8-1.1 | 3/4″ by 0.055-inch (No. 16 carbon sheet steel gage) cold-rolled channels, 12″ on center with 2.5-pound flat metal lath applied to one face and tied with 0.049″ (No. 18 B.W. gage) wire at 6″ spacing. Neat gypsum plaster applied each side. | — | — | 2d | — |
| 9. Solid wallboard partition | 9-1.1 | One full-length layer 1/2″ Type X gypsum wallboarde laminated to each side of 1″ full-length V-edge gypsum coreboard with approved laminating compound. Vertical joints of face layer and coreboard staggered [at least] not less than 3″. | — | — | 2d | — |
| 10. Hollow (studless) gypsum wallboard partition | 10-1.1 | One full-length layer of 5/8″ Type X gypsum wallboarde attached to both sides of wood or metal top and bottom runners laminated to each side of 1″ × 6″ full-length gypsum coreboard ribs spaced 24″ on center with approved laminating compound. Ribs centered at vertical joints of face plies and joints staggered 24″ in opposing faces. Ribs may be recessed 6″ from the top and bottom. | — | — | — | 21/4d |
|  | 10-1.2 | 1″ regular gypsum V-edge full-length backing board attached to both sides of wood or metal top and bottom runners with nails or 15/8″ drywall screws at 24″ on center. Minimum width of runners 15/8″. Face layer of 1/2″ regular full-length gypsum wallboard laminated to outer faces of backing board with approved laminating compound. | — | — | 45/8d | — |
| 11. Noncombustible studs—interior partition with plaster each side | 11-1.1 | 31/4″ × 0.044″ (No. 18 carbon sheet steel gage) steel studs spaced 24″ on center. 5/8″ gypsum plaster on metal lath each side mixed 1:2 by weight, gypsum to sand aggregate. | — | — | — | 43/4d |
| 11. Noncombustible studs—interior partition with plaster each side | 11-1.2 | 33/8″ × 0.055″ (No. 16 carbon sheet steel gage) approved nailablek studs spaced 24" on center. 5/8″ neat gypsum wood-fibered plaster each side over 3/8″ rib metal lath nailed to studs with 6d common nails, 8″ on center. Nails driven 11/4″ and bent over. | — | — | 55/8 | — |
| 11. Noncombustible studs—interior partition with plaster each side | 11-1.3 | 4″ × 0.044″ (No. 18 carbon sheet steel gage) channel-shaped steel studs at 16″ on center. On each side approved resilient clips pressed onto stud flange at 16″ vertical spacing, 1/4″ pencil rods snapped into or wire tied onto outer loop of clips, metal lath wire-tied to pencil rods at 6″ intervals, 1″ perlite gypsum plaster, each side. | — | 75/8d | — | — |
| 11. Noncombustible studs—interior partition with plaster each side | 11-1.4 | 21/2″ × 0.044″ (No. 18 carbon sheet steel gage) steel studs spaced 16″ on center. Wood fibered gypsum plaster mixed 1:1 by weight gypsum to sand aggregate applied on 3/4-pound metal lath wire tied to studs, each side. 3/4″ plaster applied over each face, including finish coat. | — | — | 41/4d | — |
| 12. Wood studs interior partition with plaster each side | 12-1.1l,m | 2″ × 4″ wood studs 16″ on center with 5/8″ gypsum plaster on metal lath. Lath attached by 4d common nails bent over or No. 14 gage by 11/4″ by 3/4″ crown width staples spaced 6″ on center. Plaster mixed 1:11/2 for scratch coat and 1:3 for brown coat, by weight, gypsum to sand aggregate. | — | — | — | 51/8 |
| 12. Wood studs interior partition with plaster each side | 12-1.2l | 2″ × 4″ wood studs 16″ on center with metal lath and 7/8″ neat wood-fibered gypsum plaster each side. Lath attached by 6d common nails, 7″ on center. Nails driven 11/4″ and bent over. | — | — | 51/2d | — |
| 12. Wood studs interior partition with plaster each side | 12-1.3l | 2″ × 4″ wood studs 16″ on center with 3/8″ perforated or plain gypsum lath and 1/2 ″ gypsum plaster each side. Lath nailed with 11/8″ by No. 13 gage by 19/64″ head plasterboard blued nails, 4″ on center. Plaster mixed 1:2 by weight, gypsum to sand aggregate. | — | — | — | 51/4 |
| 12. Wood studs interior partition with plaster each side | 12-1.4l | 2″ × 4″ wood studs 16″ on center with 3/8″ Type X gypsum lath and 1/2″ gypsum plaster each side. Lath nailed with 11/8″ by No. 13 gage by 19/64″ head plasterboard blued nails, 5″ on center. Plaster mixed 1:2 by weight, gypsum to sand aggregate. | — | — | — | 51/4 |
| 13.[Noncumbustible] Noncombustible studs—interior partition with gypsum wallboard each side | 13-1.1 | 0.018″ (No. 25 carbon sheet steel gage) channel-shaped studs 24″ on center with one full-length layer of 5/8″ Type X gypsum wallboarde applied vertically attached with 1″ long No. 6 drywall screws to each stud. Screws are 8″ on center around the perimeter and 12″ on center on the intermediate stud. [The wallboard may be] Where applied horizontally [when], the Type X gypsum wallboard shall be attached to 35/8″ studs and the horizontal joints [are] shall be staggered with those on the opposite side. Screws for the horizontal application shall be 8″ on center at vertical edges and 12″ on center at intermediate studs. | — | — | — | 27/8d |
| 13.[Noncumbustible] Noncombustible studs—interior partition with gypsum wallboard each side | 13-1.2 | 0.018″ (No. 25 carbon sheet steel gage) channel-shaped studs 25″ on center with two full-length layers of 1/2″ Type X gypsum wallboarde applied vertically each side. First layer attached with 1″-long, No. 6 drywall screws, 8″ on center around the perimeter and 12″ on center on the intermediate stud. Second layer applied with vertical joints offset one stud space from first layer using 15/8″ long, No. 6 drywall screws spaced 9″ on center along vertical joints, 12″ on center at intermediate studs and 24″ on center along top and bottom runners. | — | — | 35/8d | — |
| 13.[Noncumbustible] Noncombustible studs—interior partition with gypsum wallboard each side | 13-1.3 | 0.055″ (No. 16 carbon sheet steel gage) approved nailable metal studse 24″ on center with full-length 5/8″ Type X gypsum wallboarde applied vertically and nailed 7″ on center with 6d cement-coated common nails. Approved metal fastener grips used with nails at vertical butt joints along studs. | — | — | — | 47/8 |
| 14.Wood studs—interior partition with gypsum wallboard each side | 14-1.1h,m | 2″ × 4″ wood studs 16″ on center with two layers of 3/8″ regular gypsum wallboarde each side, 4d coolern or wallboardn nails at 8″ on center first layer, 5d coolern or wallboardn nails at 8″ on center second layer with laminating compound between layers, joints staggered. First layer applied full length vertically, second layer applied horizontally or vertically. | — | — | — | 5 |
| 14.Wood studs—interior partition with gypsum wallboard each side | 14-1.2l, m | 2″ × 4″ wood studs 16″ on center with two layers 1/2″ regular gypsum wallboarde applied vertically or horizontally each sidek, joints staggered. Nail base layer with 5d coolern or wallboardn nails at 8″ on center face layer with 8d coolern or wallboardn nails at 8″ on center. | — | — | — | 51/2 |
| 14.Wood studs—interior partition with gypsum wallboard each side | 14-1.3l, m | 2″ × 4″ wood studs 24″ on center with 5/8″ Type X gypsum wallboarde applied vertically or horizontally nailed with 6d coolern or wallboardn nails at 7″ on center with end joints on nailing members. Stagger joints each side. | — | — | — | 43/4 |
| 14.Wood studs—interior partition with gypsum wallboard each side | 14-1.4l | 2″ × 4″ fire-retardant-treated wood studs spaced 24″ on center with one layer of 5/8″ Type X gypsum wallboarde applied with face paper grain (long dimension) parallel to studs. Wallboard attached with 6d coolern or wallboardn nails at 7″ on center. | — | — | — | 43/4d |
| 14.Wood studs—interior partition with gypsum wallboard each side | 14-1.5l, m | 2″ × 4″ wood studs 16″ on center with two layers 5/8″ Type X gypsum wallboarde each side. Base layers applied vertically and nailed with 6d coolern or wallboardn nails at 9″ on center. Face layer applied vertically or horizontally and nailed with 8d coolern or wallboardn nails at 7″ on center. For nail-adhesive application, base layers are nailed 6″ on center. Face layers applied with coating of approved wallboard adhesive and nailed 12″ on center. | — | — | 6 | — |
| 14.Wood studs—interior partition with gypsum wallboard each side | 14-1.6l | 2″ × 3″ fire-retardant-treated wood studs spaced 24″ on center with one layer of 5/8″ Type X gypsum wallboarde applied with face paper grain (long dimension) at right angles to studs. Wallboard attached with 6d cement-coated box nails spaced 7″ on center. | — | — | — | 35/8d |
| 15. Exterior or interior walls | 15-1.1l,m | Exterior surface with 3/4″ drop siding over 1/2″ gypsum sheathing on 2″ × 4″ wood studs at 16″ on center, interior surface treatment as required for 1-hour-rated exterior or interior 2″ × 4″ wood stud partitions. Gypsum sheathing nailed with 13/4″ by No. 11 gage by 7/16″ head galvanized nails at 8″ on center. Siding nailed with 7d galvanized smooth box nails. | — | — | — | Varies |
| 15. Exterior or interior walls | 15-1.2l,m | 2″ × 4″ wood studs 16″ on center with metal lath and 3/4″ cement plaster on each side. Lath attached with 6d common nails 7″ on center driven to 1″ minimum penetration and bent over. Plaster mix 1:4 for scratch coat and 1:5 for brown coat, by volume, cement to sand. | — | — | — | 53/8 |
| 15. Exterior or interior walls | 15-1.3l,m | 2″ × 4″ wood studs 16″ on center with 7/8″ cement plaster (measured from the face of studs) on the exterior surface with interior surface treatment as required for interior wood stud partitions in this table. Plaster mix 1:4 for scratch coat and 1:5 for brown coat, by volume, cement to sand. | — | — | — | Varies |
| 15. Exterior or interior walls | 15-1.4 | 35/8″ No. 16 gage noncombustible studs 16″ on center with 7/8″ cement plaster (measured from the face of the studs) on the exterior surface with interior surface treatment as required for interior, nonbearing, noncombustible stud partitions in this table. Plaster mix 1:4 for scratch coat and 1:5 for brown coat, by volume, cement to sand. | — | — | — | Variesd |
| 15. Exterior or interior walls | 15-1.5m | [25/8] 21/4″ × 33/4″ clay face brick with cored holes over 1/2″ gypsum sheathing on exterior surface of 2″ × 4″ wood studs at 16″ on center and two layers 5/8″ Type X gypsum wallboarde on interior surface. Sheathing placed horizontally or vertically with vertical joints over studs nailed 6″ on center with 13/4″ × No. 11 gage by 7/16″ head galvanized nails. Inner layer of wallboard placed horizontally or vertically and nailed 8″ on center with 6d coolern or wallboardn nails. Outer layer of wallboard placed horizontally or vertically and nailed 8″ on center with 8d coolern or wallboardn nails. [All joints] Joints staggered with vertical joints over studs. Outer layer joints taped and finished with compound. Nail heads covered with joint compound. 0.035 inch (No. 20 galvanized sheet gage) corrugated galvanized steel wall ties 3/4″ by 65/8″ attached to each stud with two 8d coolern or wallboardn nails every sixth course of bricks. | — | — | 10 | — |
| 15. Exterior or interior walls | 15-1.6l,m | 2″ × 6″ fire-retardant-treated wood studs 16″ on center. Interior face has two layers of 5/8″ Type X gypsum with the base layer placed vertically and attached with 6d box nails 12″ on center. The face layer is placed horizontally and attached with 8d box nails 8″ on center at joints and 12″ on center elsewhere. The exterior face has a base layer of 5/8″ Type X gypsum sheathing placed vertically with 6d box nails 8″ on center at joints and 12″ on center elsewhere. An approved building paper is next applied, followed by self-furred exterior lath attached with 21/2″, No. 12 gage galvanized roofing nails with a 3/8″ diameter head and spaced 6″ on center along each stud. Cement plaster consisting of a 1/2″ brown coat is then applied. The scratch coat is mixed in the proportion of 1:3 by weight, cement to sand with 10 pounds of hydrated lime and 3 pounds of approved additives or admixtures per sack of cement. The brown coat is mixed in the proportion of 1:4 by weight, cement to sand with the same amounts of hydrated lime and approved additives or admixtures used in the scratch coat. | — | — | 81/4 | — |
| 15. Exterior or interior walls | 15-1.7l, m | 2″ × 6″ wood studs 16″ on center. The exterior face has a layer of 5/8″ Type X gypsum sheathing placed vertically with 6d box nails 8″ on center at joints and 12″ on center elsewhere. An approved building paper is next applied, followed by 1″ by No. 18 gage self-furred exterior lath attached with 8d by 21/2″ long galvanized roofing nails spaced 6″ on center along each stud. Cement plaster consisting of a 1/2″ scratch coat, a bonding agent and a 1/2″ brown coat and a finish coat is then applied. The scratch coat is mixed in the proportion of 1:3 by weight, cement to sand with 10 pounds of hydrated lime and 3 pounds of approved additives or admixtures per sack of cement. The brown coat is mixed in the proportion of 1:4 by weight, cement to sand with the same amounts of hydrated lime and approved additives or admixtures used in the scratch coat. The interior is covered with 3/8″ gypsum lath with 1″ hexagonal mesh of 0.035 inch (No. 20 B.W. gage) woven wire lath furred out 5/16″ and 1″ perlite or vermiculite gypsum plaster. Lath nailed with 11/8″ by No. 13 gage by 19/64″ head plasterboard glued nails spaced 5″ on center. Mesh attached by 13/4″ by No. 12 gage by 3/8″ head nails with 3/8″ furrings, spaced 8″ on center. The plaster mix shall not exceed 100 pounds of gypsum to 21/2 cubic feet of aggregate. | — | — | 83/8 | — |
| 15. Exterior or interior walls | 15-1.8l,m | 2″ × 6″ wood studs 16″ on center. The exterior face has a layer of 5/8″ Type X gypsum sheathing placed vertically with 6d box nails 8″ on center at joints and 12″ on center elsewhere. An approved building paper is next applied, followed by 11/2″ by No. 17 gage self-furred exterior lath attached with 8d by 21/2″ long galvanized roofing nails spaced 6″ on center along each stud. Cement plaster consisting of a 1/2″ scratch coat, and a 1/2″ brown coat is then applied. The plaster may be placed by machine. The scratch coat is mixed in the proportion of 1:4 by weight, plastic cement to sand. The brown coat is mixed in the proportion of 1:5 by weight, plastic cement to sand. The interior is covered with 3/8″ gypsum lath with 1″ hexagonal mesh of No. 20 gage woven wire lath furred out 5/16″ and 1″ perlite or vermiculite gypsum plaster. Lath nailed with 11/8″ by No. 13 gage by 19/64″ head plasterboard glued nails spaced 5″ on center. Mesh attached by 13/4″ by No. 12 gage by 3/8″ head nails with 3/8″ furrings, spaced 8″ on center. The plaster mix shall not exceed 100 pounds of gypsum to 21/2 cubic feet of aggregate. | — | — | 83/8 | — |
| 15. Exterior or interior walls | 15-1.9 | 4″ No. 18 gage, nonload-bearing metal studs, 16″ on center, with 1″ portland cement lime plaster (measured from the back side of the 3/4-pound expanded metal lath) on the exterior surface. Interior surface to be covered with 1″ of gypsum plaster on 3/4-pound expanded metal lath proportioned by weight—1:2 for scratch coat, 1:3 for brown, gypsum to sand. Lath on one side of the partition fastened to 1/4″ diameter pencil rods supported by No. 20 gage metal clips, located [16’] 16" on center vertically, on each stud. 3″ thick mineral fiber insulating batts friction fitted between the studs. | — | — | 61/2d | — |
| 15. Exterior or interior walls | 15-1.10 | Steel studs [0.060’] 0.060″ thick, 4″ deep or 6’ at 16″ or 24″ centers, with 1/2″ Glass Fiber Reinforced Concrete (GFRC) on the exterior surface. GFRC is attached with flex anchors at 24″ on center, with 5″ leg welded to studs with two 1/2″-long flare-bevel welds, and 4″ foot attached to the GFRC skin with 5/8″ thick GFRC bonding pads that extend 21/2″ beyond the flex anchor foot on both sides. Interior surface to have two layers of 1/2″ Type X gypsum wallboard.e The first layer of wallboard to be attached with 1″-long Type S buglehead screws spaced 24″ on center and the second layer is attached with 15/8″-long Type S screws spaced at 12″ on center. Cavity is to be filled with 5″ of 4 pcf (nominal) mineral fiber batts. GFRC has 11/2″ returns packed with mineral fiber and caulked on the exterior. | — | — | 61/2 | — |
| 15. Exterior or interior walls | 15-1.11 | Steel studs 0.060″ thick, 4″ deep or 6″ at 16″ or 24″ centers, respectively, with 1/2″ Glass Fiber Reinforced Concrete (GFRC) on the exterior surface. GFRC is attached with flex anchors at 24″ on center, with 5″ leg welded to studs with two 1/2″-long flare-bevel welds, and 4″ foot attached to the GFRC skin with 5/8″-thick GFRC bonding pads that extend 21/2″ beyond the flex anchor foot on both sides. Interior surface to have one layer of 5/8″ Type X gypsum wallboarde, attached with 11/4″-long Type S buglehead screws spaced 12″ on center. Cavity is to be filled with 5″ of 4 pcf (nominal) mineral fiber batts. GFRC has 11/2″ returns packed with mineral fiber and caulked on the exterior. | — | — | — | 61/8 |
| 15. Exterior or interior walls | 15-1.12q | 2″ × 6″ wood studs at 16″ with double top plates, single bottom plate; interior and exterior sides covered with 5/8″ Type X gypsum wallboard, 4′ wide, applied horizontally or vertically with vertical joints over studs, and fastened with 21/4″ Type S drywall screws, spaced 12″ on center. Cavity to be filled with 5½″ mineral wool insulation. | — | — | — | 63/4 |
| 15. Exterior or interior walls | 15-1.13q | 2″ × 6″ wood studs at 16″ with double top plates, single bottom plate; interior and exterior sides covered with 5/8″ Type X gypsum wallboard, 4′ wide, applied vertically with all joints over framing or blocking, and fastened with 21/4″ Type S drywall screws, spaced 12″ on center. R-19 [fiberglass] mineral fiber insulation installed in stud cavity. | — | — | — | 63/4 |
| 15. Exterior or interior walls | 15-1.14q | 2″ x 6″ wood studs at 16″ with double top plates, single bottom plate; interior and exterior sides covered with 5/8” Type X gypsum wallboard, 4’ wide, applied horizontally or vertically with vertical joints over studs, and fastened with 2¼″ Type S drywall screws, spaced 7″ on center. | — | — | — | 6¾ |
| 15. Exterior or interior walls | 15-1.15q | 2″ × 4″ wood studs at 16″ with double top plates, single bottom plate; interior and exterior sides covered with 5/8″ Type X gypsum wallboard and sheathing, respectively, 4′ wide, applied horizontally or vertically with vertical joints over studs, and fastened with 21/4″ Type S drywall screws, spaced 12″ on center. Cavity to be filled with 31/2″ mineral wool insulation. | — | — | — | 43/4 |
| 15. Exterior or interior walls | 15-1.16q | 2″ × 6″ wood studs at 24″ centers with double top plates, single bottom plate; interior and exterior side covered with two layers of 5/8″ Type X gypsum wallboard, 4′ wide, applied horizontally with vertical joints over studs. Base layer fastened with 21/4″ Type S drywall screws, spaced 24″ on center, and face layer fastened with Type S drywall screws, spaced 8″ on center, wallboard joints covered with paper tape and joint compound, [fastened] fastener heads covered with joint compound. Cavity to be filled with 51/2″ mineral wool insulation. | — | — | 73/4 | — |
| 15. Exterior or interior walls | 15-2.1d | 35/8″ No. 16 gage steel studs at 24″ on center or 2″ x 4″ wood studs at 24″ on center. Metal lath attached to the exterior side of studs with minimum 1” long No. 6 drywall screws at 6″ on center and covered with minimum ¾″ thick portland cement plaster. Thin veneer brick units of clay or shale complying with ASTM C 1088, Grade TBS or better, installed in running bond in accordance with Section 1405.10. Combined total thickness of the portland cement plaster, mortar and thin veneer brick units shall be not less than 1¾″. Interior side covered with one layer of 5/8″ thick Type X gypsum wallboard attached to studs with 1″ long No. 6 drywall screws at 12″ on center. | — | — | — | 6 |
| 15. Exterior or interior walls | 15-2.2d | 35/8″ No. 16 gage steel studs at 24″ on center or 2″ x 4″ wood studs at 24″ on center. Metal lath attached to the exterior side of studs with minimum 1” long No. 6 drywall screws at 6″ on center and covered with minimum ¾″ thick portland cement plaster. Thin veneer brick units of clay or shale complying with ASTM C 1088, Grade TBS or better, installed in running bond in accordance with Section 1405.10. Combined total thickness of the portland cement plaster, mortar and thin veneer brick units shall be not less than 2″. Interior side covered with two layers of 5/8″ thick Type X gypsum wallboard. Bottom layer attached to studs with 1″ long No. 6 drywall screws at 24″ on center. Top layer attached to studs with 15/8″ long No. 6 drywall screws at 12″ on center. | — | — | 67/8 | — |
| 15. Exterior or interior walls | 15-2.3d | 35/8″ No. 16 gage steel studs at 16″ on center or 2″ x 4″ wood studs at 16″ on center. Where metal lath is used, [attached] attach to the exterior side of studs with minimum 1″ long No. 6 drywall screws at 6″ on center. Brick units of clay or shale not less than 25/8″ thick complying with ASTM C 216 installed in accordance with Section 1405.6 with a minimum 1″ [air space airspace. Interior side covered with one layer of 5/8″ thick Type X gypsum wallboard attached to studs with 1″ long No. 6 drywall screws at 12″ on center. | — | — | — | 77/8 |
| 15. Exterior or interior walls | 15-2.4d | 35/8″ No. 16 gage steel studs at 16″ on center or 2″ x 4″ wood studs at 16″ on center. Where metal lath is used, [attached] attach to the exterior side of studs with minimum 1″ long No. 6 drywall screws at 6″ on center. Brick units of clay or shale not less than 25/8″ thick complying with ASTM C 216 installed in accordance with Section 1405.6 with a minimum 1” [air space] airspace. Interior side covered with two layers of 5/8″ thick Type X gypsum wallboard. Bottom layer attached to studs with 1″ long No. 6 drywall screws at 24″ on center. Top layer attached to studs with 15/8″ long No. 6 drywall screws at 12” on center. | — | — | 8½ | — |
| 16. Exterior walls rated for fire resistance from the inside only in accordance with Section [704.5] 705.5. | 16-1.1q | 2″ × 4″ wood studs at 16″ centers with double top plates, single bottom plate; interior side covered with 5/8″ Type X gypsum wallboard, 4′ wide, applied horizontally unblocked, and fastened with 21/4″ Type S drywall screws, spaced 12″ on center, wallboard joints covered with paper tape and joint compound, fastener heads covered with joint compound. Exterior covered with 3/8″ wood structural panels [(oriented strand board)], applied vertically, horizontal joints blocked and fastened with 6d common nails (bright) — 12″ on center in the field, and 6″ on center panel edges. Cavity to be filled with 31/2″ mineral wool insulation. Rating established for exposure from interior side only. | — | — | — | 41/2 |
| 16. Exterior walls rated for fire resistance from the inside only in accordance with Section [704.5] 705.5. | 16-1.2q | 2" × 6" [(51 mm x 152 mm)] wood studs at 16″ centers with double top plates, single bottom plate; interior side covered with 5/8″ Type X gypsum wallboard, 4′ wide, applied horizontally or vertically with vertical joints over studs and fastened with 21/4″ Type S drywall screws, spaced 12″ on center, wallboard joints covered with paper tape and joint compound, fastener heads covered with joint compound, exterior side covered with 7/16″ wood structural panels [(oriented strand board)] fastened with 6d common nails (bright) spaced 12″ on center in the field and 6″ on center along the panel edges. Cavity to be filled with 51/2″ mineral wool insulation. Rating established from the gypsum-covered side only. | — | — | — | 69/16 |
| 16. Exterior walls rated for fire resistance from the inside only in accordance with Section [704.5] 705.5. | 16-1.3q | 2″ × 6″ wood studs at 16″ centers with double top plates, single bottom plates; interior side covered with 5/8″ Type X gypsum wallboard, 4′ wide, applied vertically with all joints over framing or blocking and fastened with 2¼″ Type S drywall screws spaced 7″ on center. Joints to be covered with tape and joint compound. Exterior covered with 3/8″ wood structural panels, applied vertically with edges over framing or blocking and fastened with 6d common nails (bright) at 12″ on center in the field and 6″ on center on panel edges. R-19 mineral fiber insulation installed in stud cavity. Rating established [form] from the gypsum-covered side only. | — | — | — | 61/2 |

For SI: 1 inch = 25.4 mm, 1 square inch = 645.2 mm2, 1 cubic foot = 0.0283 m3.

- Staples with equivalent holding power and penetration shall be permitted to be used as alternate fasteners to nails for attachment to wood framing.

- [Thickness] Thicknesses shown for brick and clay tile are nominal thicknesses unless plastered, in which case thicknesses are net. Thickness shown for concrete masonry and clay masonry is equivalent thickness defined in Section [721.3.1] 722.3.1 for concrete masonry and Section [721.4.1] 722.4.1.1 for clay masonry. Where all cells are solid grouted or filled with silicone-treated perlite loose-fill insulation; vermiculite loose-fill insulation; or expanded clay, shale or slate lightweight aggregate, the equivalent thickness shall be the thickness of the block or brick using specified dimensions as defined in Chapter 21. Equivalent thickness [may] shall also include the thickness of applied plaster and lath or gypsum wallboard, where specified.

- For units in which the net cross-sectional area of cored brick in any plane parallel to the surface containing the cores is [at least] not less than 75 percent of the gross cross-sectional area measured in the same plane.

- Shall be used for nonbearing purposes only.

- For all of the construction with gypsum wallboard described in this table, gypsum base for veneer plaster of the same size, thickness and core type shall be permitted to be substituted for gypsum wallboard, provided attachment is identical to that specified for the wallboard, and the joints on the face layer are reinforced and the entire surface is covered with a [minimum] not less than of 1/16-inch gypsum veneer plaster.

- The fire-resistance time period for concrete masonry units meeting the equivalent thicknesses required for a 2-hour fire-resistance rating in Item 3, and having a thickness of not less than 75/8 inches is 4 hours [when] where cores [which] that are not grouted are filled with silicone-treated perlite loose-fill insulation; vermiculite loose-fill insulation; or expanded clay, shale or slate lightweight aggregate, sand or slag having a maximum particle size of 3/8 inch.

- The fire-resistance rating of concrete masonry units composed of a combination of aggregate types or where plaster is applied directly to the concrete masonry shall be determined in accordance with ACI 216.1/TMS 216. Lightweight aggregates shall have a maximum combined density of 65 pounds per cubic foot.

- See also Note b. The equivalent thickness shall be permitted to include the thickness of cement plaster or 1.5 times the thickness of gypsum plaster applied in accordance with the requirements of Chapter 25.

- Concrete walls shall be reinforced with horizontal and vertical temperature reinforcement as required by Chapter 19.

- Studs are welded truss wire studs with 0.18 inch (No. 7 B.W. gage) flange wire and 0.18 inch (No. 7 B.W. gage) truss wires.

- Nailable metal studs consist of two channel studs spot welded back to back with a crimped web forming a nailing groove.

- Wood structural panels shall be permitted to be installed between the fire protection and the wood studs on either the interior or exterior side of the wood frame assemblies in this table, provided the length of the fasteners used to attach the fire protection is increased by an amount [at least equal to] not less than the thickness of the wood structural panel.

- [The] For studs with a slenderness ratio, le/d, greater than 33, the design stress [of studs] shall be reduced to 78 percent of allowable F’c. For studs with [the maximum] a slenderness ratio, le/d, not [greater than 78 percent of] exceeding 33, the design stress shall be reduced to 78 percent of the adjusted stress F’c calculated [stress with] for studs having a slenderness ratio le/d of 33.

- For properties of cooler or wallboard nails, see ASTM C 514, ASTM C 547 or ASTM F 1667.

- Generic fire-resistance ratings (those not designated as PROPRIETARY* in the listing) in the GA 600 shall be accepted as if herein listed.

- NCMA TEK 5-8, shall be permitted for the design of fire walls.

- The design stress of studs shall be equal to a maximum of 100 percent of the allowable F’c calculated in accordance with Section 2306.

| ABLE [720.1(3)] 721.1(3) MINIMUM PROTECTION FOR FLOOR AND ROOF SYSTEMSa,q |
| --- |
| FLOOR OR ROOF CONSTRUCTION | ITEM NUMBER | CEILING CONSTRUCTION | THICKNESS OF FLOOR OR ROOF SLAB (inches) | MINIMUM THICKNESS OF CEILING (inches) |
|  |  |  | 4 [hour] hours | 3 [hour] hours | 2 [hour] hours | 1 hour | 4 [hour] hours | 3 [hour] hours | 2 [hour] hours | 1 hour |
| 1. Siliceous aggregate concrete | 1-1.1 | Slab (no ceiling required). Minimum cover over nonprestressed reinforcement shall be not [be] less than 3/4 inch.b | 7.0 | 6.2 | 5.0 | 3.5 | — | — | — | — |
| 2. Carbonate aggregate concrete | 2-1.1 |  | 6.6 | 5.7 | 4.6 | 3.2 | — | — | — | — |
| 3. Sand-lightweight concrete | 3-1.1 |  | 5.4 | 4.6 | 3.8 | 2.7 | — | — | — | — |
| 4. Lightweight concrete | 4-1.1 |  | 5.1 | 4.4 | 3.6 | 2.5 | — | — | — | — |
| 5. Reinforced concrete | 5-1.1 | Slab with suspended ceiling of vermiculite gypsum plaster over metal lath attached to 3/4″ cold-rolled channels spaced 12″on center. Ceiling located 6″ minimum below joists. | 3 | 2 | — | — | 1 | 3/4 | — | — |
| 5. Reinforced concrete | 5-2.1 | 3/8″ Type X gypsum wallboardc attached to 0.018 inch (No. 25 carbon sheet steel gage) by 7/8″ deep by 25/8″ hat-shaped galvanized steel channels with 1″-long No. 6 screws. The channels are spaced 24″ on center, span 35″ and are supported along their length at 35″ intervals by 0.033-inch (No. 21 galvanized sheet gage) galvanized steel flat strap hangers having formed edges that engage the lips of the channel. The strap hangers are attached to the side of the concrete joists with 5/32″ by 11/4″ long power-driven fasteners. The wallboard is installed with the long dimension perpendicular to the channels. [All end] End joints occur on channels and supplementary channels are installed parallel to the main channels, 12″ each side, at end joint occurrences. The finished ceiling is located approximately 12″ below the soffit of the floor slab. | — | — | 21/2 | — | — | — | 5/8 | — |
| 6. Steel joists constructed with a poured reinforced concrete slab on metal lath forms or steel form unitsd,e | 6-1.1 | Gypsum plaster on metal lath attached to the bottom cord with single No. 16 gage or doubled No. 18 gage wire ties spaced 6″ on center. Plaster mixed 1:2 for scratch coat, 1:3 for brown coat, by weight, gypsum-to-sand aggregate for 2-hour system. For 3-hour system plaster is neat. | — | — | 21/2 | 21/4 | — | — | 3/4 | 5/8 |
| 6. Steel joists constructed with a poured reinforced concrete slab on metal lath forms or steel form unitsd,e | 6-2.1 | Vermiculite gypsum plaster on metal lath attached to the bottom chord with single No. 16 gage or doubled 0.049-inch (No. 18 B.W. gage) wire ties 6″ on center. | — | 2 | — | — | — | 5/8 | — | — |
| 6. Steel joists constructed with a poured reinforced concrete slab on metal lath forms or steel form unitsd,e | 6-3.1 | Cement plaster over metal lath attached to the bottom chord of joists with single No. 16 gage or doubled 0.049-inch (No. 18 B.W. gage) wire ties spaced 6″ on center. Plaster mixed 1:2 for scratch coat, 1:3 for brown coat for 1-hour system and 1:1 for scratch coat, 1:11/2 for brown coat for 2-hour system, by weight, cement to sand. | — | — | — | 2 | — | — | — | 5/8f |
| 6. Steel joists constructed with a poured reinforced concrete slab on metal lath forms or steel form unitsd,e | 6-4.1 | Ceiling of 5/8″ Type X wallboardc attached to 7/8″ deep by 25/8″ by 0.021 inch (No. 25 carbon sheet steel gage) hat-shaped furring channels 12″ on center with 1″ long No. 6 wallboard screws at 8″ on center. Channels wire tied to bottom chord of joists with doubled 0.049 inch (No. 18 B.W. gage) wire or suspended below joists on wire hangers.g | — | — | 21/2 | — | — | — | 5/8 | — |
| 6. Steel joists constructed with a poured reinforced concrete slab on metal lath forms or steel form unitsd,e | 6-5.1 | Wood-fibered gypsum plaster mixed 1:1 by weight gypsum to sand aggregate applied over metal lath. Lath tied 6″ on center to 3/4″ channels spaced 131/2″ on center. Channels secured to joists at each intersection with two strands of 0.049 inch (No. 18 B.W. gage) galvanized wire. | — | — | 21/2 | — | — | — | 3/4 | — |
| 7. Reinforced concrete slabs and joists with hollow clay tile fillers laid end to end in rows 21/2″ or more apart; reinforcement placed between rows and concrete cast around and over tile. | 7-1.1 | 5/8″ gypsum plaster on bottom of floor or roof construction. | — | — | 8h | — | — | — | 5/8 | — |
| 7. Reinforced concrete slabs and joists with hollow clay tile fillers laid end to end in rows 21/2″ or more apart; reinforcement placed between rows and concrete cast around and over tile. | 7-1.2 | None | — | — | — | 51/2i | — | — | — | — |
| 8. Steel joists constructed with a reinforced concrete slab on top poured on a 1/2″ deep steel deck.e | 8-1.1 | Vermiculite gypsum plaster on metal lath attached to 3/4" cold-rolled channels with 0.049" (No. 18 B.W. gage) wire ties spaced 6″ on center. | 21/2i | — | — | — | 3/4 | — | — | — |
| 9. 3″ deep cellular steel deck with concrete slab on top. Slab thickness measured to top. | 9-1.1 | Suspended ceiling of vermiculite gypsum plaster base coat and vermiculite acoustical plaster on metal lath attached at 6″ intervals to 3/4″ cold-rolled channels spaced 12″ on center and secured to 11/2" cold-rolled channels spaced 36″ on center with 0.065″ (No. 16 B.W. gage) wire. 11/2″ channels supported by No. 8 gage wire hangers at 36″ on center. Beams within envelope and with a 21/2″airspace between beam soffit and lath have a 4-hour rating. | 21/2 | — | — | — | 11/8k | — | — | — |
| 10. 11/2″-deep steel roof deck on steel framing. Insulation board, 30 pcf density, composed of wood fibers with cement binders of thickness shown bonded to deck with unified asphalt adhesive. Covered with a Class A or B roof covering. | 10-1.1 | Ceiling of gypsum plaster on metal lath. Lath attached to 3/4″ furring channels with 0.049″ (No. 18 B.W. gage) wire ties spaced 6″ on center. 3/4″ channel saddle tied to 2″ channels with doubled 0.065″ (No. 16 B.W. gage) wire ties. 2″ channels spaced 36″ on center suspended 2″ below steel framing and saddle-tied with 0.165″ (No. 8 B.W. gage) wire. Plaster mixed 1:2 by weight, gypsum-to-sand aggregate. | — | — | 17/8 | 1 | — | — | 3/4l | 3/4l |
| 11. 11/2″-deep steel roof deck on steel-framing wood fiber insulation board, 17.5 pcf density on top applied over a 15-lb asphalt- saturated felt. Class A or B roof covering. | 11-1.1 | Ceiling of gypsum plaster on metal lath. Lath attached to 3/4″ furring channels with 0.049″ (No. 18 B.W. gage) wire ties spaced 6″ on center. 3/4″ channels saddle tied to 2″ channels with doubled 0.065″ (No. 16 B.W. gage) wire ties. 2″ channels spaced 36″ on center suspended 2″ below steel framing and saddle tied with 0.165″ (No. 8 B.W. gage) wire. Plaster mixed 1:2 for scratch coat and 1:3 for brown coat, by weight, gypsum-to-sand aggregate for 1-hour system. For 2-hour system, plaster mix is 1:2 by weight, gypsum-to-sand aggregate. | — | — | 11/2 | 1 | — | — | 7/8g | 3/4l |
| 12. 11/2″ deep steel roof deck on steel-framing insulation of rigid board consisting of expanded perlite and fibers impregnated with integral asphalt waterproofing; density 9 to 12 pcf secured to metal roof deck by 1/2″ wide ribbons of waterproof, cold-process liquid adhesive spaced 6″ apart. Steel joist or light steel construction with metal roof deck, insulation, and Class A or B built-up roof covering.e | 12-1.1 | Gypsum-vermiculite plaster on metal lath wire tied at 6″ intervals to 3/4″ furring channels spaced 12″ on center and wire tied to 2″ runner channels spaced 32″ on center. Runners wire tied to bottom chord of steel joists. | — | — | 1 | — | — | — | 7/8 | — |
| 13. Double wood floor over wood joists spaced 16″ on center.m,n | 13-1.1 | Gypsum plaster over 3/8″ Type X gypsum lath. Lath initially applied with not less than four 11/8″ by No. 13 gage by 19/64″ head plasterboard blued nails per bearing. Continuous stripping over lath along all joist lines. Stripping consists of 3″ wide strips of metal lath attached by 11/2″ by No. 11 gage by 1/2″ head roofing nails spaced 6″ on center. Alternate stripping consists of 3″ wide 0.049″ diameter wire stripping weighing 1 pound per square yard and attached by No.16 gage by 11/2″ by 3/4″ crown width staples, spaced 4″ on center. Where alternate stripping is used, the lath nailing [may] shall consist of two nails at each end and one nail at each intermediate bearing. Plaster mixed 1:2 by weight, gypsum-to-sand aggregate. | — | — | — | — | — | — | — | 7/8 |
| 13. Double wood floor over wood joists spaced 16″ on center.m,n | 13-1.2 | Cement or gypsum plaster on metal lath. Lath fastened with 11/2″ by No. 11 gage by 7/16″ head barbed shank roofing nails spaced 5″ on center. Plaster mixed 1:2 for scratch coat and 1:3 for brown coat, by weight, cement to sand aggregate. | — | — | — | — | — | — | — | 5/8 |
| 13. Double wood floor over wood joists spaced 16″ on center.m,n | 13-1.3 | Perlite or vermiculite gypsum plaster on metal lath secured to joists with 11/2″ by No. 11 gage by 7/16″ head barbed shank roofing nails spaced 5″ on center. | — | — | — | — | — | — | — | 5/8 |
| 13. Double wood floor over wood joists spaced 16″ on center.m,n | 13-1.4 | 1/2″ Type X gypsum wallboardc nailed to joists with 5d coolero or wallboardo nails at 6″ on center. End joints of wallboard centered on joists. | — | — | — | — | — | — | — | 1/2 |
| 14. Plywood stressed skin panels consisting of 5/8″-thick interior C-D (exterior glue) top stressed skin on 2″ × 6″nominal (minimum) stringers. Adjacent panel edges joined with 8d common wire nails spaced 6″ on center. Stringers spaced 12″ maximum on center. | 14-1.1 | 1/2″-thick wood fiberboard weighing 15 to 18 pounds per cubic foot installed with long dimension parallel to stringers or 3/8″ C-D (exterior glue) plywood glued and/or nailed to stringers. Nailing to be with 5d coolero or wallboardo nails at 12″ on center. Second layer of 1/2″ Type X gypsum wallboardc applied with long dimension perpendicular to joists and attached with 8d coolero or wallboardo nails at 6″ on center at end joints and 8″ on center elsewhere. Wallboard joints staggered with respect to fiberboard joints. | — | — | — | — | — | — | — | 1 |
| 15. Vermiculite concrete slab proportioned 1:4 (portland cement to vermiculite aggregate) on a 11/2"-deep steel deck supported on individually protected steel framing. Maximum span of deck 6’-10" where deck is less than 0.019 inch (No. 26 carbon steel sheet gage) or greater. Slab reinforced with 4" × 8" 0.109/0.083" (No. 12/14 B.W. gage) welded wire mesh. | 15-1.1 | None. | — | — | — | 3j | — | — | — | — |
| 16. Perlite concrete slab proportioned 1:6 (portland cement to perlite aggregate) on a 11/4″-deep steel deck supported on individually protected steel framing. Slab reinforced with 4" × 8" 0.109/0.083" (No. 12/14 B.W. gage) welded wire mesh. | 16-1.1 | None. | — | — | — | 31/2j | — | — | — | — |
| 17. Perlite concrete slab proportioned 1:6 (portland cement to perlite aggregate) on a 9/16″-deep steel deck supported by steel joists 4’ on center. Class A or B roof covering on top. | 17-1.1 | Perlite gypsum plaster on metal lath wire tied to 3/4″ furring channels attached with 0.065-inch (No. 16 B.W. gage) wire ties to lower chord of joists. | — | 2p | 2p | — | — | 7/8 | 3/4 | — |
| 18. Perlite concrete slab proportioned 1:6 (portland cement to perlite aggregate) on 11/4″-deep steel deck supported on individually protected steel framing. Maximum span of deck 6′-10″ where deck is less than 0.019″ (No. 26 carbon sheet steel gage) and 8′-0″ where deck is 0.019″ (No. 26 carbon sheet steel gage) or greater. Slab reinforced with 0.042″ (No. 19 B.W. gage) hexagonal wire mesh. Class A or B roof covering on top. | 18-1.1 | None. | — | 21/4p | 21/4p | — | — | — | — | — |
| 19. Floor and beam construction consisting of 3″-deep cellular steel floor unit mounted on steel members with 1:4 (proportion of portland cement to perlite aggregate) perlite-concrete floor slab on top. | 19-1.1 | Suspended envelope ceiling of perlite gypsum plaster on metal lath attached to 3/4″ cold-rolled channels, secured to 11/2″ cold-rolled channels spaced 42″ on center supported by 0.203 inch (No. 6 B.W. gage) wire 36″ on center. Beams in envelope with 3″ minimum airspace between beam soffit and lath have a 4-hour rating. | 2p | — | — | — | 1l | — | — | — |
| 20. Perlite concrete proportioned 1:6 (portland cement to perlite aggregate) poured to 1/8-inch thickness above top of corrugations of 15/16″-deep galvanized steel deck maximum span 8′-0″ for 0.024-inch (No. 24 galvanized sheet gage) or 6′ 0″ for 0.019-inch (No. 26 galvanized sheet gage) with deck supported by individually protected steel framing. Approved polystyrene foam plastic insulation board having a flame spread not exceeding 75 (1″ to 4″ thickness) with vent holes that approximate 3 percent of the board surface area placed on top of perlite slurry. (– continued ) | 20-1.1 | None. | — | — | Varies | — | — | — | — | — |
| 20. Continued - A 2′ by 4′ insulation board contains six 23/4″ diameter holes. Board covered with 21/4″ minimum perlite concrete slab. Slab reinforced with mesh consisting of 0.042 inch (No. 19 B.W. gage) galvanized steel wire twisted together to form 2″ hexagons with straight 0.065 inch (No. 16 B.W. gage) galvanized steel wire woven into mesh and spaced 3″. Alternate slab reinforcement shall be permitted to consist of 4″ × 8″, 0.109/0.238-inch (No. 12/4 B.W. gage), or 2″ × 2″, 0.083/ 0.083-inch (No. 14/14 B.W. gage) welded wire fabric. Class A or B roof covering on top. | 20-1.1 | None. | — | — | Varies | — | — | — | — | — |
| 21. Wood joists, wood I-joists, floor trusses and flat or pitched roof trusses spaced a maximum 24″ o.c. with 1/2″ wood structural panels with exterior glue applied at right angles to top of joist or top chord of trusses with 8d nails. The wood structural panel thickness shall be not [be] less than nominal 1/2″ nor less than required by Chapter 23. | 21-1.1 | Base layer 5/8″ Type X gypsum wallboard applied at right angles to joist or truss 24″ o.c. with 11/4″ Type S or Type W drywall screws 24″ o.c. Face layer 5/8″ Type X gypsum wallboard or veneer base applied at right angles to joist or truss through base layer with 17/8″ Type S or Type W drywall screws 12″ o.c. at joints and intermediate joist or truss. Face layer Type G drywall screws placed 2″ back on either side of face layer end joints, 12″ o.c. | — | — | — | Varies | — | — | — | 11/4 |
| 22. Steel joists, floor trusses and flat or pitched roof trusses spaced a maximum 24″ o.c. with 1/2″ wood structural panels with exterior glue applied at right angles to top of joist or top chord of trusses with No. 8 screws. The wood structural panel thickness shall be not [be] less than nominal 1/2″ nor less than required by Chapter 23. | 22-1.1 | Base layer 5/8″ Type X gypsum board applied at right angles to steel framing 24″ on center with 1″ Type S drywall screws spaced 24″ on center. Face layer 5/8″ Type X gypsum board applied at right angles to steel framing attached through base layer with 15/8″ Type S drywall screws 12″ on center at end joints and intermediate joints and 11/2″ Type G drywall screws 12 inches on center placed 2″ back on either side of face layer end joints. Joints of the face layer are offset 24″ from the joints of the base layer. | — | — | — | Varies | — | — | — | 11/4 |
| 23. Wood I-joist (minimum joist depth 91/4″ with a minimum flange depth of 15/16″ and a minimum flange cross- sectional area of [2.3] 2.25 square inches) at 24″ o.c. spacing with [1 inch] a minimum 1" × 4" [inch (nominal) wood furring] (3/4" × 3.5" actual) ledger strip [spacer] applied parallel to and covering the bottom of the bottom flange of each member, tacked in place. 2″ mineral [fiber] wool insulation, 3.5 pcf (nominal) installed adjacent to the bottom flange of the I-joist and supported by the 1″ × 4″ [furring] ledger strip [spacer]. | 23-1.1 | 1/2″ deep single leg resilient channel 16″ on center (channels doubled at wallboard end joints), placed perpendicular to the furring strip and joist and attached to each joist by 17/8″ Type S drywall screws. 5/8″ Type C gypsum wallboard applied perpendicular to the channel with end joints staggered [at least] not less than 4′ and fastened with 11/8″ Type S drywall screws spaced 7″ on center. Wallboard joints to be taped and covered with joint compound. | — | — | — | Varies | — | — | — | 5/8 |
| 24. Wood I-joist (minimum I-joist depth 9¼" with a minimum flange depth of 1½" and a minimum flange cross-sectional area of 5.25 square inches; minimum web thickness of 3/8") @ 24" o.c., 1½" mineral wool insulation (2.5 pcf – nominal) resting on hat-shaped furring channels. | 24-1.1 | Minimum 0.026" thick hat-shaped channel 16" o.c. (channels doubled at wallboard end joints), placed perpendicular to the joist and attached to each joist by [15/8"] 11/4" Type S drywall screws. 5/8" Type C gypsum wallboard applied perpendicular to the channel with end joints staggered and fastened with 11/8" Type S drywall screws spaced 12" o.c. in the field and 8" o.c. at the wallboard ends. Wallboard joints to be taped and covered with joint compound. | — | — | — | Varies | — | — | — | 5/8 |
| 25. Wood I-joist (minimum I-joist depth 9¼" with a minimum flange depth of 1½" and a minimum flange cross-sectional area of 5.25 square inches; minimum web thickness of 7/16") @ 24" o.c., 1½" mineral wool insulation (2.5 pcf – nominal) resting on resilient channels. | 25-1.1 | Minimum 0.019" thick resilient channel 16" o.c. (channels doubled at wallboard end joints), placed perpendicular to the joist and attached to each joist by 15/8" Type S drywall screws. 5/8" Type C gypsum wallboard applied perpendicular to the channel with end joints staggered and fastened with 1" Type S drywall screws spaced 12" o.c. in the field and 8" o.c. at the wallboard ends. Wallboard joints to be taped and covered with joint compound. | — | — | — | Varies | — | — | — | 5/8 |
| 26. Wood I-joist (minimum I-joist depth 9¼" with a minimum flange thickness of 1½" and a minimum flange cross-sectional area of 2.25 square inches; minimum web thickness of 3/8") @ 24" o.c. | 26-1.1 | Two layers of ½" Type X gypsum wallboard applied with the long dimension perpendicular to the I-joists with end joints staggered. The base layer is fastened with 15/8" Type S drywall screws spaced 12" o.c. and the face layer is fastened with 2" Type S drywall screws spaced 12" o.c. in the field and 8" o.c. on the edges. Face layer end joints shall not occur on the same I-joist as base layer end joints and edge joints shall be offset 24" from base layer joints. Face layer to also be attached to base layer with 1½" Type G drywall screws spaced 8” o.c. placed 6" from face layer end joints. Face layer wallboard joints to be taped and covered with joint compound. | — | — | — | Varies | — | — | — | 1 |
| 27. Wood I-joist (minimum I-joist depth 9½" with a minimum flange depth of 115/16" and a minimum flange cross-sectional area of 1.95 square inches; minimum web thickness of 3/8") @ 24" o.c. | 27-1.1 | Minimum 0.019" thick resilient channel 16" o.c. (channels doubled at wallboard end joints), placed perpendicular to the joist and attached to each joist by 1⅝" Type S drywall screws. Two layers of ½" Type X gypsum wallboard applied with the long dimension perpendicular to the I-joists with end joints staggered. The base layer is fastened with 1¼" Type S drywall screws spaced 12" o.c. and the face layer is fastened with 1⅝" Type S drywall screws spaced 12" o.c. Face layer end joints shall not occur on the same I-joist as base layer end joints and edge joints shall be offset 24" from base layer joints. Face layer to also be attached to base layer with 1½" Type G drywall screws spaced 8" o.c. placed 6" from face layer end joints. Face layer wallboard joints to be taped and covered with joint compound. | — | — | — | Varies | — | — | — | 1 |
| 28. Wood I-joist (minimum I-joist depth 9¼" with a minimum flange depth of 1½" and a minimum flange cross-sectional area of 2.25 square inches; minimum web thickness of 3/8") @ 24" o.c. Unfaced fiberglass insulation or mineral wool insulation is installed between the I-joists supported on the upper surface of the flange by stay wires spaced 12" o.c. | 28-1.1 | Base layer of 5/8" Type C gypsum wallboard attached directly to I-joists with 1⅝" Type S drywall screws spaced 12" o.c. with ends staggered. Minimum 0.0179" thick hat-shaped 7/8-inch furring channel 16" o.c. (channels doubled at wallboard end joints), placed perpendicular to the joist and attached to each joist by 1⅝" Type S drywall screws after the base layer of gypsum wallboard has been applied. The middle and face layers of 5/8" Type C gypsum wallboard applied perpendicular to the channel with end joints staggered. The middle layer is fastened with 1" Type S drywall screws spaced 12" o.c. The face layer is applied parallel to the middle layer but with the edge joints offset 24" from those of the middle layer and fastened with 1⅝" Type S drywall screws 8" o.c. The joints shall be taped and covered with joint compound. | — | — | — | Varies | — | — | 2¾ | — |
| 29. Channel-shaped 18 gage steel joists (minimum depth 8") spaced a maximum 24" o.c. supporting tongue-and-groove wood structural panels (nominal minimum 3/4" thick) applied perpendicular to framing members. Structural panels attached with 1⅝" Type S-12 screws spaced 12" o.c. | 29-1.1 | Base layer 5/8" Type X gypsum board applied perpendicular to bottom of framing members with 1⅛" Type S-12 screws spaced 12" o.c. Second layer 5/8" Type X gypsum board attached perpendicular to framing members with 1⅝" Type S-12 screws spaced 12" o.c. Second layer joints offset 24" from base layer. Third layer 5/8" Type X gypsum board attached perpendicular to framing members with 2⅜" Type S-12 screws spaced 12" o.c. Third layer joints offset 12" from second layer joints. Hat-shaped 7/8-inch rigid furring channels applied at right angles to framing members over third layer with two 2⅜" Type S-12 screws at each framing member. Face layer 5/8" Type X gypsum board applied at right angles to furring channels with 1⅛" Type S screws spaced 12" o.c. | — | — | Varies | — | — | — | 33/8 | — |
| 30. Wood I-joist (minimum I-joist depth 91/2" with a minimum flange depth of 11/2" and a minimum flange cross-sectional area of 2.25 square inches, minimum web thickness of 3/8") @ 24" o.c. Fiberglass insulation placed between I-joists supported by the resilient channels. | 30-1.1 | Minimum 0.019" thick resilient channel 16" o.c. (channels doubled at wallboard end joints), placed perpendicular to the joists and attached to each joist by 11/4" Type S drywall screws. Two layers of 1/2" Type X gypsum wallboard applied with the long dimension perpendicular to the I-joists with end joints staggered. The base layer is fastened with 11/4" Type S drywall screws spaced 12" o.c. and the face layer is fastened with 15/8" Type S drywall screws spaced 12" o.c. Face layer end joints shall not occur on the same I-joist as base layer end joints and edge joints shall be offset 24" from base layer joints. Face layer to be attached to base layer with 11/2" Type G drywall screws spaced 8" o.c. placed 6" from face layer end joints. Face layer wallboard joints to be taped and covered with joint compound. | — | — | Varies | — | — | — | — | 1 |

[Table 720.1(3) Notes.]

For SI: 1 inch = 25.4 mm, 1 foot = 304.8 mm, 1 pound = 0.454 kg, 1 cubic foot = 0.0283m3, 1 pound per square inch = 6.895 kPa = 1 pound per lineal foot = 1.4882 kg/m.

- Staples with equivalent holding power and penetration shall be permitted to be used as alternate fasteners to nails for attachment to wood framing.

- [When] Where the slab is in an unrestrained condition, minimum reinforcement cover shall be not [be] less than 15/8 inches for 4[-hour] hours (siliceous aggregate only); 11/4 inches for 4[-] and 3[-hour] hours; 1 inch for 2[-hour] hours (siliceous aggregate only); and 3/4 inch for all other restrained and unrestrained conditions.

- For all of the construction with gypsum wallboard described in this table, gypsum base for veneer plaster of the same size, thickness and core type shall be permitted to be substituted for gypsum wallboard, provided attachment is identical to that specified for the wallboard, and the joints on the face layer are reinforced and the entire surface is covered with [a minimum of] not less than 1/16-inch gypsum veneer plaster.

- Slab thickness over steel joists measured at the joists for metal lath form and at the top of the form for steel form units.

- (a) The maximum allowable stress level for H-Series joists shall not exceed 22,000 psi.

(b) The allowable stress for K-Series joists shall not exceed 26,000 psi, the nominal depth of such joist shall be not [be] less than 10 inches and the nominal joist weight shall be not [be] less than 5 pounds per [lineal] linear foot.

- Cement plaster with 15 pounds of hydrated lime and 3 pounds of approved additives or admixtures per bag of cement.

- Gypsum wallboard ceilings attached to steel framing shall be permitted to be suspended with 11/2-inch cold-formed carrying channels spaced 48 inches on center[, which] that are suspended with No.8 SWG galvanized wire hangers spaced 48 inches on center. Cross-furring channels are tied to the carrying channels with No.18 SWG galvanized wire hangers spaced 48 inches on center. Cross-furring channels are tied to the carrying channels with No. 18 SWG galvanized wire (double strand) and spaced as required for direct attachment to the framing. This alternative is [also] applicable to those steel framing assemblies recognized under Note q.

- Six-inch hollow clay tile with 2-inch concrete slab above.

- Four-inch hollow clay tile with 11/2-inch concrete slab above.

- Thickness measured to bottom of steel form units.

- Five-eighths inch of vermiculite gypsum plaster plus 1/2 inch of approved vermiculite acoustical plastic.

- Furring channels spaced 12 inches on center.

m.	Double wood floor shall be permitted to be either of the following:

- Subfloor of 1-inch nominal boarding, a layer of asbestos paper weighing not less than 14 pounds per 100 square feet and a layer of 1-inch nominal tongue-and-groove finished flooring; or

- Subfloor of 1-inch nominal tongue-and-groove boarding or 15/32-inch wood structural panels with exterior glue and a layer of 1-inch nominal tongue-and-groove finished flooring or 19/32-inch wood structural panel finish flooring or a layer of Type I GradeM-1 particleboard not less than5/8-inch thick.

- The ceiling shall be permitted to be omitted over unusable space, and flooring shall be permitted to be omitted where unusable space occurs above.

- For properties of cooler or wallboard nails, see ASTM C 514, ASTM C 547 or ASTM F 1667.

- Thickness measured on top of steel deck unit.

- Generic fire-resistance ratings (those not designated as PROPRIETARY* in the listing) in the GA 600 shall be accepted as if herein listed.

[720.1.1] 721.1.1 Thickness of protective coverings. The thickness of fire-resistant materials required for protection of structural members shall be not less than set forth in Table [720.1(1)] 721.1(1), except as modified in this section. The figures shown shall be the net thickness of the protecting materials and shall not include any hollow space in back of the protection.

[720.1.2] 721.1.2 Unit masonry protection. Where required, metal ties shall be embedded in bed joints of unit masonry for protection of steel columns. Such ties shall be as set forth in Table [720.1(1)] 721.1(1) or be equivalent thereto.

[720.1.3] 721.1.3 Reinforcement for cast-in-place concrete column protection. Cast-in-place concrete protection for steel columns shall be reinforced at the edges of such members with wire ties of not less than 0.18 inch (4.6 mm) in diameter wound spirally around the columns on a pitch of not more than 8 inches (203 mm) or by equivalent reinforcement.

[720.1.4] 721.1.4 Plaster application. The finish coat is not required for plaster protective coatings where [they] such coatings comply with the design mix and thickness requirements of Tables [720.1(1)] 721.1(1), [720.1(2)] 721.1(2), and [720.1(3)] 721.1(3).

[720.1.5] 721.1.5 Bonded prestressed concrete tendons. For members having a single tendon or more than one tendon installed with equal concrete cover measured from the nearest surface, the cover shall be not [be] less than that set forth in Table [720.1(1)] 721.1(1). For members having multiple tendons installed with variable concrete cover, the average tendon cover shall be not [be] less than that set forth in Table [720.1(1)] 721.1(1), provided:

1.	The clearance from each tendon to the nearest exposed surface is used to determine the average cover.

2.	In no case can the clear cover for individual tendons be less than one-half of that set forth in Table [720.1(1)] 721.1(1). A minimum cover of 3/4 inch (19.1 mm) for slabs and 1 inch (25 mm) for beams is required for any aggregate concrete.

3.	For the purpose of establishing a fire-resistance rating, tendons having a clear covering less than that set forth in Table [720.1(1)] 721.1(1) shall not contribute more than 50 percent of the required ultimate moment capacity for members less than 350 square inches (0.226 m2) in cross-sectional area and 65 percent for larger members. For structural design purposes, however, tendons having a reduced cover are assumed to be fully effective.

SECTION BC [721] 722
CALCULATED FIRE RESISTANCE

[721.1] 722.1 General. The provisions of this section contain procedures by which the fire resistance of specific materials or combinations of materials is established by calculations. These procedures apply only to the information contained in this section and shall not be otherwise used. The calculated fire resistance of concrete, concrete masonry[,] and clay masonry assemblies shall be permitted in accordance with ACI 216.1/TMS [0216.1] 216. The calculated fire resistance of steel assemblies shall be permitted in accordance with Chapter 5 of [ASCE/SEI 29] ASCE 29. The calculated fire resistance of exposed wood members and wood decking shall be permitted in accordance with Chapter 16 of [ANSI/AF&PA] ANSI/AWC National Design Specification for Wood Construction (NDS).

[721.1.1] 722.1.1 Definitions. The following [words and] terms [shall, for the purposes of this chapter and as used elsewhere] are defined in [this code, have the meanings shown herein.] Chapter 2:

CERAMIC FIBER BLANKET. [A mineral wool insulation material made of alumina-silica fibers and weighing 4 to 10 pounds per cubic foot (pcf) (64 to 160 kg/m3).]

CONCRETE, CARBONATE AGGREGATE. [Concrete made with aggregates consisting mainly of calcium or magnesium carbonate, such as limestone or dolomite, and containing 40 percent or less quartz, chert, or flint.]

CONCRETE, CELLULAR. [A lightweight insulating concrete made by mixing a preformed foam with portland cement slurry and having a dry unit weight of approximately 30 pcf (480 kg/m3).]

CONCRETE, LIGHTWEIGHT AGGREGATE. [Concrete made with aggregates of expanded clay, shale, slag or slate or sintered fly ash or any natural lightweight aggregate meeting ASTM C 330 and possessing equivalent fire-resistance properties and weighing 85 to 115 pcf (1360 to 1840 kg/m3).]

CONCRETE, PERLITE. [A lightweight insulating concrete having a dry unit weight of approximately 30 pcf (480 kg/m3) made with perlite concrete aggregate. Perlite aggregate is produced from a volcanic rock which, when heated, expands to form a glass-like material of cellular structure.]

CONCRETE, SAND-LIGHTWEIGHT. [Concrete made with a combination of expanded clay, shale, slag, slate, sintered fly ash, or any natural lightweight aggregate meeting ASTM C 330 and possessing equivalent fire-resistance properties and natural sand. Its unit weight is generally between 105 and 120 pcf (1680 and 1920 kg/m3).]

CONCRETE, SILICEOUS AGGREGATE. [Concrete made with normal-weight aggregates consisting mainly of silica or compounds other than calcium or magnesium carbonate, which contains more than 40-percent quartz, chert, or flint.]

CONCRETE, VERMICULITE. [A lightweight insulating concrete made with vermiculite concrete aggregate which is laminated micaceous material produced by expanding the ore at high temperatures. When added to a portland cement slurry the resulting concrete has a dry unit weight of approximately 30 pcf (480 kg/m3).]

GLASS FIBERBOARD. [Fibrous glass roof insulation consisting of inorganic glass fibers formed into rigid boards using a binder. The board has a top surface faced with asphalt and kraft reinforced with glass fiber.]

MINERAL BOARD. [A rigid felted thermal insulation board consisting of either felted mineral fiber or cellular beads of expanded aggregate formed into flat rectangular units.]

[721.2] 722.2 Concrete assemblies. The provisions of this section contain procedures by which the fire-resistance ratings of concrete assemblies are established by calculations.

[721.2.1] 722.2.1 Concrete walls. Cast-in-place and precast concrete walls shall comply with Section [721.2.1.1] 722.2.1.1. Multiwythe concrete walls shall comply with Section [721.2.1.2] 722.2.1.2. Joints between precast panels shall comply with Section [721.2.1.3] 722.2.1.3. Concrete walls with gypsum wallboard or plaster finish shall comply with Section [721.2.1.4] 722.2.1.4.

[721.2.1.1] 722.2.1.1 Cast-in-place or precast walls. The minimum equivalent [thickness] thicknesses of cast-in-place or precast concrete walls for fire-resistance ratings of 1 hour to 4 hours are shown in Table [721.2.1.1] 722.2.1.1. For solid walls with flat vertical surfaces, the equivalent thickness is the same as the actual thickness. The values in Table [721.2.1.1] 722.2.1.1 apply to plain, reinforced or prestressed concrete walls.

| TABLE [721.1.1] 722.2.1.1 MINIMUM EQUIVALENT THICKNESS OF CAST-IN-PLACE OR PRECAST CONCRETE WALLS, LOAD BEARING OR NONLOAD-BEARING |
| --- |
| CONCRETE TYPE | MINIMUM SLAB THICKNESS (inches) FOR FIRE-RESISTANCE RATING OF |
|  | [1-hour] 1 hour | 11/2[-hour] hours | 2[-hour] hours | 3[-hour] hours | 4[-hour] hours |
| Siliceous | 3.5 | 4.3 | 5.0 | 6.2 | 7.0 |
| Carbonate | 3.2 | 4.0 | 4.6 | 5.7 | 6.6 |
| Sand-[Lightweight] lightweight | 2.7 | 3.3 | 3.8 | 4.6 | 5.4 |
| Lightweight | 2.5 | 3.1 | 3.6 | 4.4 | 5.1 |

For SI: 1 inch = 25.4 mm.

[721.2.1.1.1] 722.2.1.1.1 Hollow-core precast wall panels. For hollow-core precast concrete wall panels in which the cores are of constant cross section throughout the length, calculation of the equivalent thickness by dividing the net cross-sectional area (the gross cross section minus the area of the cores) of the panel by its width shall be permitted.

[721.2.1.1.2] 722.2.1.1.2 Core spaces filled. Where all of the core spaces of hollow-core wall panels are filled with loose-fill material, such as expanded shale, clay[,] or slag, or vermiculite or perlite, the fire-resistance rating of the wall is the same as that of a solid wall of the same concrete type and of the same overall thickness.

[721.2.1.1.3] 722.2.1.1.3 Tapered cross sections. The thickness of panels with tapered cross sections shall be that determined at a distance 2t or 6 inches (152 mm), whichever is less, from the point of minimum thickness, where t is the minimum thickness.

[721.2.1.1.4] 722.2.1.1.4 Ribbed or undulating surfaces. The equivalent thickness of panels with ribbed or undulating surfaces shall be determined by one of the following expressions:

For s ≥ 4t, the thickness to be used shall be t

For s ≤ 2t, the thickness to be used shall be te

For 4t> s> 2t, the thickness to be used shall be

(Equation 7-3)

where:

Spacing of ribs or undulations.

Minimum thickness.

Equivalent thickness of the panel calculated as the net cross-sectional area of the panel divided by the width, in which the maximum thickness used in the calculation shall not exceed 2t.

[721.2.1.2] 722.2.1.2 Multiwythe walls. For walls that consist of two wythes of different types of concrete, the fire-resistance ratings shall be permitted to be determined from Figure [721.2.1.2] 722.2.1.2.

For SI: 1 inch = 25.4 mm.

FIGURE [721.2.1.2] 722.2.1.2
FIRE-RESISTANCE RATINGS OF
TWO-WYTHE CONCRETE WALLS

[721.2.1.2.1] 722.2.1.2.1 Two or more wythes. The fire-resistance rating for wall panels consisting of two or more wythes shall be permitted to be determined by the formula:

(Equation 7-4)

where:

The fire endurance of the assembly, minutes.

The fire endurances of the individual wythes, minutes. Values of Rn0.59 for use in Equation 7-4 are given in Table [721.2.1.2(1)] 722.2.1.2(1). Calculated fire-resistance ratings are shown in Table [721.2.1.2(2)] 722.2.1.2(2).

| TABLE [721.2.1.2(1)] 722.2.1.2(1) VALUES OF Rn0.59 FOR USE IN EQUATION 7-4 |
| --- |
| TYPE OF MATERIAL | THICKNESS OF MATERIAL (inches) |
|  | 11/2 | 2 | 21/2 | 3 | 31/2 | 4 | 41/2 | 5 | 51/2 | 6 | 61/2 | 7 |
| Siliceous aggregate concrete | 5.3 | 6.5 | 8.1 | 9.5 | 11.3 | 13.0 | 14.9 | 16.9 | 18.8 | 20.7 | 22.8 | 25.1 |
| Carbonate aggregate concrete | 5.5 | 7.1 | 8.9 | 10.4 | 12.0 | 14.0 | 16.2 | 18.1 | 20.3 | 21.9 | 24.7 | 27.2c |
| Sand-lightweight concrete | 6.5 | 8.2 | 10.5 | 12.8 | 15.5 | 18.1 | 20.7 | 23.3 | 26.0c | Note c | Note c | Note c |
| Lightweight concrete | 6.6 | 8.8 | 11.2 | 13.7 | 16.5 | 19.1 | 21.9 | 24.7 | 27.8c | Note c | Note c | Note c |
| Insulating concretea | 9.3 | 13.3 | 16.6 | 18.3 | 23.1 | 26.5c | Note c | Note c | Note c | Note c | Note c | Note c |
| Airspaceb | __ | __ | __ | __ | __ | __ | __ | __ | __ | __ | __ | __ |

For SI: 1 inch = 25.4 mm, 1 pound per cubic foot = 16.02 kg/m3.

a.	Dry unit weight of 35 pcf or less and consisting of cellular, perlite or vermiculite concrete.

b.	The Rn0.59 value for one 1/2″ to 31/2″ airspace is 3.3. The Rn0.59 value for two 1/2″ to 31/2″ airspaces is 6.7.

c.	The fire-resistance rating for this thickness exceeds 4 hours.

| TABLE [721.2.1.2(2)] 722.2.1.2(2) FIRE-RESISTANCE RATINGS BASED ON R0.59 |
| --- |
| Ra, MINUTES | R0.59 |
| 60 | 11.20 |
| 120 | 16.85 |
| 180 | 21.41 |
| 240 | 25.37 |

a. Based on Equation 7-4.

[721.2.1.2.2] 722.2.1.2.2 Foam plastic insulation. The fire-resistance ratings of precast concrete wall panels consisting of a layer of foam plastic insulation sandwiched between two wythes of concrete shall be permitted to be determined by use of Equation 7-4. Foam plastic insulation with a total thickness of less than 1 inch (25 mm) shall be disregarded. The Rn value for thickness of foam plastic insulation of 1 inch (25 mm) or greater, for use in the calculation, is 5 minutes; therefore Rn0.59 = 2.5.

[721.2.1.3] 722.2.1.3 Joints between precast wall panels. Joints between precast concrete wall panels [which] that are not insulated as required by this section shall be considered as openings in walls. Uninsulated joints shall be included in determining the percentage of openings permitted by Table [704.8] 705.8. Where openings are not permitted or are required by this code to be protected, the provisions of this section shall be used to determine the amount of joint insulation required. Insulated joints shall not be considered openings for purposes of determining compliance with the allowable percentage of openings in Table [704.8] 705.8.

[721.2.1.3.1] 722.2.1.3.1 Ceramic fiber joint protection. Figure [721.2.1.3.1] 722.2.1.3.1 shows thicknesses of ceramic fiber blankets to be used to insulate joints between precast concrete wall panels for various panel thicknesses and for joint widths of 3/8 inch (9.5 mm) and 1 inch (25 mm) for fire-resistance ratings of 1 hour to 4 hours. For joint widths between 3/8 inch (9.5 mm) and 1 inch (25 mm), the thickness of ceramic fiber blanket is allowed to be determined by direct interpolation. Other tested and labeled materials are acceptable in place of ceramic fiber blankets.

For SI: 1 inch = 25.4 mm.

FIGURE [721.2.1.3.1] 722.2.1.3.1
CERAMIC FIBER JOINT PROTECTION

[721.2.1.4] 722.2.1.4 Walls with gypsum wallboard or plaster finishes. The fire-resistance rating of cast-in-place or precast concrete walls with finishes of gypsum wallboard or plaster applied to one or both sides shall be permitted to be calculated in accordance with the provisions of this section.

[721.2.1.4.1] 722.2.1.4.1 Nonfire-exposed side. Where the finish of gypsum wallboard or plaster is applied to the side of the wall not exposed to fire, the contribution of the finish to the total fire-resistance rating shall be determined as follows: The thickness of the finish shall first be corrected by multiplying the actual thickness of the finish by the applicable factor determined from Table [721.2.1.4(1)] 722.2.1.4(1) based on the type of aggregate in the concrete. The corrected thickness of finish shall then be added to the actual or equivalent thickness of concrete and fire-resistance rating of the concrete and finish determined from [Table 721.2.1.1, Figure 721.2.1.2 or Table 721.2.1.2(1)] Tables 722.2.1.1, and 722.2.1.2(1) and Figure 722.2.1.2.

| TABLE [721.2.1.4(1)] 722.2.1.4(1) MULTIPLYING FACTOR FOR FINISHES ON NONFIRE-EXPOSED SIDE OF WALL |
| --- |
| TYPE OF FINISH APPLIED TO CONCRETE OR CONCRETE MASONRY WALL | TYPE OF AGGREGATE USED IN CONCRETE OR CONCRETE MASONRY |
|  | Concrete: siliceous or carbonate Concrete Masonry: siliceous or carbonate; solid clay brick | Concrete: sand-lightweight Concrete Masonry: clay tile; hollow clay brick; concrete masonry units of expanded shale and < 20% sand | Concrete: lightweight Concrete Masonry: concrete masonry units of expanded shale, expanded clay, expanded slag, or pumice < 20% sand | Concrete Masonry: concrete masonry units of expanded slag, expanded clay, or pumice |
| Portland cement-sand plaster | 1.00 | 0.75a | 0.75a | 0.50a |
| Gypsum-sand plaster | 1.25 | 1.00 | 1.00 | 1.00 |
| Gypsum-vermiculite or perlite plaster | 1.75 | 1.50 | 1.25 | 1.25 |
| Gypsum wallboard | 3.00 | 2.25 | 2.25 | 2.25 |

For SI: 1 inch = 25.4 mm.

a.	For portland cement-[sandplaster] sand plaster 5/8 inch or less in thickness and applied directly to the masonry on the nonfire-exposed side of the wall, the multiplying factor shall be 1.00.

| TABLE [721.2.1.4(2)] 722.2.1.4(2) TIME ASSIGNED TO FINISH MATERIALS ON FIRE-EXPOSED SIDE OF WALL |
| --- |
| FINISH DESCRIPTION | TIME (minute) |
| Gypsum wallboard | 10 |
| 3/8 inch | 10 |
| 1/2 inch | 15 |
| 5/8 inch | 20 |
| 2 layers of 3/8 inch | 25 |
| 1 layer of 3/8 inch, 1 layer of 1/2 inch | 35 |
| 2 layers of 1/2 inch | 40 |
| Type X gypsum wallboard |  |
| 1/2 inch | 25 |
| 5/8 inch | 40 |
| Portland cement-sand plaster applied directly to concrete masonry | See Note a |
| Portland cement-sand plaster on metal lath |  |
| 3/4 inch | 20 |
| 7/8 inch | 25 |
| 1 inch | 30 |
| Gypsum sand plaster on 3/8-inch gypsum lath |  |
| 1/2 inch | 35 |
| 5/8 inch | 40 |
| 3/4 inch | 50 |
| Gypsum sand plaster on metal lath |  |
| 3/4 inch | 50 |
| 7/8 inch | 60 |
| 1 inch | 80 |

For SI: 1 inch = 25.4 mm.

a.	The actual thickness of portland cement-sand plaster, provided it is 5/8 inch or less in thickness, shall be permitted to be included in determining the equivalent thickness of the masonry for use in Table [721.3.2] 722.3.2.

[721.2.1.4.2] 722.2.1.4.2 Fire-exposed side. Where gypsum wallboard or plaster is applied to the fire-exposed side of the wall, the contribution of the finish to the total fire-resistance rating shall be determined as follows: The time assigned to the finish as established by Table [721.2.1.4(2)] 722.2.1.4(2) shall be added to the fire-resistance rating determined from [Table 721.2.1.1 or Figure 721.2.1.2, or Table 721.2.1.2(1)] Tables 722.2.1.1 and 722.2.1.2(1) and Figure 722.2.1.2 for the concrete alone, or to the rating determined in Section [721.2.1.4.1] 722.2.1.4.1 for the concrete and finish on the nonfire-exposed side.

[721.2.1.4.3] 722.2.1.4.3 Nonsymmetrical assemblies. For a wall having no finish on one side or different types or thicknesses of finish on each side, the calculation procedures of Sections [721.2.1.4.1] 722.2.1.4.1 and [721.2.1.4.2] 722.2.1.4.2 shall be performed twice, assuming either side of the wall to be the fire-exposed side. The fire-resistance rating of the wall shall not exceed the lower of the two values.

Exception: For an exterior wall with a fire separation distance greater than 5 feet (1524 mm), the fire shall be assumed to occur on the interior side only.

[721.2.1.4.4] 722.2.1.4.4 Minimum concrete fire-resistance rating. Where finishes applied to one or both sides of a concrete wall contribute to the fire-resistance rating, the concrete alone shall provide not less than one-half of the total required fire-resistance rating. Additionally, the contribution to the fire resistance of the finish on the nonfire-exposed side of a load-bearing wall shall not exceed one-half the contribution of the concrete alone.

[721.2.1.4.5] 722.2.1.4.5 Concrete finishes. Finishes on concrete walls that are assumed to contribute to the total fire-resistance rating of the wall shall comply with the installation requirements of Section [721.3.2.5] 722.3.2.5.

[721.2.2] 722.2.2 Concrete floor and roof slabs. Reinforced and prestressed floors and roofs shall comply with Section [721.2.2.1] 722.2.2.1. Multicourse floors and roofs shall comply with Sections [721.2.2.2] 722.2.2.2 and [721.2.2.3] 722.2.2.3, respectively.

[721.2.2.1] 722.2.2.1 Reinforced and prestressed floors and roofs. The minimum thicknesses of reinforced and prestressed concrete floor or roof slabs for fire-resistance ratings of 1 hour to 4 hours are shown in Table [721.2.2.1] 722.2.2.1.

Exception: Minimum thickness shall not be required for floors and ramps within open and enclosed parking garages constructed in accordance with Section 406.

| TABLE [721.2.2.1] 722.2.2.1 MINIMUM SLAB THICKNESS (inches) |
| --- |
| CONCRETE TYPE | FIRE-RESISTANCE RATING ([hour] hours) |
|  | 1 | 11/2 | 2 | 3 | 4 |
| Siliceous | 3.5 | 4.3 | [5.0] 5 | 6.2 | [7.0] 7 |
| Carbonate | 3.2 | [4.0] 4 | 4.6 | 5.7 | 6.6 |
| Sand-lightweight | 2.7 | 3.3 | 3.8 | 4.6 | 5.4 |
| Lightweight | 2.5 | 3.1 | 3.6 | 4.4 | 5.1 |

For SI: 1 inch = 25.4 mm.

[721.2.2.1.1] 722.2.2.1.1 Hollow-core prestressed slabs. For hollow-core prestressed concrete slabs in which the cores are of constant cross section throughout the length, the equivalent thickness shall be permitted to be obtained by dividing the net cross-sectional area of the slab including grout in the joints, by its width.

[721.2.2.1.2] 722.2.2.1.2 Slabs with sloping soffits. The thickness of slabs with sloping soffits (see Figure [721.2.2.1.2] 722.2.2.1.2) shall be determined at a distance 2t or 6 inches (152 mm), whichever is less, from the point of minimum thickness, where t is the minimum thickness.

For SI: 1 inch = 25.4 mm

FIGURE [721.2.2.1.2] 722.2.2.1.2
DETERMINATION OF SLAB THICKNESS
FOR SLOPING SOFFITS

[721.2.2.1.3] 722.2.2.1.3 Slabs with ribbed soffits. The thickness of slabs with ribbed or undulating soffits (see Figure [721.2.2.1.3] 722.2.2.1.3) shall be determined by one of the following expressions, whichever is applicable:

For s ≥ 4t, the thickness to be used shall be t

For s < 2t, the thickness to be used shall be te

For 4t > s > 2t, the thickness to be used shall be

(Equation 7-5)

where:

Spacing of ribs or undulations.

Minimum thickness.

Equivalent thickness of the slab calculated as the net area of the slab divided by the width, in which the maximum thickness used in the calculation shall not exceed 2t.

For SI: 1 inch = 25.4 mm.

FIGURE [721.2.2.1.3] 722.2.2.1.3
SLABS WITH RIBBED OR UNDULATING SOFFITS

[721.2.2.2] 722.2.2.2 Multicourse floors. The fire-resistance ratings of floors that consist of a base slab of concrete with a topping (overlay) of a different type of concrete shall comply with Figure [721.2.2.2] 722.2.2.2.

For SI: 1 inch = 25.4 mm.

FIGURE [721.2.2.2] 722.2.2.2
FIRE-RESISTANCE RATINGS FOR TWO-COURSE CONCRETE FLOORS

[721.2.2.3] 722.2.2.3 Multicourse roofs. The fire-resistance ratings of roofs [which] that consist of a base slab of concrete with a topping (overlay) of an insulating concrete or with an insulating board and built-up roofing shall comply with Figures [721.2.2.3(1)] 722.2.2.3(1) and [721.2.2.3(2)] 722.2.2.3(2).

For SI: 1 inch = 25.4 mm.

FIGURE [721.2.2.3(1)] 722.2.2.3(1)
FIRE-RESISTANCE RATINGS FOR CONCRETE
ROOF ASSEMBLIES

For SI: 1 inch = 25.4 mm.

FIGURE [721.2.2.3(2)] 722.2.2.3(2)
FIRE-RESISTANCE RATINGS FOR CONCRETE
ROOF ASSEMBLIES

[721.2.2.3.1] 722.2.2.3.1 Heat transfer. For the transfer of heat, three-ply built-up roofing contributes 10 minutes to the fire-resistance rating. The fire-resistance rating for concrete assemblies such as those shown in Figure [721.2.2.3(1)] 722.2.2.3(1) shall be increased by 10 minutes. This increase is not applicable to those shown in Figure [721.2.2.3(2)] 722.2.2.3(2).

[721.2.2.4] 722.2.2.4 Joints in precast slabs. Joints between adjacent precast concrete slabs need not be considered in calculating the slab thickness provided that a concrete topping [at least] not less than 1 inch (25 mm) thick is used. Where no concrete topping is used, joints must be grouted to a depth of [at least] not less than one-third the slab thickness at the joint, but not less than 1 inch (25 mm), or the joints must be made fire resistant by other approved methods.

[721.2.3] 722.2.3 Concrete cover over reinforcement. The minimum thickness of concrete cover over reinforcement in concrete slabs, reinforced beams and prestressed beams shall comply with this section.

| TABLE [721.2.3(1)] 722.2.3(1) COVER THICKNESS FOR REINFORCED CONCRETE FLOOR OR ROOF SLABS (inches) |
| --- |
| CONCRETE AGGREGATE TYPE | FIRE-RESISTANCE RATING (hours) |
|  | Restrained | Unrestrained |
|  | 1 | 11/2 | 2 | 3 | 4 | 1 | 11/2 | 2 | 3 | 4 |
| Siliceous | 3/4 | 3/4 | 3/4 | 3/4 | 3/4 | 3/4 | 3/4 | 1 | 11/4 | 15/8 |
| Carbonate | 3/4 | 3/4 | 3/4 | 3/4 | 3/4 | 3/4 | 3/4 | 3/4 | 11/4 | 11/4 |
| Sand-lightweight or lightweight | 3/4 | 3/4 | 3/4 | 3/4 | 3/4 | 3/4 | 3/4 | 3/4 | 11/4 | 11/4 |

For SI: 1 inch = 25.4 mm.

| TABLE [721.2.3(2)] 722.2.3(2) COVER THICKNESS FOR PRESTRESSED CONCRETE FLOOR OR ROOF SLABS (inches) |
| --- |
| CONCRETE AGGREGATE TYPE | FIRE-RESISTANCE RATING (hours) |
|  | Restrained | Unrestrained |
|  | 1 | 11/2 | 2 | 3 | 4 | 1 | 11/2 | 2 | 3 | 4 |
| Siliceous | 3/4 | 3/4 | 3/4 | 3/4 | 3/4 | 11/8 | 11/2 | 13/4 | 23/8 | 23/4 |
| Carbonate | 3/4 | 3/4 | 3/4 | 3/4 | 3/4 | 1 | 13/8 | 15/8 | 21/8 | 21/4 |
| Sand-lightweight or lightweight | 3/4 | 3/4 | 3/4 | 3/4 | 3/4 | 1 | 13/8 | 11/2 | 2 | 21/4 |

For SI: 1 inch = 25.4 mm.

| TABLE [721.2.3(3)] 722.2.3(3) MINIMUM COVER FOR MAIN REINFORCING BARS OF REINFORCED CONCRETE BEAMSc (APPLICABLE TO ALL TYPES OF STRUCTURAL CONCRETE) |
| --- |
| RESTRAINED OR UNRESTRAINEDa | BEAM WIDTHb (inches) | FIRE-RESISTANCE RATING (hours) |
|  |  | 1 | 11/2 | 2 | 3 | 4 |
|  | 5 | 3/4 | 3/4 | 3/4 | 1a | 11/4a |
| Restrained | 7 | 3/4 | 3/4 | 3/4 | 3/4 | 3/4 |
|  | ≥10 | 3/4 | 3/4 | 3/4 | 3/4 | 3/4 |
|  | 5 | 3/4 | 1 | 11/4 | — | — |
| Unrestrained | 7 | 3/4 | 3/4 | 3/4 | 13/4 | 3 |
|  | ≥10 | 3/4 | 3/4 | 3/4 | 1 | 13/4 |

For SI: 1 inch = 25.4 mm, 1 foot = 304.8 mm.

- Tabulated values for restrained assemblies apply to beams spaced more than 4 feet on center. For restrained beams spaced 4 feet or less on center, minimum cover of 3/4 inch is adequate for ratings of 4 hours or less.

- For beam widths between the tabulated values, the minimum cover thickness can be determined by direct interpolation.

- The cover for an individual reinforcing bar is the minimum thickness of concrete between the surface of the bar and the fire-exposed surface of the beam. For beams in which several bars are used, the cover for corner bars used in the calculation shall be reduced to one-half of the actual value. The cover for an individual bar must be not less than one-half of the value given in Table [721.2.3(3)] 722.2.3(3) nor less than 3/4 inch.

| TABLE [721.2.3(4)] 722.2.3(4) MINIMUM COVER FOR PRESTRESSED CONCRETE BEAMS 8 INCHES OR GREATER IN WIDTHb |
| --- |
| RESTRAINED OR UNRESTRAINEDa | CONCRETE AGGREGATE TYPE | BEAM WIDTHb (inches) | FIRE-RESISTANCE RATING (hours) |
|  |  |  | 1 | 11/2 | 2 | 3 | 4 |
| Restrained | Carbonate or siliceous | 8 | 11/2 | 11/2 | 11/2 | 13/4a | 21/2a |
|  | Carbonate or siliceous | ≥ 12 | 11/2 | 11/2 | 11/2 | 11/2 | 17/8a |
|  | [Sand lightweight] Sand-lightweight | 8 | 11/2 | 11/2 | 11/2 | 11/2 | 2a |
|  | [Sand lightweight] Sand-lightweight | ≥ 12 | 11/2 | 11/2 | 11/2 | 11/2 | 15/8a |
| Unrestrained | Carbonate or siliceous | 8 | 11/2 | 13/4 | 21/2 | 5c | — |
|  | Carbonate or siliceous | ≥ 12 | 11/2 | 11/2 | 17/8a | 21/2 | 3 |
|  | [Sand lightweight] Sand-lightweight | 8 | 11/2 | 11/2 | 2 | 31/4 | — |
|  | [Sand lightweight] Sand-lightweight | ≥ 12 | 11/2 | 11/2 | 15/8 | 2 | 21/2 |

For SI: 1 inch = 25.4 mm, 1 foot = 304.8 mm.

- Tabulated values for restrained assemblies apply to beams spaced more than 4 feet on center. For restrained beams spaced 4 feet or less on center, minimum cover of 3/4 inch is adequate for 4-hour ratings or less.

- For beam widths between 8 inches and 12 inches, minimum cover thickness can be determined by direct interpolation.

- Not practical for 8-inch-wide beam but shown for purposes of interpolation.

| TABLE [721.2.3(5)] 722.2.3(5) MINIMUM COVER FOR PRESTRESSED CONCRETE BEAMS OF ALL WIDTHS |
| --- |
| RESTRAINED OR UNRESTRAINEDa | CONCRETE AGGREGATE TYPE | BEAM AREAb A (square inches) | FIRE-RESISTANCE RATING (hours) |
|  |  |  | 1 | 11/2 | 2 | 3 | 4 |
| Restrained | All | 40≤A≤ 150 | 11/2 | 11/2 | 2 | 21/2 | — |
|  | Carbonate or siliceous | 150 < A ≤ 300 | 11/2 | 11/2 | 11/2 | 13/4 | 21/2 |
|  |  | 300 < A | 11/2 | 11/2 | 11/2 | 11/2 | 2 |
|  | [Sand lightweight] Sand-lightweight | 150 < A | 11/2 | 11/2 | 11/2 | 11/2 | 2 |
| Unrestrained | All | 40≤ A ≤ 150 | 2 | 21/2 | — | — | — |
|  | Carbonate or siliceous | 150 < A ≤ 300 | 11/2 | 13/4 | 21/2 | — | — |
|  |  | 300 < A | 11/2 | 11/2 | 2 | 3c | 4c |
|  | [Sand lightweight] Sand-lightweight | 150 < A | 11/2 | 11/2 | 2 | 3c | 4c |

For SI: 1 inch = 25.4 mm, 1 foot = 304.8 mm.

a.	Tabulated values for restrained assemblies apply to beams spaced more than 4 feet on center. For restrained beams spaced 4 feet or less on center, minimum cover of 3/4 inch is adequate for 4-hour ratings or less.

b.	The cross-sectional area of a stem is permitted to include a portion of the area in the flange, provided the width of the flange used in the calculation does not exceed three times the average width of the stem.

c.	U-shaped or hooped stirrups spaced not to exceed the depth of the member and having a minimum cover of 1 inch shall be provided.

[721.2.3.1] 722.2.3.1 Slab cover. The minimum thickness of concrete cover to the positive moment reinforcement shall comply with Table [721.2.3(1)] 722.2.3(1) for reinforced concrete and Table [721.2.3(2)] 722.2.3(2) for prestressed concrete. These tables are applicable for solid or hollow-core one-way or two-way slabs with flat undersurfaces. These tables are applicable to slabs that are either cast in place or precast. For precast prestressed concrete not covered elsewhere, the procedures contained in PCI MNL 124 shall be acceptable.

[721.2.3.2] 722.2.3.2 Reinforced beam cover. The minimum thickness of concrete cover to the positive moment reinforcement (bottom steel) for reinforced concrete beams is shown in Table [721.2.3(3)] 722.2.3(3) for fire-resistance ratings of 1 hour to 4 hours.

[721.2.3.3] 722.2.3.3 Prestressed beam cover. The minimum thickness of concrete cover to the positive moment prestressing tendons (bottom steel) for restrained and unrestrained prestressed concrete beams and stemmed units shall comply with the values shown in Tables [721.2.3(4)] 722.2.3(4) and [721.2.3(5)] 722.2.3(5) for fire-resistance ratings of 1 hour to 4 hours. Values in Table [721.2.3(4)] 722.2.3(4) apply to beams 8 inches (203 mm) or greater in width. Values in Table [721.2.3(5)] 722.2.3(5) apply to beams or stems of any width, provided the cross-section area is not less than 40 square inches (25 806 mm2). In case of differences between the values determined from Table [721.2.3(4)] 722.2.3(4) or [721.2.3(5)] 722.2.3(5), it is permitted to use the smaller value. The concrete cover shall be calculated in accordance with Section [721.2.3.3.1] 722.2.3.3.1. The minimum concrete cover for nonprestressed reinforcement in prestressed concrete beams shall comply with Section [721.2.3.2] 722.2.3.2.

[721.2.3.3.1] 722.2.3.3.1 Calculating concrete cover. The concrete cover for an individual tendon is the minimum thickness of concrete between the surface of the tendon and the fire-exposed surface of the beam, except that for [ungrouped] ungrouted ducts, the assumed cover thickness is the minimum thickness of concrete between the surface of the duct and the fire-exposed surface of the beam. For beams in which two or more tendons are used, the cover is assumed to be the average of the minimum cover of the individual tendons. For corner tendons (tendons equal distance from the bottom and side), the minimum cover used in the calculation shall be one-half the actual value. For stemmed members with two or more prestressing tendons located along the vertical centerline of the stem, the average cover shall be the distance from the bottom of the member to the centroid of the tendons. The actual cover for any individual tendon shall be not [be] less than one-half the smaller value shown in Tables [721.2.3(4)] 722.2.3(4) and [721.2.3(5)] 722.2.3(5), or 1 inch (25 mm), whichever is greater.

[721.2.4] 722.2.4 Concrete columns. Concrete columns shall comply with this section.

| TABLE [721.2.4] 722.2.4 MINIMUM DIMENSION OF CONCRETE COLUMNS (inches) |
| --- |
| TYPES OF CONCRETE | FIRE-RESISTANCE RATING (hours) |
|  | 1 | 11/2 | 2a | 3a | 4b |
| Siliceous | 8 | 9 | 10 | 12 | 14 |
| Carbonate | 8 | 9 | 10 | 11 | 12 |
| Sand-lightweight | 8 | 81/2 | 9 | 101/2 | 12 |

For SI: 1 inch = 25 mm.

- The minimum dimension is permitted to be reduced to 8 inches for rectangular columns with two parallel sides at least 36 inches in length.

- The minimum dimension is permitted to be reduced to 10 inches for rectangular columns with two parallel sides at least 36 inches in length.

[721.2.4.1] 722.2.4.1 Minimum size. The minimum overall dimensions of reinforced concrete columns for fire-resistance ratings of 1 hour to 4 hours for exposure to fire on all sides shall comply with this section.

[721.2.4.1.1] 722.2.4.1.1 Concrete strength less than or equal to 12,000 psi. For columns made with concrete having a specified compressive strength, f’c, of less than or equal to 12,000 psi (82.7 MPa), the minimum dimension shall comply with Table [721.2.4] 722.2.4.

[721.2.4.1.2] 722.2.4.1.2 Concrete strength greater than 12,000 psi. For columns made with concrete having a specified compressive strength, f’c, greater than 12,000 psi (82.7 MPa), for fire-resistance ratings of 1 hour to 4 hours the minimum dimension shall be 24 inches (610 mm).

[721.2.4.2] 722.2.4.2 Minimum cover for R/C columns. The minimum thickness of concrete cover to the main longitudinal reinforcement in columns, regardless of the type of aggregate used in the concrete[,] and the specified compressive strength of concrete, f’c, shall be not [be] less than 1 inch (25 mm) times the number of hours of required fire resistance or 2 inches (51 mm), whichever is less.

[721.2.4.3] 722.2.4.3 Tie and spiral reinforcement. For concrete columns made with concrete having a specified compressive strength, f’c, greater than 12,000 psi (82.7 MPa), tie and spiral reinforcement shall comply with the following:

1.	The free ends of rectangular ties shall terminate with a 135-degree (2.4 rad) standard tie hook.

2.	The free ends of circular ties shall terminate with a 90-degree (1.6 rad) standard tie hook.

3.	The free ends of spirals, including at lap splices, shall terminate with a 90-degree (1.6 rad) standard tie hook.

The hook extension at the free end of ties and spirals shall be the larger of six bar diameters and the extension required by Section 7.1.3 of ACI 318. Hooks shall project into the core of the column.

[721.2.4.4] 722.2.4.4 Columns built into walls. The minimum dimensions of Table [721.2.4] 722.2.4 do not apply to a reinforced concrete column that is built into a concrete or masonry wall provided all of the following are met:

1.	The fire-resistance rating for the wall is equal to or greater than the required rating of the column;

2.	The main longitudinal reinforcing in the column has cover not less than that required by Section [721.2.4.2] 722.2.4.2; and

3.	Openings in the wall are protected in accordance with Table [715.4] 716.5.

Where openings in the wall are not protected as required by Section [715.4] 716.5, the minimum dimension of columns required to have a fire-resistance rating of 3 hours or less shall be 8 inches (203 mm), and 10 inches (254 mm) for columns required to have a fire-resistance rating of 4 hours, regardless of the type of aggregate used in the concrete.

[721.2.4.5] 722.2.4.5 Precast cover units for steel columns. See Section [721.5.1.4] 722.5.1.4.

[721.3] 722.3 Concrete masonry. The provisions of this section contain procedures by which the fire-resistance ratings of concrete masonry are established by calculations.

[721.3.1] 722.3.1 Equivalent thickness. The equivalent thickness of concrete masonry construction shall be determined in accordance with the provisions of this section.

[721.3.1.1] 722.3.1.1 Concrete masonry unit plus finishes. The equivalent thickness of concrete masonry assemblies, Tea, shall be computed as the sum of the equivalent thickness of the concrete masonry unit, Te, as determined by Section [721.3.1.2] 722.3.1.2, [721.3.1.3,] 722.3.1.3 or [721.3.1.4] 722.3.1.4, plus the equivalent thickness of finishes, Tef, determined in accordance with Section [721.3.2] 722.3.2:

(Equation 7-6)

[721.3.1.2] 722.3.1.2 Ungrouted or partially grouted construction. Te shall be the value obtained for the concrete masonry unit determined in accordance with ASTM C 140.

[721.3.1.3] 722.3.1.3 Solid grouted construction. The equivalent thickness, Te, of solid grouted concrete masonry units is the actual thickness of the unit.

[721.3.1.4] 722.3.1.4 Airspaces and cells filled with loose-fill material. The equivalent thickness of completely filled hollow concrete masonry is the actual thickness of the unit [when] where loose-fill materials are: sand, pea gravel, crushed stone, or slag that meet ASTM C 33 requirements; pumice, scoria, expanded shale, expanded clay, expanded slate, expanded slag, expanded fly ash, or cinders that comply with ASTM C 331; or perlite or vermiculite meeting the requirements of ASTM C 549 and ASTM C 516, respectively.

[721.3.2] 722.3.2 Concrete masonry walls. The fire-resistance rating of walls and partitions constructed of concrete masonry units shall be determined from Table [721.3.2] 722.3.2. The rating shall be based on the equivalent thickness of the masonry and type of aggregate used.

| TABLE [721.3.2] 722.3.2 MINIMUM EQUIVALENT THICKNESS (inches) OF BEARING OR NONBEARING CONCRETE MASONRY WALLSa,b,c,d |
| --- |
| TYPE OF AGGREGATE | FIRE-RESISTANCE RATING (hours) |
|  | 1/2 | 3/4 | 1 | 11/4 | 11/2 | 13/4 | 2 | 21/4 | 21/2 | 23/4 | 3 | 31/4 | 31/2 | 33/4 | 4 |
| Pumice or expanded slag | 1.5 | 1.9 | 2.1 | 2.5 | 2.7 | 3.0 | 3.2 | 3.4 | 3.6 | 3.8 | 4.0 | 4.2 | 4.4 | 4.5 | 4.7 |
| Expanded shale, clay or slate | 1.8 | 2.2 | 2.6 | 2.9 | 3.3 | 3.4 | 3.6 | 3.8 | 4.0 | 4.2 | 4.4 | 4.6 | 4.8 | 4.9 | 5.1 |
| Limestone, cinders or unexpanded slag | 1.9 | 2.3 | 2.7 | 3.1 | 3.4 | 3.7 | 4.0 | 4.3 | 4.5 | 4.8 | 5.0 | 5.2 | 5.5 | 5.7 | 5.9 |
| Calcareous or siliceous gravel | 2.0 | 2.4 | 2.8 | 3.2 | 3.6 | 3.9 | 4.2 | 4.5 | 4.8 | 5.0 | 5.3 | 5.5 | 5.8 | 6.0 | 6.2 |

For SI: 1 inch = 25.4 mm.

a.	Values between those shown in the table can be determined by direct interpolation.

b.	Where combustible members are framed into the wall, the thickness of solid material between the end of each member and the opposite face of the wall, or between members set in from opposite sides, shall be not [be] less than 93 percent of the thickness shown in the table.

c.	Requirements of ASTM C 55, ASTM C 73, ASTM C 90 or ASTM C 744 shall apply.

d.	Minimum required equivalent thickness corresponding to the hourly fire-resistance rating for units with a combination of aggregate shall be determined by linear interpolation based on the percent by volume of each aggregate used in manufacture.

[721.3.2.1] 722.3.2.1 Finish on nonfire-exposed side. Where plaster or gypsum wallboard is applied to the side of the wall not exposed to fire, the contribution of the finish to the total fire-resistance rating shall be determined as follows: The thickness of gypsum wallboard or plaster shall be corrected by multiplying the actual thickness of the finish by applicable factor determined from Table [721.2.1.4(1)] 722.2.1.4(1). This corrected thickness of finish shall be added to the equivalent thickness of masonry and the fire-resistance rating of the masonry and finish determined from Table [721.3.2] 722.3.2.

[721.3.2.2] 722.3.2.2 Finish on fire-exposed side. Where plaster or gypsum wallboard is applied to the fire-exposed side of the wall, the contribution of the finish to the total fire-resistance rating shall be determined as follows: The time assigned to the finish as established by Table [721.2.1.4(2)] 722.2.1.4(2) shall be added to the fire-resistance rating determined in Section [721.3.2] 722.3.2 for the masonry alone, or in Section [721.3.2.1] 722.3.2.1 for the masonry and finish on the nonfire-exposed side.

[721.3.2.3] 722.3.2.3 Nonsymmetrical assemblies. For a wall having no finish on one side or having different types or thicknesses of finish on each side, the calculation procedures of this section shall be performed twice, assuming either side of the wall to be the fire-exposed side. The fire-resistance rating of the wall shall not exceed the lower of the two values calculated.

Exception: For exterior walls with a fire separation distance greater than 5 feet (1524 mm), the fire shall be assumed to occur on the interior side only.

[721.3.2.4] 722.3.2.4 Minimum concrete masonry fire-resistance rating. Where the finish applied to a concrete masonry wall contributes to its fire-resistance rating, the masonry alone shall provide not less than one-half the total required fire-resistance rating.

[721.3.2.5] 722.3.2.5 Attachment of finishes. Installation of finishes shall be as follows:

1.	Gypsum wallboard and gypsum lath applied to concrete masonry or concrete walls shall be secured to wood or steel furring members spaced not more than 16 inches (406 mm) on center (o.c.).

2.	Gypsum wallboard shall be installed with the long dimension parallel to the furring members and shall have all joints finished.

3.	Other aspects of the installation of finishes shall comply with the applicable provisions of Chapters 7 and 25.

[721.3.3] 722.3.3 Multiwythe masonry walls. The fire-resistance rating of wall assemblies constructed of multiple wythes of masonry materials shall be permitted to be based on the fire-resistance rating period of each wythe and the continuous airspace between each wythe in accordance with the following formula:

(Equation 7-7)

where:

Fire [endurance]-resistance rating of the assembly (hours).

Fire [endurance]-resistance rating of wythes for 1, 2, n (hours), respectively.

0.30, factor for each continuous airspace for 1, 2, ...n, respectively, having a depth of 1/2 inch (12.7 mm) or more between wythes.

[721.3.4] 722.3.4 Concrete masonry lintels. Fire-resistance ratings for concrete masonry lintels shall be determined based upon the nominal thickness of the lintel and the minimum thickness of concrete masonry or concrete, or any combination thereof, covering the main reinforcing bars, as determined [according to] in accordance with Table [721.3.4] 722.3.4, or by approved alternate methods.

| TABLE [721.3.4] 722.3.4 MINIMUM COVER OF LONGITUDINAL REINFORCEMENT IN FIRE-RESISTANCE-RATED REINFORCED CONCRETE MASONRY LINTELS (inches) |
| --- |
| NOMINAL WIDTH OF LINTEL (inches) | FIRE-RESISTANCE RATING (hours) |
|  | 1 | 2 | 3 | 4 |
| 6 | 11/2 | 2 | — | — |
| 8 | 11/2 | 11/2 | 13/4 | 3 |
| 10 or greater | 11/2 | 11/2 | 11/2 | 13/4 |

For SI: 1 inch = 25.4 mm.

[721.3.5] 722.3.5 Concrete masonry columns. The fire-resistance rating of concrete masonry columns shall be determined based upon the least plan dimension of the column in accordance with Table [721.3.5] 722.3.5 or by approved alternate methods.

| TABLE [721.3.5] 722.3.5 MINIMUM DIMENSION OF CONCRETE MASONRY COLUMNS (inches) |
| --- |
| FIRE-RESISTANCE RATING (hours) |
| 1 | 2 | 3 | 4 |
| 8 inches | 10 inches | 12 inches | 14 inches |

For SI: 1 inch = 25.4 mm.

[721.4] 722.4 Clay brick and tile masonry. The provisions of this section contain procedures by which the fire-resistance ratings of clay brick and tile masonry are established by calculations.

[721.4.1] 722.4.1 Masonry walls. The fire-resistance rating of masonry walls shall be based upon the equivalent thickness as calculated in accordance with this section. The calculation shall take into account finishes applied to the wall and airspaces between wythes in multiwythe construction.

| TABLE [721.4.1(1)] 722.4.1(1) FIRE-RESISTANCE PERIODS OF CLAY MASONRY WALLS |
| --- |
| MATERIAL TYPE | MINIMUM REQUIRED EQUIVALENT THICKNESS FOR FIRE RESISTANCEa,b,c (inches) |
|  | 1 hour | 2 [hour] hours | 3 [hour] hours | 4 [hour] hours |
| Solid brick of clay or shaled | 2.7 | 3.8 | 4.9 | 6.0 |
| Hollow brick or tile of clay or shale, unfilled | 2.3 | 3.4 | 4.3 | 5.0 |
| Hollow brick or tile of clay or shale, grouted or filled with materials specified in Section [721.4.1.1.3] 722.4.1.1.3 | 3.0 | 4.4 | 5.5 | 6.6 |

For SI: 1 inch = 25.4 mm.

- Equivalent thickness as determined from Section [721.4.1.1] 722.4.1.1.

- Calculated fire resistance between the hourly increments listed shall be determined by linear interpolation.

- Where combustible members are framed in the wall, the thickness of solid material between the end of each member and the opposite face of the wall, or between members set in from opposite sides, shall be not [be] less than 93 percent of the thickness shown.

- For units in which the net cross-sectional area of cored brick in any plane parallel to the surface containing the cores is at least 75 percent of the gross cross-sectional area measured in the same plane.

| TABLE [721.4.1(2)] 722.4.1(2) FIRE-RESISTANCE RATINGS FOR BEARING STEEL FRAME BRICK VENEER WALLS OR PARTITIONS |
| --- |
| WALL OR PARTITION ASSEMBLY | PLASTER SIDE EXPOSED (hours) | BRICK FACED SIDE EXPOSED (hours) |
| Outside facing of steel studs: 1/2″ wood fiberboard sheathing next to studs, 3/4″ airspace formed with 3/4″ × 15/8″ wood strips placed over the fiberboard and secured to the studs; metal or wire lath nailed to such strips, 33/4″ brick veneer held in place by filling 3/4″ airspace between the brick and lath with mortar. Inside facing of studs: 3/4″unsanded gypsum plaster on metal or wire lath attached to 5/16″ wood strips secured to edges of the studs. | 1.5 | 4 |
| Outside facing of steel studs: 1″ insulation board sheathing attached to studs, 1″ airspace, and 33/4″ brick veneer attached to steel frame with metal ties every 5th course. Inside facing of studs: 7/8″ sanded gypsum plaster (1:2 mix) applied on metal or wire lath attached directly to the studs. | 1.5 | 4 |
| Same as above except use 7/8″ vermiculite—gypsum plaster or 1″ sanded gypsum plaster (1:2 mix) applied to metal or wire. | 2 | 4 |
| Outside facing of steel studs: 1/2″ gypsum sheathing board, attached to studs, and 33/4″ brick veneer attached to steel frame with metal ties every 5th course. Inside facing of studs: 1/2″ sanded gypsum plaster (1:2 mix) applied to 1/2″ perforated gypsum lath securely attached to studs and having strips of metal lath 3 inches wide applied to all horizontal joints of gypsum lath. | 2 | 4 |

For SI: 1 inch = 25.4 mm.

| TABLE [721.4.1(3)] 722.4.1(3) VALUES OF Rn0.59 |
| --- |
| Rn0.59 | R (hours) |
| 1 | 1.0 |
| 2 | 1.50 |
| 3 | 1.91 |
| 4 | 2.27 |

| TABLE [721.4.1(4)] 722.4.1(4) COEFFICIENTS FOR PLASTER, pla |
| --- |
| THICKNESS OF PLASTER (inch) | ONE SIDE | TWO [SIDE] SIDES |
| 1/2 | 0.3 | 0.6 |
| 5/8 | 0.37 | 0.75 |
| 3/4 | 0.45 | 0.90 |

For SI: 1 inch = 25.4 mm.

a.	Values listed in the table are for 1:3 sanded gypsum plaster.

| TABLE [721.4.1(5)] 722.4.1(5) REINFORCED MASONRY LINTELS |
| --- |
| NOMINAL LINTEL WIDTH (inches) | MINIMUM LONGITUDINAL REINFORCEMENT COVER FOR FIRE RESISTANCE ([inch] inches) |
|  | 1 hour | 2 [hour] hours | 3 [hour] hours | 4 [hour] hours |
| 6 | 11/2 | 2 | NP | NP |
| 8 | 11/2 | 11/2 | 13/4 | 3 |
| 10 or more | 11/2 | 11/2 | 11/2 | 13/4 |

For SI: 1 inch = 25.4 mm.

NP = Not permitted.

| TABLE [721.4.1(6)] 722.4.1(6) REINFORCED CLAY MASONRY COLUMNS |
| --- |
| COLUMN SIZE | FIRE-RESISTANCE RATING |
|  | ([hour] hours) |
|  | 1 | 2 | 3 | 4 |
| Minimum column dimension (inches) | 8 | 10 | 12 | 14 |

For SI: 1 inch = 25.4 mm.

[721.4.1.1] 722.4.1.1 Equivalent thickness. The fire-resistance ratings of walls or partitions constructed of solid or hollow clay masonry units shall be determined from Table [721.4.1(1)] 722.4.1(1) or [721.4.1(2)] 722.4.1(2). The equivalent thickness of the clay masonry unit shall be determined by Equation 7-8 [when] where using Table [721.4.1(1)] 722.4.1(1). The fire-resistance rating determined from Table [721.4.1(1)] 722.4.1(1) shall be permitted to be used in the calculated fire-resistance rating procedure in Section [721.4.2] 722.4.2.

(Equation 7-8)

where:

The equivalent thickness of the clay masonry unit (inches).

The net volume of the clay masonry unit (inch3).

The specified length of the clay masonry unit (inches).

The specified height of the clay masonry unit (inches).

[721.4.1.1.1] 722.4.1.1.1 Hollow clay units. The equivalent thickness, Te, shall be the value obtained for hollow clay units as determined in accordance with Equation 7-8. The net volume, Vn, of the units shall be determined using the gross volume and percentage of void area determined in accordance with ASTM C 67.

[721.4.1.1.2] 722.4.1.1.2 Solid grouted clay units. The equivalent thickness of solid grouted clay masonry units shall be taken as the actual thickness of the units.

[721.4.1.1.3] 722.4.1.1.3 Units with filled cores. The equivalent thickness of the hollow clay masonry units is the actual thickness of the unit [when] where completely filled with loose-fill materials of: sand, pea gravel, crushed stone, or slag that meet ASTM C 33 requirements; pumice, scoria, expanded shale, expanded clay, expanded slate, expanded slag, expanded fly ash, or cinders in compliance with ASTM C 331; or perlite or vermiculite meeting the requirements of ASTM C 549 and ASTM C 516, respectively.

[721.4.1.2] 722.4.1.2 Plaster finishes. Where plaster is applied to the wall, the total fire-resistance rating shall be determined by the formula:

(Equation 7-9)

where:

The fire [endurance]-resistance of the assembly (hours).

The fire [endurance]-resistance of the individual wall (hours).

Coefficient for thickness of plaster.

Values for Rn0.59 for use in Equation 7-9 are given in Table [721.4.1(3)] 722.4.1(3). Coefficients for thickness of plaster shall be selected from Table [721.4.1(4)] 722.4.1(4) based on the actual thickness of plaster applied to the wall or partition and whether one or two sides of the wall are plastered.

[721.4.1.3] 722.4.1.3 Multiwythe walls with airspace. Where a continuous airspace separates multiple wythes of the wall or partition, the total fire-resistance rating shall be determined by the formula:

(Equation 7-10)

where:

The fire [endurance]-resistance of the assembly (hours).

The fire [endurance]-resistance of the individual wythes (hours).

Coefficient for continuous airspace.

Values for Rn0.59 for use in Equation 7-10 are given in Table [721.4.1(3)] 722.4.1(3). The coefficient for each continuous airspace of 1/2 inch to 31/2 inches (12.7 to 89 mm) separating two individual wythes shall be 0.3.

[721.4.1.4] 722.4.1.4 Nonsymmetrical assemblies. For a wall having no finish on one side or having different types or thicknesses of finish on each side, the calculation procedures of this section shall be performed twice, assuming either side to be the fire-exposed side of the wall. The fire resistance of the wall shall not exceed the lower of the two values determined.

Exception: For exterior walls with a fire separation distance greater than 5 feet (1524 mm), the fire shall be assumed to occur on the interior side only.

[721.4.2] 722.4.2 Multiwythe walls. The fire-resistance rating for walls or partitions consisting of two or more dissimilar wythes shall be permitted to be determined by the formula:

(Equation 7-11)

where:

The fire [endurance]-resistance of the assembly (hours).

The fire [endurance]-resistance of the individual wythes (hours).

Values for  for use in Equation 7-11 are given in Table [721.4.1(3)] 722.4.1(3).

[721.4.2.1] 722.4.2.1 Multiwythe walls of different material. For walls that consist of two or more wythes of different materials (concrete or concrete masonry units) in combination with clay masonry units, the fire-resistance rating of the different materials shall be permitted to be determined from Table [721.2.1.1] 722.2.1.1 for concrete; Table [721.3.2] 722.3.2 for concrete masonry units or Table [721.4.1(1)] 722.4.1(1) or [721.4.1(2)] 722.4.1(2) for clay and tile masonry units.

[721.4.3] 722.4.3 Reinforced clay masonry lintels. Fire-resistance ratings for clay masonry lintels shall be determined based on the nominal width of the lintel and the minimum covering for the longitudinal reinforcement in accordance with Table [721.4.1(5)] 722.4.1(5).

[721.4.4] 722.4.4 Reinforced clay masonry columns. The fire-resistance ratings shall be determined based on the last plan dimension of the column in accordance with Table [721.4.1(6)] 722.4.1(6). The minimum cover for longitudinal reinforcement shall be 2 inches (51 mm).

[721.5] 722.5 Steel assemblies. The provisions of this section contain procedures by which the fire-resistance ratings of steel assemblies are established by calculations.

[721.5.1] 722.5.1 Structural steel columns. The fire-resistance ratings of structural steel columns shall be based on the size of the element and the type of protection provided in accordance with this section.

FIGURE 721.5.1(1)
DETERMINATION OF THE HEATED PERIMETER
OF STRUCTURAL STEEL COLUMNS

FIGURE 722.5.1(1)
DETERMINATION OF THE HEATED PERIMETER
OF STRUCTURAL STEEL COLUMNS

FIGURE [721.5.1(2)] 722.5.1(2)
[GYPSUM WALLBOARD PROTECTED] GYPSUM-PROTECTED STRUCTURAL STEEL
COLUMNS WITH SHEET STEEL COLUMN COVERS

For SI: 1 inch = 25.4 mm, 1 foot = 305 mm.

- Structural steel column, either wide flange or tubular shapes.

- Type X gypsum [wallboard] board or gypsum panel products in accordance with ASTM C [36. For single-layer applications, the wallboard] 1177, C 1178, C 1278, C 1396 or C 1658. The total thickness of gypsum board or gypsum panel products calculated as h in Section 722.5.1.2 shall be applied vertically to an individual column using one of the following methods:

- As a single layer with no horizontal joints.

- [For] As multiple [-layer applications,] layers with no horizontal joints [are] permitted [at a minimum spacing of 8 feet, provided that the] in any layer.

- As multiple layers with horizontal joints [in successive layers] are staggered [at least] not less than 12 inches[.] vertically between layers and not less than 8 feet vertically in any single layer. The total required thickness of [wallboard] gypsum board or gypsum panel products shall be determined on the basis of the specified fire-resistance rating and the weight-to-heated-perimeter ratio (W/D) of the column. For fire-resistance ratings of 2 hours or less, one of the required layers of gypsum [wallboard] board or gypsum panel product may be applied to the exterior of the sheet steel column covers with 1-inch long Type S screws spaced 1 inch from the wallboard edge and 8 inches on center. For such installations, 0.0149-inch minimum thickness galvanized steel corner beads with 11/2-inch legs shall be attached to the wallboard with Type S screws spaced 12 inches on center.

3.	For fire-resistance ratings of 3 hours or less, the column covers shall be fabricated from 0.0239-inch minimum thickness galvanized or stainless steel. For 4-hour fire-resistance ratings, the column covers shall be fabricated from 0.0239-inch minimum thickness stainless steel. The column covers shall be erected with the Snap Lock or Pittsburgh joint details.

For fire-resistance ratings of 2 hours or less, column covers fabricated from 0.0269-inch minimum thickness galvanized or stainless steel shall be permitted to be erected with lap joints. The lap joints shall be permitted to be located anywhere around the perimeter of the column cover. The lap joints shall be secured with 1/2-inch-long No.8 sheet metal screws spaced 12 inches on center.

The column covers shall be provided with a minimum expansion clearance of 1/8 inch per linear foot between the ends of the cover and any restraining construction.

FIGURE [721.5.1(3)] 722.5.1(3)
[GYPSUM WALLBOARD PROTECTED] GYPSUM-PROTECTED STRUCTURAL STEEL COLUMNS WITH STEEL STUD/SCREW ATTACHMENT SYSTEM

For SI: 1 inch = 25.4 mm, 1 foot = -305 mm.

- Structural steel column, either wide flange or tubular shapes.

- 15/8-inch deep studs fabricated from 0.0179-inch minimum thickness galvanized steel with 15/16 or 17/16-inch legs. The length of the steel studs shall be 1/2 inch less than the height of the assembly.

- Type X gypsum [wallboard] board or gypsum panel products in accordance with ASTM [C 36. For single-layer applications, the wallboard] C 177, C 1178, C 1278, C 1396 or C 1658. The total thickness of gypsum board or gypsum panel products calculated as h in Section 722.5.1.2 shall be applied vertically to an individual column using one of the following methods:

1.	As a single layer with no horizontal joints.

2.	[For] As multiple [-layer applications,] layer with no horizontal joints [are] permitted [at a minimum spacing of 8 feet, provided that the] in any layer.

3.	As multiple layers with horizontal joints [in successive layers are] staggered [at least] not less than 12 inches vertically between layers and not less than 8 feet vertically in any single layer. The total required thickness of [wallboard] gypsum board or gypsum panel products shall be determined on the basis of the specified fire-resistance rating and the weight-to-heated-perimeter ratio (W/D) of the column.

- Galvanized 0.0149-inch minimum thickness steel corner beads with 11/2-inch legs attached to the [wallboard] gypsum board or gypsum panel products with 1-inch-long Type S screws spaced 12 inches on center.

- No. 18 SWG steel tie wires spaced 24 inches on center.

- Sheet metal angles with 2-inch legs fabricated from 0.0221-inch minimum thickness galvanized steel.

- Type S screws, 1 inch long, shall be used for attaching the first layer of [wallboard] gypsum board or gypsum panel product to the steel studs and the third layer to the sheet metal angles at 24 inches on center. Type S screws 13/4-inch long shall be used for attaching the second layer of [wallboard] gypsum board or gypsum panel product to the steel studs and the fourth layer to the sheet metal angles at 12 inches on center. Type S screws 21/4 inches long shall be used for attaching the third layer of [wallboard] gypsum board or gypsum panel product to the steel studs at 12 inches on center.

FIGURE [721.5.1(4)] 722.5.1(4)
FIRE RESISTANCE OF STRUCTURAL STEEL COLUMNS
PROTECTED WITH VARIOUS THICKNESSES OF
TYPE X GYPSUM WALLBOARDa

For SI: 1 inch = 25.4 mm, 1 pound per linear foot/inch = 0.059 kg/m/mm.

a.	The W/D ratios for typical wide flange columns are listed in Table [721.5.1(1)] 722.5.1(1). For other column shapes, the W/D ratios shall be determined in accordance with Section [720.5.1.1] 722.5.1.1.

FIGURE [721.5.1(5)] 722.5.1(5)
WIDE FLANGE STRUCTURAL STEEL COLUMNS WITH
SPRAY-APPLIED FIRE-RESISTANT MATERIALS

FIGURE [721.5.1(6)] 722.5.1(6)
CONCRETE PROTECTED STRUCTURAL STEEL COLUMNSa,b

a.	When the inside perimeter of the concrete protection is not square, L shall be taken as the average of L1 and L2. When the thickness of concrete cover is not constant, h shall be taken as the average of h1 and h2.

b.	Joints shall be protected with a minimum 1 inch thickness of ceramic fiber blanket but in no case less than one-half the thickness of the column cover (see Section [721.2.1.3] 722.2.1.3).

For SI: 1 inch = 25.4 mm.

FIGURE [721.5.1(7)] 722.5.1(7)
CONCRETE OR CLAY MASONRY PROTECTED
STRUCTURAL STEEL COLUMNS

d = Depth of a wide flange column, outside diameter of pipe column, or outside dimension of structural tubing column (inches).

tweb= Thickness of web of wide flange column (inches).

w = Width of flange of wide flange column (inches).

| TABLE [721.5.1(1)] 722.5.1(1) W/D RATIOS FOR STEEL COLUMNS |
| --- |
| STRUCTURAL SHAPE | CONTOUR PROFILE | BOX PROFILE | STRUCTURAL SHAPE | CONTOUR PROFILE | BOX PROFILE |
| W14 × 233 | [2.49] 2.55 | 3.65 | W10 × 112 | [1.78] 1.81 | 2.57 |
| × 211 | [2.28] 2.32 | 3.35 | × 100 | [1.61] 1.64 | 2.33 |
| × 193 | [2.10] 2.14 | 3.09 | × 88 | [1.43] 1.45 | 2.08 |
| × 176 | [1.93] 1.96 | 2.85 | × 77 | [1.26] 1.28 | 1.85 |
| × 159 | [1.75] 1.78 | 2.60 | × 68 | [1.13] 1.15 | 1.66 |
| × 145 | [1.61] 1.64 | 2.39 | × 60 | [1.00] 1.01 | 1.48 |
| × 132 | [1.52] 1.56 | 2.25 | × 54 | [0.91] 0.922 | 1.34 |
| × 120 | [1.39] 1.42 | 2.06 | × 49 | [0.83] 0.84 | 1.23 |
| × 109 | [1.27] 1.29 | 1.88 | × 45 | [0.87] 0.888 | 1.24 |
| × 99 | [1.16] 1.18 | 1.72 | × 39 | [0.76] 0.78 | 1.09 |
| × 90 | [1.06] 1.08 | 1.58 | × 33 | [0.65] 0.661 | 0.93 |
| × 82 | [1.20] 1.23 | 1.68 |  |
| × 74 | [1.09] 1.12 | 1.53 | W8 × 67 | [1.34] 1.37 | 1.94 |
| × 68 | [1.01] 1.04 | 1.41 | × 58 | [1.18] 1.20 | 1.71 |
| × 61 | [0.91] 0.928 | 1.28 | × 48 | [0.99S] 1.00 | 1.44 |
| × 53 | [0.89] 0.915 | 1.21 | × 40 | [0.83] 0.849 | 1.23 |
| × 48 | [0.81] 0.835 | 1.10 | × 35 | [0.73] 0.749 | 1.08 |
| × 43 | [0.73] 0.752 | 0.99 | × 31 | [0.65] 0.665 | 0.97 |
|  | × 28 | [0.67] 0.688 | 0.96 |
| W12 × 190 | [2.46] 2.50 | 3.51 | × 24 | [0.58] 0.591 | 0.83 |
| × 170 | [2.22] 2.26 | 3.20 | × 21 | [0.57] 0.577 | 0.77 |
| × 152 | [2.01] 2.04 | 2.90 | × 18 | [0.49] 0.499 | 0.67 |
| × 136 | [1.82] 1.86 | 2.63 |  |
| × 120 | [1.62] 1.65 | 2.36 | W6 × 25 | [0.69] 0.696 | 1.00 |
| × 106 | [1.44] 1.47 | 2.11 | × 20 | [0.56] 0.563 | 0.82 |
| × 96 | [1.32] 1.34 | 1.93 | × 16 | [0.57] 0.583 | 0.78 |
| × 87 | [1.20] 1.22 | 1.76 | × 15 | [0.42] 0.431 | 0.63 |
| × 79 | [1.10] 1.11 | 1.61 | × 12 | [0.43] 0.448 | 0.60 |
| × 72 | [1.00] 1.02 | 1.48 | × 9 | [0.33] 0.338 | 0.46 |
| × 65 | [0.91] 0.925 | 1.35 |  |
| × 58 | [0.91] 0.925 | 1.31 | W5 × 19 | [0.64] 0.644 | 0.93 |
| × 53 | [0.84] 0.855 | 1.20 | × 16 | [0.54] 0.55 | 0.80 |
| × 50 | [0.89] 0.909 | 1.23 |  |
| × 45 | [0.81] 0.829 | 1.12 | W4 × 13 | [0.54] 0.556 | 0.79 |
| × 40 | [0.72] 0.734 | 1.00 |  |

For SI: 1 pound per linear foot per inch = 0.059 kg/m/mm.

| TABLE [721.5.1(2)] 722.5.1(2) PROPERTIES OF CONCRETE |
| --- |
| PROPERTY | NORMAL WEIGHT CONCRETE | STRUCTURAL LIGHTWEIGHT CONCRETE |
| Thermal conductivity (kc) | 0.95 Btu/hr • ft • °F | 0.35 Btu/hr • ft • °F |
| Specific heat (cc) | 0.20 Btu/lb °F | 0.20 Btu/lb °F |
| Density (Pc) | 145 lb/ft3 | 110 lb/ft3 |
| Equilibrium (free) moisture content (m) by volume | 4% | 5% |

For SI: 1 inch = 25.4 mm, 1 foot = 304.8 mm, 1 lb/ft3 = 16.0185 kg/m3, Btu/hr • ft •°F = 1.731 W/(m • Κ)

| TABLE [721.5.1(3)] 722.5.1(3) THERMAL CONDUCTIVITY OF CONCRETE OR CLAY MASONRY UNITS |
| --- |
| DENSITY (dm) OF UNITS (lb/ft3) | THERMAL CONDUCTIVITY (K) OF UNITS (Btu/hr • ft • °F) |
| Concrete Masonry Units |
| 80 | 0.207 |
| 85 | 0.228 |
| 90 | 0.252 |
| 95 | 0.278 |
| 100 | 0.308 |
| 105 | 0.340 |
| 110 | 0.376 |
| 115 | 0.416 |
| 120 | 0.459 |
| 125 | 0.508 |
| 130 | 0.561 |
| 135 | 0.620 |
| 140 | 0.685 |
| 145 | 0.758 |
| 150 | 0.837 |
| Clay Masonry Units |
| 120 | 1.25 |
| 130 | 2.25 |

For SI: 1 pound per cubic foot = 16.0185 kg/m3, Btu [per hour foot]/hr • ft • °F = 1.731 W/(m • K).

| TABLE [721.5.1(4)] 722.5.1(4) WEIGHT-TO-HEATED-PERIMETER RATIOS (W/D) FOR TYPICAL WIDE FLANGE BEAM AND GIRDER SHAPES |
| --- |
| STRUCTURAL SHAPE | CONTOUR PROFILE | BOX PROFILE | STRUCTURAL SHAPE | CONTOUR PROFILE | BOX PROFILE |
| W36 × 300 | [2.47] 2.50 | 3.33 | W24 × 68 | [0.92] 0.942 | 1.21 |
| × 280 | [2.31] 2.35 | 3.12 | × 62 | [0.92] 0.934 | 1.14 |
| × 260 | [2.16] 2.18 | 2.92 | × 55 | [0.82] 0.828 | 1.02 |
| × 245 | [2.04] 2.08 | 2.76 |  |  |  |
| × 230 | [1.92] 1.95 | 2.61 | W21 × 147 | [1.83] 1.87 | 2.60 |
| × 210 | [1.94] 1.96 | 2.45 | × 132 | [1.66] 1.68 | 2.35 |
| × 194 | [1.80] 1.81 | 2.28 | × 122 | [1.54] 1.57 | 2.19 |
| × 182 | [1.69] 1.72 | 2.15 | × 111 | [1.41] 1.43 | 2.01 |
| × 170 | [1.59] 1.60 | 2.01 | × 101 | [1.29] 1.30 | 1.84 |
| × 160 | [1.50] 1.51 | 1.90 | × 93 | [1.38] 1.40 | 1.80 |
| × 150 | [1.41] 1.43 | 1.79 | × 83 | [1.24] 1.26 | 1.62 |
| × 135 | [1.28] 1.29 | 1.63 | × 73 | [1.10] 1.11 | 1.44 |
|  | × 68 | [1.03] 1.04 | 1.35 |
| W33 × 241 | [2.11] 2.13 | 2.86 | W21 × 62 | [0.94] 0.952 | 1.23 |
| × 221 | [1.94] 1.97 | 2.64 | × 57 | [0.93] 0.952 | 1.17 |
| × 201 | [1.78] 1.79 | 2.42 | × 50 | [0.83] 0.838 | 1.04 |
| × 152 | [1.51] 1.53 | 1.94 | × 44 | [0.73] 0.746 | 0.92 |
| × 141 | [1.41] 1.43 | 1.80 |  |
| × 130 | [1.31] 1.32 | 1.67 | W18 × 119 | [1.69] 1.72 | 2.42 |
| × 118 | [1.19] 1.21 | 1.53 | × 106 | [1.52] 1.55 | 2.18 |
|  | × 97 | [1.39] 1.42 | 2.01 |
| W30 × 211 | [2.00] 2.01 | 2.74 | × 86 | [1.24] 1.27 | 1.80 |
| × 191 | [1.82] 1.85 | 2.50 | × 76 | [1.11] 1.13 | 1.60 |
| × 173 | 1.66 | 2.28 | × 71 | [1.21] 1.22 | 1.59 |
| × 132 | [1.45] 1.47 | 1.85 | × 65 | [1.11] 1.13 | 1.47 |
| × 124 | [1.37] 1.39 | 1.75 | × 60 | [1.03] 1.04 | 1.36 |
| × 116 | [1.28] 1.30 | 1.65 | × 55 | [0.95] 0.963 | 1.26 |
| × 108 | [1.20] 1.21 | 1.54 | × 50 | [0.87] 0.88 | 1.15 |
| × 99 | [1.10] 1.12 | 1.42 | × 46 | [0.86] 0.878 | 1.09 |
|  | × 40 | [0.75] 0.768 | 0.96 |
| W27 × 178 | [1.85] 1.87 | 2.55 | × 35 | [0.66] 0.672 | 0.85 |
| × 161 | [1.68] 1.70 | 2.33 |  |
| × 146 | [1.53] 1.55 | 2.12 | W16 × 100 | [1.56] 1.59 | 2.25 |
| × 114 | [1.36] 1.39 | 1.76 | × 89 | [1.40] 1.43 | 2.03 |
| × 102 | [1.23] 1.24 | 1.59 | × 77 | [1.22] 1.25 | 1.78 |
| × 94 | [1.13] 1.15 | 1.47 | × 67 | [1.07] 1.09 | 1.56 |
| × 84 | [1.02] 1.03 | 1.33 | × 57 | [1.07] 1.09 | 1.43 |
|  | × 50 | [0.94] 0.962 | 1.26 |
|  | × 45 | [0.85] 0.870 | 1.15 |
| W24 × 162 | [1.85] 1.88 | 2.57 | × 40 | [0.76] 0.780 | 1.03 |
| × 146 | [1.68] 1.70 | 2.34 | × 36 | [0.69] 0.702 | 0.93 |
| × 131 | [1.52] 1.54 | 2.12 | × 31 | [0.65] 0.661 | 0.83 |
| × 117 | [1.36] 1.38 | 1.91 | × 26 | [0.55] 0.558 | 0.70 |
| × 104 | [1.22] 1.24 | 1.71 |  |
| × 94 | [1.26] 1.28 | 1.63 | W14 × 132 | [1.83] 1.89 | 3.00 |
| x 84 | [1.13] 1.15 | 1.47 | x 120 | [1.67] 1.71 | 2.75 |
| × 76 | [1.03] 1.05 | 1.34 | × 109 | [1.53] 1.57 | 2.52 |
| W14 × 99 | [1.39] 1.43 | 2.31 | W10 × 30 | [0.79] 0.806 | 1.12 |
| × 90 | [1.27] 1.31 | 2.11 | × 26 | [0.69] 1.708 | 0.98 |
| × 82 | [1.41] 1.45 | 2.12 | × 22 | [0.59] 0.606 | 0.84 |
| × 74 | [1.28] 1.32 | 1.93 | × 19 | [0.59] 0.607 | 0.78 |
| × 68 | [1.19] 1.22 | 1.78 | × 17 | [0.54] 0.543 | 0.70 |
| × 61 | [1.07] 1.10 | 1.61 | × 15 | [0.48] 0.484 | 0.63 |
| × 53 | [1.03] 1.06 | 1.48 | × 12 | [0.38] 0.392 | 0.51 |
| × 48 | [0.94] 0.970 | 1.35 |  |
| W14 × 43 | [0.85] 0.874 | 1.22 | W8 × 67 | [1.61] 1.65 | 2.55 |
| × 38 | [0.79] 0.809 | 1.09 | × 58 | [1.41] 1.44 | 2.26 |
| × 34 | [0.71] 0.725 | 0.98 | × 48 | [1.18] 1.21 | 1.91 |
| × 30 | [0.63] 0.644 | 0.87 | × 40 | [1.00] 1.03 | 1.63 |
| × 26 | [0.61] 0.628 | 0.79 | × 35 | [0.88] 0.907 | 1.44 |
| × 22 | [0.52] 0.534 | 0.68 | × 31 | [0.79] 0.803 | 1.29 |
|  | × 28 | [0.80] 0.819 | 1.24 |
| W12 × 87 | [1.44] 1.47 | 2.34 | × 24 | [0.69] 0.704 | 1.07 |
| × 79 | [1.32] 1.34 | 2.14 | × 21 | [0.66] 0.675 | 0.96 |
| × 72 | [1.20] 1.23 | 1.97 | × 18 | [0.57] 0.583 | 0.84 |
| × 65 | [1.09] 1.11 | 1.79 | × 15 | [0.54] 0.551 | 0.74 |
| × 58 | [1.08] 1.10 | 1.69 | × 13 | [0.47] 0.483 | 0.65 |
| × 53 | [0.99] 1.02 | 1.55 | × 10 | [0.37] 0.375 | 0.51 |
| × 50 | [1.04] 1.06 | 1.54 |  |
| × 45 | [0.95] 0.974 | 1.40 | W6 × 25 | [0.82] 0.839 | 1.33 |
| × 40 | [0.85] 0.860 | 1.25 | × 20 | [0.67] 0.678 | 1.09 |
| × 35 | [0.79] 0.810 | 1.11 | × 16 | [0.66] 0.684 | 0.96 |
| × 30 | [0.69] 0.699 | 0.96 | × 15 | [0.51] 0.521 | 0.83 |
| × 26 | [0.60] 0.612 | 0.84 | × 12 | [0.51] 0.526 | 0.75 |
| × 22 | [0.61] 0.623 | 0.77 | × 9 | [0.39] 0.398 | 0.57 |
| × 19 | [0.53] 0.540 | 0.67 |  |
| × 16 | [0.45] 0.457 | 0.57 | W5 × 19 | [0.76] 0.776 | 1.24 |
| × 14 | [0.40] 0.405 | 0.50 | × 16 | [0.65] 0.664 | 1.07 |
| W10 × 112 | [2.14] 2.17 | 3.38 | W4 × 13 | [0.65] 0.670 | 1.05 |
| × 100 | [1.93] 1.97 | 3.07 |  |
| × 88 | [1.70] 1.74 | 2.75 |  |
| × 77 | [1.52] 1.54 | 2.45 |  |
| × 68 | [1.35] 1.38 | 2.20 |  |
| × 60 | [1.20] 1.22 | 1.97 |  |
| × 54 | [1.09] 1.11 | 1.79 |  |
| × 49 | [0.99] 1.01 | 1.64 |  |
| × 45 | [1.03] 1.06 | 1.59 |  |
| × 39 | 0.94 | 1.40 |  |
| × 33 | 0.77 | 1.20 |  |

For SI: Pounds per linear foot per inch = 0.059 kg/m/mm.

| TABLE [721.5.1(5)] 722.5.1(5) FIRE RESISTANCE OF CONCRETE MASONRY PROTECTED STEEL COLUMNS |
| --- |
| COLUMN SIZE | CONCRETE MASONRY DENSITY POUNDS PER CUBIC FOOT | MINIMUM REQUIRED EQUIVALENT THICKNESS FOR FIRE-RESISTANCE RATING OF CONCRETE MASONRY PROTECTION ASSEMBLY, Te (inches) | COLUMN SIZE | CONCRETE MASONRY DENSITY POUNDS PER CUBIC FOOT | MINIMUM REQUIRED EQUIVALENT THICKNESS FOR FIRE-RESISTANCE RATING OF CONCRETE MASONRY PROTECTION ASSEMBLY, Te (inches) |
|  |  | 1[-] hour | 2[-hour] hours | 3[-hour] hours | 4[-hour] hours |  |  | 1[-] hour | 2[-hour] hours | 3-[-hour] hours | 4[-hour] hours |
| W14 × 82 | 80 | 0.74 | 1.61 | 2.36 | 3.04 | W10 × 68 | 80 | 0.72 | 1.58 | 2.33 | 3.01 |
|  | 100 | 0.89 | 1.85 | 2.67 | 3.40 |  | 100 | 0.87 | 1.83 | 2.65 | 3.38 |
|  | 110 | 0.96 | 1.97 | 2.81 | 3.57 |  | 110 | 0.94 | 1.95 | 2.79 | 3.55 |
|  | 120 | 1.03 | 2.08 | 2.95 | 3.73 |  | 120 | 1.01 | 2.06 | 2.94 | 3.72 |
| W14 × 68 | 80 | 0.83 | 1.70 | 2.45 | 3.13 | W10 × 54 | 80 | 0.88 | 1.76 | 2.53 | 3.21 |
|  | 100 | 0.99 | 1.95 | 2.76 | 3.49 |  | 100 | 1.04 | 2.01 | 2.83 | 3.57 |
|  | 110 | 1.06 | 2.06 | 2.91 | 3.66 |  | 110 | 1.11 | 2.12 | 2.98 | 3.73 |
|  | 120 | 1.14 | 2.18 | 3.05 | 3.82 |  | 120 | 1.19 | 2.24 | 3.12 | 3.90 |
| W14 × 53 | 80 | 0.91 | 1.81 | 2.58 | 3.27 | W10 × 45 | 80 | 0.92 | 1.83 | 2.60 | 3.30 |
|  | 100 | 1.07 | 2.05 | 2.88 | 3.62 |  | 100 | 1.08 | 2.07 | 2.90 | 3.64 |
|  | 110 | 1.15 | 2.17 | 3.02 | 3.78 |  | 110 | 1.16 | 2.18 | 3.04 | 3.80 |
|  | 120 | 1.22 | 2.28 | 3.16 | 3.94 |  | 120 | 1.23 | 2.29 | 3.18 | 3.96 |
| W14 × 43 | 80 | 1.01 | 1.93 | 2.71 | 3.41 | W10 × 33 | 80 | 1.06 | 2.00 | 2.79 | 3.49 |
|  | 100 | 1.17 | 2.17 | 3.00 | 3.74 |  | 100 | 1.22 | 2.23 | 3.07 | 3.81 |
|  | 110 | 1.25 | 2.28 | 3.14 | 3.90 |  | 110 | 1.30 | 2.34 | 3.20 | 3.96 |
|  | 120 | 1.32 | 2.38 | 3.27 | 4.05 |  | 120 | 1.37 | 2.44 | 3.33 | 4.12 |
| W12 × 72 | 80 | 0.81 | 1.66 | 2.41 | 3.09 | W8 × 40 | 80 | 0.94 | 1.85 | 2.63 | 3.33 |
|  | 100 | 0.91 | 1.88 | 2.70 | 3.43 |  | 100 | 1.10 | 2.10 | 2.93 | 3.67 |
|  | 110 | 0.99 | 1.99 | 2.84 | 3.60 |  | 110 | 1.18 | 2.21 | 3.07 | 3.83 |
|  | 120 | 1.06 | 2.10 | 2.98 | 3.76 |  | 120 | 1.25 | 2.32 | 3.20 | 3.99 |
| W12 × 58 | 80 | 0.88 | 1.76 | 2.52 | 3.21 | W8 × 31 | 80 | 1.06 | 2.00 | 2.78 | 3.49 |
|  | 100 | 1.04 | 2.01 | 2.83 | 3.56 |  | 100 | 1.22 | 2.23 | 3.07 | 3.81 |
|  | 110 | 1.11 | 2.12 | 2.97 | 3.73 |  | 110 | 1.29 | 2.33 | 3.20 | 3.97 |
|  | 120 | 1.19 | 2.23 | 3.11 | 3.89 |  | 120 | 1.36 | 2.44 | 3.33 | 4.12 |
| W12 × 50 | 80 | 0.91 | 1.81 | 2.58 | 3.27 | W8 × 24 | 80 | 1.14 | 2.09 | 2.89 | 3.59 |
|  | 100 | 1.07 | 2.05 | 2.88 | 3.62 |  | 100 | 1.29 | 2.31 | 3.16 | 3.90 |
|  | 110 | 1.15 | 2.17 | 3.02 | 3.78 |  | 110 | 1.36 | 2.42 | 3.28 | 4.05 |
|  | 120 | 1.22 | 2.28 | 3.16 | 3.94 |  | 120 | 1.43 | 2.52 | 3.41 | 4.20 |
| W12 × 40 | 80 | 1.01 | 1.94 | 2.72 | 3.41 | W8 × 18 | 80 | 1.22 | 2.20 | 3.01 | 3.72 |
|  | 100 | 1.17 | 2.17 | 3.01 | 3.75 |  | 100 | 1.36 | 2.40 | 3.25 | 4.01 |
|  | 110 | 1.25 | 2.28 | 3.14 | 3.90 |  | 110 | 1.42 | 2.50 | 3.37 | 4.14 |
|  | 120 | 1.32 | 2.39 | 3.27 | 4.06 |  | 120 | 1.48 | 2.59 | 3.49 | 4.28 |
| 4 × 4 × 1/2 wall thickness | 80 | 0.93 | 1.90 | 2.71 | 3.43 | 4 double extra strong 0.674 wall thickness | 80 | 0.80 | 1.75 | 2.56 | 3.28 |
|  | 100 | 1.08 | 2.13 | 2.99 | 3.76 |  | 100 | 0.95 | 1.99 | 2.85 | 3.62 |
|  | 110 | 1.16 | 2.24 | 3.13 | 3.91 |  | 110 | 1.02 | 2.10 | 2.99 | 3.78 |
|  | 120 | 1.22 | 2.34 | 3.26 | 4.06 |  | 120 | 1.09 | 2.20 | 3.12 | 3.93 |
| 4 × 4 × 3/8 wall thickness | 80 | 1.05 | 2.03 | 2.84 | 3.57 | 4 extra strong 0.337 wall thickness | 80 | 1.12 | 2.11 | 2.93 | 3.65 |
|  | 100 | 1.20 | 2.25 | 3.11 | 3.88 |  | 100 | 1.26 | 2.32 | 3.19 | 3.95 |
|  | 110 | 1.27 | 2.35 | 3.24 | 4.02 |  | 110 | 1.33 | 2.42 | 3.31 | 4.09 |
|  | 120 | 1.34 | 2.45 | 3.37 | 4.17 |  | 120 | 1.40 | 2.52 | 3.43 | 4.23 |
| 4 × 4 × 1/4 wall thickness | 80 | 1.21 | 2.20 | 3.01 | 3.73 | 4 standard 0.237 wall thickness | 80 | 1.26 | 2.25 | 3.07 | 3.79 |
|  | 100 | 1.35 | 2.40 | 3.26 | 4.02 |  | 100 | 1.40 | 2.45 | 3.31 | 4.07 |
|  | 110 | 1.41 | 2.50 | 3.38 | 4.16 |  | 110 | 1.46 | 2.55 | 3.43 | 4.21 |
|  | 120 | 1.48 | 2.59 | 3.50 | 4.30 |  | 120 | 1.53 | 2.64 | 3.54 | 4.34 |
| 6 × 6 × 1/2 wall thickness | 80 | 0.82 | 1.75 | 2.54 | 3.25 | 5 double extra strong 0.750 wall thickness | 80 | 0.70 | 1.61 | 2.40 | 3.12 |
|  | 100 | 0.98 | 1.99 | 2.84 | 3.59 |  | 100 | 0.85 | 1.86 | 2.71 | 3.47 |
|  | 110 | 1.05 | 2.10 | 2.98 | 3.75 |  | 110 | 0.91 | 1.97 | 2.85 | 3.63 |
|  | 120 | 1.12 | 2.21 | 3.11 | 3.91 |  | 120 | 0.98 | 2.02 | 2.99 | 3.79 |
| 6 × 6 × 3/8 wall thickness | 80 | 0.96 | 1.91 | 2.71 | 3.42 | 5 extra strong 0.375 wall thickness | 80 | 1.04 | 2.01 | 2.83 | 3.54 |
|  | 100 | 1.12 | 2.14 | 3.00 | 3.75 |  | 100 | 1.19 | 2.23 | 3.09 | 3.85 |
|  | 110 | 1.19 | 2.25 | 3.13 | 3.90 |  | 110 | 1.26 | 2.34 | 3.22 | 4.00 |
|  | 120 | 1.26 | 2.35 | 3.26 | 4.05 |  | 120 | 1.32 | 2.44 | 3.34 | 4.14 |
| 6 × 6 × 1/4 wall thickness | 80 | 1.14 | 2.11 | 2.92 | 3.63 | 5 standard 0.258 wall thickness | 80 | 1.20 | 2.19 | 3.00 | 3.72 |
|  | 100 | 1.29 | 2.32 | 3.18 | 3.93 |  | 100 | 1.34 | 2.39 | 3.25 | 4.00 |
|  | 110 | 1.36 | 2.43 | 3.30 | 4.08 |  | 110 | 1.41 | 2.49 | 3.37 | 4.14 |
|  | 120 | 1.42 | 2.52 | 3.43 | 4.22 |  | 120 | 1.47 | 2.58 | 3.49 | 4.28 |
| 8 × 8 × 1/2 wall thickness | 80 | 0.77 | 1.66 | 2.44 | 3.13 | 6 double extra strong 0.864 wall thickness | 80 | 0.59 | 1.46 | 2.23 | 2.92 |
|  | 100 | 0.92 | 1.91 | 2.75 | 3.49 |  | 100 | 0.73 | 1.71 | 2.54 | 3.29 |
|  | 110 | 1.00 | 2.02 | 2.89 | 3.66 |  | 110 | 0.80 | 1.82 | 2.69 | 3.47 |
|  | 120 | 1.07 | 2.14 | 3.03 | 3.82 |  | 120 | 0.86 | 1.93 | 2.83 | 3.63 |
| 8 × 8 × 3/8 wall thickness | 80 | 0.91 | 1.84 | 2.63 | 3.33 | 6 extra strong 0.432 wall thickness | 80 | 0.94 | 1.90 | 2.70 | 3.42 |
|  | 100 | 1.07 | 2.08 | 2.92 | 3.67 |  | 100 | 1.10 | 2.13 | 2.98 | 3.74 |
|  | 110 | 1.14 | 2.19 | 3.06 | 3.83 |  | 110 | 1.17 | 2.23 | 3.11 | 3.89 |
|  | 120 | 1.21 | 2.29 | 3.19 | 3.98 |  | 120 | 1.24 | 2.34 | 3.24 | 4.04 |
| 8 × 8 × 1/4 wall thickness | 80 | 1.10 | 2.06 | 2.86 | 3.57 | 6 standard 0.280 wall thickness | 80 | 1.14 | 2.12 | 2.93 | 3.64 |
|  | 100 | 1.25 | 2.28 | 3.13 | 3.87 |  | 100 | 1.29 | 2.33 | 3.19 | 3.94 |
|  | 110 | 1.32 | 2.38 | 3.25 | 4.02 |  | 110 | 1.36 | 2.43 | 3.31 | 4.08 |
|  | 120 | 1.39 | 2.48 | 3.38 | 4.17 |  | 120 | 1.42 | 2.53 | 3.43 | 4.22 |

For SI: 1 inch = 25.4 mm, 1 pound per cubic feet = 16.02 kg/m3.

Note: Tabulated values assume 1-inch air gap between masonry and steel section.

| TABLE [721.5.1(6)] 722.5.1(6) FIRE RESISTANCE OF CLAY MASONRY PROTECTED STEEL COLUMNS |
| --- |
| COLUMN SIZE | CLAY MASONRY DENSITY, POUNDS PER CUBIC FOOT | MINIMUM REQUIRED EQUIVALENT THICKNESS FOR FIRE-RESISTANCE RATING OF CLAY MASONRY PROTECTION ASSEMBLY, Te (inches) | COLUMN SIZE | CLAY MASONRY DENSITY, POUNDS PER CUBIC FOOT | MINIMUM REQUIRED EQUIVALENT THICKNESS FOR FIRE-RESISTANCE RATING OF CLAY MASONRY PROTECTION ASSEMBLY, Te (inches) |
|  |  | 1[-] hour | 2[-hour] hours | 3[-hour] hours | 4[-hour] hours |  |  | 1[-] hour | 2[-hour] hours | 3[-hour] hours | 4[-hour] hours |
| W14 × 82 | 120 | 1.23 | 2.42 | 3.41 | 4.29 | W10 × 68 | 120 | 1.27 | 2.46 | 3.26 | 4.35 |
|  | 130 | 1.40 | 2.70 | 3.78 | 4.74 |  | 130 | 1.44 | 2.75 | 3.83 | 4.80 |
| W14 × 68 | 120 | 1.34 | 2.54 | 3.54 | 4.43 | W10 × 54 | 120 | 1.40 | 2.61 | 3.62 | 4.51 |
|  | 130 | 1.51 | 2.82 | 3.91 | 4.87 |  | 130 | 1.58 | 2.89 | 3.98 | 4.95 |
| W14 × 53 | 120 | 1.43 | 2.65 | 3.65 | 4.54 | W10 × 45 | 120 | 1.44 | 2.66 | 3.67 | 4.57 |
|  | 130 | 1.61 | 2.93 | 4.02 | 4.98 |  | 130 | 1.62 | 2.95 | 4.04 | 5.01 |
| W14 × 43 | 120 | 1.54 | 2.76 | 3.77 | 4.66 | W10 × 33 | 120 | 1.59 | 2.82 | 3.84 | 4.73 |
|  | 130 | 1.72 | 3.04 | 4.13 | 5.09 |  | 130 | 1.77 | 3.10 | 4.20 | 5.13 |
| W12 × 72 | 120 | 1.32 | 2.52 | 3.51 | 4.40 | W8 × 40 | 120 | 1.47 | 2.70 | 3.71 | 4.61 |
|  | 130 | 1.50 | 2.80 | 3.88 | 4.84 |  | 130 | 1.65 | 2.98 | 4.08 | 5.04 |
| W12 × 58 | 120 | 1.40 | 2.61 | 3.61 | 4.50 | W8 × 31 | 120 | 1.59 | 2.82 | 3.84 | 4.73 |
|  | 130 | 1.57 | 2.89 | 3.98 | 4.94 |  | 130 | 1.77 | 3.10 | 4.20 | 5.17 |
| W12 × 50 | 120 | 1.43 | 2.65 | 3.66 | 4.55 | W8 × 24 | 120 | 1.66 | 2.90 | 3.92 | 4.82 |
|  | 130 | 1.61 | 2.93 | 4.02 | 4.99 |  | 130 | 1.84 | 3.18 | 4.28 | 5.25 |
| W12 × 40 | 120 | 1.54 | 2.77 | 3.78 | 4.67 | W8 × 18 | 120 | 1.75 | 3.00 | 4.01 | 4.91 |
|  | 130 | 1.72 | 3.05 | 4.14 | 5.10 |  | 130 | 1.93 | 3.27 | 4.37 | 5.34 |
| Steel tubing | Steel pipe |
| Nominal tube size (inches) | Clay masonry density, pounds per cubic foot | Minimum required equivalent thickness for fire-resistance rating of clay. Masonry protection assembly Te , (inches) | Nominal pipe size (inches) | Clay masonry density, pounds per cubic foot | Minimum required equivalent thickness for fire-resistance rating of clay. Masonry protection assembly Te , (inches) |
|  |  | 1-hour | 2-hour | 3-hour | 4-hour |  |  | 1-hour | 2-hour | 3-hour | 4-hour |
| 4 × 4 × 1/2 wall thickness | 120 | 1.44 | 2.72 | 3.76 | 4.68 | 4 double extra strong 0.674 wall thickness | 120 | 1.26 | 2.55 | 3.60 | 4.52 |
|  | 130 | 1.62 | 3.00 | 4.12 | 5.11 |  | 130 | 1.42 | 2.82 | 3.96 | 4.95 |
| 4 × 4 × 3/8 wall thickness | 120 | 1.56 | 2.84 | 3.88 | 4.78 | 4 extra strong 0.337 wall thickness | 120 | 1.60 | 2.89 | 3.92 | 4.83 |
|  | 130 | 1.74 | 3.12 | 4.23 | 5.21 |  | 130 | 1.77 | 3.16 | 4.28 | 5.25 |
| 4 × 4 × 1/4 wall thickness | 120 | 1.72 | 2.99 | 4.02 | 4.92 | 4 standard 0.237 wall thickness | 120 | 1.74 | 3.02 | 4.05 | 4.95 |
|  | 130 | 1.89 | 3.26 | 4.37 | 5.34 |  | 130 | 1.92 | 3.29 | 4.40 | 5.37 |
| 6 × 6 × 1/2 wall thickness | 120 | 1.33 | 2.58 | 3.62 | 4.52 | 5 double extra strong 0.750 wall thickness | 120 | 1.17 | 2.44 | 3.48 | 4.40 |
|  | 130 | 1.50 | 2.86 | 3.98 | 4.96 |  | 130 | 1.33 | 2.72 | 3.84 | 4.83 |
| 6 × 6 × 3/8 wall thickness | 120 | 1.48 | 2.74 | 3.76 | 4.67 | 5 extra strong 0.375 wall thickness | 120 | 1.55 | 2.82 | 3.85 | 4.76 |
|  | 130 | 1.65 | 3.01 | 4.13 | 5.10 |  | 130 | 1.72 | 3.09 | 4.21 | 5.18 |
| 6 × 6 × 1/4 wall thickness | 120 | 1.66 | 2.91 | 3.94 | 4.84 | 5 standard 0.258 wall thickness | 120 | 1.71 | 2.97 | 4.00 | 4.90 |
|  | 130 | 1.83 | 3.19 | 4.30 | 5.27 |  | 130 | 1.88 | 3.24 | 4.35 | 5.32 |
| 8 × 8 × 1/2 wall thickness | 120 | 1.27 | 2.50 | 3.52 | 4.42 | 6 double extra strong 0.864 wall thickness | 120 | 1.04 | 2.28 | 3.32 | 4.23 |
|  | 130 | 1.44 | 2.78 | 3.89 | 4.86 |  | 130 | 1.19 | 2.60 | 3.68 | 4.67 |
| 8 × 8 ×3/8 wall thickness | 120 | 1.43 | 2.67 | 3.69 | 4.59 | 6 extra strong 0.432 wall thickness | 120 | 1.45 | 2.71 | 3.75 | 4.65 |
|  | 130 | 1.60 | 2.95 | 4.05 | 5.02 |  | 130 | 1.62 | 2.99 | 4.10 | 5.08 |
| 8 × 8 × 1/4 wall thickness | 120 | 1.62 | 2.87 | 3.89 | 4.78 | 6 standard 0.280 wall thickness | 120 | 1.65 | 2.91 | 3.94 | 4.84 |
|  | 130 | 1.79 | 3.14 | 4.24 | 5.21 |  | 130 | 1.82 | 3.19 | 4.30 | 5.27 |

For SI: 1 inch = 25.4 mm, 1 pound per cubic foot = 16.02 kg/m3.

| TABLE [721.5.1(7)] 722.5.1(7) MINIMUM COVER (inch) FOR STEEL COLUMNS ENCASED IN NORMAL-WEIGHT CONCRETEa [FIGURE [721.5.1(6)(c)] 722.5.1(6)(c)] |
| --- |
| STRUCTURAL SHAPE | FIRE-RESISTANCE RATING (hours) |
|  | 1 | 11/2 | 2 | 3 | 4 |
| W14 × 233 | 1 | 1 | 1 | [1/2] 11/2 | 2 |
| × 176 |  |  |  |  | 21/2 |
| × 132 |  |  |  | 2 |  |
| × 90 |  |  | 11/2 |  |  |
| × 61 |  |  |  |  | 3 |
| × 48 |  | 11/2 |  | 21/2 |  |
| × 43 |  |  |  |  |  |
| W12 × 152 | 1 | 1 | 1 | 2 | 21/2 |
| × 96 |  |  |  |  |  |
| × 65 |  | 11/2 | 11/2 |  | 3 |
| × 50 |  |  |  | 21/2 |  |
| × 40 |  |  |  |  |  |
| W10 × 88 | 1 | 11/2 | 11/2 | 2 | 3 |
| × 49 | 1 |  |  | 21/2 |  |
| × 45 |  |  |  |  |  |
| × 39 |  |  |  |  | 31/2 |
| × 33 |  |  | 2 |  |  |
| W8 × 67 | 1 | 1 | 11/2 | 21/2 | 3 |
| × 58 |  |  |  |  |  |
| × 48 |  | 11/2 |  |  | 31/2 |
| × 31 |  |  | 2 | 3 |  |
| × 21 |  |  |  |  |  |
| × 18 |  |  |  |  | 4 |
| W6 × 25 | 1 | 11/2 | 2 | 3 | 31/2 |
| × 20 |  | 2 | 21/2 |  | 4 |
| × 16 |  |  |  | 31/2 |  |
| × 15 | 11/2 |  |  |  |  |
| × 9 |  |  |  |  |  |

For SI: 1 inch = 25.4 mm.

a. The tabulated thicknesses are based upon the assumed properties of normal-weight concrete given in Table [721.5.1(2)] 722.5.1(2).

| TABLE [721.5.1(8)] 722.5.1(8) MINIMUM COVER (inch) FOR STEEL COLUMNS ENCASED IN STRUCTURAL LIGHTWEIGHT CONCRETEa [FIGURE [721.5.1 (6)(c)] 722.5.1(6)(c)] |
| --- |
| STRUCTURAL SHAPE | FIRE-RESISTANCE RATING (HOURS) |
|  | 1 | 11/2 | 2 | 3 | 4 |
| W14 × 233 | 1 | 1 | 1 | 1 | 11/2 |
| × 193 |  |  |  | 11/2 |  |
| × 74 |  |  |  |  | 2 |
| × 61 |  |  |  |  | 21/2 |
| × 43 |  |  | 11/2 | 2 |  |
| W12 × 65 | 1 | 1 | 1 | 11/2 | 2 |
| × 53 |  |  |  | 2 | 21/2 |
| × 40 |  |  | 11/2 |  |  |
| W10 × 112 | 1 | 1 | 1 | 11/2 | 2 |
| × 88 |  |  |  |  |  |
| × 60 |  |  |  | 2 | 21/2 |
| × 33 |  |  | 11/2 |  |  |
| W8 × 35 | 1 | 1 | 11/2 | 2 | 21/2 |
| × 28 |  |  |  |  | 3 |
| × 24 |  |  |  | 21/2 |  |
| × 18 |  | 11/2 |  |  |  |

For SI: 1 inch = 25.4 mm.

a.	The tabulated thicknesses are based upon the assumed properties of structural lightweight concrete given in Table [721.5.1(2)] 722.5.1(2).

| TABLE [721.5.1(9)] 722.5.1(9) MINIMUM COVER (inch) FOR STEEL COLUMNS IN NORMAL-WEIGHT PRECAST COVERSa [FIGURE [721.5.1 (6)(a)] 722.5.1(6)(a)] |
| --- |
| STRUCTURAL SHAPE | FIRE-RESISTANCE RATING (hours) |
|  | 1 | 11/2 | 2 | 3 | 4 |
| W14 × 233 | 11/2 | 11/2 | 11/2 | 21/2 | 3 |
| × 211 |  |  |  |  | 31/2 |
| × 176 |  |  | 2 |  |  |
| × 145 |  |  |  | 3 |  |
| × 109 |  | 2 | 21/2 |  |  |
| × 99 |  |  |  |  | 4 |
| × 61 |  |  |  | 31/2 |  |
| × 43 |  |  |  |  | 41/2 |
| W12 × 190 | 11/2 | 11/2 | 11/2 | 21/2 | 31/2 |
| × 152 |  |  | 2 |  |  |
| × 120 |  |  |  | 3 | 4 |
| × 96 |  |  |  |  |  |
| × 87 |  | 2 | 21/2 | 31/2 |  |
| × 58 |  |  |  |  | 41/2 |
| × 40 |  |  |  |  |  |
| W10 × 112 | 11/2 | 11/2 | 2 | 3 | 31/2 |
| × 88 |  |  |  |  | 4 |
| × 77 |  | 2 | 21/2 |  |  |
| × 54 |  |  |  | 31/2 |  |
| × 33 |  |  |  |  | 41/2 |
| W8 × 67 | 11/2 | 11/2 | 2 | 3 | 4 |
| × 58 |  | 2 | 21/2 | 31/2 |  |
| × 48 |  |  |  |  |  |
| × 28 |  |  |  |  | 41/2 |
| × 21 |  | 21/2 | 3 |  |  |
| × 18 |  |  |  | 4 |  |
| W6 × 25 | 11/2 | 2 | 21/2 | 31/2 | 41/2 |
| × 20 |  | 21/2 | 3 |  |  |
| × 16 |  |  |  | 4 |  |
| × 12 | 2 |  |  |  |  |
| × 9 |  |  |  |  | 5 |

For SI: 1 inch = 25.4 mm.

a.	The tabulated thicknesses are based upon the assumed properties of normal-weight concrete given in Table [721.5.1(2)] 722.5.1(2).

| TABLE [721.5.1(10)] 722.5.1(10) MINIMUM COVER (inch) FOR STEEL COLUMNS IN STRUCTURAL LIGHTWEIGHT PRECAST COVERSa [FIGURE [721.5.1(6)(a)] 722.5.1(6)(a)] |
| --- |
| STRUCTURAL SHAPE | FIRE-RESISTANCE RATING (hours) |
|  | 1 | 11/2 | 2 | 3 | 4 |
| W14 × 233 | 11/2 | 11/2 | 11/2 | 2 | 21/2 |
| × 176 |  |  |  |  | 3 |
| × 145 |  |  |  | 21/2 |  |
| × 132 |  |  |  |  |  |
| × 109 |  |  |  |  |  |
| × 99 |  |  | 2 |  |  |
| × 68 |  |  |  |  | 31/2 |
| × 43 |  |  |  | 3 |  |
| W12 × 190 | 11/2 | 11/2 | 11/2 | 2 | 21/2 |
| × 152 |  |  |  |  |  |
| × 136 |  |  |  |  | 3 |
| × 106 |  |  |  | 21/2 |  |
| × 96 |  |  |  |  | 31/2 |
| × 87 |  |  |  |  |  |
| × 65 |  |  | 2 |  |  |
| × 40 |  |  |  | 3 |  |
| W10 × 112 | 11/2 | 11/2 | 11/2 | 2 | 3 |
| × 100 |  |  |  | 21/2 |  |
| × 88 |  |  |  |  |  |
| × 77 |  |  | 2 |  | 31/2 |
| × 60 |  |  |  |  |  |
| × 39 |  |  |  | 3 |  |
| × 33 |  | 2 |  |  |  |
| W8 × 67 | 11/2 | 11/2 | 11/2 | 21/2 | 3 |
| × 48 |  |  | 2 | 3 | 31/2 |
| × 35 |  |  |  |  |  |
| × 28 |  | 2 |  |  |  |
| × 18 |  |  | 21/2 |  | 4 |
| W6 × 25 | 11/2 | 2 | 2 | 3 | 31/2 |
| × 15 |  |  | 21/2 |  | 4 |
| × 9 |  |  |  | 31/2 |  |

For SI: 1 inch = 25.4 mm.

a.	The tabulated thicknesses are based upon the assumed properties of structural lightweight concrete given in Table [721.5.1(2)] 722.5.1(2).

[721.5.1.1] 722.5.1.1 General. These procedures establish a basis for determining the fire resistance of column assemblies as a function of the thickness of fire-resistant material and, the weight, W, and heated perimeter, D, of structural steel columns. As used in these sections, W is the average weight of a structural steel column in pounds per linear foot. The heated perimeter, D, is the inside perimeter of the fire-resistant material in inches as illustrated in Figure [721.5.1(1)] 722.5.1(1).

[721.5.1.1.1] 722.5.1.1.1 Nonload-bearing protection. The application of these procedures shall be limited to column assemblies in which the fire-resistant material is not designed to carry any of the load acting on the column.

[721.5.1.1.2] 722.5.1.1.2 Embedments. In the absence of substantiating fire-endurance test results, ducts, conduit, piping, and similar mechanical, electrical, and plumbing installations shall not be embedded in any required fire-resistant materials.

[721.5.1.1.3] 722.5.1.1.3 Weight-to-perimeter ratio. Table [721.5.1(1)] 722.5.1(1) contains weight-to-heated-perimeter ratios (W/D) for both contour and box fire-resistant profiles, for the wide flange shapes most often used as columns. For different fire-resistant protection profiles or column cross sections, the weight-to-heated-perimeter ratios (W/D) shall be determined in accordance with the definitions given in this section.

[721.5.1.2] 722.5.1.2 Gypsum wallboard protection. The fire resistance of structural steel columns with [weight to-heated-perimeter] weight-to-heated-perimeter ratios (W/D) less than or equal to 3.65 and [which] that are protected with Type X gypsum wallboard shall be permitted to be determined from the following expression:

(Equation 7-12)

where:

Fire resistance (minutes).

Total thickness of gypsum wallboard (inches).

Heated perimeter of the structural steel column (inches).

Total weight of the structural steel column and gypsum wallboard protection (pounds per linear foot).

[721.5.1.2.1] 722.5.1.2.1 Attachment. The gypsum [wallboard] board or gypsum panel products shall be supported as illustrated in either Figure [721.5.1(2)] 722.5.1(2) for fire-resistance ratings of 4 hours or less, or Figure [721.5.1(3)] 722.5.1(3) for fire-resistance ratings of 3 hours or less.

[721.5.1.2.2] 722.5.1.2.2 Gypsum wallboard equivalent to concrete. The determination of the fire resistance of structural steel columns from Figure [721.5.1(4)] 722.5.1(4) is permitted for various thicknesses of gypsum wallboard as a function of the weight-to-heated-perimeter ratio (W/D) of the column. For structural steel columns with weight-to-heated-perimeter ratios (W/D) greater than 3.65, the thickness of gypsum wallboard required for specified fire-resistance ratings shall be the same as the thickness determined for a W14 x 233 wide flange shape.

[721.5.1.3] 722.5.1.3 Spray-applied fire-resistant materials. The fire resistance of wide-flange structural steel columns protected with spray-applied fire-resistant materials, as illustrated in Figure [721.5.1(5)] 722.5.1(5), shall be permitted to be determined from the following expression:

(Equation 7-13)

where:

Fire resistance (minutes).

Thickness of spray-applied fire-resistant material (inches).

Heated perimeter of the structural steel column (inches).

Material-dependent constants.

Weight of structural steel column (pounds per linear foot).

Exception: The fire resistance of structural steel columns protected with intumescent or mastic fire-resistant coatings shall be determined on the basis of fire resistance tests in accordance with Section 703.2.

[721.5.1.3.1] 722.5.1.3.1 Material-dependent constants. The material-dependent constants, C1and C2, shall be determined for specific fire-resistant materials on the basis of standard [fire endurance] fire-resistance tests in accordance with Section 703.2. Unless evidence is submitted to the commissioner substantiating a broader application, this expression shall be limited to determining the fire resistance of structural steel columns with weight-to-heated-perimeter ratios (W/D) between the largest and smallest columns for which standard [fire endurance] fire-resistance test results are available.

[721.5.1.3.2] 722.5.1.3.2 Identification. Spray-applied fire-resistant materials shall be identified by density and thickness required for a given fire-resistance rating.

[721.5.1.4] 722.5.1.4 Concrete-protected columns. The fire resistance of structural steel columns protected with concrete, as illustrated in Figure [721.5.1(6)] 722.5.1(6)(a) and (b), shall be permitted to be determined from the following expression:

(Equation 7-14)

where:

As used in these expressions:

Fire endurance at equilibrium moisture conditions (minutes).

Fire endurance at zero moisture content (minutes).

Equilibrium moisture content of the concrete by volume (percent).

Average weight of the steel column (pounds per linear foot).

Heated perimeter of the steel column (inches).

Thickness of the concrete cover (inches).

Ambient temperature thermal conductivity of the concrete (Btu/hr ft °F).

Ambient temperature thermal capacity of the steel column = 0.11W (Btu/hr °F).

Concrete density (pounds per cubic foot).

Ambient temperature specific heat of concrete (Btu/lb °F).

Interior dimension of one side of a square concrete box protection (inches).

[721.5.1.4.1] 722.5.1.4.1 Reentrant space filled. For wide-flange structural steel columns completely encased in concrete with all reentrant spaces filled (Figure [721.5.1(6)(c)] 722.5.1(6)(c)), the thermal capacity of the concrete within the reentrant spaces shall be permitted to be added to the thermal capacity of the steel column, as follows:

(Equation 7-15)

where:

Flange width of the steel column (inches).

Depth of the steel column (inches).

Cross-sectional area of the steel column (square inches).

[721.5.1.4.2] 722.5.1.4.2 Concrete properties unknown. If specific data on the properties of concrete are not available, the values given in Table [721.5.1(2)] 722.5.1(2) are permitted.

[721.5.1.4.3] 722.5.1.4.3 Minimum concrete cover. For structural steel column encased in concrete with all reentrant spaces filled, Figure [721.5.1(6)(c)] 722.5.1(6)(c) and Tables [721.5.1(7)] 722.5.1(7) and [721.5.1(8)] 722.5.1(8) indicate the thickness of concrete cover required for various fire-resistance ratings for typical wide-flange sections. The thicknesses of concrete indicated in these tables [also] apply to structural steel columns larger than those listed.

[721.5.1.4.4] 722.5.1.4.4 Minimum precast concrete cover. For structural steel columns protected with precast concrete column covers as shown in Figure [721.5.1 (6)(a)] 722.5.1(6)(a), Tables [721.5.1(9)] 722.5.1(9) and [721.5.1(10)] 722.5.1(10) indicate the thickness of the column covers required for various fire-resistance ratings for typical wide-flange shapes. The thicknesses of concrete given in these tables [also] apply to structural steel columns larger than those listed.

[721.5.1.4.5] 722.5.1.4.5 Masonry protection. The fire resistance of structural steel columns protected with concrete masonry units or clay masonry units as illustrated in Figure [721.5.1(7)] 722.5.1(7), shall be permitted to be determined from the following expression:

(Equation 7-16)

where:

Fire-resistance rating of column assembly (hours).

Average weight of steel column (pounds per foot).

Heated perimeter of steel column (inches) [see Figure [721.5.1(7)] 722.5.1(7)].

Equivalent thickness of concrete or clay masonry unit (inches) (see Table [721.3.2] 722.3.2 Note a or Section [721.4.1] 722.4.1).

Thermal conductivity of concrete or clay masonry unit (Btu/hr ft °F) [see Table [721.5.1(3)] 722.5.1(3)].

Cross-sectional area of steel column (square inches).

Density of the concrete or clay masonry unit (pounds per cubic foot).

Inner perimeter of concrete or clay masonry protection (inches) [see Figure [721.5.1(7)] 722.5.1(7)].

[721.5.1.4.6] 722.5.1.4.6 Equivalent concrete masonry thickness. For structural steel columns protected with concrete masonry, Table [721.5.1(5)] 722.5.1(5) gives the equivalent thickness of concrete masonry required for various fire-resistance ratings for typical column shapes. For structural steel columns protected with clay masonry, Table [721.5.1(6)] 722.5.1(6) gives the equivalent thickness of concrete masonry required for various fire-resistance ratings for typical column shapes.

[721.5.2] 722.5.2 Structural steel beams and girders. The fire-resistance ratings of structural steel beams and girders shall be based upon the size of the element and the type of protection provided in accordance with this section.

FIGURE 722.5.2
DETERMINATION OF THE HEATED PERIMETER OF
STRUCTURAL STEEL BEAMS AND GIRDERS

[721.5.2.1] 722.5.2.1 Determination of fire resistance. These procedures establish a basis for determining resistance of structural steel beams and girders [which] that differ in size from that specified in approved fire-resistance-rated assemblies as a function of the thickness of fire-resistant material and the weight (W) and heated perimeter (D) of the beam or girder. As used in these sections, W is the average weight of a structural steel [member] element in pounds per linear foot (plf). The heated perimeter, D, is the inside perimeter of the fire-resistant material in inches as illustrated in Figure [721.5.2] 722.5.2.

[721.5.2.1.1] 722.5.2.1.1 Weight-to-heated perimeter. The weight-to-heated-perimeter ratios (W/D), for both contour and box fire-resistant protection profiles, for the wide flange shapes most often used as beams or girders are given in Table [721.5.1(4)] 722.5.1(4). For different shapes, the weight-to-heated-perimeter ratios (W/D) shall be determined in accordance with the definitions given in this section.

[721.5.2.1.2] 722.5.2.1.2 Beam and girder substitutions. Except as provided for in Section [721.5.2.2] 722.5.2.2, structural steel beams in approved [fire-resistant] fire-resistance-rated assemblies shall be considered the minimum permissible size. Other beam or girder shapes shall be permitted to be substituted provided that the weight-to-heated-perimeter ratio (W/D) of the substitute beam is equal to or greater than that of the beam specified in the approved assembly.

[721.5.2.2] 722.5.2.2 Spray-applied fire-resistant materials. The provisions in this section apply to structural steel beams and girders protected with spray-applied fire-resistant materials. Larger or smaller beam and girder shapes shall be permitted to be substituted for beams specified in approved unrestrained or restrained fire-resistance-rated assemblies, provided that the thickness of the fire-resistant material is adjusted in accordance with the following expression:

(Equation 7-17)

where:

Thickness of spray-applied fire-resistant material in inches.

Weight of the structural steel beam or girder in pounds per linear foot.

Heated perimeter of the structural steel beam or girder in inches.

Subscript 1 refers to the beam and fire-resistant material thickness in the approved assembly.

Subscript 2 refers to the substitute beam or girder and the required thickness of fire-resistant material.

Exception: The [fire resistance] fire-resistance of structural steel beams and girders protected with intumescent or mastic fire-resistant coatings shall be determined on the basis of fire-resistance tests in accordance with Section 703.2.

[721.5.2.2.1] 722.5.2.2.1 Minimum thickness. The use of Equation 7-17 is subject to the following conditions:

1.	The weight-to-heated-perimeter ratio for the substitute beam or girder (W2/D2) shall be not [be] less than 0.37.

2.	The thickness of fire protection materials for the substitute beam or girder (T1) shall be not [be] less than 3/8 inch (9.5 mm).

3.	The unrestrained or restrained beam rating shall be not [be] less than 1 hour.

4.	[When] Where used to adjust the material thickness for a restrained beam, the use of this procedure is limited to structural steel sections classified as compact in accordance with AISC 360.

[721.5.2.3] 722.5.2.3 Structural steel trusses. The fire resistance of structural steel trusses protected with fire-resistant materials spray applied to each of the individual truss elements shall be permitted to be determined in accordance with this section. The thickness of the fire-resistant material shall be determined in accordance with Section [721.5.1.3] 722.5.1.3. The weight-to-heated-perimeter ratio (W/D) of truss elements which can be simultaneously exposed to fire on all sides shall be determined on the same basis as columns, as specified in Section [721.5.1.1] 722.5.1.1. The weight-to-heated-perimeter ratio (W/D) of truss elements which directly support floor or roof assembly shall be determined on the same basis as beams and girders, as specified in Section [721.5.2.1] 722.5.2.1.

Exception: The fire resistance of structural steel trusses protected with intumescent or mastic fire-resistant coatings shall be determined on the basis of fire-resistance tests in accordance with Section 703.2.

[721.6] 722.6 Wood assemblies. The provisions of this section contain procedures by which the fire-resistance ratings of wood assemblies are established by calculations.

[721.6.1] 722.6.1 General. This section contains procedures for calculating the fire-resistance ratings of walls, floor/ceiling and roof/ceiling assemblies based in part on the standard method of testing referenced in Section 703.2.

[721.6.1.1] 722.6.1.1 Maximum fire-resistance rating. Fire-resistance ratings calculated for assemblies using the methods in Section [721.6] 722.6 shall be limited to a maximum of 1 hour.

[721.6.1.2] 722.6.1.2 Dissimilar membranes. Where dissimilar membranes are used on a wall assembly that requires consideration of fire exposure from both sides, the calculation shall be made from the least fire-resistant (weaker) side.

[721.6.2] 722.6.2 Walls, floors and roofs. These procedures apply to both load-bearing and nonload-bearing assemblies.

| TABLE [721.6.2(1)] 722.6.2(1) TIME ASSIGNED TO WALLBOARD MEMBRANESa,b,c,d |
| --- |
| DESCRIPTION OF FINISH | TIMEe (minutes) |
| 3/8-inch wood structural panel bonded with exterior glue | 5 |
| 15/32-inch wood structural panel bonded with exterior glue | 10 |
| 19/32-inch wood structural panel bonded with exterior glue | 15 |
| 3/8-inch gypsum wallboard | 10 |
| 1/2-inch gypsum wallboard | 15 |
| 5/8-inch gypsum wallboard | 30 |
| 1/2-inch Type X gypsum wallboard | 25 |
| 5/8-inch Type X gypsum wallboard | 40 |
| Double 3/8-inch gypsum wallboard | 25 |
| 1/2- + 3/8-inch gypsum wallboard | 35 |
| Double 1/2-inch gypsum wallboard | 40 |

For SI: 1 inch = 25.4 mm.

- These values apply only [when] where membranes are installed on framing members [which] that are spaced 16 inches o.c or less.

- Gypsum [wall board] wallboard installed over framing or furring shall be installed so that all edges are supported, except 5/8-inch Type X gypsum wallboard shall be permitted to be installed horizontally with the horizontal joints staggered 24 inches each side and unsupported but finished.

- On wood frame floor/ceiling or roof/ceiling assemblies, gypsum board shall be installed with the long dimension perpendicular to framing members and shall have all joints finished.

- The membrane on the unexposed side shall not be included in determining the fire resistance of the assembly. [When] Where dissimilar membranes are used on a wall assembly, the calculation shall be made from the least fire-resistant (weaker) side.

- The time assigned is not a finished rating.

| TABLE [721.6.2(2)] 722.6.2(2) TIME ASSIGNED FOR CONTRIBUTION OF WOOD FRAMEa,b,c |
| --- |
| DESCRIPTION | TIME ASSIGNED TO FRAME (minutes) |
| Wood studs 16 inches o.c. | 20 |
| Wood floor and roof joists 16 inches o.c. | 10 |

For SI: 1 inch = 25.4 mm.

- This table does not apply to studs or joists spaced more than 16 inches o.c.

- All studs shall be nominal 2 × 4 and all joists shall have a nominal thickness of [at least] not less than 2 inches.

- Allowable spans for joists shall be determined in accordance with Sections [2308.8, 2308.10.2 and 2308.10.3] 2308.4.2.1, 2308.7.1 and 2308.7.2.

| TABLE [721.6.2(3)] 722.6.2(3) MEMBRANEa ON EXTERIOR FACE OF WOOD STUD WALLS |
| --- |
| SHEATHING | PAPER | EXTERIOR FINISH |
| 5/8-inch T & G lumber 5/16-inch exterior glue plywood 1/2-inch gypsum wallboard 5/8-inch gypsum wallboard 1/2-inch fiberboard | Sheathing paper | Lumber siding Wood shingles and shakes 1/4-inch fiber-cement lap, panel or shingle siding 1/4-inch wood structural panels—exterior type 1/4-inch hardboard Metal siding Stucco on metal lath Masonry veneer Vinyl siding |
| None | — | 3/8-inch exterior-grade wood structural panels |

For SI: 1 inch = 25.4 mm.

a.	Any combination of sheathing, paper, and exterior finish is permitted.

| TABLE [721.6.2(4)] 722.6.2(4) FLOORING OR ROOFING OVER WOOD FRAMINGa |
| --- |
| ASSEMBLY | STRUCTURAL MEMBERS | SUBFLOOR OR ROOF DECK | FINISHED FLOORING OR ROOFING |
| Floor | Wood | 15/32-inch wood structural panels or 11/16 inch T & G softwood | Hardwood or softwood flooring on building paper resilient flooring, parquet floor felted-synthetic fiber floor coverings, carpeting, or ceramic tile on 1/4-inch-thick fiber-cement underlayment or 3/8-inch-thick panel-type underlay Ceramic tile on 11/4-inch mortar bed |
| Roof | Wood | 15/32-inch wood structural panels or 11/16 inch T & G softwood | Finished roofing material with or without insulation |

For SI: 1 inch = 25.4 mm.

a.	This table applies only to wood joist construction. It is not applicable to wood truss construction.

| TABLE [721.6.2(5)] 722.6.2(5) TIME ASSIGNED FOR ADDITIONAL PROTECTION |
| --- |
| DESCRIPTION OF ADDITIONAL PROTECTION | FIRE RESISTANCE (minutes) |
| Add to the fire-resistance rating of wood stud walls if the spaces between the studs are completely filled with glass fiber mineral wool batts weighing not less than 2 pounds per cubic foot (0.6 pound per square foot of wall surface) or rockwool or slag material wool batts weighing not less than 3.3 pounds per cubic foot (1 pound per square foot of wall surface), or cellulose insulation having a nominal density not less than 2.6 pounds per cubic foot. | 15 |
| For SI: 1 pound/cubic foot = 16.0185 kg/m3. |  |

[721.6.2.1] 722.6.2.1 Fire-resistance rating of wood frame assemblies. The fire-resistance rating of a wood frame assembly is equal to the sum of the time assigned to the membrane on the fire-exposed side, the time assigned to the framing members and the time assigned for additional contribution by other protective measures such as insulation. The membrane on the unexposed side shall not be included in determining the fire resistance of the assembly.

[721.6.2.2] 722.6.2.2 Time assigned to membranes. Table [721.6.2(1)] 722.6.2(1) indicates the time assigned to membranes on the fire-exposed side.

[721.6.2.3] 722.6.2.3 Exterior walls. For an exterior wall with a fire separation distance greater than 5 feet (1524 mm), the wall is assigned a rating dependent on the interior membrane and the framing as described in Tables [721.6.2(1)] 722.6.2(1) and [721.6.2(2)] 722.6.2(2). The membrane on the outside of the nonfire-exposed side of exterior walls with a fire separation distance greater than 5 feet (1524 mm) [may] shall consist of sheathing, sheathing paper[,] and siding as described in Table [721.6.2(3)] 722.6.2(3).

[721.6.2.4] 722.6.2.4 Floors and roofs. In the case of a floor or roof, the standard test provides only for testing for fire exposure from below. Except as noted in Section 703.3, Item 5, floor or roof assemblies of wood framing shall have an upper membrane consisting of a subfloor and finished floor conforming to Table [721.6.2(4)] 722.6.2(4) or any other membrane that has a contribution to fire resistance of [at least] not less than 15 minutes in Table [721.6.2(1)] 722.6.2(1).

[721.6.2.5] 722.6.2.5 Additional protection. Table [721.6.2(5)] 722.6.2(5) indicates the time increments to be added to the fire resistance where glass fiber, rock wool, slag mineral wool[,] or cellulose insulation is incorporated in the assembly.

[721.6.2.6] 722.6.2.6 Fastening. Fastening of wood frame assemblies and the fastening of membranes to the wood framing members shall be done in accordance with Chapter 23.

[721.6.3 Design of fire-resistant exposed wood members. The fire-resistance rating, in minutes, of timber beams and columns with a minimum nominal dimension of 6 inches (152 mm) is equal to:]

[Beams:	 for beams which may be exposed to fire on four sides.

(Equation 7-18)]

[ for beams which may be exposed to fire on three sides.

(Equation 7-19)]

[Columns:	 for columns which may be exposed to fire on four sides.

(Equation 7-20)]

[for columns which may be exposed to fire on three sides.

(Equation 7-21)]

[where:]

The breadth (width) of a beam or larger side of a column before exposure to fire (inches).]

The depth of a beam or smaller side of a column before exposure to fire (inches).]

Load factor, based on Figure 721.6.3(1).]

[721.6.3.1 Equation 7-21. Equation 7-21 applies only where the unexposed face represents the smaller side of the column. If a column is recessed into a wall, its full dimension shall be used for the purpose of these calculations.]

[FIGURE 721.6.3(1)]
[LOAD FIGURE]

[Ke = The effective length factor as noted in Figure 72 1.6.3(2).]

[l = The unsupported length of columns (inches).]

[FIGURE 721.6.3(2)]
[EFFECTIVE LENGTH FACTORS]

[721.6.3.2 Allowable loads. Allowable loads on beams and columns are determined using design values given in AF&PA NDS.]

[721.6.3.3 Fastener protection. Where minimum 1-hour fire resistance is required, connectors and fasteners shall be protected from fire exposure by 1½ inches (38 mm) of wood, or other approved covering or coating for a 1-hour rating. Typical details for commonly used fasteners and connectors are shown in AITC Technical Note 7.]

[721.6.3.4 Minimum size. Wood members are limited to dimensions of 6 inches (152 mm) nominal or greater. Glued-laminated timber beams utilize standard laminating combinations except that a core lamination is removed. The tension zone is moved inward and the equivalent of an extra nominal 2-inch-thick (51 mm) outer tension lamination is added.]

[721.7 Other reference documents. Refer to Section 703.3, Item 1, and NBS BMS 71 and NBS TRBM 44 for fire-resistance ratings of materials and assemblies.]

§ 9. Chapter 8 of the New York city building code, as amended by local law number 141 for the year 2013, is amended to read as follows:

CHAPTER 8
INTERIOR FINISHES

SECTION BC 801
GENERAL

801.1 Scope. [Provisions] The provisions of this chapter shall govern the use of materials used as interior finishes, trim and decorative materials.

801.2 Interior wall and ceiling finish. The provisions of Section 803 shall limit the allowable fire performance and smoke development of interior wall and ceiling finish materials based on occupancy classification.

801.3 Interior floor finish. The provisions of Section 804 shall limit the allowable fire performance of interior floor finish materials based on occupancy classification.

801.4 Decorative materials and trim. Decorative materials and trim shall be restricted by combustibility [and the], fire performance or flame propagation performance criteria [of NFPA 701,] in accordance with Section 806.

801.5 Applicability in flood hazard areas. For buildings in flood hazard areas as established in Appendix G, interior finishes, trim and decorative materials below the design flood elevation shall be flood-damage-resistant materials.

801.6 Application. Combustible materials complying with the requirements of this chapter shall be permitted to be used as finish for walls, ceilings, floors and other interior surfaces of buildings.

801.7 Windows. Show windows in the exterior walls of the first story above grade plane shall be permitted to be of wood or of unprotected metal framing.

801.8 Foam plastics. Foam plastics shall not be used as interior finish except as provided in Section 803.4. Foam plastics shall not be used as interior trim except as provided in Section [806.3] 806.5 or 2604.2. This section shall apply both to exposed foam plastics and to foam plastics used in conjunction with a textile or vinyl facing or cover.

SECTION BC 802
DEFINITIONS

802.1 [General] Definitions. The following [words and] terms [shall, for the purposes of this chapter and as used elsewhere in this code, have the meanings shown herein.] are defined in Chapter 2:

EXPANDED VINYL WALL COVERING. [Wall covering consisting of a woven textile backing, an expanded vinyl base coat layer and a non-expanded vinyl skin coat. The expanded base coat layer is a homogeneous vinyl layer that contains a blowing agent. During processing, the blowing agent decomposes, causing this layer to expand by forming closed cells. The total thickness of the wall covering is approximately 0.055 inch to 0.070 inch (1.4 mm to 1.8 mm).]

FLAME SPREAD. [The propagation of flame over a surface.]

FLAME SPREAD INDEX. [A comparative measure, expressed as a dimensionless number, derived from visual measurements of the spread of flame versus time for a material tested in accordance with ASTM E 84.]

INTERIOR FINISH. [Interior finish includes interior wall and ceiling finish and interior floor finish.]

INTERIOR FLOOR FINISH. [The exposed floor surfaces of buildings including coverings applied over a finished floor or stair, including risers.]

INTERIOR FLOOR-WALL BASE. [Interior floor finish trim used to provide a functional and/or decorative border at the intersection of walls and floors.]

INTERIOR WALL AND CEILING FINISH. [The exposed interior surfaces of buildings including, but not limited to: fixed or movable walls and partitions; toilet room privacy partitions; columns; ceilings; and interior wainscoting, paneling or other finish applied structurally or for decoration, acoustical correction, surface insulation, structural fire resistance or similar purposes, but not including trim.]

SITE-FABRICATED STRETCH SYSTEM. [A system, fabricated on site and intended for acoustical, tackable or aesthetic purposes, that is comprised of three elements: (a) a frame (constructed of plastic, wood, metal or other material) used to hold fabric in place, (b) a core material (infill, with the correct properties for the application), and (c) an outside layer, comprised of a textile, fabric or vinyl, that is stretched taut and held in place by tension or mechanical fasteners via the frame.]

SMOKE-DEVELOPED INDEX. [A comparative measure, expressed as a dimensionless number, derived from measurements of smoke obscuration versus time for a material tested in accordance with ASTM E 84.]

TRIM. [Picture molds, chair rails, baseboards, handrails, door and window frames and similar decorative or protective materials used in fixed applications.]

SECTION BC 803
WALL AND CEILING FINISHES

803.1 General. Interior wall and ceiling finish materials shall be accepted as compliant for fire performance and smoke development in accordance with Section 803.1.1 or Section 803.1.2, and installed in accordance with the criteria therein. [Materials tested in accordance with Section 803.1.2 shall not be required to be tested in accordance with Section 803.1.1.]

[Exceptions:]

803.1.1 Interior wall and ceiling finish materials. Interior wall and ceiling finish materials shall be tested and classified in accordance with ASTM E 84 or UL 723. Such interior finish materials shall be grouped in the following classes in accordance with their flame spread and smoke-developed indexes.

Class A = Flame spread index 0-25; smoke developed index 0-450.

Class B = Flame spread index 26-75; smoke developed index 0-450.

Class C = Flame spread index 76-200; smoke developed index 0-450.

Exception: Materials tested in accordance with Section 803.1.2 need not be classified in accordance with Section 803.1.1.

803.1.2 Room corner test for interior wall or ceiling finish materials. As an alternative to Section 803.1.1, interior wall or ceiling finish materials shall be permitted to be tested in accordance with NFPA 286. Interior wall or ceiling finish materials tested in accordance with NFPA 286 shall comply with Section 803.1.2.1.

803.1.2.1 Acceptance criteria for NFPA 286. The interior finish shall comply with the following:

1.	During the 40 kW exposure, flames shall not spread to the ceiling.

2.	The flame shall not spread to the outer extremity of the sample on any wall or ceiling.

3.	Flashover, as defined in NFPA 286, shall not occur.

4.	The peak heat release rate throughout the test shall not exceed 800 kW.

5.	The total smoke released throughout the test shall not exceed 10,764 square feet (1,000 m2).

803.1.3 Room corner test for textile wall coverings and expanded vinyl wall coverings. Textile wall coverings and expanded vinyl wall coverings shall meet the criteria of Section 803.1.3.1 when tested in the manner intended for use in accordance with the Method B protocol of NFPA 265 using the product-mounting system, including adhesive.

803.1.3.1 Acceptance criteria for NFPA 265. The interior finish shall comply with the following:

1.	During the 40 kW exposure, flames shall not spread to the ceiling.

2.	The flame shall not spread to the outer extremities of the samples on the 8-foot by 12-foot (203 mm by 305 mm) walls.

3.	Flashover, as defined in NFPA 265, shall not occur.

4.	The total smoke released throughout the test shall not exceed 10,764 square feet (1,000 m2).

803.1.4 Flame-spread and smoke-developed tests for textile wall or ceiling coverings. Specimens shall be tested and indexed per ASTM E 84 or UL 723, and classified for flame spread per Section 803.1.4.1.

803.1.4.1 Acceptance criteria for textile and expanded vinyl wall or ceiling coverings tested to ASTM E 84 or UL 723. Textile wall and ceiling coverings and expanded vinyl wall and ceiling coverings shall have a Class A flame spread index per Section 803.1.1; shall meet the smoke developed index requirements of Section 803.1.1; and shall be protected by an automatic sprinkler system installed in accordance with Section 903.3.1.1 or 903.3.1.2. Test specimen preparation and mounting shall be in accordance with ASTM E 2404.

[1.] 803.2 Thickness exemption. Materials having a thickness less than 0.036 inch (0.9 mm) applied directly to the surface of walls or ceilings shall not be required to be tested.

[2.] 803.3 Heavy timber exemption. Exposed portions of [structural members] building elements complying with the requirements for buildings of Type IV construction in Section 602.4 shall not be subject to interior finish requirements.

803.4 Foam plastics. Foam plastics shall not be used as interior finish except as provided in Section 2603.9. This section shall apply both to exposed foam plastics and to foam plastics used in conjunction with a textile or vinyl facing or cover.

[3.] 803.5 Textile wall coverings. Where used as interior wall finish materials, textile wall coverings, including materials having woven or nonwoven, napped, tufted, looped or similar surface and carpet and similar textile materials, shall be tested in the manner intended for use, using the product mounting system, including adhesive, and shall comply with the requirements of Section 803.1.2, 803.1.3 or 803.1.4.1.

[4.] 803.6 Textile ceiling coverings. Where used as interior ceiling finish materials, textile ceiling coverings, including materials having woven or nonwoven, napped, tufted, looped or similar surface and carpet and similar textile materials, shall be tested in the manner intended for use, using the product mounting system, including adhesive, and shall comply with the requirements of Section 803.1.2 or 803.1.4.1.

[5.] 803.7 Expanded vinyl wall coverings. Where used as interior wall finish materials, expanded vinyl wall coverings shall be tested in the manner intended for use, using the product mounting system, including adhesive, and shall comply with the requirements of Section 803.1.2, 803.1.3 or 803.1.4.1.

[6.] 803.8 Expanded vinyl ceiling coverings. Where used as interior ceiling finish materials, expanded vinyl ceiling coverings shall be tested in the manner intended for use, using the product mounting system, including adhesive, and shall comply with the requirements of Section 803.1.2 or 803.1.4.1.

[7.] 803.9 High-density polyethylene (HDPE) and polypropylene (PP). Where high-density polyethylene or polypropylene is used as an interior finish[,] it shall comply with [the requirements of] Section 803.1.2.

[8.] 803.10 Site-fabricated stretch systems. Where used as interior wall or interior ceiling finish materials, site-fabricated stretch systems containing all three components described in the definition in Chapter 2 shall be tested in the manner intended for use, and shall comply with the requirements of Section 803.1.1 or 803.1.2. If the materials are tested in accordance with ASTM E 84 or UL 723, specimen preparation and mounting shall be in accordance with ASTM E 2573.

| [TABLE 803.1 INTERIOR WALL AND CEILING FINISH REQUIREMENTS BY OCCUPANCYk |
| --- |
| GROUP | SPRINKLEREDl | NONSPRINKLERED |
|  | Exit enclosures and exit passagewaysa,b | Corridors | Rooms and enclosed spacesc | Exit enclosures and exit passagewaysa,b | Corridors | Rooms and enclosed spacesc |
| A-1 & A-2 | B | B | C | A | Ad | Be |
| A-3f, A-4, A-5 | B | B | C | A | Ad | C |
| B, E, M, R-1 | B | B | B | A | A | B |
| F | B | C | C | A | B | B |
| H | B | B | Cg | A | A | B |
| I-1 | B | C | C | A | B | B |
| I-2 | B | B | Bh,i | A | A | B |
| I-3 | A | Aj | C | A | A | B |
| I-4 | B | B | Bh,i | A | A | B |
| R-2 | B | B | C | A | A | C |
| R-3 | C | C | C | C | C | C |
| S | B | C | C | A | B | C |
| U | No restrictions | No restrictions |

For SI: 1 inch = 25.4 mm, 1 square foot = 0.0929 m2.

a.	Class C interior finish materials shall be permitted for wainscotting or paneling of not more than 1,000 square feet of applied surface area in the grade lobby where applied directly to a noncombustible base or over furring strips applied to a noncombustible base and fireblocked as required by Section 803.3.1.

b.	In exit enclosures of buildings less than three stories above grade plane of other than Group I-3, Class B interior finish for nonsprinklered buildings and Class C interior finish for sprinklered buildings shall be permitted.

c.	Requirements for rooms and enclosed spaces shall be based upon spaces enclosed by partitions. Where a fire-resistance rating is required for structural elements, the enclosing partitions shall extend from the floor to the ceiling. Partitions that do not comply with this shall be considered enclosing spaces and the rooms or spaces on both sides shall be considered one. In determining the applicable requirements for rooms and enclosed spaces, the specific occupancy thereof shall be the governing factor regardless of the group classification of the building or structure.

d.	Lobby areas in Group A-1, A-2 and A-3 occupancies shall not be less than Class B materials.

e.	Class C interior finish materials shall be permitted in places of assembly with an occupant load of 300 persons or less.

f.	For churches and places of worship, wood used for ornamental purposes, trusses, paneling or chancel furnishing shall be permitted.

g.	Class B material is required where the building exceeds two stories.

h.	Class C interior finish materials shall be permitted in administrative spaces.

i.	Class C interior finish materials shall be permitted in rooms with a capacity of four persons or less.

j.	Class B materials shall be permitted as wainscotting extending not more than 48 inches above the finished floor in exit access corridors.

k.	Finish materials as provided for in other sections of this code.

l.	Applies when the exit enclosures, exit passageways, corridors, or rooms and enclosed spaces are protected by a sprinkler system installed in accordance with Section 903.3.1.1 or 903.3.1.2.]

[803.1.1 Flame-spread and smoke-development tests. Interior wall and ceiling finish materials shall be tested and accorded indices for flame spread and smoke development in accordance with ASTM E 84 or UL 723.]

[803.1.1.1 Classification of flame spread indices. Such interior finish materials shall be grouped in the following flame spread classes in accordance with their flame spread index.]

[Class A: Flame spread 0-25.]

[Class B: Flame spread 26-75.]

[Class C: Flame spread 76-200.]

[803.1.1.2 Interior flame spread index requirements based on occupancy group. Interior wall and ceiling finish shall have a flame spread index not greater than that for the classification rating specified in Table 803.1 for the group and location designated.]

[803.1.1.3 Interior smoke developed index requirements based on occupancy group. Except where permitted for interior trim in Section 806.5, acceptable smoke-developed indices shall range from 0-450 with the following restrictions:]

[Exits, corridors				25 or less]

[Occupancy Group I				50 or less]

[Rooms in which the net floor area]

[per occupant is 10 square feet or less]	[100 or less]

[803.1.2 Room corner test for interior wall or ceiling finish materials (including textiles). As an alternative to Section 803.1.1, interior wall or ceiling finish materials shall be permitted to be tested in accordance with NFPA 286. Interior wall or ceiling finish materials tested in accordance with NFPA 286 shall comply with Section 803.1.2.1. Interior wall and ceiling finish materials tested in accordance with NFPA 286 and meeting the acceptance criteria of Section 803.1.2.1, shall be permitted to be used where a Class A classification in accordance with ASTM E 84 or UL 723 is required.]

[803.1.2.1 Acceptance criteria for NFPA 286. During the 40 kW exposure, the interior finish shall comply with Item 1. During the 160 kW exposure, the interior finish shall comply with Item 2. During the entire test, the interior finish shall comply with Items 3 and 4.]

[1.	During the 40 kW exposure, flames shall not spread to the ceiling.]

[2.	During the 160 kW exposure, the interior finish shall comply with the following:]

[2.1. Flame shall not spread to the outer extremity of the sample on any wall or ceiling.]

[2.2. Flashover, as defined in NFPA 286, shall not occur.]

[3.	The peak rate of heat release throughout the NFPA 286 test shall not exceed 800 kW.]

[4.	The total smoke released throughout the NFPA 286 test shall not exceed 10,764 square feet (1,000 m2).]

[803.1.3 Room corner test for textile wall coverings and expanded vinyl wall coverings. Textile wall coverings and expanded vinyl wall coverings shall meet the criteria of Section 803.1.3.1 when tested in the manner intended for use in accordance with the Method B protocol of NFPA 265 using the product-mounting system, including adhesive.]

[803.1.3.1 Acceptance criteria for NFPA 265. During the 40 kW exposure the interior finish shall comply with Item 1. During the 150 kW exposure, the interior finish shall comply with Item 2. During the entire test, the interior finish shall comply with Item 3.]

[1.	During the 40 kW exposure, flames shall not spread to the ceiling.]

[2.	During the 150 kW exposure, the interior finish shall comply with the following:]

[2.1.	Flame shall not spread to the outer extremities of the samples on the 8-foot by 12-foot (203 mm by 305 mm) walls.]

[2.2.	Flashover, as described in NFPA 265, shall not occur.]

[3.	The total smoke released throughout the NFPA 265 test shall not exceed 10,764 square feet (1,000 m2).]

[803.1.4 Flame-spread and smoke-development tests for textile wall or ceiling coverings. Specimens shall be tested and indexed per ASTM E 84 or UL 723, and classified for flame spread per Section 803.1.4.1.]

[803.1.4.1 Acceptance criteria for textile and expanded vinyl wall or ceiling coverings tested to ASTM E 84 or UL 723. Textile wall and ceiling coverings and expanded vinyl wall and ceiling coverings shall have a Class A flame spread index per Section 803.1.1.1; shall meet the smoke-developed index requirements of Section 803.1.1.3; and shall be protected by an automatic sprinkler system installed in accordance with Section 903.3.1.1 or 903.3.1.2.]

803.11 Interior finish requirements based on group. Interior wall and ceiling finish shall have a flame spread index and smoke-developed index not greater than that specified in Table 803.11 for the group and location designated. Interior wall and ceiling finish materials tested in accordance with NFPA 286 and meeting the acceptance criteria of Section 803.1.2.1, shall be permitted to be used where a Class A classification, in accordance with ASTM E 84 or UL 723, is required.

| TABLE 803.11 INTERIOR WALL AND CEILING FINISH REQUIREMENTS BY OCCUPANCYk |
| --- |
| GROUP | SPRINKLEREDl | NONSPRINKLERED |
|  | Interior exit stairways, interior exit ramps and exit passagewaysa,b | Corridors and enclosure for exit access stairways and exit access ramps | Rooms and enclosed spacesc | Interior exit stairways, interior exit ramps and exit passagewaysa,b | Corridors and enclosure for exit access stairways and exit access ramps | Rooms and enclosed spacesc |
| A-1 & A-2 | B | B | C | A | Ad | Be |
| A-3f, A-4, A-5 | B | B | C | A | Ad | C |
| B, E, M, R-1 | B | B | B | A | A | B |
| F | B | C | C | A | B | B |
| H | B | B | Cg | A | A | B |
| I-1 | B | C | C | A | B | B |
| I-2 | B | B | Bh,i | A | A | B |
| I-3 | A | Aj | C | A | A | B |
| I-4 | B | B | Bh,i | A | A | B |
| R-2 | B | B | C | A | A | C |
| R-3 | C | C | C | C | C | C |
| S | B | C | C | A | B | C |
| U | No restrictions | No restrictions |

For SI: 1 inch = 25.4 mm, 1 square foot = 0.0929 m2.

a.	Class C interior finish materials shall be permitted for wainscotting or paneling of not more than 1,000 square feet (92 m2) of applied surface area in the grade lobby where applied directly to a noncombustible base or over furring strips applied to a noncombustible base and fireblocked as required by Section 803.13.1.

b.	In other than Group I-3 occupancies in buildings less than three stories above grade plane, Class B interior finish for nonsprinklered buildings and Class C interior finish for sprinklered buildings shall be permitted in interior exit stairways and ramps.

c.	Requirements for rooms and enclosed spaces shall be based upon spaces enclosed by partitions. Where a fire-resistance rating is required for structural elements, the enclosing partitions shall extend from the floor to the ceiling. Partitions that do not comply with this shall be considered enclosing spaces and the rooms or spaces on both sides shall be considered one. In determining the applicable requirements for rooms and enclosed spaces, the specific occupancy thereof shall be the governing factor regardless of the group classification of the building or structure.

d.	Lobby areas in Group A-1, A-2 and A-3 occupancies shall not be less than Class B materials.

e.	Class C interior finish materials shall be permitted in places of assembly with an occupant load of 300 persons or less.

f.	For places of religious worship, wood used for ornamental purposes, trusses, paneling or chancel furnishing shall be permitted.

g.	Class B material is required where the building exceeds two stories.

h.	Class C interior finish materials shall be permitted in administrative spaces.

i.	Class C interior finish materials shall be permitted in rooms with a capacity of four persons or less.

j.	Class B materials shall be permitted as wainscotting extending not more than 48 inches above the finished floor in corridors and exit access stairways and ramps.

k.	Finish materials as provided for in other sections of this code.

l.	Applies when protected by an automatic sprinkler system installed in accordance with Section 903.3.1.1 or 903.3.1.2.

[803.2] 803.12 Stability. Interior finish materials regulated by this chapter shall be applied or otherwise fastened in such a manner that such materials will not readily become detached where subjected to room temperatures of 200°F (93°C) for not less than 30 minutes.

[803.3] 803.13 Application of interior finish materials to fire-resistance-rated [structural] or noncombustible building elements. Where interior finish materials are applied on walls, ceilings or structural elements required to have a fire-resistance rating or to be of noncombustible construction, [they] these finish materials shall comply with the provisions of this section.

[803.3.1] 803.13.1 Direct attachment and furred construction. Where walls and ceilings are required by any provision in this code to be of fire-resistance-rated or noncombustible construction, the interior finish material shall be applied directly against such construction or to furring strips not exceeding 13/4 inches (44 mm), applied directly against such surfaces.[The intervening spaces between such furring strips shall comply with one of the following:]

803.13.1.1 Furred construction. If the interior finish material is applied to furring strips, the intervening spaces between such furring strips shall comply with one of the following:

1.	Be filled with material that is inorganic or noncombustible;

2.	Be filled with material that meets the requirements of a Class A material in accordance with Section 803.1.1 or 803.1.2; or

3.	Be [fire blocked] fireblocked at a maximum of 8 feet (2438 mm) in [any] every direction in accordance with Section [BC 717] 718.

[803.3.2] 803.13.2 Set-out construction. Where walls and ceilings are required to be of fire-resistance-rated or noncombustible construction and walls are set out or ceilings are dropped distances greater than specified in Section [803.3.1] 803.13.1, Class A finish materials, in accordance with Section 803.1.1 or 803.1.2, shall be used [except where].

Exceptions:

1.	Where interior finish materials are protected on both sides by an automatic sprinkler system in accordance with Section 903.3.1.1 or 903.3.1.2 [or attached to noncombustible backing or furring strips installed as specified in Section 803.3.1].

2.	Where interior finish materials are attached to noncombustible backing or furring strips installed as specified in Section 803.13.1.1.

803.13.2.1 Hangers and assembly members. The hangers and assembly members of such dropped ceilings that are below the [main ceiling line] horizontal-fire-resistance-rated floor or roof assemblies shall be of noncombustible materials[, except that in Types III and V construction, fire-retardant-treated wood shall be permitted]. The construction of each [set-out] set out wall and horizontal fire-resistance-rated floor or roof assembly shall be of fire-resistance-rated construction as required elsewhere in this code.

Exception: In Type III and V construction, fire-retardant-treated wood shall be permitted for use as hangers and assembly members of dropped ceilings.

[803.3.3 Attachment to heavy] 803.13.3 Heavy timber construction. Wall and ceiling finishes of all classes as permitted in this chapter that are installed directly against the wood decking or planking of Type IV construction or to wood furring strips applied directly to the wood decking or planking shall be fireblocked as specified in Section [803.3.1] 803.13.1.1.

[803.3.4] 803.13.4 Materials. An interior wall or ceiling finish material that is not more than ¼ inch (6.4 mm) thick shall be applied directly [against a noncombustible backing] onto the wall, ceiling or building element without the use of furring strips and shall not be suspended away from the building element to which that finish material is applied.

Exceptions:

1.	Noncombustible interior finish materials.

2.	Materials that meet the requirements of Class A materials in accordance with Section 803.1.1 or 803.1.2 where the qualifying tests were made with the material [suspended or] furred out from the noncombustible backing.

3.	Materials that meet the requirements of Class A materials in accordance with Section 803.1.1 or 803.1.2 where the qualifying tests were made with the material suspended away from the noncombustible backing shall be permitted to be used suspended away from the building element.

[803.4 Foam plastics. Foam plastics shall not be used as interior finish except as provided in Section 2603.9. This section shall apply both to exposed foam plastics and to foam plastics used in conjunction with a textile or vinyl facing or cover.]

[803.5 Toxicity. Interior wall or ceiling finishes, other than textiles, upon exposure to fire, shall not produce products of decomposition or combustion that are more toxic in point of concentration than those given off by wood or paper when decomposing or burning under comparable conditions as tested in accordance with NFPA 269.]

SECTION BC 804
INTERIOR FLOOR FINISH

804.1 General. Interior floor finish and floor covering materials shall comply with this section.

804.2 Classification. Interior floor finish and floor covering materials required by Section 804.4.1 to be of Class I or II materials shall be classified in accordance with NFPA 253 or ASTM E 648. The classification referred to herein corresponds to the classifications determined by NFPA 253 or ASTM E 648 as follows: Class I, 0.45 watts/cm2 or greater; Class II, 0.22 watts/cm2 or greater.

804.3 Testing and identification. Interior floor finish and floor covering materials shall be tested by an approved agency in accordance with NFPA 253 or ASTM E 648 and identified by a hang tag or other suitable method so as to identify the manufacturer or supplier and style, and shall indicate the interior floor finish or floor covering classification [according to] in accordance with Section 804.2. Carpet-type floor coverings shall be tested as proposed for use, including underlayment. Test reports confirming the information provided in the manufacturer’s product identification shall be furnished to the department upon request.

804.4 Interior floor finish limitations. In buildings and spaces classified in Occupancy Group H and in all exits and exit passageways of any occupancy group, floor finishes shall be of noncombustible materials.

Exception: Interior floor finish may be of combustible materials in the following spaces. Carpet-type materials must be able to withstand a minimum critical radiant flux as specified in Section 804.4.1.

1.	Buildings of Type VB Construction.

2.	Interior stairs in buildings of Type III, IV and V construction in Occupancy Group B, F, M or S-2, when the buildings are two stories in height or less.

3.	Interior stairs in buildings of Type III, IV and V construction in Occupancy Groups R-2 and R-3 when the buildings are three stories in height or less.

4.	Interior stairs in buildings of Type III, IV and V construction in Occupancy Group R-2 when occupied by three families or less.

804.4.1 Minimum critical radiant flux. Interior floor finishes shall not be less than Class I in Occupancy Groups I-2 and I-3 and not less than Class II in Occupancy Groups A, B, E, H, I-4, M, R-1, R-2 and S. In all other occupancy groups, the interior floor finish shall comply with the DOC FF-1 “pill test” (CPSC 16 CFR, Part 1630).

804.5 Volatile organic compounds emissions in carpet and carpet cushion. [On and after July 1, 2013 carpet] Carpet and carpet cushion as defined in Section 17-1401 of the Administrative Code shall comply with the limits on volatile organic compound emissions set forth in Chapter 14 of Title 17 of such code.

SECTION BC 805
COMBUSTIBLE FLOORING MATERIALS IN TYPES I AND II
CONSTRUCTION

805.1 Application. Combustible materials installed on or embedded in floors of buildings of Type I or II construction shall comply with Sections 805.1.1 through 805.1.4.

[Exception] Exceptions:

- Stages and platforms constructed in accordance with Sections 410.3 and 410.4, respectively.

2.	Bleachers, grandstands and folding and telescopic seating within assembly spaces constructed in accordance with Section 1029.1.1.

805.1.1 Subfloor construction. Floor sleepers, bucks and nailing blocks shall not be constructed of combustible materials, unless the space between the fire-resistance-rated floor assembly and the flooring is either solidly filled with noncombustible materials or fireblocked in accordance with Section [717] 718, and provided that such open spaces shall not extend under or through permanent partitions or walls.

805.1.2 Wood finish flooring. Wood finish flooring is permitted to be attached directly to the embedded or fireblocked wood sleepers and shall be permitted where cemented directly to the top surface of approved fire-resistance-rated floor assemblies or directly to a wood subfloor attached to sleepers as provided for in Section 805.1.1.

805.1.3 Insulating boards. Combustible insulating boards not more than ½-inch (12.7 mm) thick and covered with finish flooring are permitted where attached directly to a noncombustible floor assembly or to wood subflooring attached to sleepers as provided for in Section 805.1.1.

805.1.4 Carpet-type floor coverings. Carpet-type floor coverings are permitted where cemented directly to the top surface of approved fire-resistance-rated construction or directly to a wood subfloor attached to sleepers as provided for in Section 805.1.1.

SECTION BC 806
DECORATIVE MATERIALS AND TRIM

806.1 Decorations. All decorations shall comply with the requirements of the New York City Fire Code.

806.2 Reserved.

806.3 Reserved.

806.4 Reserved.

806.5 Foam plastic as trim. Foam plastic used as trim shall comply with Section 2604.2 and shall not be permitted in [Group R-3] occupancies other than Group R-3, within individual dwelling units of Group R-1 and R-2 occupancies, [and where] or unless approved in accordance with [the special provisions of] Section 2603.9. [Foam plastics used as trim in any occupancy shall comply with the requirements of Section 2604.2.]

[806.4] 806.6 Pyroxylin plastic. Imitation leather or other material consisting of or coated with a pyroxylin or similarly hazardous base shall not be used in Group A occupancies.

[806.5] 806.7 Interior trim. Material, other than foam plastic used as interior trim, shall have a minimum Class C flame spread index [as described in Section 803.1.1] and maximum smoke-developed index [of 450,] when tested in accordance with ASTM E 84 or UL 723 as described in Section 803.1.1. Combustible trim, excluding handrails and guardrails, shall not exceed 10 percent of the specific wall or ceiling area in which it is attached.

[806.6] 806.8 Interior floor-wall base. Interior floor-wall base that is 6 inches (152 mm) or less in height shall be tested in accordance with Section 804.2 and shall be not [be] less than Class II. Where a Class I floor finish is required, the floor-wall base shall be Class I.

Exception: Interior trim materials that comply with Section [806.5] 806.7.

SECTION BC 807
INSULATION

807.1 Insulation. Thermal and acoustical insulation shall comply with Section [719] 720.

SECTION BC 808
ACOUSTICAL CEILING SYSTEMS

808.1 Acoustical ceiling systems. The quality, design, fabrication and erection of metal suspension systems for acoustical tile and lay-in panel ceilings in buildings or structures shall conform [with] to generally accepted engineering practice, the provisions of this chapter and other applicable requirements of this code.

808.1.1 Materials and installation. Acoustical materials complying with the interior finish requirements of Section 803 shall be installed in accordance with the manufacturer’s recommendations and applicable provisions for applying interior finish.

808.1.1.1 Suspended acoustical ceilings. Acoustical ceilings that are to be suspended below floor or roof construction by means of a framing system shall consist of supporting hangers of minimum ¼-inch diameter (6.4 mm) steel rods, carrying channels of minimum 1½-inch deep (38 mm) cold-rolled steel weighing [0.457] 0.440 pounds per linear foot [(0.707 kg/m)] (0.681 kg/m), and a supporting grid complying with Appendix R. Use of wire hangers shall not be permitted. Direct hung suspension systems shall not be permitted.

Exception: Acoustical ceiling systems in [Group] Groups R-2 and R-3 occupancies shall be permitted to be installed in accordance with ASTM C 635 and ASTM C 636 without modifications.

808.1.1.2 Fire-resistance-rated construction. Acoustical ceiling systems that are part of fire-resistance-rated construction shall be installed in the same manner used in the assembly tested and shall comply with the provisions of Chapter 7.

§ 10. Chapter 9 of the New York city building code, as amended by local law number 141 for the year 2013, the definition of “Natural Gas Alarm” and sections 28-908.7.1.1.2 and 28-908.10 as added by local law number 157 for the year 2016, sections 28-903.1.1, 28-903.2.11.9, 28-903.3.1.1.1, 28-903.3.3, 28-904.2, 28-904.2.1, 28-907.1, 28-907.1.1, 28-907.1.1.1, 28-908.10, 28-908.11 and 28-917.1.1 as amended by local law number 195 for the year 2018, section 28-903.2.2 as amended by local law number 78 for the year 2015, section 28-907.2.2 as added by local law number 51 for the year 2014, section 28-907.2.11.5 as added by local law number 113 for the year 2018, section 28-907.3.5 and item 8 of section 28-911.1.5 as added by local law number 17 for the year 2014, section 28-908.7 as amended by, and section 28-908.7.4 as renumbered by, local law number 10 for the year 2014, and section 28-908.7.3 as amended by, and section 28-908.7.3.1 as added by, local law number 191 for the year 2018, is amended to read as follows:

CHAPTER 9
FIRE PROTECTION SYSTEMS

SECTION BC 901
GENERAL

901.1 Scope. The provisions of this chapter shall specify where fire protection systems are required and shall apply to the design, installation and operation of fire protection systems.

901.1.1 Referenced standards. Where this code makes reference to the nationally recognized standards NFPA 13, NFPA 13D, NFPA 13R, NFPA 14, NFPA 20, [or] NFPA 72, or NFPA 92, such standard shall be as modified for New York City in accordance with Appendix Q.

901.2 Fire protection systems. Fire protection systems shall be installed, repaired, operated and maintained in accordance with this code and the New York City Fire Code. Any fire protection system for which an exception or reduction to the provisions of this code has been granted shall be considered to be a required system.

Exception: Any fire protection system or portion thereof not required by this code shall be permitted to be installed provided that such system meets the requirements of this code.

901.2.1 Fire protection systems within a building. Fire protection systems shall be dedicated to one building only.

Exception: Upon review and approval by the commissioner and the Fire Department, multiple buildings may be served by one fire protection system.

901.3 Modifications. No person shall remove or modify any fire protection system installed or maintained under the provisions of this code or the New York City Fire Code without approval by the commissioner.

901.4 Threads. Threads provided for Fire Department connections to sprinkler systems, standpipes, yard hydrants or any other fire hose connection shall be compatible with the connections used by the Fire Department.

901.5 Acceptance tests. Fire protection systems shall be tested in accordance with the requirements of this code and the New York City Fire Code. When required[,] by this chapter, the tests shall be conducted in the presence of the department [or] and performed by an approved agency. Tests required by this code, the New York City Fire Code and the standards listed in this code shall be conducted at the expense of the owner or the owner’s representative. It shall be unlawful to occupy portions of a structure until the required fire protection systems within that portion of the structure have been tested and approved.

901.6 Supervisory service. Where required, fire protection systems shall be monitored by a central supervising station in accordance with NFPA 72.

901.6.1 Automatic sprinkler systems. Automatic sprinkler systems shall be monitored by a central supervising station.

Exceptions:

1.	A central supervising station is not required for automatic sprinkler systems protecting one- and two-family dwellings.

2.	Limited area sprinkler systems serving [fewer] no more than [20] 6 sprinkler heads.

901.6.2 Fire alarm systems. Fire alarm systems required by the provisions of Section 907.2 of this code and the New York City Fire Code shall be monitored by a central supervising station in accordance with Section [907.14] 907.6.5.

Exceptions:

1.	Single- and multiple-station smoke alarms and carbon monoxide alarms required by Section 907.2.11.

2.	Smoke detectors in Group I-3 occupancies.

3.	Supervisory service is not required for automatic sprinkler systems in one- and two-family dwellings.

901.6.3 Group H. Manual fire alarm, automatic fire-extinguishing and emergency alarm systems in Group H occupancies shall be monitored by an approved supervising station.

Exception: When approved by the Fire Department, on-site monitoring at a constantly attended location shall be permitted provided that notifications to the Fire Department will be equal to those provided by a central supervising station.

901.7 Fire areas. Where buildings, or portions thereof, are divided into fire areas so as not to exceed the limits established for requiring a fire protection system in accordance with this chapter, such fire areas shall be separated by fire barriers constructed in accordance with Section 707 or horizontal assemblies constructed in accordance with Section [712] 711, or both, having a fire-resistance rating of not less than that determined in accordance with Section [707.3.9] 707.3.10.

901.8 Construction documents. Construction documents shall comply with Chapter 1 of Title 28 of the Administrative Code, Section 107 and other applicable provisions of this code and its referenced standards.

901.9 Special provisions for prior code buildings. The provisions of this chapter shall apply to alterations and changes of use or occupancy to prior code buildings in accordance with Sections 901.9.1 through 901.9.6.

901.9.1 Additions, alterations or repairs. Additions, alterations, renovations or repairs to existing systems shall conform to that required for new systems without requiring the existing system to comply with all of the requirements of this code, except as otherwise required in Sections 901.9.2 through 901.9.6. Additions, alterations or repairs shall not cause an existing installation to become unsafe, hazardous or overloaded.

901.9.1.1 Minor additions, alterations, renovations and repairs. Minor additions, alterations, renovations and repairs to existing systems shall meet the provisions for new construction, unless such work is done in the same manner and arrangement as was in the existing system, is not hazardous and is approved.

901.9.2 Additional requirements based on change of occupancy or use. Fire protection systems governed by this chapter shall be provided:

1.	To the entire building as if the building were hereafter erected, where a change is made in the main use or dominant occupancy of such building.

2.	Throughout a space, where a change is made in the occupancy group classification or usage of the space.

901.9.3 Additional requirements for enlargements. Fire protection systems shall be provided in enlarged portions of a building and where this chapter would require such systems in new construction for a space or building.

Exception: Section 901.9.3 shall not require sprinklers to be installed in enlarged portions of unsprinklered buildings to be occupied exclusively as one- or two-family dwellings. This exception shall not apply where sprinklers are otherwise required by the provisions of Sections 901.9.2 or 901.9.4.

901.9.4 Additional requirements based on value of alterations. Fire protection systems shall be provided to buildings and spaces in accordance with the provisions of Sections 901.9.4.1 through 901.9.4.3.

901.9.4.1 Alterations requiring fire protection systems throughout a building. If the value of alterations to the building equals or exceeds 60 percent of the value of the existing building, or, in the case of a building containing 4 or more dwelling units, 50 percent of the value of the existing building, the entire building shall be made to comply with the fire protection requirements of this chapter as if it were hereafter erected.

901.9.4.2 Alterations requiring fire protection systems in the space being altered. If the value of alterations of a space is between 30 percent and 60 percent of the value of the existing building, or, in the case of a building containing 4 or more dwelling units, if the value of alterations of a space is between 30 percent and 50 percent of the value of the existing building, those portions of the building being altered shall be made to comply with the fire protection requirements of this chapter.

901.9.4.3 Additional requirements for buildings containing 4 or more dwelling units. For buildings containing 4 or more dwelling units, if the value of alterations to an existing space classified in [occupancy group] Occupancy Group R-1 or R-2 exceeds 50 percent of the value of the space, such space shall be made to comply with the fire protection requirements of this chapter.

901.9.5 Additional provisions. In buildings or spaces not otherwise required to provide fire protection systems in accordance with this chapter, fire protection systems shall be provided for the types of alterations described in Sections 901.9.5.1 through 901.9.5.4.

901.9.5.1 Additional requirements for providing smoke and carbon monoxide alarms in dwelling units during alterations involving removal of existing interior finishes. Smoke and/or carbon monoxide alarms complying with the location, interconnection and power source requirements of this chapter shall be provided throughout a dwelling unit when alteration work results in the removal of existing and/or installation of new interior wall or ceiling finishes permitting the installation of concealed wiring for all the required alarms throughout the dwelling unit.

901.9.5.2 Additional requirements for providing standpipes in newly constructed stair shafts. Where an alteration includes the addition or replacement of an entire exit stair shaft that is a required means of egress, the entire shaft shall be equipped with a standpipe in accordance with Section 905.

901.9.5.3 Additional requirements for enlargements of buildings with existing standpipe systems. Where the alteration involves the addition of stories to a building with an existing standpipe system, and one or more stair shafts are not currently equipped with standpipes, standpipes shall be provided to all stair shafts in accordance with this chapter.

Exception: Additional standpipes are not required where:

1.	The alteration involves the addition of only one story;

2.	Existing standpipes in existing stair shafts are extended in accordance with this chapter;

3.	Standpipe hose connections are provided in compliance with Section 905.4, Item 6; and

4.	The demand on the standpipe system, including any additional demand, with respect to flow and pressure does not exceed the capacity of the existing approved system.

901.9.5.4 Additional requirements for enlargements of buildings with no existing standpipe systems. Where the alteration involves the addition of stories to a building with no existing standpipe system, standpipes shall be provided to all stair shafts in accordance with this chapter.

Exception: Standpipes are not required where:

1.	the alteration involves the addition of only one story;

2.	the completed building does not exceed 7 stories; and

3.	the completed building does not exceed 85 feet (25.9 m) in height.

901.9.6 Seismic supports. The determination as to whether seismic requirements apply to an alteration shall be made in accordance with the 1968 Building Code and interpretations by the department relating to such determinations. Any applicable seismic loads and requirements shall be permitted to be determined in accordance with Chapter 16 of this code or the 1968 Building Code and Reference Standard RS 9-6 of such code.

SECTION BC 902
DEFINITIONS

902.1 Definitions. The following [words and] terms [shall, for the purposes of this chapter, and as used elsewhere in this code, have the meanings shown herein.] are defined in Chapter 2:

ALARM NOTIFICATION APPLIANCE. [A fire alarm system component such as a bell, horn, speaker, light or text display that provides audible, tactile or visible outputs, or any combination thereof.]

ALARM SIGNAL. [A signal indicating an emergency requiring immediate action, such as a signal indicative of fire.]

ALARM VERIFICATION FEATURE. [A feature of automatic fire detection and alarm systems to reduce unwanted alarms wherein smoke detectors report alarm conditions for a minimum period of time, or confirm alarm conditions within a given time period, after being automatically reset, in order to be accepted as a valid alarm-initiation signal.]

ANIMAL SERVICE FACILITY.

ANNUNCIATOR. [A unit containing one or more indicator lamps, alphanumeric displays or other equivalent means in which each indication provides status information about a circuit, condition or location.]

AUDIBLE ALARM NOTIFICATION APPLIANCE. [A notification appliance that alerts by the sense of hearing.]

AUTOMATIC. [As applied to fire protection devices, a device or system providing an emergency function as a result of a predetermined temperature rise, rate of temperature rise or combustion products, without the necessity for human intervention.]

AUTOMATIC FIRE-EXTINGUISHING SYSTEM. [An approved system of devices and equipment that automatically detects a fire and discharges an approved fire-extinguishing agent onto or in the area of a fire.]

AUTOMATIC SMOKE DETECTION SYSTEM. [A fire alarm system that has initiation devices that utilize smoke detectors for protection of an area such as a room or space with detectors to provide early warning of fire.]

AUTOMATIC SPRINKLER SYSTEM. [An automatic sprinkler system, for fire protection purposes, is an integrated system of underground and overhead piping designed in accordance with fire protection engineering standards. The system includes a suitable water supply.  The portion of the system above the ground is a network of specially sized or hydraulically designed piping installed in a structure or area, generally overhead, and to which automatic sprinklers are connected in a systematic pattern. The system is usually activated by heat from a fire and discharges water over the fire area.]

AUTOMATIC WATER MIST SYSTEM.

AVERAGE AMBIENT SOUND LEVEL. [The root mean square, A-weighted sound pressure level measured over a 24-hour period, or the time any person is present, whichever time period is less.]

CARBON DIOXIDE EXTINGUISHING SYSTEMS. [A system supplying carbon dioxide (CO2) from a pressurized vessel through fixed pipes and nozzles. The system includes a manual- or automatic-actuating mechanism.]

CARBON MONOXIDE ALARM. [A single- or multiple- station alarm responsive to carbon monoxide.]

CARBON MONOXIDE DETECTOR. [A listed device that senses carbon monoxide.]

CARBON [MONOXIDE PRODUCING] MONOXIDE-PRODUCING EQUIPMENT. [Any furnace, boiler, water heater, fireplace, cooking appliance, gas clothes dryer, apparatus, appliance or device that burns coal, kerosene, oil, wood, fuel gases and other petroleum products including, but not limited to, methane, natural gas, liquefied natural gas and manufactured fuel gases.]

CEILING LIMIT. [The maximum concentration of an air-borne contaminant to which one may be exposed, as published in DOL 29 CFR Part 1910.1000.]

CLEAN AGENT. [Electrically nonconducting, volatile or gaseous fire extinguishant that does not leave a residue upon evaporation.]

COMMERCIAL COOKING SYSTEM. [A system consisting of commercial cooking equipment, exhaust hood, filters, exhaust duct system, fire suppression system and other related appurtenances designed to capture grease-laden cooking vapors and exhaust them safely to the outdoors.]

COMMERCIAL MOTOR VEHICLE.

CONSTANTLY ATTENDED LOCATION. [A designated location at a facility staffed by trained personnel on a continuous basis where alarm or supervisory signals are monitored and facilities are provided for notification of the Fire Department or other emergency services.]

DELUGE SPRINKLER SYSTEM. [A sprinkler system employing open sprinklers attached to a piping system connected to a water supply through a valve that is opened by the operation of a detection system installed in the same areas as the sprinklers. When this valve opens, water flows into the piping system and discharges from all sprinklers attached thereto.]

DETECTOR, HEAT. [A fire detector that senses heat - either abnormally high temperature or rate of rise, or both.]

DRY-CHEMICAL EXTINGUISHING AGENT. [A powder composed of small particles, usually of sodium bicarbonate, potassium bicarbonate, urea-potassium-based bicarbonate, potassium chloride or monoammonium phosphate, with added particulate material supplemented by special treatment to provide resistance to packing, resistance to moisture absorption (caking) and the proper flow capabilities.]

ELECTRICAL CIRCUIT PROTECTIVE SYSTEM.

EMERGENCY ALARM SYSTEM. [A system to provide indication and warning of emergency situations involving hazardous materials.]

EMERGENCY VOICE/ALARM COMMUNICATIONS. [Dedicated manual or automatic facilities for originating and distributing voice instructions, as well as alert and evacuation signals pertaining to a fire emergency, to the occupants of a building.]

FIRE ALARM BOX, MANUAL. [See “Manual Fire Alarm Box.”]

FIRE ALARM CONTROL UNIT. [A system component that receives inputs from automatic and manual fire alarm devices and may be capable of supplying power to detection devices and transponder(s) or off-premises transmitter(s). The control unit may be capable of providing a transfer of power to the notification appliances and transfer of condition to relays or devices.]

FIRE ALARM SIGNAL. [A signal initiated by a fire alarm-initiating device such as a manual fire alarm box, automatic fire detector, water flow switch, or other device whose activation is indicative of the presence of a fire or fire signature.]

FIRE ALARM SYSTEM. [A system or portion of a combination system consisting of components and circuits arranged to monitor and annunciate the status of fire alarm or supervisory signal-initiating devices and to initiate the appropriate response to those signals.]

FIRE AREA. [The aggregate floor area enclosed and bounded by fire walls, fire barriers, exterior walls and/or horizontal assemblies of a building. Areas of the building not provided with surrounding walls shall be included in the fire area if such areas are included within the horizontal projection of the roof or floor next above.]

FIRE COMMAND CENTER. [The principal attended or unattended location where the status of detection, alarm communications and control systems is displayed, and from which the system(s) can be manually controlled.]

FIRE DETECTOR, AUTOMATIC. [A device designed to detect the presence of a fire signature and to initiate action.]

FIRE PROTECTION SYSTEM. [Approved devices, equipment and systems or combinations of systems used to detect a fire, activate an alarm, extinguish or control a fire, control or manage smoke and products of a fire or any combination thereof.]

FIRE PUMP. [A pump used exclusively for fire protection. A pump used only to fill a tank is not a fire pump.]

Fire pump, automatic standpipe. [A fire pump located at or below street level that supplies the lower 300 feet of a standpipe system or a combined standpipe and sprinkler system.]

Fire pump, foam. [A fire pump used to boost water supply pressures in a fire protection system where such system uses firefighting foam as an additive.]

Fire pump, limited service. [A fire pump with a motor rating not exceeding 30 hp and utilizing a limited service fire pump controller.]

Fire pump, special service. [A fire pump that is located above street level and that receives its water supply from a gravity tank or suction tank.]

Fire pump, sprinkler booster pump. [A fire pump that supplies sprinkler systems only.]

Fire pump, water mist system. [A fire pump used to boost water supply pressures in a fire protection system where such system utilizes water misting technology.]

FIRE SAFETY FUNCTIONS. [Building and fire control functions that are intended to increase the level of life safety for occupants or to control the spread of harmful effects of fire.]

FOAM-EXTINGUISHING SYSTEM. [A special system discharging foam made from concentrates, either mechanically or chemically, over the area to be protected.]

HALOGENATED EXTINGUISHING SYSTEM. [A fire-extinguishing system using one or more atoms of an element from the halogen chemical series: fluorine, chlorine, bromine and iodine.]

INITIATING DEVICE. [A system component that originates transmission of a change-of-state condition, such as in a smoke detector, manual fire alarm box or supervisory switch.]

LIMITED AREA SPRINKLER SYSTEM. [An automatic sprinkler system serving fewer than 20 sprinkler heads on any single connection.]

LISTED. [See Chapter 1 of Title 28 of the Administrative Code.]

MANUAL FIRE ALARM BOX. [A manually operated device used to initiate an alarm signal.]

MULTIPLE-STATION ALARM DEVICE. [Two or more single-station alarm devices that are capable of interconnection such that actuation of one causes all integral or separate audible alarms to operate. It also can consist of one single-station alarm device having connections to other detectors or to a manual fire alarm box.]

MULTIPLE-STATION SMOKE ALARM. [Two or more single-station alarm devices that are capable of interconnection such that actuation of one causes the appropriate alarm signal to operate in all interconnected alarms.]

NOTIFICATION ZONE.

POST-FIRE SMOKE PURGE SYSTEM. [A mechanical or natural ventilation system intended to move smoke from the smoke zone to the exterior of the building. Such systems are intended for the timely restoration of operations and overhaul activities once a fire is extinguished. Post-fire smoke purge systems are not intended or designed to be life safety systems.]

PRESIGNAL SYSTEM. [A fire alarm system having a feature that allows initial fire alarm signals to sound in a constantly attended central location and for which a human action is subsequently required to achieve a general alarm, or a feature that allows the control equipment to delay the general alarm by more than 1 minute after the start of the alarm processing.]

RECORD DRAWINGS. [Drawings (“as builts”) that document the location of all devices, appliances, wiring sequences, wiring methods and connections of the components of a fire alarm system as installed.]

SINGLE-STATION SMOKE ALARM. [An assembly incorporating the detector, the control equipment and the alarm-sounding device in one unit, operated from a power supply either in the unit or obtained at the point of installation.]

SMOKE ALARM. [A single- or multiple-station alarm responsive to smoke.]

SMOKE DETECTOR. [A listed device that senses visible or invisible particles of combustion.]

SMOKEPROOF ENCLOSURE. [An exit stairway designed and constructed so that the movement of the products of combustion produced by a fire occurring in any part of the building into the enclosure is limited.]

STANDPIPE SYSTEM. [Piping installed in a building or structure that serves to transfer water from a water supply to hose connections at one or more locations in a building or structure for fire-fighting purposes.]

STANDPIPE, TYPES OF. [Standpipe types are as follows:]

Automatic dry. [A dry standpipe system, normally filled with pressurized air, that is arranged through the use of a device, such as dry pipe valve, to admit water into the system piping automatically upon the opening of a hose valve. The water supply for an automatic dry standpipe system shall be capable of supplying the system demand.]

Automatic wet. [A wet standpipe system that has a water supply that is capable of supplying the system demand automatically.]

Manual dry. [A dry standpipe system that does not have a permanent water supply attached to the system. Manual dry standpipe systems require water from a Fire Department pumper to be pumped into the system through the Fire Department connection in order to meet the system demand.]

Manual wet. [A wet standpipe system connected to a water supply for the purpose of maintaining water within the system but that does not have a water supply capable of delivering the system demand attached to the system. Manual-wet standpipe systems require water from a Fire Department pumper to be pumped into the system in order to meet the system demand.]

Semiautomatic dry. [A dry standpipe system that is arranged through the use of a device, such as a deluge valve, to admit water into the system piping upon activation of a remote control device located at a hose connection. A remote control activation device shall be provided at each hose connection. The water supply for a semiautomatic dry standpipe system shall be capable of supplying the system demand.]

STANDPIPE SYSTEM, CLASSES OF. [Standpipe classes are as follows:]

Class I system. [A system providing 2½ inch (64 mm) hose connections to supply water for use by the Fire Department and those trained in handling heavy fire streams.]

Class II system. [A system providing 1½-inch (38 mm) hose stations to supply water for use primarily by the building occupants or by the Fire Department during initial response.]

Class III system. [A system providing 1½-inch (38 mm) hose stations to supply water for use by building occupants and 2½-inch (64 mm) hose connections to supply a larger volume of water for use by the Fire Department and those trained in handling heavy fire streams.]

SUPERVISING STATION. [A facility that receives signals from protected premises’ fire alarm systems and at which personnel are in attendance at all times to respond to these signals.]

Supervising station, central. [A supervising station that is listed and approved by the Fire Department for central station service.]

Supervising station, proprietary. [A supervising station under the same ownership as the protected premises’ fire alarm system(s) that it supervises (monitors) and to which alarm, supervisory, or trouble signals are received and where personnel are in attendance at all times to supervise operation and investigate signals.]

Supervising station, remote. [A supervising station to which alarm, supervisory, or trouble signals or any combination of those signals emanating from protected premises’ fire alarm systems are received and where personnel are in attendance at all times to respond.]

SUPERVISORY SERVICE. [The service required to monitor performance of guard tours and the operative condition of fixed suppression systems or other systems for the protection of life and property.]

SUPERVISORY SIGNAL. [A signal indicating the need for action in connection with the supervision of guard tours, fire suppression systems or equipment, fire alarm systems, or the maintenance features of related systems.]

SUPERVISORY SIGNAL-INITIATING DEVICE. [An initiation device, such as a valve supervisory switch, water-level indicator or low-air pressure switch on a dry-pipe sprinkler system, whose change of state signals an off-normal condition and its restoration to normal of a fire protection or life safety system, or a need for action in connection with the supervision of guard tours, fire suppression systems or equipment, fire alarm systems, or the maintenance features of related systems.]

TIRES, BULK STORAGE OF. [Storage of tires where the area available for storage exceeds 20,000 cubic feet (566 m3).]

TROUBLE SIGNAL. [A signal initiated by the fire alarm system or device indicative of a fault in a monitored circuit or component.]

VALUE (OF ALTERATIONS TO DETERMINE REQUIRED FIRE PROTECTION). [The value of alterations shall be determined by adding the estimated cost of the proposed alteration, excluding minor alterations and ordinary repairs, computed as of the time of submitting the application for construction document approval, to the actual cost of any and all alterations made in the preceding 12-month period. Where the proposed alteration includes an enlargement, the value of such alteration shall include the cost of the enlargement.]

VALUE (OF EXISTING BUILDING OR SPACE). [See Section 202.]

VISIBLE ALARM NOTIFICATION APPLIANCE. [A notification appliance that alerts by the sense of sight.]

[WET-CHEMICAL] WET CHEMICAL EXTINGUISHING [SYSTEM] AGENT. [A solution of water and potassium-carbonate-based chemical, potassium-acetate-based chemical or a combination thereof, forming an extinguishing agent.]

WIRELESS PROTECTION SYSTEM. [A system or a part of a system that can transmit and receive signals without the aid of wire.]

ZONE. [A defined area within the protected premises. A zone can define an area from which a signal can be received, an area to which a signal can be sent or an area in which a form of control can be executed.]

ZONE, NOTIFICATION. [An area within a building or facility covered by notification appliances which are activated simultaneously.]

SECTION BC 903
AUTOMATIC SPRINKLER SYSTEMS

903.1 General. Automatic sprinkler systems shall comply with this section. Installation of automatic sprinkler systems shall comply with the special inspection requirements of Chapter 17.

903.1.1 Alternative protection. Where permitted by the New York City Fire Code, the Fire Department may approve the installation of alternative automatic fire-extinguishing systems complying with this code and the New York City Fire Code in lieu of automatic sprinkler protection.

903.1.2 Construction documents. Construction documents for automatic sprinkler systems shall contain plans that include the following data and information:

1.	The location and size of water supplies and the location, [spacing,] number, and type of sprinkler heads to be used, with approximate location and size of all feed mains, valves and other essential features of the system. For hydraulically calculated systems, hydraulic data substantiating pipe sizes shown shall be submitted and hydraulic reference points and areas must be indicated on the plan. If any other methods are utilized to size the sprinkler system and its components, as allowed by NFPA 13, supporting documentation shall be submitted.

2.	A diagram showing the proposed sprinkler system in relation to principal construction features of the building, such as its size, walls, columns, and partitions; and such other information as may be necessary for the evaluation of the system.

3.	The location, number, and type of any electrical or automatic devices or alarms to be used in the system.

4.	In buildings where a new separate fire sprinkler system is required, the available water pressure at the top and bottom floors of each zone shall be shown on the riser diagram.

5.	For street pressure-fed systems and fire pumps, a statement from the New York City Department of Environmental Protection, giving the minimum water pressure in the main serving the building.

903.2 Where required. Approved automatic sprinkler systems in new buildings and structures shall be provided in the locations described in [this section] Sections 903.2.1 through 903.2.13.

Exceptions:

1.	Sprinklers shall not be required in electrical equipment rooms where all of the following conditions are met:

1.1	The room is dedicated to electrical equipment only.

1.2	Only dry-type electrical equipment is used.

1.3	Equipment is installed in a 2-hour fire-rated enclosure including protection for penetrations.

1.4	No combustible storage is permitted to be stored in the room.

2.	Sprinklers shall not be permitted in elevator machine rooms and elevator machinery spaces.

3.	Sprinklers shall not be required in rooms and spaces protected by an alternative fire suppression system in accordance with the New York City Fire Code and Section 904 of this code.

903.2.1 Group A. An automatic sprinkler system shall be provided throughout buildings and portions thereof used as Group A occupancies as provided in this section. For Group A-1, A-2, A-3 and A-4 occupancies, the automatic sprinkler system shall be provided throughout the story where the fire area containing the Group A-1, A-2, A-3 or A-4 occupancy is located, and throughout all stories from the Group A occupancy to, and including, the levels of exit discharge serving the Group A occupancy. For Group A-5 occupancies, the automatic sprinkler system shall be provided in the spaces indicated in Section 903.2.1.5. In all Group A occupancies providing live entertainment, dressing rooms and property rooms used in conjunction with such assembly occupancy shall be provided with an automatic sprinkler system. Stages shall comply with Section [410.6] 410.7.

903.2.1.1 Group A-1. An automatic sprinkler system shall be provided for fire areas containing Group A-1 occupancies and intervening floors of the building where one of the following conditions exists:

1.	The fire area exceeds 12,000 square feet (1115 m2).

2.	The fire area has an occupant load of 300 or more.

3.	The fire area is located on a floor other than a level of exit discharge serving such occupancies.

4.	The fire area contains a multitheater complex.

903.2.1.2 Group A-2. An automatic sprinkler system shall be provided for Group A-2 occupancies where any one of the following conditions exists:

1.	The fire area exceeds 5,000 square feet (464.5 m2).

2.	The fire area has an occupant load of 300 or more.

3.	The aggregate occupant load of all fire areas occupied by Group A, located on any given floor other than the level of exit discharge, is 300 or more.

4.	The A-2 occupancy is used as a cabaret.

903.2.1.3 Group A-3. An automatic sprinkler system shall be provided for fire areas containing Group A-3 occupancies and intervening floors of the building where one of the following conditions exists:

1.	The fire area exceeds 12,000 square feet (1115 m2).

2.	The fire area has an occupant load of 300 or more.

3.	The aggregate occupant load of all fire areas occupied by Group A, located on any given floor other than the level of exit discharge, is 300 or more.

Exception: Areas used exclusively as participant sports areas where the main floor area is located at the same level as the level of exit discharge of the main entrance and exit.

903.2.1.4 Group A-4. An automatic sprinkler system shall be provided for fire areas containing Group A-4 occupancies and intervening floors of the building where one of the following conditions exists:

1.	The fire area exceeds 12,000 square feet (1115 m2).

2.	The fire area has an occupant load of 300 or more.

3.	The aggregate occupant load of all fire areas occupied by Group A, located on any given floor other than the level of exit discharge, is 300 or more.

Exception: Areas used exclusively as participant sports areas where the main floor area is located at the same level as the level of exit discharge of the main entrance and exit.

903.2.1.5 Group A-5. An automatic sprinkler system shall be provided in all enclosed areas of the structure, including but not limited to the concession concourse, concession stands, retail areas, press boxes and other accessory occupancies, in excess of 1,000 square feet (93 m2).

903.2.1.6 Assembly occupancies on roofs. Where an occupied roof has an assembly occupancy with an occupant load exceeding 100 for Group A-2 and 300 for other Group A occupancies, all floors between the occupied roof and the level of exit discharge shall be equipped with an automatic sprinkler system in accordance with Section 903.3.1.1 or 903.3.1.2.

Exception: Open parking garages of Type I or Type II construction.

903.2.1.7 Multiple fire areas. An automatic sprinkler system shall be provided where multiple fire areas of Group A-1, A-2, A-3 or A-4 occupancies share exit or exit access components and the combined occupant load of theses fire areas is 300 or more.

903.2.2 Group B. An automatic sprinkler system shall be installed for Group B occupancies as provided in Sections 903.2.2.1 and 903.2.2.2.

903.2.2.1 Ambulatory health care facilities. An automatic sprinkler system shall be installed throughout all fire areas containing a Group B ambulatory health care facility occupancy [when either of the following conditions exists at any time:]. In buildings where ambulatory care is provided on levels other than the level of exit discharge, an automatic sprinkler system shall be installed throughout the entire floor where such care is provided as well as all floors below, and all floors between the level of ambulatory care and the nearest level of exit discharge, including the level of exit discharge.

[1.	Four or more care recipients are incapable of self-preservation.]

[2.	One or more care recipients who are incapable of self-preservation are located at other than the level of exit discharge serving such an occupancy.]

903.2.2.2 Animal service facilities. An automatic sprinkler system shall be provided for animal service facilities. [This provision shall be retroactive and shall apply to all such facilities in existence on the effective date of this provision, and such facilities shall achieve compliance no later than December 31, 2016.]

Exceptions:

1.	Animal service facilities [which] that provide 24 hour in-person supervision of animals sheltered therein and are equipped with smoke alarms.

2.	Animal service facilities that were in operation on or before December 31, 2016, and are equipped with an automatic smoke detection system.

903.2.3 Group E. An automatic sprinkler system shall be provided for Group E occupancies as follows:

1.	Throughout all Group E fire areas greater than [20,000 square feet (1858 m2)] 12,000 square feet (1115 m2) in area.

2.	Throughout every portion of educational buildings below the level of exit discharge.

Exception: An automatic sprinkler system is not required in any fire area or area below the level of exit discharge where every classroom throughout the building has [at least] not fewer than one exterior exit door at ground level without intervening corridors, passageways, [or exit enclosures] interior exit stairways or ramps or exit passageways.

903.2.4 Group F. An automatic sprinkler system shall be provided throughout all buildings containing a Group F occupancy where any one of the following conditions exists:

- Where a Group F-1 fire area exceeds 12,000 square feet (1115 m2);

- Where a Group F-1 fire area is located more than three stories above grade plane; [or]

- Where the combined area of all Group F-1 fire areas on all floors, including any mezzanines, exceeds 24,000 square feet (2230 m2); [or]

4.	Where required by Section 280 of the New York State Labor Law for “factory buildings” defined in Section 2 of such law[.];or

5.	Where a Group F-1 occupancy used for the manufacture of upholstered furniture or mattresses exceeds 2,500 square feet (232 m2 ).

903.2.4.1 Woodworking operations. An automatic sprinkler system shall be provided throughout [any] all Group F-1 occupancy fire [area] areas that [contains wood working] contain woodworking operations in excess of 2,500 square feet (232 m2) in area that generate finely divided combustible waste or use finely divided combustible materials.

903.2.4.2 Repair garages. An automatic sprinkler system shall be provided throughout all buildings used as repair garages in accordance with Section 406, as follows:

1.	Buildings two or more stories in height, including basements, with a fire area containing a repair garage exceeding 10,000 square feet (929 m2).

2.	One-story buildings with a fire area containing a repair garage exceeding 12,000 square feet (1115 m2).

3.	A Group F-1 fire area used for the repair of commercial trucks or buses where the fire area exceeds 5,000 square feet (464 m2).

4.	Buildings with a repair garage servicing vehicles parked in the basement.

903.2.4.3 Group F-1 fire areas. An automatic sprinkler system shall be provided throughout any Group F-1 occupancy fire area where any one of the following conditions exists:

1.	The fire area exceeds 7,500 square feet (697 m2).

2.	The fire area of any size is located more than three stories above grade.

903.2.5 Group H. Automatic sprinkler systems shall be provided in high-hazard occupancies as required in the New York City Fire Code and Sections 903.2.5.1 through 903.2.5.3 [and the New York City Fire Code] of this code.

903.2.5.1 General. An automatic sprinkler system shall be installed in Group H occupancies. An automatic sprinkler system shall be installed throughout buildings with a main use or dominant occupancy of Group H.

903.2.5.2 Group H-5 occupancies. An automatic sprinkler system shall be installed throughout buildings containing Group H-5 occupancies. The design of the sprinkler system shall be not [be] less than that required by this code for the occupancy hazard classifications in accordance with Table 903.2.5.2. Where the design area of the sprinkler system consists of a corridor protected by one row of sprinklers, the maximum number of sprinklers required to be calculated is 13.

TABLE 903.2.5.2
GROUP H-5 SPRINKLER DESIGN CRITERIA

| LOCATION | OCCUPANCY HAZARD CLASSIFICATION |
| --- | --- |
| Fabrication areas | Ordinary Hazard Group 2 |
| Service corridors | Ordinary Hazard Group 2 |
| Storage rooms without dispensing | Ordinary Hazard Group 2 |
| Storage rooms with dispensing | Extra Hazard Group 2 |
| Corridors | Ordinary Hazard Group 2 |

903.2.5.3 Pyroxylin plastics. An automatic sprinkler system shall be provided in buildings, or portions thereof, where cellulose nitrate film or pyroxylin plastics are manufactured, stored or handled in quantities exceeding 100 pounds (45 kg).

903.2.6 Group I. An automatic sprinkler system shall be provided in Group I occupancies. An automatic sprinkler system shall be installed throughout buildings with a main use or dominant occupancy of Group I.

[Exception:] Exceptions:

1.	An automatic sprinkler system installed in accordance with Section 903.3.1.2 or 903.3.1.3 shall be allowed in Group I-1 facilities if located in an I-1 occupancy building or a residential building, provided such building is six stories or less in height.

2.	An automatic sprinkler system is not required where Group I-4 day care facilities are at the level of exit discharge and where every room where care is provided has not fewer than one exterior exit door.

3.	In buildings where Group I-4 day care is provided on levels other than the level of exit discharge, an automatic sprinkler system in accordance with Section 903.3.1.1 shall be installed on the entire floor where care is provided, all floors between the level of care and the level of exit discharge, and all floors below the level of exit discharge other than areas classified as an open parking garage.

903.2.7 Group M. An automatic sprinkler system shall be provided throughout buildings containing a Group M occupancy where one of the following conditions exists:

1.	A Group M fire area exceeds 12,000 square feet (1115 m2).

2.	A Group M fire area is located more than three stories above grade plane.

3.	The combined area of all Group M fire areas on all floors, including any mezzanines, exceeds 24,000 square feet (2230 m2).

4.	A Group M occupancy used for the display and sale of upholstered furniture or mattresses exceeds 5,000 square feet (464 m2).

903.2.7.1 High-piled storage. An automatic sprinkler system shall be provided in accordance with the New York City Fire Code in all buildings of Group M where storage of merchandise is in high-piled or rack storage arrays.

903.2.7.2 Group M fire areas. An automatic sprinkler system shall be provided throughout any Group M occupancy fire area where any one of the following conditions exists:

1.	The fire area exceeds 7,500 square feet (697 m2).

2.	The fire area of any size contains an unenclosed stair or escalator connecting two or more floors

903.2.8 Group R. An automatic sprinkler system shall be installed in Group R fire areas. An automatic sprinkler system shall be installed throughout buildings with a main use or dominant occupancy of Group R.

Exception: An automatic sprinkler system shall not be required in detached one- and two-family dwellings and multiple single-family dwellings (townhouses), provided that such structures are not more than three stories above grade plane in height and have separate means of egress.

903.2.9 Group S-1. An automatic sprinkler system shall be provided throughout all buildings containing a Group S-1 occupancy where any one of the following conditions exists:

1.	A Group S-1 fire area exceeds 12,000 square feet (1115 m2)[;].

2.	The building is greater than 1,000 square feet (92.9 m2) in area and the main use or dominant occupancy is Group S-1[; or].

3.	A Group S-1 fire area is located more than three stories above grade plane.

4.	The combined area of all Group S-1 fire areas on all floors, including any mezzanines, exceeds 24,000 square feet (2230 m2).

5.	A Group S-1 fire area used for the storage of commercial motor vehicles where the fire area exceeds 5,000 square feet (464 m2).

6.	A Group S-1 occupancy used for the storage of upholstered furniture or mattresses exceeds 2,500 square feet (232 m2).

903.2.9.1 Group S-1 fire areas. An automatic sprinkler system shall be provided throughout any Group S-1 occupancy fire area where the fire area exceeds 500 square feet [(16 m2)] (46.5 m2).

903.2.9.2 Bulk storage of tires. Buildings and structures where the area for the storage of tires exceeds 500 square feet [(47 m2)] (46.5 m2) or 7,500 cubic feet (212 m3) shall be equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1.

903.2.9.3 High-piled storage. An automatic sprinkler system shall be provided in accordance with the New York City Fire Code in all buildings or portions thereof in Group S-1 occupancies where the storage of merchandise is in high-piled or rack storage arrays.

903.2.10 Group S-2. An automatic sprinkler system shall be installed throughout buildings greater than 5,000 square feet (465 m2) in area where the main use or dominant occupancy is Group S-2.

903.2.10.1 Commercial parking garages. An automatic sprinkler system shall be provided throughout buildings used for storage of commercial trucks [or], buses or other commercial motor vehicles where the fire area exceeds 5,000 square feet (465 m2).

903.2.10.2 Group S-2 fire areas. An automatic sprinkler system shall be provided throughout any Group S-2 occupancy fire area greater than 5,000 square feet (465 m2).

903.2.10.3 Parking garages. An automatic sprinkler system shall be provided throughout buildings classified as enclosed parking garages in accordance with Section 406.4 or where an open or enclosed parking garage is located beneath other occupancy groups.

Exception: Parking garages located beneath Group R-3 occupancies.

903.2.10.4 High-piled storage. An automatic sprinkler system shall be provided in all buildings or portions thereof of Group S-2 occupancies in accordance with the New York City Fire Code.

903.2.11 Specific building areas and hazards. An automatic sprinkler system shall be installed for building design or hazards in the locations set forth in Sections 903.2.11.1 through 903.2.11.13.

903.2.11.1 Above- or below-grade stories.  An automatic sprinkler system shall be installed throughout every above- or below-grade story of all buildings where the floor area exceeds 1,500 square feet (139.4 m2) and where [at least] not fewer than one of the following types of exterior wall openings is provided:

1.	Openings below grade that lead directly to ground level by an exterior stairway complying with Section [1009] 1011 or an outside ramp complying with Section [1010] 1012. Openings shall be located in each 50 linear feet (15 240 mm), or fraction thereof, of exterior walls facing onto a street, public way or frontage space, in the story on at least one side. The required openings shall be distributed such that the lineal distance between adjacent openings does not exceed 50 feet (15 240 mm).

2.	Openings entirely above the adjoining ground level totaling [at least] not less than 20 square feet (1.86 m2) in each 50 linear feet (15 240 mm), or fraction thereof, of exterior walls facing onto a street, public way or frontage space, in the story on at least one side. The required openings shall be distributed such that the lineal distance between adjacent openings does not exceed 50 feet (15 240 mm). The bottom of the clear opening shall not exceed 36 inches (914 mm) measured from the floor.

903.2.11.1.1 Opening dimensions and access. Such openings shall have a minimum dimension of not less than 30 inches (762 mm). Such openings shall be accessible to the Fire Department from the exterior and shall not be obstructed in a manner that [fire fighting] firefighting or rescue cannot be accomplished from the exterior.

903.2.11.1.2 Openings on one side only. Where such openings in a story are provided on only one side and the opposite wall of such story is more than 100 feet (30 480 mm) from such openings, the story shall be equipped throughout with an approved automatic sprinkler system, or openings as specified above shall be provided on [at least] not fewer than two sides of the story.

903.2.11.1.3 Below-grade stories. Where any portion of a below-grade story is located more than 75 feet (22 860 mm) from openings required by Section 903.2.11.1, or where walls, partitions, or other obstructions are installed that restrict the application of water from hose streams, the below-grade story shall be equipped throughout with an approved automatic sprinkler system.

903.2.11.2 Other above-grade stories. An automatic sprinkler system shall be installed throughout every above-grade story of buildings below a height of 100 feet (30 480 mm), other than the first story or ground floor, on which access is not provided directly from the outdoors by at least one window or readily identifiable access panel within each 50 feet (15 240 mm) or fraction thereof of horizontal length of every wall that fronts on a street or frontage space required pursuant to Section 501.3.1.

903.2.11.2.1 Opening dimensions and access. Such windows shall be openable from the inside or breakable from both the inside and the outside, and shall have a size when open of at least 24 inches by 36 inches (610 mm by 914 mm). Such panels shall be openable from both the inside and outside and shall have a height when open of 48 inches (1219 mm) and a width of at least 32 inches (813 mm). The sill of the window or panel shall not be higher than 36 inches (914 mm) above the inside floor. Where not all of the windows are openable or breakable, the windows intended to satisfy the requirements of this section shall be readily identifiable.

903.2.11.3 Other below-grade stories. An automatic sprinkler system shall be installed throughout every first basement or cellar story below grade of buildings on which access is not provided directly from the outdoors within each 100 feet (30 480 mm) or fraction thereof of horizontal length of every wall that fronts on a street or frontage space required pursuant to Section 501.3.1.

Exceptions:

1.	One- and two-family dwellings need not provide direct access.

2.	Any building classified in Occupancy Group R-2 not more than three stories in height and with not more than two dwelling units on any story need not provide direct access when such first basement or cellar story is used for dwelling units or for uses accessory to the residential use in the building.

3.	Except as provided in Exception 2, above, for Group R-1 and R-2 occupancies, only one direct access from the outdoors to the first basement or cellar story consisting of a stair or door shall be required when such story is used for dwelling units or for uses accessory to the residential use in the building.

903.2.11.3.1 Opening dimensions and access. Such access shall be by stairs, doors, windows or other means that provide an opening 48 inches (1219 mm) high and 32 inches (813 mm) wide, the sill of which shall not be higher than 36 inches (914 mm) above the inside floor. If an areaway is used to provide below grade access, the minimum horizontal dimension shall be at least one-third the depth of the areaway or 6 feet (1829 mm), whichever is less.

903.2.11.4 Signs obstructing openings. Where wall signs are erected to cover doors or windows of existing buildings, access panels shall be provided as necessary to comply with the requirements of Section 903.2.11.

903.2.11.5 Compliance with the New York State Multiple Dwelling Law. Nothing in Section 903.2.11 shall be construed so as to supersede any applicable provisions of Section 54 of the New York State Multiple Dwelling Law relating to access to cellars or basements in multiple dwellings.

903.2.11.6 Rubbish and linen chutes. An automatic sprinkler system shall be installed at the top of rubbish and linen chutes, in chute access rooms, and in their terminal rooms. Chutes [extending through three or more floors] shall have additional sprinkler heads installed [within such chutes at alternate floors.] at alternate floors and at the lowest intake. Where a rubbish chute extends through a building more than one floor below the lowest intake, or through areas with no openings, such an extension shall have sprinklers installed that are recessed from the drop area of the chute and protected from freezing in accordance with Section 903.3.1.1. Such sprinklers shall be installed at alternate floors, beginning with the second level below the last intake and ending with the floor above the discharge. [Chute] All chute sprinklers shall be accessible for servicing and shall not obstruct the vertical path for rubbish or linens.

903.2.11.7 Buildings [over] 55 feet (16 764 mm) or more in height. An automatic sprinkler system shall be installed throughout buildings that have one or more stories with [a floor level having] an occupant load of 30 or more [that is] located 55 feet (16 764 mm) or more above the lowest level of Fire Department vehicle access, measured to the finished floor.

Exceptions:

1.	Open parking structures without any other occupancy groups, unless otherwise required.

2.	Occupancies in Group F-2, unless required by the New York State Department of Labor.

903.2.11.8 Ducts conveying hazardous exhausts. Where required by the New York City Mechanical Code, automatic sprinklers shall be provided in ducts conveying hazardous exhaust[,] or flammable or combustible materials.

Exception: Ducts [in which] where the largest cross-sectional diameter of the duct is less than 10 inches (254 mm).

903.2.11.9 Commercial cooking operations. An automatic sprinkler system shall not be installed in a commercial kitchen exhaust hood and duct system. Fire-extinguishing systems shall be installed in commercial cooking systems in accordance with this code and the New York City Fire Code.

903.2.11.10 Other buildings, occupancies and areas. In addition to the requirements of Section 903.2, the provisions indicated in Table 903.2.11.10 also require the installation of a suppression system for certain buildings and areas. Suppression systems shall also be required as provided for in other sections of this code, the New York City Fuel Gas Code, and the New York City Mechanical Code.

TABLE 903.2.11.10
ADDITIONAL REQUIRED SUPPRESSION SYSTEMS

| Occupancy Group, specified use, materials or equipment (in alphabetical order) | Code section |
| --- | --- |
| Aerosol warehouses | FC 2804.4.1 |
| Aircraft hangers | BC 412.4.6, BC 412.4.6.1, BC 412.6.5 |
| Airport traffic control towers | BC 412.3.6 |
| Atriums | BC 404.3 |
| Automated storage; buildings with | FC 2309.2 |
| Children’s play structures | BC 424.3 |
| Chutes; refuse and laundry | BC [708.13] 713.13 |
| Chute vestibules | BC Appendix Q [21.16.2.1.1] 22.15.2.2.1 |
| Cold storage buildings: ice plants, food plants and food processing rooms with foam insulation up to 10 inches in thickness | BC 2603.3 |
| Combustible fibers; storage at waterfront structures | FC 2906.6 |
| Combustible fibers, loose; storage of more than 1,000 sq ft of | FC 2904.5 |
| Commercial cooking systems | BC [904.11] 904.12 FC 904.11 |
| Commercial cooking systems with solid fuel storage | FC 904.11.7 |
| Commercial cooking system with Type I hood | BC 904.2.1 MC 509.1 |
| Covered mall and open mall buildings | BC [402.9] 402.5 |
| Dead end public streets; buildings on | FC 503.8.1 |
| Dip tank rooms | FC 1505.1 |
| Dip tanks | FC 1505.6.1 |
| Dry cleaning machines | FC 1208.3 |
| Dry cleaning plants | FC 1208.2 |
| Drying rooms | BC 417.4 |
| Elevator lobbies | BC [708.14.1] 3006.1.1 |
| Exhausted enclosures | FC 2703.8.5.3 |
| Extra-high-rack combustible storage; buildings with | FC 2308.5.1 |
| Flammable and combustible liquid in Group H-2 or H-3 areas | FC 3405.3.7.3 |
| Flammable and combustible liquid storage rooms | FC 3404.3.7.5.1 |
| Flammable and combustible liquid storage warehouses | FC 3404.3.8.4 |
| Flammable finishes | BC 416.5 |
| Fuel-oil tanks and fuel-oil burning equipment; rooms containing | MC 1305.13.3 |
| Furnaces: Class A and B | FC 2106.1 |
| Furnaces: Class C and D | FC 2106.2 |
| Gas rooms | FC 2703.8.4 |
| Glazing in smoke partition | BC [711.2] 710.2 |
| Group H-2 | BC [415.6.2.4] 415.9.1.3 |
| Group H-5, including but not limited to: workstations, gas cabinet, exhausted enclosures, pass-throughs in exit access corridors and exhaust ducts | BC [415.8] 415.11 |
| Group I-2 | BC [407.5] 407.6 |
| Hardening and tempering tanks | FC 1505.8.4 |
| Hazardous exhaust system ducts | MC [510.7] 510.8 |
| Hazardous materials; indoor handling or use of | FC 2705.1.8 |
| Hazardous materials; indoor storage of | FC 2704.5 |
| Hazardous Production Material ("HPM") corridors | FC 1803.10.3 |
| Hazardous Production Material ("HPM") exhaust ducts | FC 1803.10.4 |
| Hazardous Production Material ("HPM") facilities | FC 1803.10 |
| Hazardous Production Material ("HPM") gas cabinets | FC 1803.10.2 |
| Hazardous Production Material ("HPM") work station exhaust | FC 1803.10.1.1 |
| High Pressure Gas Installations; buildings with | FGC G.2.3 |
| Highly toxic and toxic compressed gases; exhausted enclosures for | FC 3704.1.3 |
| Highly toxic and toxic compressed gases; gas cabinets containing | FC 3704.1.2 |
| Highly toxic and toxic compressed gases; gas rooms utilizing | FC 3704.2.2.6 |
| Highly toxic and toxic compressed gases; outdoor storage of | FC 3704.3.3 |
| High-rise buildings | BC 403.3 |
| Incidental uses | BC 509.4.2 |
| Equipment platforms | BC [505.5.2] 505.3.2 |
| Kiosks in covered mall buildings | BC [402.11] 402.6.2 |
| Kiosks, displays, booths, or concession stands; covered | FC 314.5.1 |
| Laboratory units; non-production | BC [424.6.1] 427.6.1 |
| Liquefied petroleum gas ("LPG") within buildings accessible to the public; storage of | FC 3809.9 |
| Liquids, Class II and III, below grade storage of | FC 3404.3.5.1 |
| Liquids, Class II and III, below grade storage of, accessory to retail | BC 414.2.5.1 |
| Medical gas; storage of | FC 3006.2.1 |
| Organic coatings; manufacturing of | BC 418.1 |
| Oxidizer, solid and liquid; storage areas | FC 4004.1.4 |
| Plastic light diffusing system | BC 2606.7.4 |
| Pyroxylin plastic; areas with | FC 4204.1.1 |
| Pyroxylin plastic; storage and manufacturing | FC 4204.2 |
| Pyroxylin plastic; storage vaults | FC 4204.1.3 |
| Rack storage | FC 2308.2 |
| Radioactive materials and radiation-producing equipment; uses and occupancies involving | BC [425.3.4] 428.3.4 |
| Resin application areas | FC 1511.3 |
| Silane gas; exhausted enclosures or gas cabinets for | FC 4106.2.2 |
| Small arms ammunition and primers, black powder or smokeless propellant; storage of | FC 3306.7 |
| Solid-piled and shelf storage | FC 2307.2 |
| Smoke-protected assembly seating | BC [1028.6.2.3] 1029.6.2.3 |
| Special amusement buildings | BC 411.4 |
| Spray booths and rooms | FC 1504.6 |
| Spray booths involving the use of organic peroxide coatings | FC 1509.6 |
| Spray finishing in Group A, E, I or R | FC 1504.1 |
| Stages | BC [410.6] 410.7 |
| Sterilization systems; rooms with | FC 3506.3.2 |
| Storage | FC Table 2306.2 FC 2306.4 |
| Substandard width public streets; buildings on | FC 503.8.2 |
| Textile ceiling finish | BC 803 |
| Textile wall coverings | BC 803 |
| Underground buildings and spaces | BC 405.3 |
| Unlimited area buildings | BC 507 |

903.2.11.11 Steel-plated and vault-like occupancies. An automatic sprinkler system shall be installed throughout all steel-plated or similarly reinforced or secured vault-like occupancies regardless of area.

903.2.11.12 Refuse collection and disposal areas. An automatic sprinkler system shall be installed throughout all areas used for the storage and sorting of refuse and recyclables.

903.2.11.13 Laundry drying areas. An automatic sprinkler system shall be installed in spaces in which two or more clothes drying machines are installed. Sprinkler heads shall be spaced to cover the areas 5 feet (1524 mm) on all sides of the drying machines.

903.2.12 During construction. Automatic sprinkler systems required during construction, alteration and demolition operations shall be provided in accordance with [Chapter 33 and] the New York City Fire Code and Chapter 33 of this code.

903.2.13 Type IV construction with cross-laminated timber or structural composite lumber. Automatic sprinkler systems in accordance with NFPA 13 shall be required throughout buildings utilizing Type IV construction with cross-laminated timber or structural composite lumber as follows:

1.	In all occupancies where the building is more than 3 stories above grade plane.

2.	In Group B occupancies, where a floor exceeds 28,500 square feet (2,648 m2).

903.3 Installation requirements. Automatic sprinkler systems shall be designed and installed in accordance with Sections 903.3.1 through [903.3.6] 903.3.8.

903.3.1 Standards. Sprinkler systems shall be designed and installed in accordance with Section 903.3.1.1, 903.3.1.2 or 903.3.1.3.

903.3.1.1 NFPA 13 sprinkler systems. Where the provisions of this code require that a building or portion thereof be equipped throughout with an automatic sprinkler system in accordance with this section, sprinklers shall be installed throughout in accordance with NFPA 13 [as modified in Appendix Q] except as provided in Section 903.3.1.1.1 and 903.2.

903.3.1.1.1 Exempt locations protected by other means. When approved by the Fire Department, automatic sprinklers shall not be required in the following:

1.	In rooms or areas protected with an approved automatic fire detection system in accordance with Section 907.2 that will respond to visible or invisible particles of combustion, and an alternative automatic fire-extinguishing system in accordance with this code and the New York City Fire Code. Sprinklers shall not be omitted from any room merely because it is of fire-resistance-rated construction or contains electrical equipment. This exemption shall not apply to a generator or transformer room unless, in addition to the above requirements, such room is separated from the remainder of the building by walls and floor/ceiling or roof/ceiling assemblies having a fire-resistance rating of not less than 2 hours, and the generator in such room shall not use high pressure flammable gas in excess of 15 psig (103 kPa gauge).

2.	Machine rooms, machinery spaces, control rooms and control spaces associated with occupant evacuation elevators designed in accordance with Section 3008.

903.3.1.2 NFPA 13R sprinkler systems. Where allowed in buildings of Group R, up to and including six stories in height, automatic sprinkler systems shall be installed throughout in accordance with NFPA 13R [as modified in Appendix Q].

The number of stories of Group R occupancies constructed in accordance with Sections 510.2 and 510.4 shall be measured from the horizontal assembly creating separate buildings.

903.3.1.2.1 Balconies and decks. Sprinkler protection shall be provided for exterior balconies, decks and ground-floor patios of dwelling units where the building is of Type V construction and automatic sprinkler protection is required for the Group R occupancy. Side wall sprinklers that are used to protect such areas shall be permitted to be located such that their deflectors are within 1 inch (25 mm) to 6 inches (152 mm) below the structural members, and a maximum distance of 14 inches (356 mm) below the deck of the exterior balconies and decks that are constructed of open wood joist construction.

903.3.1.2.2 Open-ended corridors. Sprinkler protection and freeze protection shall be provided in open-ended corridors and associated exterior stairways and ramps as specified in Section 1027.6, Exception 3.

903.3.1.3 NFPA 13D sprinkler systems. Where allowed, automatic sprinkler systems in one- and two-family dwellings and townhouses, up to and including six stories in height, shall be installed throughout in accordance with NFPA 13D [as modified].

903.3.2 Quick-response and residential sprinklers. Where automatic sprinkler systems are required by this code, quick-response or residential automatic sprinklers shall be installed in all of the following areas in accordance with Section 903.3.1 and their listings:

1.	Throughout all spaces within a smoke compartment containing [patient dwelling] care recipient sleeping units in Group I-2 in accordance with this code.

2.	Throughout all spaces within a smoke compartment containing treatment rooms in ambulatory care facilities.

[2.] 3.	Dwelling units and sleeping units in Group [R and] I-1 and R occupancies.

[3.] 4.	Light-hazard occupancies as defined in NFPA 13.

903.3.3 Obstructed locations. Automatic sprinklers shall be installed with due regard to obstructions that will delay activation or obstruct the water distribution pattern. Automatic sprinklers shall be installed in or under covered kiosks, displays, booths, concession stands, or equipment that exceeds 4 feet (1219 mm) in width. Not less than a 3-foot (914 mm) clearance shall be maintained between automatic sprinklers and the top of piles of combustible fibers.

Exception: Kitchen equipment under exhaust hoods protected with a fire-extinguishing system in accordance with this code and the New York City Fire Code.

903.3.4 Actuation. Automatic sprinkler systems shall be automatically actuated unless [otherwise] specifically provided for in this code.

903.3.5 Water supplies. Water supplies for automatic sprinkler systems shall comply with this section and the standards referenced in Section 903.3.1. The potable water supply shall be protected against back flow in accordance with the requirements of this section, the New York City Plumbing Code, and Rules of the New York City Department of Environmental Protection.

903.3.5.1 Domestic services. Where the domestic service provides the water supply for the automatic sprinkler system, the supply shall be in accordance with NFPA 13, 13R, and 13D.

903.3.5.1.1 [Limited area sprinkler systems. Limited area sprinkler systems serving fewer than 20 sprinklers on any single connection are permitted to be connected to the domestic service where a wet automatic standpipe is not available. Limited area sprinkler systems connected to domestic water supplies shall comply with NFPA 13.]

[The domestic service shall be capable of supplying the simultaneous domestic demand and the sprinkler demand required to be hydraulically calculated by NFPA 13, NFPA 13R or NFPA 13D.]

[903.3.5.1.2] Residential combination services. A single combination water supply shall be permitted in accordance with NFPA 13R.

903.3.5.2 Secondary on-site water supply. [A secondary on-site water supply equal to the hydraulically calculated sprinkler demand, including the hose stream requirement, shall be provided for high-rise buildings in Seismic Design Category C or D as determined by this code, and in any high-rise building with occupied floors located more than 300 feet (91 440 mm) above the lowest level of Fire Department vehicle access. The secondary water supply shall have a duration not less than 30 minutes as determined by the occupancy hazard classification in accordance with NFPA 13.] A secondary on-site water supply for high-rise buildings shall be provided in accordance with Section 403.3.3.

903.3.6 Hose threads. Fire hose threads and fittings used in connection with automatic sprinkler systems shall be approved and compatible with Fire Department hose threads.

903.3.7 Fire Department connections. The location of Fire Department connections for automatic sprinkler systems shall be installed in accordance with Sections 905 and 912.

903.3.8 Limited area sprinkler systems. Limited area sprinkler systems shall be in accordance with the standards listed in Section 903.3.1 except as provided in 903.3.8.1 through 903.3.8.5.

903.3.8.1 Number of sprinklers. Limited area sprinkler systems shall not exceed six sprinklers in any single fire area.

903.3.8.2 Occupancy hazard classification. Only areas classified by NFPA 13 as Light Hazard or Ordinary Hazard Group 1 shall be permitted to be protected by limited area sprinkler systems.

903.3.8.3 Piping arrangement. Where a limited area sprinkler system is installed in a building with an automatic wet standpipe system, sprinklers shall be supplied by the standpipe system. Where a limited area sprinkler system is installed in a building without an automatic wet standpipe system, water shall be permitted to be supplied by the plumbing system provided that the plumbing system is capable of simultaneously supplying domestic and sprinkler demands.

903.3.8.4 Supervision. Control valves shall not be installed between the water supply and sprinklers unless the valves are of an approved indicating type that are supervised or secured in the open position.

903.3.8.5 Calculations. Hydraulic calculations in accordance with NFPA 13 shall be provided to demonstrate that the available water flow and pressure are adequate to supply all sprinklers installed in any single fire area with discharge densities corresponding to the hazard classification.

903.4 Sprinkler system supervision and alarms. [All valves] Valves controlling the water supply for automatic sprinkler systems, pumps, tanks, water levels and temperatures, critical air pressures and water-flow switches on all sprinkler systems shall be electrically supervised by the fire alarm system where [a] such fire alarm system is required by Section 907.

Exceptions:

1.	Automatic sprinkler systems protecting one- and two-family dwellings.

2.	Limited area sprinkler systems in accordance with Section 903.3.8.

3.	Automatic sprinkler systems installed in accordance with NFPA 13R where a common supply main is used to supply both domestic water and the automatic sprinkler [systems] system, and a separate shutoff valve for the automatic sprinkler system is not provided.

[3.] 4.	Jockey pump control valves that are sealed or locked in the open position.

[4.] 5.	Control valves to commercial kitchen hoods, paint spray booths or dip tanks that are sealed or locked in the open position.

[5.] 6.	Valves controlling the fuel supply to fire pump engines that are sealed or locked in the open position.

[6.] 7.	Trim valves to pressure switches in dry, preaction and deluge sprinkler systems that are sealed or locked in the open position.

903.4.1 Signals and monitoring. Alarm, supervisory and trouble signals shall be distinctly different and shall be automatically transmitted to a central supervising station or when approved by the Fire Department, shall sound an audible signal at a constantly attended location.

Exceptions:

1.	Underground key or hub valves in roadway boxes provided by the city or a public utility are not required to be monitored.

2.	[Back flow] Backflow prevention device test valves, located in limited area sprinkler system supply piping, shall be locked in the open position. In occupancies required to be equipped with a fire alarm system, the backflow preventer valves shall be electrically supervised by a tamper switch installed in accordance with NFPA 72 and separately annunciated.

903.4.2 Alarms. [Approved] An approved audible [devices] device, located on the exterior of the building in an approved location, shall be connected to [every] each automatic sprinkler system. Such sprinkler water-flow alarm devices shall be activated by water flow equivalent to the flow of a single sprinkler of the smallest orifice size installed in the system. Alarm devices shall be provided on the exterior of the building in an approved location or in a location approved by the Fire Department, except in buildings equipped with a fire alarm system. Where a fire alarm system is installed, actuation of the automatic sprinkler system shall actuate the building fire alarm system.

903.4.3 Floor control valves. Approved supervised indicating control valves shall be provided at the point of connection to the riser on each floor in high-rise buildings.

903.5 Testing and maintenance. Sprinkler systems shall be tested and maintained in accordance with the New York City Fire Code.

903.6 Painting of dedicated sprinkler piping and valve handles. Dedicated sprinkler piping shall be painted and such painting certified in accordance with Sections 903.6.1 through 903.6.5. In addition to painting, sprinkler piping may also be identified by lettered legend in accordance with ANSI A13.1. Where the piping is required to be listed and labeled, such painting shall not obscure such labeling.

1.	Attachments, gauges, valves and operable parts of sprinkler systems other than valve handles.

2.	Horizontal branch lines.

3.	Where different color coding may be required by Section 3406 of the New York City Fire Code for facilities storing, handling, and using flammable and combustible liquids in connection with special operations.

903.6.1 New buildings. Cross connections and risers in new buildings, including buildings constructed pursuant to Section 28-101.4.2 of the Administrative Code, shall be painted red and the handles of valves serving dedicated sprinklers shall be painted green prior to the hydrostatic pressure test regardless of whether they will be enclosed at a later point in time.

Exception: Where a standpipe system is used as a combination standpipe and sprinkler system, the sprinkler risers and cross connections that are also used for the standpipe system shall be painted red and the handles of valves serving such combination system shall be painted yellow.

903.6.2 Alterations. Cross connections and risers for independent (stand-alone) existing sprinkler systems that are exposed during alterations, including alterations pursuant to Section 28-101.4.2 of the Administrative Code, shall be painted red and the handles of valves serving such existing sprinkler systems shall be painted green. Where the alteration requires a hydrostatic pressure test such painting shall be completed prior to such test.

Exception: Where a standpipe system is used as a combination standpipe and sprinkler system, the sprinkler risers and cross connections that are also used for the standpipe system shall be painted red and the handles of valves serving such combination system shall be painted yellow.

903.6.3 Retroactive requirement for completed buildings. Notwithstanding any other provision of law, all exposed risers and cross connections of completed buildings in existence on March 2, 2010, shall be painted red [by June 2, 2010,] and all handles of valves serving such sprinkler system shall be painted green.

Exception: Where a standpipe system is used as a combination standpipe and sprinkler system, the sprinkler risers and cross connections that are also used for the standpipe system shall be painted red and the handles of valves serving such combination system shall be painted yellow.

903.6.4 Buildings under construction on March 2, 2010. Notwithstanding any other provision of law, where construction documents were approved and permits issued for the construction of a new building or alteration of an existing building prior to March 2, 2010, and the work is not signed off by the department prior to such date, all exposed cross connections and risers in any such building shall be painted red prior to the hydrostatic pressure test, including cross connections and risers that will be enclosed at a later point in time, and handles of valves serving such sprinkler system shall be painted green.

Exceptions:

1.	Where a standpipe system is used as a combination standpipe and sprinkler system, the sprinkler risers and cross connections that are also used for the standpipe system shall be painted red and the handles of valves serving such combination system shall be painted yellow.

2.	Cross connections and risers enclosed prior to March 2, 2010, need not be painted.

903.6.5 Certification of completion of system painting. For all buildings where sprinkler and combination sprinkler and standpipe systems are not subject to a special inspection pursuant to Section [1704.23] 1705.2.9 of this code, a licensed master plumber, licensed master fire suppression piping contractor, registered design professional or an individual holding an appropriate certificate of fitness from the Fire Department for the operation and/or maintenance of such system shall certify on forms provided by the department that all required painting has been completed in accordance with Section 903.6. Such certification shall be maintained on the premises and made available for inspection by the department and the Fire Department.

SECTION BC 904
ALTERNATIVE AUTOMATIC
FIRE-EXTINGUISHING SYSTEMS

904.1 General. Automatic fire-extinguishing systems, other than automatic sprinkler systems, shall be designed, installed, inspected, tested and maintained in accordance with the provisions of this section, the New York City Fire Code, and the applicable referenced standards.

904.1.1 Construction documents. Construction documents for alternative automatic fire-extinguishing systems shall be approved by the Fire Department and shall contain plans that include at least the following data and information:

1.	Commercial kitchen suppression systems:

1.1.	Location of all surface, plenum and duct nozzles; surface dimensions and location of all cooking appliances; the location of automatic fuel shutoff and statement as to type (gas or electric); location and distance of the remote control or manual pull station;

1.2.	Identification of the grease filters to be used in any kitchen hood; the dimensions of all hoods and all related ducts, including termination of duct at the exterior of the building;

1.3.	Identification of the fire suppression piping system; the make and model of the system; the type of extinguishing agent and number and size of agent containers; size, length, and type of all piping that will be used; the number and location of all fusible links or detectors and the temperature setting; any surface, plenum and duct nozzles.

2.	For extinguishing agent systems, the plan should also include type and concentration of the extinguishing agent, the method of providing power supply to smoke or heat detectors, fire rating of partitions, location of all audible/visible alarms within and outside the location involved and the details of construction of the room to contain the extinguishing agent. If the area is not sprinklered, the following information is required:

2.1.	The size and location of the reserve supply, and

2.2	Information as to why it has been determined that water is not effective as an extinguishing agent for the fire hazard in such location.

3.	The plans must note whether the proposed system is connected to the building’s fire alarm system.

Exception: For that portion of a fire suppression piping system within an approved preengineered system, a schematic isometric diagram shall be acceptable in lieu of full plans, provided that the location and method of pressure relief must be indicated with areas and volumes to where said relief is taken.

904.2 Where required.  Automatic fire-extinguishing systems installed as an alternative to the required automatic sprinkler systems of Section 903 shall be approved by the Fire Department. Automatic fire-extinguishing systems shall not be considered alternatives for the purposes of exceptions or reductions allowed by other requirements of this code.

904.2.1 Hood system suppression. Each required commercial kitchen exhaust hood and duct system required by Chapter 5 of the New York City Mechanical Code to have a Type I hood shall be protected with an automatic fire-extinguishing system installed in accordance with this code and the New York City Fire Code.

904.3 Installation. Automatic fire-extinguishing systems shall be installed in accordance with this section.

904.3.1 Electrical wiring. Electrical wiring shall be in accordance with the New York City Electrical Code.

904.3.2 Actuation. Automatic fire-extinguishing systems shall be automatically actuated and provided with a manual means of actuation in accordance with Section [904.11.1] 904.12.1. Where more than one hazard could be simultaneously involved in fire due to their proximity, all hazards shall be protected by a single system designed to protect all hazards that could become involved.

Exception: Multiple systems shall be permitted to be installed if they are designed to operate simultaneously.

904.3.3 System interlocking. Automatic equipment interlocks with fuel shutoffs, ventilation controls, door closers, window shutters, conveyor openings, smoke and heat vents and other features necessary for proper operation of the fire-extinguishing system shall be provided as required by the design and installation standard utilized for the hazard.

904.3.4 Alarms and warning signs. Where alarms are required to indicate the operation of automatic fire-extinguishing systems, distinctive audible and visible alarms and warning signs shall be provided to warn of pending agent discharge. Where exposure to automatic-extinguishing agents poses a hazard to persons and a delay is required to ensure the evacuation of occupants before agent discharge, a separate warning signal shall be provided to alert occupants once agent discharge has begun. Audible signals shall be in accordance with Section [907.5.2.1] 907.5.2.

904.3.5 Monitoring. Where a fire alarm system is installed, automatic fire-extinguishing systems shall be monitored by the fire alarm system in accordance with NFPA 72.

904.4 Inspection and testing. Automatic fire-extinguishing systems shall be inspected and tested in accordance with the provisions of this section and the New York City Fire Code prior to acceptance.

904.4.1 Inspection. Prior to conducting final acceptance tests, all of the following items shall be inspected:

1.	Hazard specification for consistency with design hazard.

2.	Type, location and spacing of automatic- and manual initiating devices.

3.	Size, placement and position of nozzles or discharge orifices.

4.	Location and identification of audible and visible alarm devices.

5.	Identification of devices with proper designations.

6.	Operating instructions.

904.4.2 Alarm testing. Notification appliances, connections to fire alarm systems and connections to central supervising stations shall be tested in accordance with this section and Section 907 to verify proper operation.

904.4.2.1 Audible and visible signals. The audibility and visibility of notification appliances signaling agent discharge or system operation, where required, shall be verified.

904.4.3 Monitor testing. Connections to protected premises and supervising station fire alarm systems shall be tested to verify proper identification and retransmission of alarms from automatic fire-extinguishing systems.

904.5 Wet-chemical systems. Wet-chemical extinguishing systems shall be installed, maintained, periodically inspected and tested in accordance with the New York City Fire Code.

904.6 Dry-chemical systems. Dry-chemical extinguishing systems shall be installed, maintained, periodically inspected and tested in accordance with New York City Fire Code. New dry-chemical extinguishing systems are not permitted for the protection of kitchen equipment.

904.7 Foam systems. Foam-extinguishing systems shall be installed, maintained, periodically inspected and tested in accordance with the New York City Fire Code.

904.8 Carbon dioxide systems. Carbon dioxide extinguishing systems shall be installed, maintained, periodically inspected and tested in accordance with the New York City Fire Code.

904.9 Halon systems. Halogenated extinguishing systems shall not be permitted. However, existing systems shall be maintained, periodically inspected and tested in accordance with the New York City Fire Code.

904.10 Clean-agent systems. Clean-agent fire-extinguishing systems shall be installed, maintained, periodically inspected and tested in accordance with the New York City Fire Code.

904.11 Automatic water mist systems. Automatic water mist systems shall be permitted in applications that are consistent with the applicable listing or approvals and shall comply with Sections 904.11.1 through 904.11.3.

904.11.1 Design and installation requirements. Automatic water mist systems shall be designed and installed in accordance with Sections 904.11.1.1 through 904.11.1.4.

904.11.1.1 General. Automatic water mist systems shall be designed and installed in accordance with the manufacturer’s instructions and the New York City Fire Code.

904.11.1.2 Actuation. Automatic water mist systems shall be automatically actuated.

904.11.1.3 Water supply protection. Connections to a potable water supply shall be protected against backflow in accordance with the New York City Plumbing Code.

904.11.1.4 Secondary water supply. Where a secondary water supply is required for an automatic sprinkler system, an automatic water mist system shall be provided with an approved secondary water supply in accordance with the New York City Fire Code.

904.11.2 Water mist system supervision and alarms. Supervision and alarms shall be provided as required for automatic sprinkler systems in accordance with Section 903.4.

904.11.2.1 Monitoring. Monitoring shall be provided as required for automatic sprinkler systems in accordance with Section 903.4.1.

904.11.2.2 Alarms. Alarms shall be provided as required for automatic sprinkler systems in accordance with Section 903.4.2.

904.11.2.3 Floor control valves. Floor control valves shall be provided as required for automatic sprinkler systems in accordance with Section 903.4.3.

904.11.3 Testing, operation and maintenance. Automatic water mist systems shall be tested, operated and maintained in accordance with the New York City Fire Code.

904.12 Commercial cooking systems. The automatic fire-extinguishing system for commercial cooking systems shall be of a type recognized for protection of commercial cooking equipment and exhaust systems of the type and arrangement protected. Pre-engineered automatic wet-chemical extinguishing systems shall be approved by the [fire commissioner] Fire Commissioner, tested in accordance with UL 300, and listed and labeled for the intended application. The protected area shall include the area under the hood and over the cooking equipment, the area above or behind the filters and the opening of the hood into the branch duct. Where a preengineered system is installed and the size of the protected area exceeds that allowed for a single preengineered system, additional preengineered systems arranged for simultaneous operation shall be provided. Other types of automatic fire-extinguishing systems shall be listed and labeled for specific use as protection for commercial cooking operations. The system shall be installed in accordance with this code, its listing and the manufacturer’s [installation] instructions. [Automatic] Only automatic fire-extinguishing systems of the following types shall be installed in accordance with the New York City Fire Code [and the referenced standard indicated, as shown]:

1.	[Carbon dioxide extinguishing systems, in accordance with the New York City Fire Code.] Foam water sprinkler system or foam water spray systems.

2.	Wet-chemical extinguishing systems [, in accordance with the New York City Fire Code].

Automatic sprinkler systems, dry-chemical fire-extinguishing systems, and carbon dioxide fire-extinguishing systems shall not be installed to protect commercial cooking equipment and exhaust systems.

[904.11.1] 904.12.1 Manual system operation. A manual actuation device shall be located at or near a means of egress from the cooking [areas, a minimum of] area not less than 10 feet (3048 mm) [and a maximum of] and not more than 20 feet (6096 mm), from the kitchen exhaust system. The manual actuation device shall be installed not more than 48 inches [(1200 mm)] (1219 mm) or less than 42 inches (1067 mm) above the finished floor and shall clearly identify the hazard protected. The manual actuation device shall require a maximum force of 40 pounds (178 N) and a maximum movement of 14 inches (356 mm) to actuate the fire suppression system.

Exception: Automatic sprinkler systems shall not be required to be equipped with manual actuation means.

[904.11.2] 904.12.2 System interconnection. The actuation of the fire suppression system shall automatically shut down the fuel or electrical power supply to the cooking equipment. The fuel and electrical supply reset shall be manual.

[904.11.3 Carbon dioxide systems. When carbon dioxide systems are used, there shall be a nozzle at the top of the ventilating duct. Additional nozzles that are symmetrically arranged to give uniform distribution shall be installed within vertical ducts exceeding 20 feet (6096 mm) and horizontal ducts exceeding 50 feet (15 240 mm). Dampers shall be installed at either the top or the bottom of the duct and shall be arranged to operate automatically upon activation of the fire-extinguishing system. Where the damper is installed at the top of the duct, the top nozzle shall be immediately below the damper. Automatic carbon dioxide fire-extinguishing systems shall be sufficiently sized to protect against all hazards venting through a common duct simultaneously.]

[904.11.3.1 Ventilation system. Commercial-type cooking equipment protected by an automatic carbon dioxide-extinguishing system shall be arranged to shut off the ventilation system upon activation.]

[904.12 Water-mist systems. Water-mist fire-extinguishing systems shall be installed, maintained, periodically inspected and tested in accordance with the New York City Fire Code.]

904.13 Domestic cooking systems in Group I-2. In Group I-2 occupancies where cooking facilities are installed in accordance with Section 407.2.6 of this code, the domestic cooking hood provided over the cooktop or range shall be equipped with an automatic fire-extinguishing system of a type recognized for protection of domestic cooking equipment. Preengineered automatic extinguishing systems shall be tested in accordance with UL 300A and listed and labeled for the intended application. The system shall be installed in accordance with this code, its listing and the manufacturer’s instructions.

904.13.1 Manual system operation and interconnection. Manual actuation and system interconnection for the hood suppression system shall be installed in accordance with Sections 904.12.1 and 904.12.2, respectively.

904.13.2 Portable fire extinguishers for domestic cooking equipment in Group I-2. A portable fire extinguisher complying with Section 906 shall be installed within a 30-foot (9144 mm) distance of travel from domestic cooking appliances.

SECTION BC 905
STANDPIPE SYSTEMS

905.1 General. Standpipe systems shall be provided in buildings and structures in accordance with this section. Fire hose threads used in connection with standpipe systems shall be approved by the [fire commissioner] Fire Commissioner. Standpipe systems in buildings used for high-piled combustible storage shall be in accordance with the New York City Fire Code. Installation of standpipe systems shall comply with the special inspection requirements of Chapter 17.

Any space or room that contains equipment of such nature that the use of water would be ineffective in fighting a fire therein, or would be otherwise hazardous, shall have a conspicuous sign on each door opening on such space or room stating the nature of the use and the warning: “IN CASE OF FIRE, USE NO WATER.”

905.1.1 Construction documents. Construction documents for standpipe systems shall contain plans that include, at [least] a minimum, the following data and information:

1.	The locations and sizes of all risers, cross-connections, hose racks, valves, Department connections, sources of water supply, piping, and other essential features of the system;

2.	A floor plan for each group of floors that have typical riser locations and no special features within such group of floor levels, with the indication in title block of such plan indicating clearly the floors to which the arrangement is applicable;

3.	A riser diagram showing the essential features of the system, including the risers, cross-connections, valves, Fire Department connections, tanks, pumps, sources of water supply, pipe sizes, capacities, floor heights, zone pressures, and other essential data and features of the system; [and]

4.	The available water pressure at the top and bottom floors of each zone, and at each floor where the [weight pipe fittings change] pressure rating  of piping, fittings, couplings, and valves are required to change, shall be shown on the riser diagram; and

5.	For street pressure-fed systems and fire pumps, a statement from the New York City Department of Environmental Protection, giving the minimum water pressure in the main serving the building.

905.2 Installation standards. Standpipe systems shall be installed in accordance with this section and NFPA 14[as modified in Appendix Q].

905.3 Required installations. Standpipe systems shall be installed where required by Sections 905.3.1 through [905.3.6] 905.3.9 and in the locations indicated in Sections 905.4, 905.5 and 905.6. Standpipe systems are allowed to be combined with automatic sprinkler systems.

Exception: Standpipe systems are not required in buildings occupied entirely by Group R-3.

905.3.1 Applicability. Class III standpipe systems shall be installed throughout the following buildings:

1.	In buildings two stories or more in height with floor area of 10,000 square feet (929 m2) or greater on any story;

2.	In buildings three stories or more in height with floor area of 7,500 square feet (697 m2) or greater on any story;

3.	In buildings of any area with a floor level having an occupant load of 30 or more that is located 55 feet (16 764 mm) or more above the lowest level of Fire Department vehicle access; and

4.	In buildings of any area, constructed in accordance with Section 403, with occupied floors located 75 feet (22 860 mm) or more above the lowest level of Fire Department vehicle access.

Exceptions: The following exceptions are allowed as an alternative to the requirement of a Class III standpipe system:

1.	Class I standpipes are allowed in buildings equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1 or 903.3.1.2 provided that the following additional requirements are met:

1.1.	A locked noncombustible storage cabinet shall be provided on the main entrance floor. One additional locked storage cabinet shall be provided on every tenth floor above the main entrance floor, such that no occupant on any floor would have to travel more than five floors to reach a cabinet in a location within 15 feet of each standpipe riser.  Where one standpipe riser is installed in the building, such cabinet  shall contain at least one fog nozzle, one 1.5-inch (38 mm) spanner wrench, one 2.5-inch (64 mm) spanner wrench, one 2.5-inch (64 mm) by 1.5 inch (38 mm) nonswivel reducing coupling, and 125 feet (38 m) of 1.5 inch (38 mm) hose. [Where two or more standpipe risers are installed in the building, at least two of each of the above items of equipment shall be provided. However, the hose may be omitted when serving Group R-2 occupancies.]

1.1.1.	The cabinet shall be kept locked, openable by a Fire Department citywide standard key.

1.1.2.	The cabinet shall be labeled, “FOR FIRE DEPARTMENT ONLY.”

1.1.3.	A metal sign stating clearly where the storage cabinet is located shall be placed in each stair enclosure on the main entrance floor and on each floor where the cabinet is located.

1.2.	Hose valves are capped with a hose valve cap fastened to the valve with a chain.

2.	Class I manual standpipes are allowed in open parking garages where the highest floor is located not more than 150 feet (45 720 mm) above the lowest level of Fire Department vehicle access.

3.	Class I manual dry standpipes are allowed in open parking garages that are subject to freezing temperatures, provided that the hose connections are located as required for Class [II] III standpipes in accordance with Section [905.5] 905.6.

4.	Class I standpipes are allowed in below-grade stories equipped throughout with an automatic sprinkler system.

5.	Standpipe outlets may be omitted in portions of first floors or basements that are completely separated from the entrance hall or enclosed stairways leading to the upper floors, provided that portable fire extinguishers are installed, subject to the approval of the [fire commissioner] Fire Commissioner.

905.3.2 Group A. Class I automatic wet standpipes shall be provided in nonsprinklered Group A buildings having an occupant load exceeding 1,000 persons.

Exceptions:

1.	Open-air-seating spaces without enclosed spaces.

2.	Class I automatic dry and semiautomatic dry standpipes or manual wet standpipes are allowed in buildings where the highest floor surface used for human occupancy is not more than 75 feet (22 860 mm)[or less] above the lowest level of Fire Department vehicle access. Dry standpipes are permitted only where subject to freezing temperatures.

905.3.3 Covered mall buildings. Covered mall buildings and buildings connected thereto shall be equipped throughout with a Class I automatic wet standpipe system, except as permitted by Sections 905.3.3.1 through 905.3.3.3.

905.3.3.1 Covered-mall building height. Covered-mall buildings where the highest occupied floor level is located not more than 30 feet (9144 mm) above the lowest level of the Fire Department vehicle access shall be permitted to be provided with Class I hose connections connected to the mall sprinkler system in accordance with Section 8.17.5.2 of NFPA 13 regarding hose connections for Fire Department use and under the following conditions:

1.	Any individual outlet shall be capable of delivering water flow at a rate of 250 gallons per minute (946 L/m) while concurrently supplying the mall sprinkler demand; and

2.	Each of the two most hydraulically remote outlets shall be capable of concurrently delivering 250 gallons per minute (946 L/m) at a pressure of 100 pounds per square inch (689.4 kPa) with no mall sprinkler demand, based on a supply pressure at the system Fire Department connection of not more than 175 pounds per square inch (1207 kPa). Adequacy of the water supply available to the Fire Department [to meet the hydraulic calculations] shall be demonstrated through hydraulic calculations provided by the registered design professional.

905.3.3.2 Location of hose connections. Hose connections shall be provided in accordance with Section 905.4 and at each of the following locations:

1.	Within the mall at the entrance to each exit passageway or exit.

2.	At each floor-level landing within [enclosed stairways] interior exit stairways opening directly on the mall.

3.	At exterior public entrances to the mall of a covered mall building.

4. 	At public entrances at the perimeter line of an open mall building.

5.	At other locations as necessary so that the distance to reach all portions of a tenant space does not exceed 150 feet (45 720 mm) from a hose connection.

905.3.3.3 Installation standard. Except as provided in Sections 905.3.3.1 and 905.3.3.2, the Class I hose connections and Fire Department connections shall be designed in conformance with NFPA 14.

905.3.4 Stages. Stages greater than 1,000 square feet in area (93 m2)[and], or any assembly occupancy [with a stage and] having an occupant load of 1,000 or [greater] more with a stage of any size, shall be equipped with a Class III wet standpipe system with [1½ inch and 2½ inch (38 mm and 64 mm)] a hose [connections] station on each side of the stage. Such hose stations shall comply with Section 905.6 and shall have sufficient hose to provide protection for the entire stage area from either standpipe location. The exceptions allowed under Section 905.3.1 shall not apply to these hose stations.

[905.3.4.1 Hose and cabinet. The 1½ inch (38 mm) hose connections shall be equipped with sufficient lengths of 1½ inch (38 mm) hose to provide fire protection for the stage area. Hose connections shall be equipped with an approved adjustable fog nozzle and be mounted in a cabinet or on a rack.]

905.3.5 Underground buildings. Underground buildings shall be equipped throughout with a Class I automatic wet or manual wet standpipe system.

905.3.6 Helistops and heliports. Buildings with a helistop or heliport that are equipped with a standpipe shall extend the standpipe to the roof level on which the helistop or heliport is located in accordance with the New York City Fire Code. All portions of the helistop and heliport area shall be within 150 feet (45 720 mm) of a 2½-inch (64 mm) outlet on a Class I or III standpipe, in accordance with the New York City Fire Code.

905.3.7 Marinas and boatyards.  Standpipes in marine terminals, piers, wharves, marinas and boatyards shall comply with the New York City Fire Code or other requirements of the Fire Department.

905.3.8 Rooftop gardens, landscaped roofs and green roofs. Buildings with a rooftop garden, landscaped roof, green roof, or roof used for any purpose other than weather protection or maintenance that are equipped with a standpipe system shall extend the standpipe system to the roof level on which the rooftop garden, landscaped roof, green roof, or roof used for any purpose other than weather protection or maintenance is located.

905.3.9 High-piled stock or rack storage. Where exit passageways are required in accordance with Chapter 10, a standpipe system shall be provided in accordance with the New York City Fire Code in all buildings containing high-piled stock or rack storage.

905.4 Location of Class I standpipe hose connections. Class I standpipe hose connections shall be provided in all of the following locations:

1.	In every required stairway, a hose connection shall be provided for each floor level above or below grade. Hose connections shall be readily accessible and located at the riser on each floor-level landing and on the entrance floor above the standpipe riser control valve. Nonrequired enclosed stairways that do not serve as a means of egress are not required to have hose connections. Stairways without hose connections shall have a sign on the door to the stairway stating, “No standpipe connections in stairway”.

2.	On each side of the wall adjacent to the exit opening of a horizontal exit.

Exception: Where floor areas adjacent to a horizontal exit are reachable from exit stairway hose connections by a 30-foot (9144 mm) hose stream from a nozzle attached to 100 feet (30 480 mm) of hose, a hose connection shall not be required at the horizontal exit.

3.	In every exit passageway at the entrance from the exit passageway to the other areas of a building.

Exception: Where floor areas adjacent to an exit passageway are reachable from exit stairway hose connections by a 30-foot (9144 mm) hose stream from a nozzle attached to 100 feet (30 480 mm) of hose, a hose connection shall not be required at the entrance from the exit passageway to other areas of the building.

4.	In covered mall buildings, in accordance with Section 905.3.3.2.

5.	Where the roof has a slope of less than four units vertical in 12 units horizontal (33.3-percent slope), each standpipe shall be provided with a hose connection located either on the roof or at the highest landing of stairways with stair access to the roof. An additional hose connection shall be provided at the top of the most hydraulically remote standpipe for testing purposes. This additional hose connection shall not be required when a roof manifold is installed in accordance with NFPA 14.

6.	Where the most remote portion of a floor or story is more than 150 feet (45 720 mm) from a hose connection, additional hose connections shall be provided in approved locations. For the purposes of this section, a penthouse with an occupant load greater than 10 shall be considered a story.

7.	In any staircase where the change in elevation between floor landings is more than 25 feet (7620 mm), in addition to the hose connections required by Item 1, a hose connection shall be installed at the first intermediate stair landing below the higher floor level.

905.4.1 Protection. Risers and laterals of Class I standpipe systems not located within an enclosed stairway or pressurized enclosure shall be protected by a degree of fire resistance equal to that required for vertical enclosures in the building in which they are located. No standpipe riser shall be placed in any shaft containing a gas or fuel pipeline.

Exception: In buildings equipped throughout with an approved automatic sprinkler system, laterals that are not located within an enclosed stairway or pressurized enclosure are not required to be enclosed in fire resistance rated construction.

905.4.2 Interconnection. In buildings where more than one standpipe is provided, the standpipes shall be interconnected in accordance with NFPA 14.

905.5 Location of Class II standpipe hose connections. Class II standpipe hose connections shall be [accessible and located in accordance with Section 905.3.4] prohibited.

905.5.1 Reserved.

[905.5.2 Protection. Fire-resistance-rated protection of risers and laterals of Class II standpipe systems is not required.]

905.6 Location of Class III standpipe hose connections. Class III standpipe systems shall have 2½-inch (64 mm) hose connections located as required for Class I standpipes in Section 905.4[and shall have Class II hose connections as required in Section 905.5]. At each hose connection, there shall be a hose station. The hose stations shall be equipped with a minimum of 125 feet (38 100 mm) but not more than a maximum of 150 feet (45 720 mm) of 1½-inch (38 mm) fire hose connected to an adjustable fog nozzle. The hose shall be attached to the 2½-inch (64 mm) hose connection by a 2½-inch (64 mm) x 1½-inch (38 mm) non-swivel reducing coupling. The hose shall be mounted on a rack and may be located in a cabinet, in accordance with Section 905.7. A pressure restricting device shall be installed when required by NFPA 14. Such pressure restricting device and reducing coupling shall be installed in such a manner that they are readily removable by the Fire Department.

905.6.1 Protection. Risers and laterals of Class III standpipe systems shall be protected as required for Class I systems in accordance with Section 905.4.1.

905.6.2 Interconnection. In buildings where more than one standpipe is provided, the standpipes shall be interconnected in accordance with NFPA 14.

905.7 Cabinets. Cabinets containing [fire-fighting] firefighting equipment such as standpipes, fire hoses, fire extinguishers or Fire Department valves shall not be blocked from use or obscured from view.

905.7.1 Cabinet equipment identification. Cabinets shall be identified in an approved manner by a permanently attached sign with white letters not less than 2 inches (51 mm) high and a red background color, indicating the equipment contained therein.

[Exception:] Exceptions:

1.	Doors not large enough to accommodate a written sign with 2-inch lettering shall be marked with a permanently attached pictogram indicating the equipment contained therein, in addition to corresponding smaller white lettering on a red background adjacent to such pictogram.

2.	Doors that have either an approved visual identification clear glass panel or a complete glass door panel are not required to be marked.

905.7.2 Locking cabinet doors. Cabinets shall be unlocked.

Exceptions:

1.	Visual identification panels of glass or other approved transparent frangible material that is easily broken and allows access.

2.	Approved locking arrangements.

3.	Locking of cabinets shall be permitted in Group I-3.

905.8 Dry standpipes. Dry standpipes shall not be installed.

Exception: Where subject to freezing and in accordance with NFPA 14.

905.9 Valve supervision. Valves controlling water supplies shall be supervised in the open position so that a change in the normal position of the valve will generate a supervisory signal at the central supervising station required by Section 903.4. Where a fire alarm system is provided, a signal shall also be transmitted to the fire alarm system.

Exceptions:

1.	Valves to underground key or hub valves in roadway boxes provided by the city or a public utility do not require supervision.

2.	Valves locked in the normal position and inspected as provided in this code in buildings not equipped with a fire alarm system.

905.10 During construction. Standpipe systems required during construction, alteration and demolition operations shall be provided in accordance with Section 3303.8.

905.11 Painting of dedicated standpipes. Dedicated standpipes and the handles of valves serving standpipes shall be painted and such painting certified in accordance with Sections 905.11.1 through 905.11.6. In addition to painting, standpipe piping may also be identified by lettered legend in accordance with ANSI A13.1. Where the piping is required to be listed and labeled such painting shall not obscure such labeling.

Exceptions:

1.	Attachments, gauges, valves and operable parts of standpipes other than valve handles.

2.	Where different color coding may be required by Section 3406 of the New York City Fire Code for facilities storing, handling, and using flammable and combustible liquids in connection with special operations.

905.11.1 New buildings. All portions of a standpipe system and the handles of valves serving the standpipe system in new buildings, including buildings constructed pursuant to Section 28-101.4.2 of the Administrative Code, shall be painted red prior to the hydrostatic pressure test whether or not they are intended to be enclosed at the end of construction.

905.11.2 Alterations. Existing handles of valves serving existing standpipe systems and existing unpainted standpipe risers that are exposed during alterations, including alterations pursuant to Section 28-101.4.2 of the Administrative Code shall be painted red. Where the alteration requires a hydrostatic pressure test such painting shall be completed prior to such test.

905.11.3 Retroactive requirement for completed buildings. Notwithstanding any other provision of law, all portions of exposed standpipe systems and handles of valves serving the standpipe system of completed buildings in existence March 2, 2010 shall be painted red [by June 2, 2010].

905.11.4 Buildings under construction on March 2, 2010. Notwithstanding any other provision of law, where construction documents were approved and permits issued for the construction of a new building or alteration of an existing building prior to March 2, 2010, and the work is not signed off by the department prior to such date, all exposed portions of the standpipe system and handles of valves serving the standpipe system shall be painted red prior to the hydrostatic pressure test, including portions that will be enclosed at a later point in time.

Exception: Portions of the standpipe system enclosed prior to March 2, 2010, need not be painted.

905.11.5 Combination standpipe and sprinkler systems. Where a standpipe system that is used as a combination standpipe and sprinkler system is required to be painted pursuant to Section 905.11.1, 905.11.2, 905.11.3 or 905.11.4, the sprinkler risers and cross connections that are also used for the standpipe system shall be painted red, and the handles of valves serving such combination standpipe and sprinkler system shall be painted yellow.

905.11.6 Certification of completion of system painting. For all buildings where standpipe and combination sprinkler and standpipe systems are not subject to a special inspection pursuant to Section [1704.24] 1705.30 of this code, a licensed master plumber, licensed master fire suppression piping contractor, registered design professional or an individual holding an appropriate certificate of fitness from the Fire Department for the operation and/or maintenance of such system shall certify on forms provided by the department that all required painting has been completed in accordance with Section 905.11. Such certification shall be maintained on the premises and made available for inspection by the department and the Fire Department.

SECTION BC 906
PORTABLE FIRE EXTINGUISHERS

906.1 General. Portable fire extinguishers shall be provided in occupancies and locations as required by the New York City Fire Code.

SECTION BC 907
FIRE ALARM AND DETECTION SYSTEMS

907.1 General. This section covers the application, installation, performance and maintenance of fire alarm systems and their components. Systems shall be designed and installed in accordance with NFPA 72 [as modified in Appendix Q] and the New York City Electrical Code. Systems shall be tested and maintained in accordance with this code and the New York City Fire Code.

907.1.1 Construction documents. Construction documents for fire alarm systems shall be submitted for review and approval to the Fire Department prior to system installation. Construction documents shall include, but not be limited to, all of the following:

1.	A floor plan that indicates the use of all rooms.

2.	Locations of alarm-initiating devices.

3.	Locations of alarm notification appliances, including candela ratings for visible alarm notification appliances.

4.	Location of fire command center, fire alarm control units, transponders and notification power supplies.

5.	Location of remote annunciators.

6.	Location of all primary, secondary and local sources of power.

7.	Fire alarm riser diagram showing all fire alarm devices indicated on the floor plans. Quantities of devices on the floor plans shall match the quantities indicated on the riser diagram. Riser diagram shall include class and style of circuits and levels of survivability. The riser diagram shall show the interface of fire safety control functions.

8.	Copies of any variances granted by the department or the Fire Department.

9.	Legend of all fire alarm symbols and abbreviations used.

10.	Design criteria for fire alarm audibility in various occupancies indicated on plans.

11.	Fire alarm sequence of operation for the fire alarm system in a matrix format.

12.	Classification of the central supervising station.

907.1.1.1 Amended construction documents. Amendments to approved construction documents shall be submitted[,] and approved by the Fire Department before the final inspection of the work or equipment is completed, and such amendments when approved shall be deemed part of the original construction documents. The Fire Department may allow minor revisions of construction documents to be made and submitted to the Fire Department after the completion of work but prior to sign-off of the work in accordance with rules promulgated by the Fire Department regarding such amendments.

907.1.2 Equipment. Systems and their components shall be listed for the purpose for which they are installed. The fire alarm control unit shall meet the requirements of the Fire Department.

907.2 Where required. An approved fire alarm system installed in accordance with the provisions of this code and NFPA 72[as modified by Appendix Q] shall be provided in accordance with Sections 907.2.1 through [907.2.22] 907.2.23 and provide occupant notification in accordance with Section 907.5, unless other requirements are provided by another section of this code.

A minimum of one manual fire alarm box shall be provided in an approved location to initiate a fire alarm signal for fire alarm systems employing automatic fire detectors or waterflow detection devices. Where other sections of this code allow elimination of fire alarm boxes due to sprinklers, a single fire alarm box shall be installed.

Exceptions:

1.	The manual fire alarm box is not required for fire alarm systems dedicated to elevator recall control and supervisory service.

2.	The manual fire alarm box is not required for Group R-2 occupancies unless required by the Fire Department to provide a means for fire watch personnel to initiate an alarm during a sprinkler system impairment event. Where provided, the manual fire alarm box shall not be located in an area that is accessible to the public.

In all occupancies where an automatic fire alarm system is required by this section, selective coverage smoke detectors shall be located as follows, unless partial or total coverage automatic detection is specified.

1.	In each mechanical equipment, electrical, transformer, telephone equipment or similar room, in elevator machine rooms, and in elevator lobbies.

2.	In air distribution systems in accordance with Section 606 of the New York City Mechanical Code.

907.2.1 Group A. A manual and automatic fire alarm system that activates the occupant notification system in accordance with Section 907.5 shall be installed in Group A occupancies [having an] where the occupant load [of] due to the assembly occupancy is 300 or more. Group A occupancies not separated from one another in accordance with Section 707.3.10 shall be considered as a single occupancy for the purposes of applying this section. Portions of Group E occupancies occupied for assembly purposes shall be provided with a fire alarm system as required for the Group E occupancy.

Exceptions:

1.	Manual fire alarm boxes are not required where the building is equipped throughout with an automatic sprinkler system and the notification appliances will activate upon sprinkler water flow. This exception shall not apply to Group A-2 occupancies used as a cabaret.

2.	A Group A-2 occupancy used as a cabaret with an occupant load of 75 or more, including associated stages, dressing rooms, and property rooms, shall be equipped with a manual fire alarm system. Such a Group A-2 occupancy with an occupant load of 300 or more shall also be equipped with an automatic fire alarm system.

3.	Group A occupancies with a stage in accordance with Section 410, and having an occupant load of 75 or more, shall be provided with a voice/alarm communication system as required by Sections [410.8] 410.9 and 907.2.1.1.

907.2.1.1 System initiation in Group A occupancies. Activation of the fire alarm in Group A-1 occupancies with an occupant load of 300 or more, and in all other Group A occupancies with an occupant load of 1,000 or more, shall initiate a presignal system in accordance with NFPA 72 [as amended by Appendix Q] at a constantly attended location from which the Fire Department shall be notified and live voice evacuation instructions shall be initiated using an emergency voice/alarm communications system in accordance with Section 907.5.2.2.

907.2.1.2 Emergency voice/alarm communication captions. Stadiums, arenas and grandstands required to caption audible public announcements shall be in accordance with Section 907.5.2.2.4.

907.2.2 Group B. A manual and automatic fire alarm system shall be installed in Group B occupancies [that are protected by an automatic sprinkler system] where one of the following conditions exists:

1.	The combined Group B occupant load of all floors is 500 or more.

2.	The Group B occupant load is more than 100 persons above or below the lowest level of exit discharge.

3.	The [Group B] fire area contains [a Group B] an ambulatory [health] care facility, which shall comply with Section 907.2.2.1.

Where such Group B occupancies meeting any one of the above conditions are not protected by an automatic sprinkler system, a partial coverage automatic smoke detection system shall be installed in accordance with NFPA 72.

907.2.2.1 [Group B ambulatory health] Ambulatory care facilities. Fire areas containing [Group B] ambulatory [health] care facilities shall be provided with an electronically supervised automatic partial-coverage smoke detection system installed within the ambulatory [health] care facility and in public use areas outside of tenant spaces and along the path of egress, including public corridors and elevator lobbies.

Exception: Buildings equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1, provided the occupant notification appliances will activate throughout the notification zones upon sprinkler waterflow.

907.2.2.2 Large-area buildings. Group B occupancies having a total gross area exceeding 100,000 square feet (9290 m2) located in buildings where the highest occupied floor is [less than] 75 feet (22 860 mm) or less above the lowest level of Fire Department vehicle access shall be provided with automatic smoke detection connected to an automatic fire alarm system in accordance with Section 907.2.13.1 and emergency voice/alarm communication system in accordance with Section 907.5.2.2 that initiates a total evacuation signal.

907.2.3 Group E. A manual and automatic fire alarm system shall be installed in Group E occupancies. An emergency voice/alarm communication system meeting the requirements of Section 907.5.2.2 and installed in accordance with Section 907.6 shall be installed in Group E occupancies. [When automatic] Automatic sprinkler systems [or], smoke detectors [are installed,] and/or other initiating devices, shall be installed in accordance with other sections of this code. When such systems, initiating devices, and/or detectors are installed, they shall be connected to the building fire alarm system.

Exception: Emergency voice/alarm communication systems meeting the requirements of Section 907.5.2.2 and installed in accordance with Section 907.6 shall not be required in Group E occupancies with occupant loads of 100 or less, provided that activation of the manual and automatic fire alarm system initiates an approved occupant notification signal in accordance with Section 907.5.

907.2.4 Group F. A manual and automatic fire alarm system shall be installed in Group F occupancies that are two or more stories in height and have an occupant load of 100 or more, or when 25 persons or more are above or below the lowest level of exit discharge.

907.2.5 Group H. A manual and automatic fire alarm system shall be installed in Group H-5 occupancies and in occupancies used for the manufacture of organic coatings. In addition to the automatic fire alarm system requirements of Section 907.2, an automatic smoke detection system shall be installed for highly toxic gases, organic peroxides and oxidizers in accordance with the New York City Fire Code [, and shall be connected to a central supervising station].

[Exceptions: A smoke detection system shall not be required in detached storage buildings equipped throughout with an approved automatic fire-extinguishing system and used only to store the following:]

[1.	Organic peroxides.]

[2.	Liquid or solid oxidizers.]

Exception: Where exempt under the New York City Fire Code.

907.2.6 Group I. A manual and automatic fire alarm system that activates the occupant notification system in accordance with Section 907.5 shall be installed in Group I occupancies. An automatic smoke detection system that activates the occupant notification system shall be provided in accordance with Sections 907.2.6.1. 907.2.6.2 and 907.2.6.3.3.

907.2.6.1 Group I-1. An automatic smoke detection system shall be installed in corridors, waiting areas open to corridors and habitable spaces other than sleeping units and kitchens. The system shall be activated in accordance with Section 907.5.

Exception: Smoke detection is not required for exterior balconies.

907.2.6.1.1 Smoke detectors within dwelling and sleeping units. Smoke detectors and notification appliances shall be installed in dwelling units and such notification appliances shall activate only in the unit in which the alarm originates. Such detectors and appliances shall be annunciated by dwelling unit at a constantly attended location from which the fire alarm system is capable of being manually activated. Smoke detectors are required in the following areas:

1.	Sleeping areas;

2.	Every room in the path of the means of egress from the sleeping area to the door leading from the dwelling unit; and

3.	Each story within the unit, including below-grade stories. For dwelling units with split levels and without an intervening door between the adjacent levels, a smoke detector installed on the upper level shall suffice for the adjacent lower level.

907.2.6.2 Group I-2. An automatic smoke detection system shall be installed in corridors in nursing homes (both intermediate-care and skilled nursing facilities), corridors in detoxification facilities and spaces permitted to be open to the corridors by Section 407.2. The system shall be activated in accordance with Section 907.5. Hospitals shall be equipped with smoke detection as required in Section 407. A one-way voice communication system activated in accordance with Section 907.5.2.2 shall be provided at the fire command center for use by Fire Department personnel. A two-way voice communication system in accordance with Section 907.2.13.3 shall be provided for Group I-2 buildings.

[907.2.6.2.1 Group I-2 hospital buildings. Group I-2 hospital buildings where the highest occupied floor is less than 75 feet (22 860 mm)  above the lowest level of Fire Department vehicle access shall be provided with partial coverage automatic smoke detection connected to an automatic fire alarm system in accordance with Section 907.2.13.1 and an emergency voice/alarm communication system in accordance with Section 907.5.2.2.]

907.2.6.3 Group I-3. Group I-3 occupancies shall be equipped with a manual and automatic fire alarm system and automatic smoke detection system installed for alerting staff.

907.2.6.3.1 System initiation. Actuation of an automatic fire-extinguishing system, automatic sprinkler system, a manual fire alarm box, a fire detector, or a smoke detector shall initiate an approved alarm signal that automatically notifies staff.

907.2.6.3.2 Manual fire alarm boxes. Manual fire alarm boxes are not required to be located in accordance with Section 907.4.2 where the fire alarm boxes are provided at staff-attended locations having direct supervision over areas where manual fire alarm boxes have been omitted.

907.2.6.3.2.1 Manual fire alarm boxes in detainee areas. Manual fire alarm boxes are allowed to be locked in areas occupied by detainees, provided that staff members are present within the subject area and have keys readily available to operate the manual fire alarm boxes.

907.2.6.3.3 Automatic smoke detection system. An automatic smoke detection system shall be installed throughout resident housing [units] areas, including sleeping [areas] units and contiguous day rooms, group activity spaces and other common spaces normally accessible to residents.

Exceptions:

1.	Other approved smoke detection arrangements providing equivalent protection, including, but not limited to, placing detectors in exhaust ducts from cells or behind protective guards listed for the purpose, are allowed when necessary to prevent damage or tampering.

2.	Sleeping units in Use Conditions 2 and 3 as described in Section 308.

3.	Smoke detectors are not required in sleeping units with four or fewer occupants in smoke compartments that are equipped throughout with an approved automatic sprinkler system installed in accordance with Section 903.3.1.1.

907.2.7 Group M. A manual and automatic fire alarm system shall be installed in Group M occupancies where any one of the following conditions exists:

1.	Where a Group M fire area exceeds 12,000 square feet (1115 m2);

2.	Where a Group M fire area is located more than three stories above grade;

3.	Where the combined area of all Group M fire areas on all floors, including mezzanines, exceeds 24,000 square feet (2230 m2); or

4.	Where a Group M fire area in a below-grade story exceeds 1,500 square feet (139 m2).

Where such occupancies are not protected by an automatic sprinkler system, a manual fire alarm and partial coverage automatic smoke detection or automatic heat detection system shall be installed in accordance with NFPA 72.

907.2.7.1 Large-area buildings. Group M occupancies having a total gross area exceeding 100,000 square feet (9290 m2) located in buildings where the highest occupied floor is [less than] 75 feet (22 860 mm) or less above the lowest level of Fire Department vehicle access and covered mall buildings having a total gross area exceeding 50,000 square feet (4645 m2) shall be provided with automatic smoke detection connected to an automatic fire alarm system in accordance with Section 907.2.13.1 and an emergency voice/alarm communication system in accordance with Section 907.5.2.2 initiating a total evacuation signal.

907.2.8 Group R-1. Fire alarm systems shall be installed in Group R-1 occupancies as required in Sections 907.2.8.1 through [907.2.8.4] 907.2.8.5.

907.2.8.1 Manual fire alarm system. A manual fire alarm system that activates the occupant notification system in accordance with Section 907.5 shall be installed in Group R-1 occupancies.

Exception: A manual fire alarm system is not required in buildings not over two stories in height where all individual [dwelling] sleeping units and contiguous attic and crawl spaces are separated from each other and public or common areas by at least 1-hour fire partitions and each individual dwelling unit has an exit directly to a public way, exit court or yard.

907.2.8.2 Automatic smoke detection system. An automatic smoke detection system that activates the occupant notification system in accordance with Section 907.5 shall be installed in all public corridors serving dwelling units [and] or sleeping units in accordance with Section 907.2.8.3.

Exception: An automatic fire detection system is not required in buildings that do not have public corridors serving [dwelling] sleeping units and each [dwelling] sleeping unit has a means of egress door opening directly to an exterior exit access that leads directly to an exit.

907.2.8.3 Smoke detectors within dwelling units and sleeping units. Smoke detectors and audible notification appliances shall be installed in dwelling units and sleeping units and shall be annunciated by dwelling unit and sleeping unit at a constantly attended location from which the fire alarm system is capable of being manually activated. Smoke detectors are required in the following areas:

- In sleeping areas.

- In every room in the path of the means of egress from the sleeping area to the door leading from the dwelling unit and sleeping unit.

3.	In each story within the unit, including below-grade stories. For dwelling units and sleeping units with split levels and without an intervening door between the adjacent levels, a smoke alarm installed on the upper level shall suffice for the adjacent lower level.

907.2.8.4 Group R-1 student dormitories. A manual and automatic smoke detection system shall be installed in occupancies for student or school staff dormitory housing in all of the following locations:

1.	Common spaces outside of sleeping units.

2.	Laundry rooms, mechanical equipment rooms and storage rooms.

3.	Interior corridors serving sleeping units.

Exception: An automatic smoke detection system is not required in buildings that do not have interior corridors serving sleeping units or dwelling units and where each sleeping unit or dwelling unit either has a means of egress door opening directly to an exterior exit access that leads directly to an exit or a means of egress door opening directly to an exit.

Required smoke alarms for student or staff dormitory housing shall be interconnected with the fire alarm system in accordance with NFPA 72.

[907.2.8.4] 907.2.8.5 Large Group R-1 occupancies. Group R-1 occupancies with a total of more than 50 sleeping rooms above street level located in buildings where the highest occupied floor is [less than] 75 feet (22 860 mm) or less above the lowest level of Fire Department vehicle access, or communal sleeping facilities above street level occupied or designed to be occupied by more than 50 lodgers, shall be provided with automatic smoke detection connected to an automatic fire alarm system in accordance with Section 907.2.13.1 and an emergency voice/alarm communication system in accordance with Section 907.5.2.2 that initiates a total evacuation signal.

907.2.9 Group R-2. A fire alarm system without alarm notification appliances and smoke alarms shall be installed in accordance with this section in Group R-2 occupancies, other than student apartments, where such occupancy satisfies any one of the following conditions:

1.	Any dwelling unit is located three or more stories above the lowest level of exit discharge, including dwelling units in penthouses of any area;

2.	Any dwelling unit is located more than one story below the highest level of exit discharge of exits serving the dwelling unit; or

3.	The building contains more than 16 dwelling units.

Actuation of smoke detectors shall not initiate a signal to alarm notification appliances. The activation of any detector required by this section shall initiate a signal at a central station or a constantly attended location. Smoke detectors shall be located as follows:

1.	In each mechanical equipment, electrical, transformer, telephone equipment or similar room[, greater than 75 square feet (6.96 m2) in area].

2.	In air distribution systems in accordance with Section 606 of the New York City Mechanical Code.

3.	In elevator machine rooms and in elevator lobbies.

907.2.9.1 Group R-2 student apartments. Where the main use or dominant occupancy of a building is classified as R-2 student apartments, as defined in Section 310.2, fire alarm systems shall be installed in accordance with Section 907.2.8. Where the main use or dominant occupancy of a building is not classified as R-2 student apartments and the building is occupied partially by Group R-2 student apartments, fire alarm systems shall be installed in accordance with Sections 907.2.9.1.1 through 907.2.9.2.

907.2.9.1.1 Manual fire alarm system. A manual fire alarm system shall be installed throughout all public corridors serving student apartments and student-related uses. Student-related uses shall include common spaces such as recreation rooms, lounges, dining rooms, laundry rooms and storage rooms.

Exceptions:

1.	A manual fire alarm system is not required in buildings not over two stories in height where all individual dwelling units and contiguous attic and crawl spaces are separated from each other and public or common areas by at least 1-hour fire partitions and each individual dwelling unit has an exit directly to a public way, exit court or yard.

2.	A manual fire alarm system is not required in buildings containing fewer than 15 student apartments.

907.2.9.1.2 Automatic fire alarm system. An automatic fire alarm system without alarm notification appliances shall be installed in accordance with this section in Group R-2 student apartments and student-related uses. The activation of any smoke detector required by this section shall initiate a signal at a central station or a constantly attended location. Smoke detectors shall be located as follows:

1.	In each mechanical equipment, electrical, transformer, telephone equipment or similar room, in elevator machine rooms, and in elevator lobbies.

2.	In air distribution systems in accordance with Section 606 of the New York City Mechanical Code.

3.	Throughout all public corridors serving student apartments and student-related uses. Student-related uses shall include common spaces such as recreation rooms, lounges, dining rooms, laundry rooms and storage rooms. However, smoke detectors shall not be required in such public corridors in buildings containing fewer than 15 student apartments.

Exception: An automatic fire alarm system is not required in buildings not over two stories in height where all individual dwelling units and contiguous attic and crawl spaces are separated from each other and public or common areas by at least 1-hour fire barriers and each individual dwelling unit has an exit directly to a public way, exit court or yard.

907.2.9.2 Smoke alarms. Single- and multiple-station smoke alarms shall be installed in accordance with Section 907.2.11.

907.2.10 [Reserved.] Group S. A manual and automatic fire alarm system shall be installed in Group S occupancies where any one of the following conditions exists:

1.	Group S fire area has an occupant load of 300 occupants or more;

2.	The combined occupant load of all Group S fire areas on all floors, including mezzanines, is 300 or more.

907.2.10.1 Large-area buildings. Group S occupancies having a total gross area exceeding 500,000 square feet (46 452 m2) located in buildings, where the highest occupied floor is 75 feet (22 860) or less above the lowest level of Fire Department vehicle access, shall be provided with automatic smoke detection connected to an automatic fire alarm system in accordance with Section 907.2.13.1 and an emergency voice/alarm communication system in accordance with Section 907.5.2.2 that initiates a total evacuation signal.

907.2.11 Single- and multiple-station smoke alarms. Listed single- and multiple-station smoke alarms complying with UL 217 shall be installed in accordance with Sections 907.2.11.1 through [907.2.11.4] 907.2.11.7 and NFPA 72.

907.2.11.1 Smoke alarms in Groups R-2[,] and R-3 [, and I-1]. Single- or multiple-station smoke alarms shall be installed and maintained in Groups R-2[,] and R-3 [, and I-1], regardless of occupant load at all of the following locations within all dwelling units:

1.	On the ceiling or wall outside of each room used for sleeping purposes within 15 feet (4572 mm) from the door to such room.

2.	In each room used for sleeping purposes.

[Exception: Single- or multiple-station smoke alarms in Group I-1 shall not be required where smoke detectors are provided in the sleeping rooms as part of an automatic smoke detection system.]

3.	In each story within a dwelling unit, including below-grade stories and penthouses of any area, but not including crawl spaces and uninhabitable attics. In dwellings or dwelling units with split levels and without an intervening door between the adjacent levels, a smoke alarm installed on the upper level shall suffice for the adjacent lower level provided that the lower level is less than one full story below the upper level.

907.2.11.1.1 Group R-2 occupancy. Smoke alarms shall be provided with the capability to support visible alarm notification appliances in accordance with ICC/ANSI A117.1.

907.2.11.2 Power source. Required smoke alarms shall receive their primary power from a dedicated branch circuit or the unswitched portion of a branch circuit also used for power or lighting, or both, and shall be equipped with a battery backup. Smoke alarms shall emit a signal when the batteries are low. Wiring shall be permanent and without a disconnecting switch other than as required for over-current protection.

Exception: Smoke alarms with integral strobes shall not require battery backup provided that the smoke alarms are connected to an emergency or standby power electrical source.

907.2.11.3 Installation near cooking appliances. Smoke alarms shall not be installed in the following locations unless this would prevent placement of a smoke alarm in a location required by Section 907.2.11.1:

1.	Ionization smoke alarms shall not be installed less than 20 feet (6096 mm) horizontally from a permanently installed cooking appliance.

2.	Ionization smoke alarms with an alarm-silencing switch shall not be installed less than 10 feet (3048 mm) horizontally from a permanently installed cooking appliance.

3.	Photoelectric smoke alarms shall not be installed less than 6 feet (1829 mm) horizontally from a permanently installed cooking appliance.

907.2.11.4 Installation near bathrooms. Smoke alarms shall be installed not less than 3 feet (914 mm) horizontally from the door or opening of a bathroom that contains a bathtub or shower unless this would prevent placement of a smoke alarm required by Section 907.2.11.1.

[907.2.11.3] 907.2.11.5 Interconnection. Where more than one smoke alarm [or detector] is required to be installed within an individual dwelling unit or sleeping unit in Group [I-1,] R-2[,] and R-3 occupancies, [or within an individual dwelling unit or sleeping unit in Group R-1,] the smoke alarms [or detectors] shall be interconnected in such a manner that the activation of one alarm [or detector] will activate all of the alarms [or detectors] in the individual unit. Physical interconnection of smoke alarms shall not be required where listed wireless alarms are installed and all alarms sound upon activation of one alarm. The alarm [or detector] shall be clearly audible in all bedrooms over background noise levels with all intervening doors closed.

[907.2.11.4 Group R-2 occupancy. Smoke alarms shall be provided with the capability to support visible alarm notification appliances in accordance with ICC/ANSI A117.1.]

[907.2.11.5] 907.2.11.6 Smoke alarms and smoke detectors in group R occupancies. On and after January 1, 2021, smoke alarms and smoke detectors shall not be installed or replaced in an individual dwelling or sleeping unit, including dwellings or units in prior code buildings, within an area of exclusion determined by a 20 foot [(6.0 m)] (6096 mm) radial distance along a horizontal flow path from a stationary or fixed cooking appliance, unless listed in accordance with the 8th edition of UL 217 for smoke alarms or the 7th edition of UL 268 for smoke detectors.

907.2.11.7 Smoke detection system. Smoke detectors listed in accordance with UL 268 and provided as part of the building fire alarm system shall be an acceptable alternative to single and multiple station smoke alarms and shall comply with the following:

1.	The fire alarm system shall comply with all applicable requirements in Section 907.

2.	Activation of a smoke detector in a dwelling unit or sleeping unit shall initiate alarm notification in the dwelling unit or sleeping unit in accordance with Section 907.5.2.

3.	Activation of a smoke detector in a dwelling unit or sleeping unit shall not activate alarm notification appliances outside of the dwelling unit or sleeping unit, provided that a supervisory signal is generated and monitored in accordance with Section 907.6.5.

907.2.12 Special amusement buildings. An automatic smoke detection system shall be provided in special amusement buildings in accordance with Sections 907.2.12.1 through 907.2.12.3.

Exception: In areas where ambient conditions will cause a smoke detection system to alarm, an approved alternative type of automatic detector shall be installed.

907.2.12.1 Alarm. [Activation] Actuation of [any] a single smoke detector, [the] automatic sprinkler system or [any] other automatic fire detection [device] system shall [immediately sound an alarm at the building] initiate a pre-signal system in accordance with NFPA 72 at a constantly attended location from which [emergency action can be initiated, including the capability of manual initiation of requirements in Section 907.2.12.2] the Fire Department shall be notified and live voice evacuation instructions shall be initiated using an emergency voice/alarm communications system in accordance with Section 907.5.2.2.

907.2.12.2 System response. The following minimum system actuations and responses shall be required upon approval by the department and the Fire Department. The activation of two or more smoke detectors, a single smoke detector equipped with an alarm verification feature, the automatic sprinkler system or other approved fire detection device shall automatically do all of the following:

1.	Cause illumination of the means of egress with light of not less than 1 foot-candle (11 lux) at the walking surface level[;].

2.	Stop any conflicting or confusing sounds and visual distractions[; and].

3.	Activate an approved directional exit marking that will become apparent in an emergency[; and].

[4.	Activate a prerecorded message, clearly audible throughout the special amusement building, instructing patrons to proceed to the nearest exit. Alarm signals used in conjunction with the prerecorded message shall produce a sound that is distinctive from other sounds used during normal operation.]

907.2.12.3 Emergency voice/alarm communication system. An emergency voice/alarm communication system, which is also allowed to serve as a public address system, shall be installed in accordance with Section 907.5.2.2[,] and be audible throughout the entire special amusement building.

907.2.13 High-rise buildings. In addition to the requirements of Sections 907.2.1 through 907.2.12, buildings constructed in accordance with Section 403 and having floors used for human occupancy located more than 75 feet (22 860 mm) above the lowest level of Fire Department vehicle access shall be provided with an automatic smoke detection connected to an automatic fire alarm system in accordance with Section 907.2.13.1, a Fire Department communication system in accordance with Section 907.2.13.2, a two-way communication system in accordance with Section 907.2.13.3, and an emergency voice/alarm communication system in accordance with Section 907.5.2.2.

Exceptions:

1.	Open parking garages in accordance with Section [406.3] 406.5.

2.	Buildings with an occupancy in Group A-5 in accordance with Section [303.1] 303.6.

3.	[Special] Low-hazard special occupancies in accordance with Section 503.1.1.

4.	Buildings with an occupancy in Group H-1, H-2 or H-3 in accordance with Section 415.

907.2.13.1 Automatic smoke detection. In addition to smoke detection otherwise required by this code, automatic smoke detection in high-rise buildings shall be in accordance with Sections 907.2.13.1.1 and 907.2.13.1.2.

Exception for Group R-2 occupancies: In R-2 occupancies, the activation of smoke detectors shall initiate a signal at a central supervising station or a constantly attended location and shall not initiate a signal to [an] alarm notification appliances.

907.2.13.1.1 Automatic smoke detection. Automatic smoke detectors shall be provided in accordance with this section. Smoke detectors shall be connected to an automatic fire alarm system. The activation of any detector required by this section shall [operate] activate the emergency voice/alarm communication system. Smoke detectors shall be located as follows:

1.	In each mechanical equipment, electrical, transformer, telephone equipment or similar room.

2.	In each elevator machine room and in elevator lobbies.

907.2.13.1.2 Duct smoke detection. Duct smoke detectors complying with Section 907.3.1 shall be located in air distribution systems in accordance with Section 606 of the New York City Mechanical Code.

907.2.13.2 Fire Department communication system. [A] The Fire Department Auxiliary Radio Communication System (ARCS)[, which] shall be in accordance with Section [917, shall be required in all high-rise buildings] 916.

[Exception: Where it is determined by the Fire Department that a radio communication system is not required.]

907.2.13.3 Two-Way Communication System. A two-way voice communication system (warden) phone that complies with the requirements of NFPA 72 shall be provided in the following locations and shall comply with the following requirements. Such phones shall communicate with the fire command center.

1.	In Group B high-rise office buildings and large area office buildings, there shall be a minimum of two phones located on every floor accessible to all occupants, with each phone located within 5 feet (1524 mm) of a different exit stair.

2.	Where elevator lobbies are permitted to be locked, the phones provided are permitted to be connected to the fire alarm system.

3.	If phones are provided in areas of rescue assistance and refuge areas, the phones are permitted to be connected to the fire alarm system.

4.	Where phones are provided to meet the requirements for stairway communication systems in Section 403.5.3.1, the phones are permitted to be connected to the fire alarm system.

5.	In all Group I-2 buildings, there shall be a phone located at staff attended locations, such as nurses’ stations or similar locations accessible to all staff members, on every patient floor per fire/smoke zone. Phones shall also be located in areas of the building where the fire alarm does not sound.

Exception: Group R-2 occupancies.

907.2.14 Atriums connecting more than two stories. A fire alarm system shall be installed in occupancies with an atrium that connects more than two stories, with smoke detection installed [throughout] in locations as required by a rational analysis in Section 909.4 and in accordance with the [atrium] system operation requirements in Section 909.17. The system shall be activated in accordance with Section 907.5. Such occupancies in Group A, E or M shall be provided with an emergency voice/alarm communication system complying with the requirements of Section 907.5.2.2.

907.2.15 High-piled combustible storage areas. An automatic fire detection system shall be installed throughout high-piled combustible storage areas where required by the New York City Fire Code.

907.2.16 Aerosol storage uses. Aerosol storage rooms and general-purpose warehouses containing aerosols shall be provided with an approved manual fire alarm system where required by the New York City Fire Code.

907.2.17 Lumber, wood structural panel and veneer mills. Lumber, wood structural panel and veneer mills shall be provided with a manual fire alarm system.

907.2.18 Underground buildings with compartment smoke control system. Where a compartment smoke control system is installed in an underground building as required by Section 405, automatic [fire] smoke detectors shall be provided in accordance with Section 907.2.18.1.

907.2.18.1 Smoke detectors. [A minimum of] Not fewer than one smoke detector listed for the intended purpose shall be installed in all of the following areas:

1.	Mechanical equipment, electrical, transformer, telephone equipment, elevator machine or similar rooms.

2.	Elevator lobbies.

3.	The main supply [and], main return, and exhaust air plenum of each air-conditioning system serving more than one story and located in a serviceable area downstream from filters on supply ducts and in return/exhaust ducts downstream of the last duct inlet.

4.	Each connection to a vertical duct or riser serving two or more floors from return air ducts or plenums of heating, ventilating and air-conditioning systems, except that in Group R occupancies, a listed smoke detector is allowed to be used in each return air riser carrying not more than 5,000 cfm (2.4 m3/s) and serving not more than 10 air inlet openings.

907.2.18.2 Alarm required. Activation of the smoke exhaust system shall activate an audible alarm at a constantly attended location.

907.2.19 Underground buildings. In underground buildings complying with Section 405 where the lowest level of a structure is more than 30 feet [(18 144 mm)] (9144 mm) below the lowest level of exit discharge, the structure shall be equipped throughout with a manual and automatic fire alarm system, including an emergency voice/alarm communication system installed in accordance with Section 907.5.2.2.

907.2.20 Covered and open mall buildings. [Covered mall buildings exceeding] Where the total floor area exceeds 50,000 square feet (4645 m2) [in total floor area shall be provided with] within either a covered mall building or within the perimeter line of an open mall building, an emergency voice/alarm communication system shall be provided. [An emergency] Emergency voice/alarm communication [system] systems serving a mall, required or otherwise, shall be accessible to the Fire Department. The system shall be provided in accordance with Section 907.5.2.2.

907.2.21 [Battery rooms. An approved automatic smoke detection system shall be installed in areas containing stationary storage battery systems having a liquid capacity of more than 50 gallons (189.3 L). Where the battery room is located in a building or space that is provided with a fire alarm system or subsystem, the smoke detectors shall be connected to such building fire alarm system or subsystem.  The detection system shall be supervised by a central supervising station, or a local alarm that will sound an audible signal at a constantly attended location.] Reserved.

907.2.22 Airport traffic control towers. An automatic smoke detection system that activates the occupant notification system in accordance with Section 907.5 shall be provided in airport control towers in [all occupiable and equipment spaces] accordance with Sections 907.2.22.1 and 907.2.22.2.

Exception: Audible appliances shall not be installed within the control tower cab.

907.2.22.1 Airport traffic control towers with multiple exits and automatic sprinklers. Airport traffic control towers with multiple exits and equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1 shall be provided with smoke detectors in all of the following locations:

1.	Airport traffic control cab.

2.	Electrical and mechanical equipment rooms.

3.	Airport terminal radar and electronics rooms.

4.	Outside each opening into interior exit stairways.

5.	Along the single means of egress permitted from observation levels.

6.	Outside each opening into the single means of egress permitted from observation levels.

907.2.22.2 Other airport traffic control towers. Airport traffic control towers with a single exit or where sprinklers are not installed throughout shall be provided with smoke detectors in all of the following locations:

1.	Airport traffic control cab.

2.	Electrical and mechanical equipment rooms.

3.	Airport terminal radar and electronics rooms.

4.	Office spaces incidental to the tower operation.

5.	Lounges for employees, including sanitary facilities.

6.	Means of egress.

7.	Accessible utility shafts.

907.2.23 Battery rooms. An approved automatic smoke detection system shall be installed in areas containing any battery systems. Where the battery room is located in a building or space that is provided with a fire alarm system or subsystem, the smoke detectors shall be connected to such building fire alarm system or subsystem.  The detection system shall be supervised by a central supervising station, or a local alarm that will sound an audible signal at a constantly attended location. Battery rooms shall also comply with the requirements of the New York City Fire Code.

907.3 Fire safety functions. Automatic fire detectors utilized for the purpose of performing fire safety functions shall be connected to the building’s fire alarm control unit where a fire alarm system is required by Section 907.2. Detectors shall, upon actuation, perform the intended function and activate the alarm notification appliances or activate a visible and audible supervisory signal at a constantly attended location.

Exception: In buildings not equipped with a fire alarm system, the automatic fire detector shall be powered by normal electrical service and, upon actuation, perform the intended function. The detectors shall be located in accordance with NFPA 72.

907.3.1 Duct smoke detectors. Smoke detectors installed in ducts shall be listed for the air velocity, temperature and humidity present in the duct. Duct smoke detectors shall be connected to the building’s fire alarm control unit when a fire alarm system is required by Section 907.2. Activation of a duct smoke detector shall initiate a visible and audible [supervisory] alarm signal at a constantly attended location and shall perform the intended fire safety function in accordance with this code and the New York City Mechanical Code. Duct smoke detectors shall not be used as a substitute for required open area detection.

Exceptions:

1.	The [supervisory] alarm signal at a constantly attended location is not required where duct smoke detectors activate the [building] building’s alarm notification appliances.

2.	In occupancies not required to be equipped with a fire alarm system, actuation of a smoke detector shall activate a visible and an audible signal in an approved location. Smoke detector trouble conditions shall activate a visible or audible signal in an approved location and shall be identified as air duct detector trouble.

907.3.2 Delayed egress locks. Where delayed egress locks are installed on means of egress doors in accordance with Section [1008.1.9.7] 1010.1.9.7, an automatic smoke or heat detection system shall be installed as required by that section.

907.3.3 Elevator emergency operation. Automatic fire detectors installed for elevator emergency operation shall be installed in accordance with the provisions of Chapter 30 of this code, ASME A17.1 and NFPA 72.

907.3.4 Wiring. The wiring to the auxiliary devices and equipment used to accomplish [the above] fire safety functions shall be monitored for integrity in accordance with NFPA 72 and the New York City Electrical Code.

907.3.5 Monitoring of hold-open devices and closers. All hold-open devices used in automatic-closing doors pursuant to the exception to Section [708.7] 713.7 shall be electrically supervised to monitor the integrity of the wiring connections among the fire alarm system, the smoke detection system, and the hold-open devices.

907.4 Initiating devices. Where manual or automatic alarm initiation is required as part of a fire alarm system, the initiating devices shall be installed in accordance with Sections 907.4.1 through [907.4.3] 907.4.4.

907.4.1 Protection of fire alarm control unit. In areas that are not continuously occupied, a single smoke detector shall be provided at the location of each fire alarm control unit, notification appliance circuit power extenders, and supervising station transmitting equipment.

Exceptions:

1.	Where ambient conditions prohibit installation of a smoke detector, a heat detector shall be permitted.

2.	In prior code buildings, where a fire alarm control unit is installed in an [exit enclosure] interior exit stairway or ramp or exit passageway, a smoke detector is not required at the location of such fire alarm control unit.

907.4.2 Manual fire alarm boxes. Where a manual fire alarm system is required by another section of this code, it shall be activated by fire alarm boxes installed in accordance with Sections 907.4.2.1 through [907.4.2.5] 907.4.2.6.

907.4.2.1 Location. Manual fire alarm boxes shall be located not more than 5 feet (1524 mm) from the entrance to each exit. Additional manual fire alarm boxes shall be located so that travel distance to the nearest box does not exceed 200 feet (60 960 mm).

907.4.2.2 Height. The height of the manual fire alarm boxes shall be [a minimum of] not less than 42 inches (1067 mm) and [a maximum of] not more than 48 inches (1219 mm) measured vertically, from the floor level to the activating handle or lever of the box.

907.4.2.3 Color. Manual fire alarm boxes shall be red in color.

907.4.2.4 Signs. Where fire alarm systems are not required to be monitored by a supervising station, an approved permanent sign that reads: WHEN ALARM SOUNDS—CALL 911 shall be installed adjacent to each manual fire alarm box.

Exception: Where the manufacturer has permanently provided this information on the manual fire alarm box.

907.4.2.5 Protective covers. The Fire Department is authorized to require the installation of listed manual fire alarm box protective covers to prevent malicious false alarms or provide the manual fire alarm box with protection from physical damage. The protective cover shall be transparent or red in color with a transparent face to permit visibility of the manual fire alarm box. Each cover shall include proper operating instructions. A protective cover that emits a local alarm signal shall not be installed unless approved. Protective covers shall not project more than that permitted by Section 1003.3.3.

907.4.2.6 Unobstructed and unobscured. Manual fire alarm boxes shall be readily accessible, unobstructed, unobscured and visible at all times.

907.4.3 Automatic smoke detection. Where an automatic smoke detection system is required, it shall utilize smoke detectors unless ambient conditions prohibit such an installation. In spaces where smoke detectors cannot be utilized due to ambient conditions, approved automatic heat detectors shall be permitted.

907.4.3.1 Automatic sprinkler system. For conditions other than specific fire safety functions noted in Section 907.3, in areas where ambient conditions prohibit the installation of smoke detectors, an automatic sprinkler system installed in such areas in accordance with Section 903.3.1.1 or 903.3.1.2 and that is connected to the fire alarm system shall be approved as automatic heat detection.

907.4.4 Fire-extinguishing systems. Where a fire alarm system is required by another section of this code or is otherwise installed, automatic fire-extinguishing systems installed in accordance with Section 904 shall be monitored by the fire alarm system.

907.5 Occupant notification systems. A fire alarm system shall annunciate at the [panel] fire alarm control unit and shall initiate occupant notification upon activation, in accordance with Sections 907.5.1 through [907.5.2.3.3] 907.5.2.3.2. Where a fire alarm system is required by another section of this code, it shall be activated by:

1.	Automatic fire detectors.

2.	[Sprinkler] Automatic sprinkler system waterflow devices.

3.	Manual fire alarm boxes.

4.	Automatic fire-extinguishing systems.

Exception: Where notification systems are allowed elsewhere in Section 907 to annunciate at a constantly attended location or to a central supervising station.

907.5.1 Presignal feature. A presignal feature shall not be installed unless approved by the Fire Department. Where a presignal feature is provided, a signal shall be annunciated at a constantly attended location approved by the Fire Department, in order that occupant notification can be activated in the event of fire or other emergency.

907.5.2 Alarm notification appliances. Alarm notification appliances shall be provided and shall be listed for their purpose.

907.5.2.1 Audible alarms. Audible alarm notification appliances shall be provided and emit a distinctive sound that is not to be used for any purpose other than that of a fire alarm.

[Exception:] Exceptions:

1.	Visible alarm notification appliances shall be allowed in lieu of audible alarm notification appliances in critical care areas of Group I-2 occupancies.

2.	Where provided, audible notification appliances located in each occupant evacuation elevator lobby in accordance with Section 3008.10.1 shall be connected to a separate notification zone for manual paging only.

907.5.2.1.1 Average sound pressure. The audible alarm notification appliances shall provide a sound pressure level of 15 decibels (dBA) above the average ambient sound level or 5 dBA above the maximum sound level having a duration of [at least] not less than 60 seconds, whichever is greater, in every occupiable space within the building. The minimum sound pressure levels shall be: 75 dBA in occupancies in Groups R and I-1; 90 dBA in mechanical equipment rooms and 60 dBA in other occupancies. For one-way voice communication system in Group R-2 occupancies, the minimum sound pressure level of the alert tone shall be 75 dBA throughout the dwelling unit.

907.5.2.1.2 Maximum sound pressure. The maximum sound pressure level for audible alarm notification appliances shall be 110 dBA at the minimum hearing distance from the audible appliance. Where the average ambient noise is greater than 95 dBA, visible alarm notification appliances shall be provided in accordance with NFPA 72 and audible alarm notification appliances shall not be required.

907.5.2.2 Emergency voice/alarm communication systems. Emergency voice/alarm communication systems required by this code shall be designed and installed in accordance with NFPA 72. The operation of any automatic fire detector, sprinkler waterflow device or manual fire alarm box shall automatically sound an alert tone followed by voice instructions giving approved information and directions for a general or staged evacuation in accordance with the building’s fire safety and evacuation plans required by the New York City Fire Code. In high-rise buildings, the system shall operate on [a minimum of] at least the alarming floor, the floor above and the floor below. Speakers shall be provided throughout the building by paging zones. At a minimum, paging zones shall be provided as follows:

1.	Each exit stairway.

2.	Each floor.

3.	Refuge areas as defined in [Section 1002.1] Chapter 2.

Exceptions:

1.	Group I-1 and I-2 occupancies. In Group I-1 and I-2 occupancies, the alarm shall sound in a constantly attended area and a general occupant notification shall be broadcast over the overhead page.

[2.	Group R-2 occupancies 125 feet or less in height. Emergency voice/alarm communication systems shall not be required in Group R-2 occupancies in buildings 125 feet (33 100 mm) or less in height.]

[3.] 2.	Group R-2 occupancies greater than [125 feet] 75 feet (22 860 mm) in height. In Group R-2 occupied buildings greater than [125 feet (33 100 mm)] 75 feet (22 860 mm) in height above the lowest level of Fire Department vehicle access, activation of any smoke detector or sprinkler water flow device shall initiate a signal at a central supervising station or constantly attended location and shall not initiate a signal to an alarm notification appliance. An emergency voice/alarm communication system shall not be required. However, a one-way voice communication shall be provided between the fire command center for use by Fire Department personnel and the following terminal areas:

[3.1.] 2.1.	Within dwelling units. An intercom system may be utilized when provided with an override feature for use by Fire Department personnel. Such intercom system shall comply with rules promulgated by the commissioner establishing installation requirements.

[3.2.] 2.2.	Within required exit stairs. Annunciation devices shall be located at least on every other story units. Such annunciation devices shall comply with rules promulgated by the commissioner establishing installation requirements.

907.5.2.2.1 Manual override. A manual override for emergency voice communication shall be provided on a selective and all-call basis for all paging zones.

907.5.2.2.2 Live voice messages. The emergency voice/alarm communication system shall have multi-channel capability to broadcast live voice messages by paging zones on a selective and all-call basis without automatic interruption of the alarm tones on the floor of incidence, floor above or floor below.

907.5.2.2.3 Alternate uses. When approved by the [fire commissioner] Fire Commissioner, the emergency voice/alarm communication system may be allowed to be used for other announcements.

907.5.2.2.4 Emergency voice/alarm communication captions. Where stadiums, arenas and grandstands provide audible public announcements, the emergency/voice alarm communication system shall be captioned. Emergency captions shall be approved by the Fire Department.

907.5.2.2.5 Emergency power. Emergency voice/alarm communications systems shall be provided with an approved emergency power source in accordance with Section 2702 of this code and the New York City Electrical Code.

907.5.2.3 Visible alarms. Visible alarm notification appliances shall be provided in accordance with Sections 907.5.2.3.1 through [907.5.2.3.3] 907.5.2.3.2.

Exceptions:

1.	Visible alarm notification appliances shall not be required in exits as defined in Chapter 2.

2.	Visible alarm notification appliances shall not be required in elevator cars.

907.5.2.3.1 Public and common areas. Visible alarm notification appliances shall be provided in public use areas and common use areas, as defined in Chapter 2.

[907.5.2.3.2 Employee work areas.] Exception: Where employee work areas have audible alarm coverage, the notification appliance circuits serving the employee work areas shall be initially designed with [a minimum of] not less than 20-percent spare capacity to account for the potential of adding visible notification appliances in the future to accommodate hearing impaired employee(s).

[907.5.2.3.3] 907.5.2.3.2 Groups I-1 and R-1. Group I-1 and R-1 dwelling units or sleeping units in accordance with Table [907.5.2.3.3] 907.5.2.3.2 shall be provided with a visible alarm notification appliance, activated by both the in-room smoke detector and the building fire alarm system.

TABLE [907.5.2.3.3] 907.5.2.3.2
VISIBLE ALARMS

| NUMBER OF UNITS | UNITS WITH VISIBLE ALARMS |
| --- | --- |
| 6 to 25 | 2 |
| 26 to 50 | 4 |
| 51 to 75 | 7 |
| 76 to 100 | 9 |
| 101 to 150 | 12 |
| 151 to 200 | 14 |
| 201 to 300 | 17 |
| 301 to 400 | 20 |
| 401 to 500 | 22 |
| 501 to 1,000 | 5% of total |
| 1,001 and over | 50 plus 3 for each 100 over 1,000 |

907.6 Installation and monitoring. A fire alarm system shall be installed and monitored in accordance with [this section] Sections 907.6.1 through 907.6.5.2 and NFPA 72 [as modified by Appendix Q].

907.6.1 Wiring. Wiring shall comply with the requirements of the New York City Electrical Code and NFPA 72 [as modified by Appendix Q]. Wireless protection systems utilizing radio-frequency transmitting devices shall comply with the special requirements for supervision of low-power wireless systems in NFPA 72[as modified by Appendix Q].

907.6.2 Power supply. The primary and secondary power supply for the fire alarm system shall be provided in accordance with the New York City Electrical Code.

Exception: Secondary power for single-station and multiple-station smoke alarms as required in Section [907.2.11.2] 907.2.11.2.

907.6.3 Zones. Each floor shall be zoned separately. For non-addressable systems, [each floor shall be zoned separately and] a zone shall not exceed 22,500 square feet (2090 m2). The length of any zone shall not exceed 300 feet (91 440 mm) in any direction.

Exception: Automatic sprinkler system zones shall not exceed the area permitted by NFPA 13.

907.6.3.1 Zoning indicator panel. A zoning indicator panel and the associated controls shall be provided at the main building entrance accessible to responding Fire Department personnel and in other locations approved by the [department] commissioner and the Fire Department. The visual zone indication shall lock in until the system is reset and shall not be canceled by the operation of an audible-alarm silencing switch.

907.6.3.2 High-rise buildings. In high-rise buildings constructed in accordance with Section 403, a separate zone by floor shall be provided for each of the following types of alarm-initiating devices where provided:

1.	Smoke detectors.

2.	Sprinkler waterflow devices.

3.	Manual fire alarm boxes.

4.	Other approved types of automatic fire detection devices or suppression systems.

907.6.4 Access. Access shall be provided to each fire alarm device and notification appliance for periodic inspection, maintenance and testing.

907.6.5 Monitoring. Fire alarm systems required by this chapter or by the New York City Fire Code shall be monitored by a central supervising station in accordance with NFPA 72 and approved by the [fire commissioner] Fire Commissioner.

Exception: Monitoring by a central supervising station is not required for:

1.	Single- and multiple-station smoke alarms required by Section 907.2.11.

2.	Smoke detectors in Group I-3 occupancies.

3.	Automatic sprinkler systems in one- and two-family dwellings.

907.6.5.1 Automatic telephone-dialing devices. Automatic telephone-dialing devices used to transmit an emergency alarm shall not be connected to any Fire Department telephone number unless approved by the Fire Commissioner.

907.6.5.2 Termination of monitoring service. Termination of fire alarm monitoring services shall be in accordance with the New York City Fire Code.

907.7 Acceptance tests and completion. Upon completion of the installation, the fire alarm system and all fire alarm components shall be tested in accordance with NFPA 72.

907.7.1 Single- and multiple-station alarm devices. When the installation of the alarm devices is complete, each device and interconnecting wiring for multiple-station alarm devices shall be tested in accordance with the smoke alarm provisions of NFPA 72.

907.7.2 Record of completion. A record of completion in accordance with NFPA 72 verifying that the system has been installed and tested in accordance with the approved construction documents and specifications shall be provided.

907.7.3 Instructions. Operating, testing and maintenance instructions, and record drawings (“as builts”) and equipment specifications shall be provided at an approved location.

907.8 Inspection, testing and maintenance. The maintenance and testing schedules and procedures for fire alarm and fire detection systems shall be in accordance with the New York City Fire Code.

SECTION BC 908
EMERGENCY ALARM SYSTEMS

908.1 Group H occupancies. Emergency alarms for the detection and notification of an emergency condition in Group H occupancies shall be provided in accordance with Section [414.7] 415.5 of this code and the New York City Fire Code.

908.2 Group H-5 occupancy. Emergency alarms for notification of an emergency condition in [an] a Hazardous Production Material (HPM) facility shall be provided as required in Section [415.8.4.6] 415.11.3.5. A continuous gas-detection system shall be provided for HPM gases in accordance with Section [415.8.7] 415.11.7 of this code and the New York City Fire Code.

908.3 Highly toxic and toxic materials. A gas detection system shall be provided to detect the presence of highly toxic or toxic gas at or below the permissible exposure limit (PEL) or ceiling limit of the gas for which detection is provided. The system shall be capable of monitoring the discharge from the treatment system at or below one-half the immediately dangerous to life and health (IDLH) limit and shall comply with the New York City Fire Code.

Exception: A gas detection system is not required for toxic gases when the physiological warning threshold level for the gas is at a level below the accepted PEL for the gas.

908.3.1 Alarms. The gas detection system shall initiate a local alarm and transmit a signal to a constantly attended control station when a short-term hazard condition is detected. The alarm shall be both visible and audible and shall provide warning both inside and outside the area where gas is detected. The audible alarm shall be distinct from all other alarms.

Exception: Signal transmission to a constantly attended control station is not required when not more than one cylinder of highly toxic or toxic gas is stored.

908.3.2 Shutoff of gas supply. The gas detection system shall automatically close the shutoff valve at the source on gas supply piping and tubing related to the system being monitored for whichever gas is detected.

Exception: Automatic shutdown is not required for reactors utilized for the production of highly toxic or toxic compressed gases where such reactors are:

1.	Operated at pressures less than 15 pounds per square inch gauge (psig) (103.4 kPa)[.];

2.	Constantly attended[.]; and

3.	Provided with readily accessible emergency shutoff valves.

908.3.3 Valve closure. The automatic closure of shutoff valves shall be in accordance with the following:

1.	When the gas-detection sampling point initiating the gas detection system alarm is within a gas cabinet or exhausted enclosure, the shutoff valve in the gas cabinet or exhausted enclosure for the specific gas detected shall automatically close.

2.	Where the gas-detection sampling point initiating the gas detection system alarm is within a gas room and compressed gas containers are not in gas cabinets or exhausted enclosures, the shutoff valves on all gas lines for the specific gas detected shall automatically close.

3.	Where the gas-detection sampling point initiating the gas detection system alarm is within a piping distribution manifold enclosure, the shutoff valve for the compressed container of specific gas detected supplying the manifold shall automatically close.

Exception: When the gas-detection sampling point initiating the gas detection system alarm is at a use location or within a gas valve enclosure of a branch line downstream of a piping distribution manifold, the shutoff valve in the gas valve enclosure for the branch line located in the piping distribution manifold enclosure shall automatically close.

908.4 Ozone gas-generator rooms. Ozone gas-generator rooms shall be equipped with a continuous gas-detection system that will shut off the generator and sound a local alarm when concentrations above the PEL occur and shall comply with the New York City Fire Code.

908.5 Repair garages. A flammable-gas detection system shall be provided in repair garages for vehicles fueled by enumerated gases in accordance with Section [406.6.6] 406.8.5 of this code and the New York City Fire Code.

908.6 Refrigerant [detector] detectors. Machinery rooms shall contain [a] refrigerant [detector] detectors with [an] audible and visual [alarm] alarms. The [detector] detectors, or [a] sampling [tube] tubes that [draws] draw air to [the] each detector, shall be located in [an] all [area] areas where refrigerant from a leak will concentrate. The alarm shall be actuated at a value not greater than the corresponding TLV-TWA values for the refrigerant classification indicated in the New York City Mechanical Code. Detectors and alarms shall be placed in approved locations. Refrigerant detectors shall initiate all functions as required by the New York City Mechanical Code and New York City Fire Code.

[908.7 Carbon monoxide alarms and detectors. Carbon monoxide alarms and detectors shall be provided and installed in accordance with Sections 908.7.1 through 908.7.4.]

[908.7.1 Group I-1 and R occupancies. Listed carbon monoxide alarms or detectors shall be installed as follows:]

[1.	Group R-1 and Group R-2 where the main use or dominant occupancy of a building is classified as Group R-2 student apartments. Carbon monoxide detectors and audible notification appliances shall be installed in affected dwelling units as per Section 908.7.1.1 and shall be annunciated by dwelling unit at a constantly attended location from which the fire alarm system is capable of being manually activated.]

[2.	Groups I-1, R-2 (other than occupancies covered by Item 1) and R-3. Carbon monoxide alarms shall be installed in affected dwelling units as per Section 908.7.1.1.]

[908.7.1.1 Affected dwelling units. Carbon monoxide alarms or detectors shall be required within the following dwelling units:]

[1.	Units on the same story where carbon monoxide- producing equipment or enclosed parking is located.]

[2.	Units on the stories immediately above and below the floor where carbon monoxide-producing equipment or enclosed parking is located.]

[3.	Units in a building containing a carbon monoxide-producing furnace, boiler, or water heater as part of a central system.]

[4.	Units in a building served by a carbon monoxide- producing furnace, boiler, or water heater as part of a central system that is located in an adjoining or attached building.]

[908.7.1.1.1 Required locations within dwelling units. Carbon monoxide alarms or detectors shall be located within dwelling units as follows:]

[1.	Outside of any room used for sleeping purposes, within 15 feet (4572 mm) of the entrance to such room.]

[2.	In any room used for sleeping purposes.]

[3.	On any story within a dwelling unit, including below-grade stories and penthouses of any area, but not including crawl spaces and uninhabitable attics.]

[908.7.1.1.2 Installation requirements. Carbon monoxide alarms or detectors shall comply with the power source, interconnection, and acceptance testing requirements as required for smoke alarms in accordance with Sections 907.2.11.2 through 907.2.11.3.]

[908.7.1.1.3 Exhaust of Carbon Monoxide in Group R-3 Occupancy (One- and Two-Family dwellings and townhouses). Means of exhausting carbon monoxide from garages shall be provided when a carbon monoxide alarm or detector is activated in a Group R-3 occupancy, provided such garage is attached within the Group R-3 occupancy. Such exhaust system shall be arranged to operate automatically upon detection of a concentration of carbon monoxide of 35 parts per million (ppm) or greater by approved automatic detection device. The system shall be capable of producing an exhaust rate of 1.5 cfm per square foot of floor area of the garage. Removal of sensor, interruption of power or cut wires shall cause the relay circuit to open and start fan. The relay contact shall close and the fan may shut off when the carbon monoxide level is below 35 ppm. Carbon monoxide exhausting means shall be connected to a separate circuit and provided with a lock and identified at the power source. Such circuit shall not be connected to a power source through an arc-fault or Ground Fault Circuit Interrupter (GFCI) devices. Additionally, when the carbon monoxide exhausting means is connected to the plug-in-type overcurrent protection device, such device shall be secured in place by an additional fastener.]

[908.7.2 Group E, I-2 and I-4 occupancies. Listed carbon monoxide detectors with built-in sounder bases shall be transmit a signal to a central supervising station and shall be permitted to initiate an audible and visual supervisory alarm at a constantly attended location.]

[1.	Carbon monoxide detectors with built-in sounder bases shall be installed within any room containing carbon monoxide-producing equipment.]

Exception: Kitchens or laboratories.]

[2.	Carbon monoxide detectors with built-in sounder bases shall be installed in corridors on the story where carbon monoxide-producing equipment unit is located, as well as one story above and one story below.]

[3.	Carbon monoxide detectors with built-in sounder bases shall be installed in all corridors on the story where enclosed parking is located, as well as one story above and one story below.]

[908.7.3 Buildings that are equipped with a fire alarm system and that contain Group A-1, A-2, A-3, Group B or Group M occupancies.  Listed carbon monoxide detectors shall be installed in buildings that are equipped with a fire alarm system and that contain Group A-1, A-2 or A-3, Group B or Group M occupancies.  Such carbon monoxide detectors installed pursuant to this section shall have built-in sounder bases, shall transmit a signal to a central supervising station and shall be permitted to initiate an audible and visual supervisory alarm at a constantly attended location.  The department shall adopt rules and/or reference standards (i) governing the installation and location of carbon monoxide detectors provided such detectors shall be required within rooms containing carbon-monoxide producing equipment and (ii) addressing the installation of such detectors or any alternative means of compliance in existing buildings.]

[Exception: Carbon monoxide detectors shall not be required in kitchens.]

[908.7.3.1 Retroactive provisions for existing buildings. Notwithstanding any other provision of law, listed carbon monoxide detectors shall be installed in existing buildings that are equipped with a fire alarm system and that contain group A-1, A-2, A-3, Group B or Group M occupancies in accordance with Section 908.7.3 by January 1, 2021.]

[908.7.4 Installation. Carbon monoxide alarms and detectors shall be listed in accordance with UL 2034 and UL 2075.]

908.7 Carbon dioxide (CO2) systems. The emergency alarm system for a carbon dioxide system, including detection, pre-discharge and discharge alarms, shall be provided in accordance with the New York City Fire Code.

908.8 Gas detection systems. Gas detection systems shall be provided in accordance with Section 918.

[908.8] 908.9 Medical gas. Medical gas pressure monitoring and alarm systems shall be provided in accordance with NFPA 99[and NFPA 99C].

[908.9] 908.10 Flammable gas. Rooms and spaces containing flammable gas distribution piping operating at levels above 15 pounds per square inch gauge (psig) (103.4 kPa) shall be provided with an approved flammable gas detection-alarm system and shall comply with the New York City Fire Code.

[908.10] 908.11 Construction documents. Construction documents for emergency alarm systems shall be submitted for review and approval to the Fire Department prior to system installation.

[908.11] 908.12 Acceptance testing and maintenance. Acceptance testing and maintenance of emergency alarm systems shall be performed in accordance with the New York City Fire Code.

SECTION BC 909
SMOKE CONTROL SYSTEMS

909.1 Scope and purpose. This section applies to mechanical or passive smoke control systems [when] where they are required by other provisions of this code. A smoke control system [is a life safety system, and], where required, facilitates the evacuation of the occupants.  The purpose of this section is to establish minimum requirements for the design, installation and acceptance testing of smoke control systems that are intended to provide a tenable environment for the evacuation or relocation of occupants. These provisions are not intended for the preservation of contents, the timely restoration of operations or for assistance in fire suppression or post-fire smoke purge. Smoke control systems regulated by this section serve a different purpose than the smoke- and heat-venting provisions found in Section 910. Mechanical smoke control systems shall not be considered exhaust systems under Chapter 5 of the New York City Mechanical Code.

909.1.1 Definitions. The following [words and] terms [shall, for the purposes of this section and as used elsewhere in this code, have the meaning shown herein.] are defined in Chapter 2:

ELEVATOR LANDING.

PRESSURIZATION. [Creation and maintenance of pressure levels in zones of a building, including elevator shafts and stairwells, that are higher than the pressure level at the smoke source, such pressure levels being produced by positive pressures of a supply of uncontaminated air; by exhausting air and smoke at the smoke source; or by a combination of these methods.]

SMOKE. [Air-borne solid and liquid particulates and gases evolved when a material undergoes pyrolysis or combustion, including the quality of air that is entrained or otherwise mixed into the mass.]

SMOKE BARRIER. [See Section 702.1.]

SMOKE CONTROL MODE. [A predefined operational configuration of a system or device for the purpose of smoke control.]

SMOKE CONTROL SYSTEM, MECHANICAL. [An engineered system that uses mechanical fans to produce pressure differences across smoke barriers or that establishes airflows to limit and direct smoke movement.]

SMOKE CONTROL SYSTEM, PASSIVE. [A system of smoke barriers arranged to limit the migration of smoke.]

SMOKE CONTROL ZONE. [A space within a building enclosed by smoke barriers.]

SMOKE DAMPER. [See Section 702.1.]

STACK EFFECT. [Vertical airflow within buildings caused by temperature differences.]

TENABLE ENVIRONMENT. [An environment in which the concentration and location of smoke is limited or otherwise restricted to allow for ready evacuation through the space.]

909.2 General design requirements. Buildings, structures or parts thereof required by this code to have a smoke control system or systems shall have such systems designed in accordance with the applicable requirements of Section 909 and the generally accepted and well-established principles of engineering relevant to the design. The construction documents shall include sufficient information and detail to adequately describe the elements of the design necessary for the proper implementation of the smoke control systems. These documents shall be accompanied by sufficient information and analysis to demonstrate compliance with these provisions.

909.3 Special inspection and test requirements. In addition to the ordinary inspection and test requirements that buildings, structures and parts thereof are required to undergo, smoke control systems subject to the provisions of Section 909 shall undergo special inspections and tests sufficient to verify the proper commissioning of the smoke control design in its final installed condition. The design submission accompanying the construction documents shall clearly detail procedures and methods to be used and the devices, flow measurement, and other items subject to such inspections and tests. Such commissioning shall be in accordance with generally accepted engineering practice and, where possible, based on published standards for the particular testing involved. The special inspections and tests required by this section shall be conducted under the same terms in Section [1704] 1705. [A record] Records of the special inspection, including device locations, duct air leakage, pressure [differences,] differentials, air/smoke flow measurements, smoke detection and control verification shall be maintained on the premises as a baseline against which future tests can be compared.

909.3.1 Periodic testing. Smoke control systems shall be verified weekly through the automatic control system in accordance with Section 909.12 and shall be tested annually to ensure proper operation of detection devices, dampers, fans and controls in accordance with the requirements of Sections 909.18.1, 909.18.3, 909.18.5 and 909.18.7. Full testing of smoke control systems in accordance with Sections 909.18 through 909.18.7 shall be conducted at 5-year intervals by an inspector qualified in accordance with Section 909.18.8.2. Test reports shall include all information required by Section 909.18.8.3 and shall be compared against the baseline special inspection report. Causes for any significant deviations from the baseline report shall be identified and corrected. A record of each inspection and test shall be maintained on the premises by the owner or lessee, and the records for at least the last 5 years of operation shall be made available for inspection by the department and the [fire commissioner] Fire Commissioner.

909.4 Analysis. A rational analysis supporting the types of smoke control systems to be employed, their methods of operation, the systems supporting them and the methods of construction to be utilized shall accompany the submitted construction documents and shall include, but not be limited to, the items indicated in Sections 909.4.1 through [909.4.6] 909.4.7. The basis of design and design analysis of the smoke control system shall be submitted to the department and the Fire Department.

909.4.1 Stack effect. The system shall be designed such that the maximum probable normal or reverse stack effect will not adversely interfere with the system’s capabilities. In determining the maximum probable stack effect, altitude, elevation, weather history and interior temperatures shall be used.

909.4.2 Temperature effect of fire. Buoyancy and expansion caused by the design fire in accordance with Section 909.9 shall be analyzed. The system shall be designed such that these effects do not adversely interfere with the system’s capabilities.

909.4.3 Wind effect. The design shall consider the adverse effects of wind. Such consideration shall be consistent with the wind-loading provisions of Chapter 16.

909.4.4 HVAC systems. The design shall consider the effects of the heating, ventilating and air-conditioning (HVAC) systems on both smoke and fire transport. The analysis shall include all permutations of systems’ status. The design shall consider the effects of the fire on the HVAC systems.

909.4.5 Climate. The design shall consider the effects of low temperatures on systems, property and occupants. Air inlets and exhausts shall be located so as to prevent snow or ice blockage.

909.4.6 Duration of operation. All portions of active or passive smoke control systems shall be capable of continued operation after detection of the fire event for a period of not less than either 20 minutes or 1.5 times the [calculated] required safe egress time, whichever is [more] greater.

909.4.7 Smoke control system interaction. The design shall consider the interaction effects of the operation of multiple smoke control systems for all design scenarios.

909.5 Smoke barrier construction. Smoke barriers required for passive smoke control and a smoke control system using the pressurization method shall comply with Section [710, and] 709. Smoke barriers shall be constructed and sealed to limit leakage areas exclusive of protected openings. The maximum allowable leakage area shall be the aggregate area calculated using the following leakage area ratios:

1.	Walls: A/AW = 0.00100

2.	[Exit enclosures] Interior exit stairways and ramps and exit passageways:

A/Aw  = 0.00035

3.	[All] Enclosed exit access stairways and ramps and all other shafts:

A/Aw= 0.00150

4.	Floors and roofs: A/AF = 0.00050

where:

A = [Total] Maximum allowable leakage area, square feet (m2).

AF = Unit floor or roof area of barrier, square feet (m2).

Aw = Unit wall area of barrier, square feet (m2).

The leakage area ratios shown do not include openings due to gaps around doors[,] and operable windows [or similar gaps. These] The total leakage area of the smoke barrier shall be [included in calculating the total leakage area] determined in accordance with Section 909.5.1 and tested in accordance with Section 909.5.2.

909.5.1 [Leakage] Total leakage area. [The total] Total leakage area of the barrier is the product of the smoke barrier gross area multiplied by the allowable leakage area ratio, plus the area of other openings such as gaps around doors and operable windows.[Compliance shall be determined by achieving the minimum air pressure difference across the barrier with the system in the smoke control mode for mechanical smoke control systems. Passive smoke control systems tested using other approved means such as door fan testing shall be approved by the department and the fire commissioner.]

909.5.2 [Opening protection.] Testing of leakage area. Compliance with the maximum allowable leakage area shall be determined by achieving the minimum air pressure difference across the barrier with the system in the smoke control mode for mechanical smoke control systems utilizing the pressurization method. Compliance with the maximum allowable leakage area of passive smoke control systems shall be verified through methods such as door fan testing or other methods, as approved by the commissioner and the Fire Commissioner.

909.5.3 Opening protection. Openings in smoke barriers shall be protected by automatic-closing devices actuated by the required controls for the mechanical smoke control system. Door openings shall be protected by fire door assemblies complying with Section [715.4.3] 716.5.3.

Exceptions:

1.	Passive smoke control systems with automatic-closing devices actuated by spot-type smoke detectors listed for releasing service installed in accordance with Section 907.3.

2.	Fixed openings between smoke zones that are protected utilizing the airflow method.

3.	In Group I-1, Group I-2, and Group B ambulatory care facilities, where [such doors are installed across corridors,] a pair of opposite-swinging doors [without a center mullion shall be installed having vision panels with approved fire-protection-rated glazing materials in approved fire-protection-rated frames] are installed across a corridor in accordance with Section 909.5.3.1, the [area of which] doors shall not [exceed that tested] be required to be protected in accordance with Section 716. The doors shall be [close fitting] close-fitting within operational tolerances and shall not have a center mullion, louvers, grilles, or door undercuts[, louvers or grilles] in excess of ¾ inch (19.1 mm). The doors shall have head and jamb stops[,] and astragals or rabbets at meeting edges [, and shall be automatic-closing by smoke detection in accordance with Section 715.4.8.3. Positive-latching devices are not required]. If allowed by the door manufacturer’s listing, positive-latching devices are not required.

4.	In Group I-1, Group I-2 and Group B ambulatory care facilities, where such doors are special-purpose horizontal sliding, accordion or folding door assemblies installed in accordance with Section 1010.1.4.3 and are automatic closing by smoke detection in accordance with Section 716.5.9.3.

[4.] 5.	Group I-3.

[5.] 6.	Openings between smoke zones with clear ceiling heights of 14 feet (4267 mm) or greater and bank-down capacity of greater than 20 minutes as determined by the design fire size.

909.5.3.1 Group I-2 and Group B ambulatory care facilities. In Group I-2 and Group B ambulatory care facilities, where doors are installed across a corridor, the doors shall be automatic closing by smoke detection in accordance with Section 716.5.9.3 and shall have a vision panel with fire protection-rated glazing materials in fire protection-rated frames, the area of which shall not exceed that tested.

[909.5.2.1] 909.5.3.2 Ducts and air transfer openings. Ducts and air transfer openings are required to be protected with a minimum Class II, 250°F (121°C) smoke damper complying with Section [716] 717.

909.6 Pressurization method. The primary mechanical means of controlling smoke shall be by pressure differences across smoke barriers. Maintenance of a tenable environment is not required in the smoke control zone of fire origin.

909.6.1 Minimum pressure difference. The minimum pressure difference across a smoke barrier shall be 0.05-inch water [gage] gauge (0.0124 kPa) in fully sprinklered buildings. In buildings permitted to be other than fully sprinklered, the smoke control system shall be designed to achieve pressure differences [at least] not less than two times the maximum calculated pressure difference produced by the design fire [, but in no case less than the values indicated in Table 909.6.1:].

| [TABLE 909.6.1] [MINIMUM PRESSURE DIFFERENCES] [ACROSS SMOKE BARRIERS] |
| --- |
| [CEILING HEIGHT] | [MINIMUM DESIGN] [PRESSURE DIFFERENCE] |
| [Less than 15 feet (4572 mm)] | [0.10-inch water gage (0.0259 kPa)] |
| [Equal to or greater than 15 feet (4572 mm), but less than 21 feet (6401 mm)] | [0.14-inch water gage (0.0349 kPa)] |
| [Equal to or greater than 21 feet (6401 mm)] | [0.18-inch water gage (0.0448 kPa)] |

909.6.2 Maximum pressure difference. The maximum air pressure difference across a smoke barrier shall be determined by required door-opening or closing forces. The actual force required to open exit doors when the system is in the smoke control mode shall be in accordance with Section [1008.1.3] 1010.1.3. Opening and closing forces for other doors shall be determined by standard engineering methods for the resolution of forces and reactions. The calculated force to set a side-hinged, swinging door in motion shall be determined by:

(Equation 9-1)

where:

Door area, square feet (m2).

Distance from door handle to latch edge of door, feet (m).

Total door opening force, pounds (N).

Force required to overcome closing device, pounds (N).

Coefficient 5.2 (1.0).

Door width, feet (m).

Design pressure difference, inches of water (Pa).

909.6.3 Pressurized stairways and elevator hoistways. Where stairways or elevator hoistways are pressurized, such pressurization systems shall comply with Section 909 of this code as smoke control systems, in addition to the requirements of Sections 909.20 and 909.21 of this code and the New York City Fire Code.

909.7 Air flow design method. [When] Where approved by the [department] commissioner, smoke migration through openings fixed in a permanently open position, which are located between smoke control zones by the use of the airflow method, shall be permitted. The design air flow shall be in accordance with this section. Air flow shall be directed to limit smoke migration from the fire zone. The geometry of openings shall be considered to prevent flow reversal from turbulent effects. Smoke control systems using the airflow method shall be designed in accordance with NFPA 92.

909.7.1 [Velocity. The minimum average velocity through a fixed opening shall not be less than:]

[	(Equation 9-2)]

[]

[where:]

[	Height of opening, feet (m).]

[	Temperature of smoke, °F (°K).]

[	Temperature of ambient air, °F (°K).]

Air velocity, feet per minute (m/minute).]

[909.7.2] Prohibited conditions. This method shall not be employed where either the quantity of air or the velocity of the airflow will adversely affect other portions of the smoke control system, unduly intensify the fire, disrupt plume dynamics or interfere with exiting. In no case shall airflow toward the fire exceed 200 feet per minute (1.02 m/s). Where the [formula in Section 909.7.1 requires] calculated airflow [to exceed] exceeds this limit, the airflow method shall not be used.

909.8 Exhaust method. [When] Where approved by the [department] commissioner, mechanical smoke control for large enclosed volumes, such as in atriums or malls, shall be permitted to utilize the exhaust method. [The design] Smoke control systems using the exhaust [volumes] method shall be designed in accordance with NFPA [92B] 92.

909.8.1 Smoke layer. The height of the lowest horizontal surface of the accumulating smoke layer shall be maintained [at least] not less than 6 feet (1829 mm) above any walking surface that forms a portion of a required egress system within the smoke zone.

909.9 Design fire. The design fire shall be based on a [Q of not less than 5,000 Btu/s (5275 kW) unless a] rational analysis performed by the registered design professional and approved by the [department] commissioner. The design fire shall be based on the analysis in accordance with Section 909.4 and this section.

909.9.1 Factors considered. The engineering analysis shall include the characteristics of the fuel, fuel load, effects included by the fire and whether the fire is likely to be steady or unsteady.

909.9.2 [Separation distance.] Design fire fuel. Determination of the design fire shall include consideration of the type of fuel, fuel spacing and configuration.

909.9.3 Heat-release assumptions. The analysis shall make use of best available data from approved sources and shall not be based on excessively stringent limitations of combustible material.

909.9.4 Sprinkler effectiveness assumptions. A documented engineering analysis shall be provided for conditions that assume fire growth is halted at the time of sprinkler activation.

909.10 Equipment. Equipment including, but not limited to, fans, ducts, automatic dampers and balance dampers, shall be suitable for its intended use, suitable for the probable exposure temperatures that the rational analysis indicates[,] and as approved by the [department] commissioner.

909.10.1 Exhaust fans. Components of exhaust fans shall be rated and certified by the manufacturer for the probable temperature rise to which the components will be exposed. This temperature rise shall be computed [by:] in accordance with NFPA 92.

[Exception: Reduced Ts as calculated based on the assurance of adequate dilution air.]

]	[(Equation 9-3)]

[where:]

Specific heat of smoke at smoke layer temperature, Btu/lb°F (kJ/kg • K).]

Exhaust rate, pounds per second (kg/s).]

[	Convective heat output of fire, Btu/s (kW).]

[	Ambient temperature, °F (°K).]

[	Smoke temperature, °F (°K).]

909.10.2 Ducts. Duct materials and joints shall be capable of withstanding the probable temperatures and pressures to which they are exposed as determined in accordance with Section 909.10.1. Ducts shall be constructed and supported in accordance with the New York City Mechanical Code. Ducts shall be leak tested to 1.5 times the maximum design pressure in accordance with nationally accepted practices. Measured leakage shall not exceed 5 percent of design flow. Results of such testing shall be a part of the documentation procedure. Ducts shall be supported directly from fire-resistance-rated structural elements of the building by substantial, noncombustible supports.

Exception: Flexible connections, [(] for the purpose of vibration isolation[)], complying with the New York City Mechanical Code[,] and that are constructed of approved fire-resistance-rated materials.

909.10.3 Equipment, inlets and outlets. Equipment shall be located so as not to expose uninvolved portions of the building to an additional fire hazard. Outside air inlets shall be located so as to minimize the potential for introducing smoke or flame into the building. Exhaust outlets shall be located so as to minimize reintroduction of smoke into the building and to limit exposure of the building or adjacent buildings to an additional fire hazard.

909.10.4 Automatic dampers. Automatic dampers, regardless of the purpose for which they are installed within the smoke control system, shall [be listed for their use] comply with Section 717.3.1.

909.10.5 Fans. In addition to other requirements, belt-driven fans shall have 1.5 times the number of belts required for the design duty[, but not less than] with the minimum number of belts being two. Fans shall be selected for stable performance based on normal temperature and, where applicable, elevated temperature. Calculations and manufacturer’s fan curves shall be part of the documentation procedures. Fans shall be supported and restrained by noncombustible devices in accordance with the requirements of Chapter 16. Motors driving fans shall not be operated beyond their nameplate horsepower (kilowatts), as determined from measurement of actual current draw, and shall have a minimum service factor of 1.15.

909.10.6 Seismic Requirements. Smoke control systems covered by Section 909 [are life safety systems and] are required to function after an earthquake. Such smoke control systems shall be seismically designed in accordance with Section 1613 and ASCE 7 [-10]. The component importance factor, Ip, shall be taken as 1.5 in accordance with ASCE 7 [-10], Section 13.1.3. The smoke control system includes all components required for its operation, including but not limited to fans, ducts, electrical power, switchboards, motor control centers, starters, and controls.

Exception: Smoke control systems in structures classified in Seismic Design Categories A or B shall have a component importance factor, Ip, of 1.0.

909.11 [Power systems] Standby power. The smoke control system shall be supplied with two sources of power. [Primary power] The primary power supply shall be from the normal building power systems [. Secondary power], while the secondary power source shall be from a standby [source] power system complying with Section [2702.1] 2702.

909.11.1 Equipment room. The standby power source shall be located in a room separate from the normal power transformers and switch gears, and ventilated directly to and from the exterior. The room shall be enclosed with not less than 2-hour fire barriers constructed in accordance with Section 707, or with not less than 2-hour fire-resistance-rated horizontal assemblies constructed in accordance with Section 711, or both.

909.11.2 Power sources and power surges. Elements of the smoke [management] control system relying on electronic volatile memories or similar systems shall be supplied with uninterruptable power sources of sufficient duration to span a 15-minute primary power interruption. Elements of the smoke [management] control system susceptible to power surges shall be suitably protected by conditioners, suppressors or other approved means.

909.12 Detection and control systems. Fire detection systems providing control input or output signals to mechanical smoke control systems or elements thereof shall comply with the requirements of Section 907. Such systems shall be equipped with a control unit complying with UL 864 and listed as smoke control equipment.

909.12.1 Verification. Control systems for mechanical smoke control systems shall include provisions for verification. Verification shall include positive confirmation of actuation, testing, manual override[,] and the presence of power downstream of all disconnects [and, through a]. A preprogrammed weekly test sequence shall report, abnormal conditions audibly, visually and by printed report. The preprogrammed weekly test shall operate all devices, equipment and components used for smoke control.

Exception: Where verification of individual components tested through the preprogrammed weekly testing sequence will interfere with, and produce unwanted effects to, normal building operation, such individual components are permitted to be bypassed from the preprogrammed weekly testing, where approved by the Fire Department and in accordance with both of the following:

1.	Where the operation of components is bypassed from the preprogrammed weekly test, presence of power downstream of all disconnects shall be verified weekly by a listed control unit.

2.	Testing of all components bypassed from the preprogrammed weekly test shall be tested semi-annually, and be tested under standby power conditions in accordance with Section 909 of the New York City Fire Code.

[909.12.1] 909.12.2 Wiring. In addition to meeting requirements of the New York City Electrical Code, all wiring, regardless of voltage, shall be fully enclosed within continuous raceways.

[909.12.2] 909.12.3 Activation. Smoke control systems shall be activated in accordance with this section.

[909.12.2.1] 909.12.3.1 Pressurization, airflow or exhaust method. Mechanical smoke control systems using the pressurization, airflow or exhaust method shall have completely automatic control.

[909.12.2.2] 909.12.3.2 Passive method. Passive smoke control systems actuated by spot-type detectors listed for releasing service shall be permitted.

[909.12.3] 909.12.4 Automatic control. Where completely automatic control is required or used, the automatic-control sequences shall be initiated from an appropriately zoned automatic sprinkler system complying with Section 903.3.1.1, manual controls that are readily accessible to the Fire Department and any smoke detectors required by engineering analysis. See Section 909.16 for manual control requirements.

[909.12.3.1] 909.12.4.1 Building Management System. Automatic and manual operation of the smoke control system may alternately be done through a Building Management System (BMS) that is approved by the Fire Department and meets the following requirements [and is approved by the Fire Department]:

1.	The BMS system shall be listed for UL 864 UUKL Smoke Control.

2.	The BMS Control Center shall be staffed 24 hours a day by operators trained in the building’s smoke control systems and their operation. [In buildings where Fire Safety Directors are required, they shall operate the] The smoke control system shall be operated by a certificate of fitness holder where required by the New York City Fire Code.

3.	The control room shall be 2-hour fire-resistance-rated construction.

4.	BMS annunciation and additional control station locations shall be located in the fire command center in accordance with Section 909.16.

909.13 Control air tubing. Control air tubing shall be of sufficient size to meet the required response times. Tubing shall be flushed clean and dry prior to final connections and shall be adequately supported and protected from damage. Tubing passing through concrete or masonry shall be sleeved and protected from abrasion and electrolytic action.

909.13.1 Materials. Control air tubing shall be hard drawn copper, Type L, ACR in accordance with ASTM B 42, ASTM B 43, ASTM B 68, ASTM B 88, ASTM B 251 and ASTM B 280. Fittings shall be wrought copper or brass, solder type, in accordance with ASME B 16.18 or ASME B16.22. Changes in direction shall be made with appropriate tool bends. Brass compression-type fittings shall be used at final connection to devices; other joints shall be brazed using a BCuP-5 brazing alloy with solidus above 1,100°F (593°C) and liquids below 1,500°F (816°C). Brazing flux shall be used on copper-to-brass joints only.

Exception: Nonmetallic tubing used within control panels and at the final connection to devices[, providing] provided all of the following conditions are met:

1.	Tubing shall [be listed by an approved agency for flame and smoke characteristics] comply with the optical density, flame spread, and the listing & labeling requirements of Section 602.2.1.3 of the New York City Mechanical Code.

2.	Tubing and connected devices shall be completely enclosed within a galvanized or paint-grade steel enclosure having a minimum thickness of 0.0296 inch (0.7534 mm) (No. 22 gage). Entry to the enclosure shall be by copper tubing with a protective grommet of neoprene or [teflon] Teflon or by suitable brass compression to male-barbed adapter.

3.	Tubing shall be identified by appropriately documented coding.

4.	Tubing shall be neatly tied and supported within the enclosure. Tubing bridging [cabinet] cabinets and [door] doors or moveable [device] devices shall be of sufficient length to avoid tension and excessive stress. Tubing shall be protected against abrasion. Tubing serving devices on doors shall be fastened along hinges.

909.13.2 Isolation from other functions. Control tubing serving other than smoke control functions shall be isolated by automatic isolation valves or shall be an independent system.

909.13.3 Testing. Control air tubing shall be tested at three times the operating pressure for not less than 30 minutes without any noticeable loss in gauge pressure prior to final connection to devices.

909.14 Marking and identification. The detection and control systems shall be clearly marked at all junctions, accesses and terminations.

909.15 Control diagrams. Identical control diagrams showing all devices in the system and identifying their location and function shall be maintained current and kept on file with the department, the Fire Department and in the fire command center in a format and manner approved by the Fire Commissioner.

909.16 [Fire-fighter’s] Firefighter’s smoke control panel. A [fire-fighter’s] firefighter’s smoke control panel for Fire Department emergency response purposes only shall be provided and shall include manual control or override of automatic control for mechanical smoke control systems. The panel shall be located in a fire command center complying with Section 911 in high-rise buildings or buildings with smoke-protected assembly seating. In all other buildings, the [fire-fighter’s] firefighter’s smoke control panel shall be installed in the ground floor lobby of the building, adjacent to the fire alarm control panel or remote annunciator, or in another approved location. The firefighter’s smoke control panel shall either be a separate panel or can be integrated with a UUKL listed fire alarm control panel. The [fire-fighter’s] firefighter’s smoke control panel shall comply with Sections 909.16.1 through 909.16.3 [, and NFPA 72 Annex E, Fire Service Annunciator and Interface]. Where required in Section [916] 917, the post-fire smoke purge system shall be manually activated from the [fire-fighter’s] firefighter’s control panel or an adjacent panel.

909.16.1 Panel indicators.  Fans within the building shall be shown on the [fire-fighter’s] firefighter’s control panel. A clear indication of the direction of airflow and the relationship of components shall be displayed. Status indicators shall be provided for all smoke control equipment, annunciated by fan and zone, and by pilot-lamp-type indicators as follows:

1.	Fans, dampers and other operating equipment in their normal status—WHITE.

2.	Fans, dampers and other operating equipment in their [off] on or [closed] open status— [RED] GREEN.

3.	Fans, dampers and other operating equipment in [their on or open] a fault status— [GREEN] YELLOW/AMBER.

4.	Fans, dampers and other operating equipment in [a fault] their off or closed status—[YELLOW/AMBER] RED.

The indicators shall be provided in the following order: WHITE, GREEN, YELLOW/AMBER then RED.

909.16.2 Panel controls. The [fire-fighter’s] firefighter’s control panel shall provide control capability over the complete [smoke-control] smoke control system equipment within the building as follows:

1.	ON-AUTO-OFF control over each individual piece of operating smoke control equipment that can also be controlled from other sources within the building. This includes stairway pressurization fans; smoke exhaust fans; supply, return and exhaust fans; elevator shaft fans and other operating equipment used or intended for smoke control purposes.

2.	OPEN-AUTO-CLOSE control over [individual] dampers relating to smoke control and that are also controlled from other sources within the building. Dampers are permitted to be controlled by individual damper or grouped by smoke zone.

3.	ON-OFF or OPEN-CLOSE control over smoke control and other critical equipment associated with a fire or smoke emergency and that can only be controlled from the [fire-fighter’s] firefighter’s control panel. The [fire-fighter’s] firefighter’s control panel shall be configured as described in Section 911.

Exceptions:

1.	[Complex systems] Systems, where approved by the commissioner and the Fire Department, where the controls and indicators are combined to control and indicate all elements of a single smoke zone as a unit.

2.	[Complex systems] Systems, where approved by the commissioner and the Fire Department, where the control is accomplished by computer interface using approved, plain English commands.

909.16.3 Control action and priorities. The [fire-fighter’s] firefighter’s control panel actions shall be as follows:

1.	ON-OFF[,] and OPEN-CLOSE control actions shall have the highest priority of any control point within the building. Once issued from the [fire-fighter’s] firefighter’s control panel, [no] automatic or manual control from any other control point within the building shall not contradict the control action. Where automatic means are provided to interrupt normal, nonemergency equipment operation or produce a specific result to safeguard the building or equipment [(i.e.,] including, but not limited to, duct freezestats, duct smoke detectors, high-temperature cutouts, temperature-actuated linkage and similar devices[)], such means shall be capable of being overridden by the [fire-fighter’s] firefighter’s control panel. The last control action as indicated by each [fire-fighter’s] firefighter’s control panel switch position shall prevail. [In no case shall control] Control actions shall not require the smoke control system to assume more than one configuration at any one time.

Exception: Power disconnects required by the New York City Electrical Code.

2.	Only the AUTO position of each three-position [fire-fighter’s] firefighter’s control panel switch shall allow automatic or manual control action from other control points within the building. The AUTO position shall be the NORMAL, nonemergency, building control position. Where a [fire-fighter’s] firefighter’s control panel is in the AUTO position, the actual status of the device (on, off, open, closed) shall continue to be indicated by the status indicator described [above. When] in Section 909.16.1. Where directed by an automatic signal to assume an emergency condition, the NORMAL position shall become the emergency condition for that device or group of devices within the zone. [In no case shall control] Control actions shall not require the smoke control system to assume more than one configuration at any one time.

909.17 System response time. Smoke-control system activation shall be initiated immediately after receipt of an appropriate automatic or manual activation command. Smoke control systems shall activate individual components (such as dampers and fans) in the sequence necessary to prevent physical damage to the fans, dampers, ducts and other equipment. For purposes of smoke control, the [fire-fighter’s] firefighter’s control panel response time shall be the same for automatic or manual smoke control action initiated from any other building control point. The total response time, including that necessary for detection, shutdown of operating equipment and smoke control system startup, shall allow for full operational mode to be achieved before the conditions in the space exceed the design smoke condition. The system response time for each component and their sequential relationships shall be detailed in the required rational analysis and verification of their installed condition reported in the required final report.

909.18 Acceptance testing. Devices, equipment, components and sequences shall be individually tested. These tests, in addition to those required by other provisions of this code, shall consist of determination of function, sequence and, where applicable, capacity of their installed condition.

909.18.1 Detection devices. Smoke or fire detectors that are a part of a smoke control system shall be tested in accordance with Chapter 9 in their installed condition. [When] Where applicable, this testing shall include verification of airflow in both minimum and maximum conditions.

909.18.2 Ducts. Ducts that are part of a smoke control system shall be traversed using generally accepted practices to determine actual air quantities.

909.18.3 Dampers. Dampers shall be tested for function in their installed condition.

909.18.4 Inlets and outlets. Inlets and outlets shall be read using generally accepted practices to determine air quantities.

909.18.5 Fans. Fans shall be examined for correct rotation. Measurements of voltage, amperage, revolutions per minute (rpm) and belt tension shall be made.

909.18.6 Smoke barriers. Measurements using inclined manometers or other approved calibrated measuring devices shall be made of the pressure differences across smoke barriers. Such measurements shall be conducted for each possible smoke control condition.

909.18.7 Controls. Each smoke zone[,] equipped with an automatic-initiation device[,] shall be put into operation by the actuation of one such device. Each additional device within the zone shall be verified to cause the same sequence without requiring the operation of fan motors in order to prevent damage. Control sequences shall be verified throughout the system, including verification of override from the [fire-fighter’s] firefighter’s control panel and simulation of standby power conditions.

909.18.8 Special inspections for smoke control. Smoke control systems shall be tested by a special inspector in accordance with Chapter 17.

909.18.8.1 Scope of testing. Special inspections shall be conducted in accordance with the following:

1.	During erection of ductwork and prior to concealment for the purposes of leakage testing and recording of device location.

2.	Prior to occupancy and after sufficient completion for the purposes of pressure-difference testing, flow measurements, and detection and control verification.

909.18.8.2 Qualifications. Special inspectors for smoke control shall have a certification as air balancers and expertise in fire protection engineering or mechanical engineering.

909.18.8.3 Reports. A complete report of testing shall be prepared by the special inspector or approved agency. The report shall include identification of all devices by manufacturer, nameplate data, design values, measured values and identification tag or mark. The report shall be reviewed by the responsible engineer and, when satisfied that the design intent has been achieved, the engineer shall seal, sign and date the report.

909.18.8.3.1 Report filing. A copy of the final report and each inspection report shall be filed with the department and Fire Commissioner, and an identical copy shall be maintained in an approved location at the building.

909.18.9 Identification and documentation. Charts, drawings and other documents identifying and locating each component of the smoke control system, and describing its proper function and maintenance requirements, shall be maintained on file at the building as an attachment to the report required by Section 909.18.8.3. Devices shall have an approved identifying tag or mark on them consistent with the other required documentation and shall be dated indicating the last time they were successfully tested and by whom.

909.18.10 Reacceptance testing. The smoke control system shall require a reacceptance test after any modifications to the system or physical changes to the building that may affect system performance. Reacceptance testing shall be a retest of the entire system in accordance with Sections 909.18.1 through 909.18.9.

909.19 System acceptance. Buildings, or portions thereof, required by this code to comply with this section shall not be issued a certificate of occupancy until such time that the department determines that the provisions of this section have been fully satisfied and a written maintenance program is approved by the New York City Fire Department.

Exception: In buildings of phased construction, the department may issue a temporary certificate of occupancy provided that those portions of the building to be occupied meet the requirements of this section and that the remainder does not pose a significant hazard to the safety of the proposed occupants or adjacent buildings.

909.20 Smokeproof enclosures. Where required by Section [1022.9] 1023.11, a smoke proof enclosure shall be constructed in accordance with this section. Where access to the roof is required by the New York City Fire Code, such access shall be from the smoke proof enclosure where a smoke proof enclosure is required. Smokeproof enclosures shall consist of one of the following systems:

1.	An enclosed interior exit stairway constructed in accordance with Section [1022.1] 1023 and accessed through an open exterior balcony.

2.	An enclosed interior exit stairway constructed in accordance with Section [1022.1] 1023 and accessed through a naturally ventilated vestibule.

3.	An enclosed interior exit stairway constructed in accordance with Section [1022.1] 1023 and accessed through a mechanically ventilated vestibule.

4.	A pressurized interior exit stairway constructed in accordance with Section [1022.1] 1023.

909.20.1 Access. Access to the interior exit stairway or ramp shall be by way of a vestibule or an open exterior balcony, unless such stairway is pressurized in accordance with Section 909.20.5. The minimum dimension of the vestibule or open exterior balcony shall not be less than the required width of the corridor leading to the vestibule or open exterior balcony but shall not have a width of less than 44 inches (1118 mm) and shall not have a length of less than 72 inches (1829 mm) in the direction of egress travel.

909.20.2 Construction. The smoke proof enclosure shall be separated from the remainder of the building by not less than 2-hour fire barriers constructed in accordance with Section 707 or horizontal assemblies constructed in accordance with Section [712] 711, or both. Openings are not permitted other than the required means of egress doors. The vestibule shall be separated from the stairway or ramp by not less than a 2-hour fire-resistance-rated fire barrier. The open exterior balcony shall be constructed in accordance with the fire-resistance-rating requirements for floor construction.

909.20.2.1 Door closers. Doors in a smoke proof enclosure shall be self- or automatic-closing by actuation of a smoke detector in accordance with Section [715.4] 716.5.9.3 and shall be installed at the floor-side entrance to the smoke proof enclosure [in accordance with Section 715.4.8]. The actuation of the smoke detector on any door shall activate the closing devices on all doors in the smoke proof enclosure at all levels. Smoke detectors shall be installed in accordance with Section 907.3.

909.20.3 Natural ventilation alternative. The provisions of Sections 909.20.3.1 through 909.20.3.3 shall apply to ventilation of smoke proof enclosures by natural means.

909.20.3.1 Balcony doors. Where access to the stairway or ramp is by way of an open exterior balcony, the door assembly into the enclosure shall be a fire door assembly in accordance with Section [715.4] 716.5.

909.20.3.2 Vestibule doors. Where access to the stairway or ramp is by way of a vestibule, the door assembly into the vestibule shall be a fire door assembly complying with Section [715.4] 716.5. The door assembly from the vestibule to the stairway shall have not less than a 90-minute fire protection rating complying with Section [715.4] 716.5.

909.20.3.3 Vestibule ventilation. Each vestibule shall have a minimum net area of 16 square feet (1.5 m2) of opening in a wall facing an outer court, yard or public way that is [at least] not less than 20 feet (6096 mm) in width.

909.20.4 Mechanical ventilation alternative. The provisions of Sections 909.20.4.1 through [909.20.4.4] 909.20.4.5 shall apply to ventilation of smoke proof enclosures by mechanical means.

909.20.4.1 Vestibule doors. The door assembly from the building into the vestibule shall be a fire door assembly complying with Section [715.4.3] 716.5.3. The door assembly from the vestibule to the stairway or ramp shall not have [not] less than a 90-minute fire protection rating and shall meet the requirements for a smoke door assembly in accordance with Section [715.4.3] 716.5.3. The door shall be installed in accordance with NFPA 105.

909.20.4.2 Vestibule ventilation. The vestibule shall be supplied with not less than one air change per minute and the exhaust shall not be less than 150 percent of supply. Supply air shall enter and exhaust air shall discharge from the vestibule through separate, tightly constructed ducts used only for that purpose. Supply air shall enter the vestibule within 6 inches (152 mm) of the floor level. The top of the exhaust register shall be located at the top of the smoke trap but not more than 6 inches (152 mm) down from the top of the trap, and shall be entirely within the smoke trap area. Doors in the open position shall not obstruct duct openings. Duct openings with controlling dampers are permitted where necessary to meet the design requirements, but dampers are not otherwise required.

909.20.4.2.1 Engineered ventilation system. Where a specially engineered system is used, the system shall exhaust a quantity of air equal to not less than 90 air changes per hour from any vestibule in the emergency operation mode and shall be sized to handle three vestibules simultaneously. Smoke detectors shall be located at the floor-side entrance to each vestibule and shall activate the system for the affected vestibule. Smoke detectors shall be installed in accordance with Section 907.3.

909.20.4.3 Smoke trap. The vestibule ceiling shall [be at least] not be less than 20 inches (508 mm) higher than the door opening into the vestibule to serve as a smoke and heat trap and to provide an upward-moving air column. The height shall not be decreased unless approved and justified by design and test.

909.20.4.4 [Stair] Stairway or ramp shaft air movement system. The [stair] stairway or ramp shaft shall be provided with a dampered relief opening and supplied with sufficient air to maintain a minimum positive pressure of 0.10 inch of water (25 Pa) in the shaft relative to the vestibule with all doors closed. The system shall maintain a maximum of 0.35 inch of water (87 Pa) in the shaft relative to the building measured with all stairway doors closed under maximum anticipated stack pressures.

909.20.4.5 Door opening force. Door opening force shall not exceed limits in Section [1008.1.3] 1010.1.3.

909.20.5 [Stair] Stairway and ramp pressurization alternative. Where the building is equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1, the vestibule is not required, provided [that] each interior exit [stairways are pressurized] stairway or ramp is pressurized to [a minimum of] not less than 0.10 [inches] inch of water (25 Pa) and [a maximum of] not more than 0.35 inches of water (87 Pa) in the shaft relative to the building measured with all interior exit stairway and ramp doors closed under maximum anticipated conditions of stack effect and wind effect.

909.20.6 Ventilating equipment. The activation of ventilating equipment required by the alternatives in Sections 909.20.4 and 909.20.5 shall be by smoke detectors installed at each floor level at an approved location at the entrance to the smokeproof enclosure. When the closing device for the [stair] stairway and ramp shaft and vestibule doors is activated by smoke detection or power failure, the mechanical equipment shall activate and operate at the required performance levels. Smoke detectors shall be installed in accordance with Section 907.3.

909.20.6.1 Ventilation systems. Smokeproof enclosure ventilation systems shall be independent of other building ventilation systems. The equipment, control wiring, power wiring and ductwork shall comply with one of the following:

1.	Equipment, control wiring, power wiring and ductwork shall be located exterior to the building and directly connected to the smokeproof enclosure or connected to the smokeproof enclosure by ductwork enclosed by not less than 2-hour fire barriers constructed in accordance with Section 707 or horizontal assemblies constructed in accordance with Section [712] 711, or both.

2.	Equipment, control wiring, power wiring and ductwork shall be located within the smokeproof enclosure with intake or exhaust directly from and to the outside or through ductwork enclosed by not less than 2-hour fire barriers constructed in accordance with Section 707 or horizontal assemblies constructed in accordance with Section [712] 711, or both.

3.	Equipment, control wiring, power wiring and ductwork shall be located within the building if separated from the remainder of the building, including other mechanical equipment, by not less than 2-hour fire barriers constructed in accordance with Section 707 or horizontal assemblies constructed in accordance with Section [712] 711, or both.

Exceptions:

1.	Control wiring and power wiring utilizing a 2-hour rated cable or cable system in accordance with UL 2196.

2.	Where encased with not less than 2 inches (51 mm) of concrete.

3.	Control wiring and power wiring protected by a listed electrical circuit protective system with a fire-resistance rating of not less than 2 hours.

909.20.6.2 Standby power. Mechanical vestibule and [stair] stairway and ramp shaft ventilation systems and automatic fire detection systems shall be [powered by a] provided with standby power [system conforming to Section] in accordance with Sections [403.4.7] 403.4.8 and [Chapter 27] 2702.

909.20.6.3 Acceptance and testing. Before the mechanical equipment is approved, the system shall be tested in the presence of the department or approved agency to confirm that the system is operating in compliance with these requirements.

909.21 Elevator hoistway pressurization alternative. Where elevator hoistway pressurization is provided in lieu of required enclosed elevator lobbies, the pressurization system shall comply with Sections 909.21.1 through 909.21.11.

909.21.1 Pressurization requirements. Elevator hoistways shall be pressurized to maintain a minimum positive pressure of 0.10 inch of water (25 Pa) and a maximum positive pressure of 0.25 inch of water (67 Pa) with respect to adjacent occupied space on all floors. This pressure shall be measured at the midpoint of each hoistway door, with all elevator cars at the floor of recall and all hoistway doors on the floor of recall open and all other hoistway doors closed. The pressure differentials shall be measured between the hoistway and the adjacent elevator landing. The opening and closing of hoistway doors at each level must be demonstrated during this test. The supply air intake shall be from an outside, uncontaminated source located a minimum distance of 20 feet (6096 mm) from any air exhaust system or outlet.

Exceptions:

1.	On floors containing only Group R occupancies, the pressure differential is permitted to be measured between the hoistway and a dwelling unit or sleeping unit.

2.	Where an elevator opens into a lobby enclosed in accordance with Section 3007.6 or 3008.7, the pressure differential is permitted to be measured between the hoistway and the floor space immediately outside of the door(s) to the enclosed lobby.

3.	The pressure differential is permitted to be measured relative to the outdoor atmosphere on floors other than the following:

3.1.	The fire floor.

3.2.	The two floors immediately below the fire floor.

3.3.	The floor immediately above the fire floor.

4.	The minimum positive pressure of 0.10 inch of water (25 Pa) and a maximum positive pressure of 0.25 inch of water (67 Pa) with respect to occupied floors are not required at the floors of recall with the doors open.

909.21.1.1 Use of ventilation systems. Ventilation systems, other than hoistway supply air systems, are permitted to be used to exhaust air from adjacent spaces on the fire floor, two floors immediately below and one floor immediately above the fire floor to the building’s exterior where necessary to maintain positive pressure relationships as required in Section 909.21.1 during operation of the elevator shaft pressurization system.

Where ventilation systems are being used as a component of the elevator hoistway pressurization system, they shall comply with Section 909.21.

909.21.2 Rational analysis. A rational analysis complying with Section 909.4 shall be submitted with the construction documents.

909.21.3 Ducts for system. Any duct system that is part of the pressurization system shall be protected with the same fire-resistance rating as required for the elevator shaft enclosure.

909.21.4 Fan system. The fan system provided for the pressurization system shall be as required by Sections 909.21.4.1 through 909.21.4.4.

909.21.4.1 Fire resistance. Where located within the building, the fan system that provides the pressurization shall be protected with the same fire-resistance rating required for the elevator shaft enclosure.

909.21.4.2 Smoke detection. The supply fan system shall be equipped with a smoke detector that will automatically shut down the supply fan system when smoke is detected within the system.

909.21.4.3 Separate systems. A separate fan system shall be used for each elevator hoistway.

909.21.4.4 Fan capacity. The supply fan capacity shall be specified by a registered design professional to meet the requirements of a designed pressurization system in accordance with the rational analysis required by Section 909.21.2.

909.21.5 Standby power. The pressurization system, including ventilation systems used per Section 909.21.1.1, shall be provided with standby power in accordance with Section 2702.

909.21.6 Activation of pressurization system. The elevator pressurization system shall be activated upon activation of either the building fire alarm system or the elevator landing smoke detectors. Where both a building fire alarm system and elevator landing smoke detectors are present, each shall be independently capable of activating the pressurization system.

909.21.7 Testing and special inspections. Special inspections for performance shall be required in accordance with Section 909.18.8. System acceptance testing shall be in accordance with Section 909.19.

909.21.8 Marking and identification. Detection and control systems shall be marked in accordance with Section 909.14.

909.21.9 Control diagrams. Control diagrams shall be provided in accordance with Section 909.15.

909.21.10 Firefighter’s smoke control panel. A control panel complying with Section 909.16 shall be provided.

909.21.11 System response time. Hoistway pressurization systems shall comply with the requirements for smoke control system response time in Section 909.17.

SECTION BC 910
SMOKE AND HEAT [VENTS] REMOVAL

910.1 General. Where required by this code [or otherwise installed], smoke and heat vents or mechanical smoke [exhaust] removal systems [and draft curtains] shall conform to the requirements of this section.

910.2 Where required. Smoke and heat vents or a mechanical smoke removal system shall be installed as required by Sections 910.2.1 and 910.2.2.

Exceptions:

1.	Frozen-food warehouses used solely for storage of Class I and II commodities where protected by an automatic sprinkler system in accordance with Section 903.3.1.1.

2.	[Where] Smoke and heat removal shall not be required in areas of buildings [are] equipped with early suppression fast-response (ESFR) sprinklers[, automatic smoke and heat vents shall not be required within these areas].

3.	Smoke and heat removal shall not be required in areas of buildings equipped with control mode special application sprinklers with a response time index of 50 (m · s)1/2 or less that are listed to control a fire in stored commodities with 12 or fewer sprinklers.

[910.2 Where required. Smoke and heat vents shall be installed in the roofs of buildings or portions thereof occupied for the uses set forth in Sections 910.2.1 and 910.2.2. Vents shall be installed at the top of a closed shaft in accordance with Section 708.12.1.]

910.2.1 Group F-1 or S-1. [Buildings] Smoke and heat vents installed in accordance with Section 910.3 or a mechanical smoke removal system installed in accordance with Section 910.4 shall be installed in buildings and portions thereof used as a Group F-1 or S-1 occupancy having more than 50,000 square feet (4645 m2) [in] of undivided area. In occupied portions of a building equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1, where the upper surface of the story is not a roof assembly, a mechanical smoke removal system in accordance with Section 910.4 shall be installed.

Exception: Group S-1 aircraft repair hangars.

910.2.2 High-piled combustible storage.[Buildings] Smoke and heat removal for buildings and portions thereof containing high-piled combustible [stock or rack] storage [in any occupancy group] shall be installed in accordance with [Section 413 of this code and] the New York City Fire Code and Section 413 of this code. Installation shall also be in conformance with Section 910.3 in unsprinklered buildings and portions thereof.

In buildings and portions thereof containing high-piled combustible storage equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1, a smoke and heat removal system shall be installed in accordance with Section 910.3 or 910.4. In occupied portions of a building equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1, where the upper surface of the story is not a roof assembly, a mechanical smoke removal system in accordance with Section 910.4 shall be installed.

910.3 [Design and installation] Smoke and heat vents. The design and installation of smoke and heat vents [and draft curtains] shall be [as specified] in accordance with Sections 910.3.1 [and Table 910.3] through 910.3.3.

[TABLE 910.3]
REQUIREMENTS FOR DRAFT CURTAINS AND SMOKE AND HEAT VENTSa]

| [OCCUPANCY GROUP AND COMMODITY CLASSIFICATION] | [DESIGNATED STORAGE HEIGHT (feet)] | [MINIMUM DRAFT CURTAIN DEPTH (feet)] | [MAXIMUM AREA FORMED BY DRAFT CURTAINS (square feet)] | [VENT AREA TO FLOOR AREA RATIO] | [MAXIMUM SPACING OF VENT CENTERS (feet)] | [MAXIMUM DISTANCE FROM VENTS TO WALL OR DRAFT CURTAINb (feet)] |
| --- | --- | --- | --- | --- | --- | --- |
| [Group F-1] | [—] | [0.2 × Hd but ≥ 4] | [50,000] | [1:100] | [120] | [60] |
| [High-piled (see Section 910.2.2) Class I-IV commodities (Option 1)] | [≤ 20] | [6] | [10,000] | [1:100] | [100] | [60] |
|  | [> 20 ≤ 40] | [6] | [8,000] | [1:75] | [100] | [55] |
| [High-piled Storage (see Section 910.2.2) Class I-IV commodities (Option 2)] | [≤ 20] | [4] | [3,000] | [1:75] | [100] | [55] |
|  | [> 20 ≤ 40] | [4] | [3,000] | [1:50] | [100] | [50] |
| [High-piled Storage (see Section 910.2.2) High hazard commodities (Option 1)] | [≤ 20] | [6] | [6,000] | [1:50] | [100] | [50] |
|  | [> 20 ≤ 30] | [6] | [6,000] | [1:40] | [90] | [45] |
| [High-piled Storage (see Section 910.2.2) Class High hazard commodities (Option 2)] | [≤ 20] | [4] | [4,000] | [1:50] | [100] | [50] |
|  | [> 20 ≤ 30] | [4] | [2,000] | [1:30] | [75] | [40] |

[For SI: 1 foot = 304.8 mm, 1 square foot = 0.0929 m2.]

[1.	Requirements for rack storage heights in excess of those indicated shall be in accordance with the New York City Fire Code. For solid-piled storage heights in excess of those indicated, an approved engineered design shall be used.]

[2.	Vents adjacent to walls or draft curtains shall be located within a horizontal distance not greater than the maximum distance specified in this column as measured perpendicular to the wall or draft curtain that forms the perimeter of the draft curtained area.]

[3.	Where draft curtains are not required, the vent area to floor area ratio shall be calculated based on a minimum draft curtain depth of 6 feet (Option 1).]

[4.	H is the height of the vent, in feet, above the floor.]

910.3.1 [Design] Listing and labeling. Smoke and heat vents shall be listed and labeled to indicate compliance with UL 793 or FM 4430.

[910.3.2 Vent operation. Smoke and heat vents shall be capable of being operated by approved automatic and manual means.  Automatic operation of smoke and heat vents shall conform to the provisions of Sections 910.3.2.1 through 910.3.2.3.]

[910.3.2.1 Gravity-operated drop-out vents.  Automatic smoke and heat vents containing heat-sensitive glazing designed to shrink and drop out of the vent opening when exposed to fire shall fully open within 5 minutes after the vent cavity is exposed to a simulated fire, represented by a time-temperature gradient that reaches an air temperature of 500°F (260°C) within 5 minutes.]

[910.3.2.2 Sprinklered buildings. Where installed in buildings provided with an automatic sprinkler system in accordance with Section 903.3.1.1, smoke and heat vents shall be designed to operate automatically.]

[910.3.2.3 Nonsprinklered buildings. Where installed in buildings not provided with an automatic sprinkler system, smoke and heat vents shall operate automatically by actuation of a heat-responsive device rated at between 100°F (38°C) and 220°F (104°C) above ambient.]

[Exception: Gravity-operated drop-out vents complying with Section 910.3.2.1.]

[910.3.3 Vent dimensions. The effective venting area shall not be less than 16 square feet (1.5 m2) with no dimension less than 4 feet (1219 mm), excluding ribs or gutters having a total width not exceeding 6 inches (152 mm).]

[910.3.4 Vent locations.] 910.3.2 Smoke and heat vent locations. Smoke and heat vents shall be located 20 feet (6096 mm) or more from adjacent lot lines and fire walls and 10 feet (3048 mm) or more from fire barriers. Vents shall be uniformly located within the roof in the areas of the building where the vents are required to be installed by Section 910.2[,] with consideration given to roof pitch[, draft curtain location], sprinkler location and structural members.

[910.3.5 Draft curtains. Where required by Table 910.3, draft curtains shall be installed on the underside of the roof in accordance with this section.]

[Exception: Where areas of buildings are equipped with early suppression fast-response (ESFR) sprinklers, draft curtains shall not be provided within these areas. Draft curtains shall only be provided at the separation between the ESFR sprinklers and the conventional non-ESFR sprinklers.]

[910.3.5.1 Construction. Draft curtains shall be constructed of sheet metal, lath and plaster, gypsum board or other approved materials that provide equivalent performance to resist the passage of smoke. Joints and connections shall be smoke tight.]

[910.3.5.2 Location and depth. The location and minimum depth of draft curtains shall be in accordance with Table 910.3.]

910.3.3 Smoke and heat vents area. The required aggregate area of smoke and heat vents shall be calculated as follows:

For buildings equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1:

(Equation 9-2)

where:

The required aggregate vent area (ft2).

Volume (ft3) of the area that requires smoke removal.

For unsprinklered buildings:

(Equation 9-3)

where:

The required aggregate vent area (ft2).

The area of the floor in the area that requires smoke removal.

910.4 Mechanical smoke [exhaust] removal systems. [Where approved by the department, engineered mechanical smoke exhaust shall be an acceptable alternate to smoke and heat vents]. Mechanical smoke removal systems shall be designed and installed in accordance with Sections 910.4.1 through 910.4.7.

[910.4.1 Location. Exhaust fans shall be uniformly spaced within each draft-curtained area and the maximum distance between fans shall not be greater than 100 feet (30 480mm).]

910.4.1 Automatic sprinklers required. The building shall be equipped throughout with an approved automatic sprinkler system in accordance with Section 903.3.1.1.

[910.4.2 Size. Fans shall have a maximum individual capacity of 30,000 cfm (14.2 m3/s). The aggregate capacity of smoke exhaust fans shall be determined by the equation:]

(Equation 9-4)]

[where:]

[	Capacity of mechanical ventilation required, in cubic feet per minute (m3/s).]

[	Area of roof vents provided in square feet (m2) in accordance with Table 910.3.]

910.4.2 Exhaust fan construction. Exhaust fans that are part of a mechanical smoke removal system shall be rated for operation at 221°F (105°C). Exhaust fan motors shall be located outside of the exhaust fan air stream.

910.4.3 [Operation. Mechanical smoke exhaust fans shall be automatically activated by the automatic sprinkler system or by heat detectors having operating characteristics equivalent to those described in Section 910.3.2. Individual manual controls of each fan unit shall also be provided.] System design criteria. The mechanical smoke removal system shall be sized to exhaust the building at a minimum rate of two air changes per hour based upon the volume of the building or portion thereof without contents. The capacity of each exhaust fan shall not exceed 30,000 cubic feet per minute (14.2 m3/sec).

910.4.3.1 Makeup air. No portion of the makeup air openings shall be higher than 6 feet (1829 mm) above the floor level. Operation of makeup air openings shall be manual or, if properly coordinated with the smoke removal system, automatic. The minimum gross area of makeup air inlets shall be 8 square feet per 1,000 cubic feet per minute (0.74 m2 per 0.4719 m3/s) of smoke exhaust.

910.4.4 Activation. The mechanical smoke removal system shall be started by manual controls.

[910.4.4 Wiring and control. Wiring for operation and control of smoke exhaust fans shall be connected ahead of the main disconnect and protected against exposure to temperatures in excess of 1,000°F (538°C) for a period of not less than 15 minutes. Controls]

910.4.5 Manual control location. Manual controls shall be located so as to be [immediately] accessible to the [fire service] Fire Department from [the] an exterior door of the building and protected against interior fire exposure by not less than 1-hour fire barriers constructed in accordance with Section 707 or horizontal assemblies constructed in accordance with Section [712] 711, or both. The location of manual controls is subject to the approval of the Fire Commissioner.

[910.4.5 Supply air. Supply air for exhaust fans shall be provided at or near the floor level and shall be sized to provide a minimum of 50 percent of required exhaust. Openings for supply air shall be uniformly distributed around the periphery of the area served.]

910.4.6 [Interlocks. In combination comfort air-handing/smoke removal systems or independent comfort air-handling systems, fans shall be controlled to shut down in accordance with the approved smoke control sequence.] Control wiring. Wiring for operation and control of mechanical smoke removal systems shall be connected ahead of the main disconnect in accordance with the New York City Electrical Code and be protected against interior fire exposure to temperatures in excess of 1,000°F (538°C) for a period of not less than 15 minutes.

910.4.7 Controls. Where building air-handling and mechanical smoke removal systems are combined or where independent building air-handling systems are provided, fans shall automatically shut down in accordance with the New York City Mechanical Code. The manual controls provided for the smoke removal system shall have the capability to override the automatic shutdown of fans that are part of the smoke removal system.

910.5 Maintenance. Smoke and heat vents and mechanical smoke removal systems shall be maintained in accordance with the New York City Fire Code.

SECTION BC 911
FIRE COMMAND CENTER

911.1 General. Where required by other sections of this code and in [all] buildings classified as high-rise buildings by this code, a fire command center for Fire Department operations shall be provided and shall comply with Sections 911.1.1 through [911.1.5] 911.1.6.

911.1.1 Location and access. The fire command center location shall be in the lobby of the building on the main entrance floor near the Fire Department designated response point.

911.1.2 Reserved.

911.1.3 Reserved.

911.1.4 Reserved.

911.1.5 Storage. Storage unrelated to operation of the fire command center shall be prohibited.

911.1.6 Required features. The fire command center shall comply with the New York City Fire Code and NFPA 72 and shall include the following features as applicable in their respective control units or panels:

1.	Fire alarm control unit:

1.1.	The emergency voice/alarm communication system control unit.

1.2.	The two-way communications system.

1.3	Fire detection and alarm system annunciator.

1.4	Controls for unlocking stairway doors and locked elevator vestibule doors simultaneously.

1.5	Sprinkler valve and water-flow detector display panels.

1.6	Emergency and standby power status indicators (generator running, generator failure to start).

1.7	Fire pump status indicators.

1.8	Elevator fire recall switch in accordance with ASME A17.1.

2.	Auxiliary Radio Communication System Panel.

3.	Elevator control panel:

3.1	Annunciator visually indicating the location of the elevators and whether they are operational.

3.2	Elevator emergency or standby power selector switch(es), where emergency or standby power is provided.

4.	The [fire-fighter’s] firefighter’s control panel required by Section 909.16 for smoke control systems installed in the building.

5.	Monitoring/Control for Post-Fire Smoke Purge:

5.1	Status indicators and controls for air distribution systems.

5.2	Manual controls of post-fire smoke purge system in accordance with Section [916.2.3] 917.2.3.

6.	A telephone for Fire Department use with controlled access to the public telephone system.

7.	Public address system, where specifically required by other sections of this code.

8.	Manual controls for the release of doors that are automatic-closing by the actuation of smoke detectors or activation of the fire alarm in accordance with the exception to Section [708.7] 713.7.

911.2 Secondary fire command center. Where required in locations described in Appendix G of this code, a secondary fire command center shall be provided subject to the approval of the Fire Department. Design and installation requirements shall be in accordance with NFPA 72.

SECTION BC 912
FIRE DEPARTMENT CONNECTIONS

912.1 Installation. Fire Department connections shall be installed in accordance with the NFPA standard applicable to the system design and shall comply with Sections 912.2 through [912.5] 912.6.

912.2 Location. With respect to hydrants, driveways, buildings and landscaping, Fire Department connections shall be so located that fire apparatus and hose connected to supply the system will not obstruct access to the buildings for other fire apparatus.

912.2.1 Fire Department connections. The location of Fire Department connections shall be as follows:

912.2.1.1 One Fire Department connection shall be provided for each 300 feet (91 140 mm) of exterior building wall or fraction thereof facing upon each street or public space.

912.2.1.2 Where buildings face upon two parallel streets or public spaces without an intersecting street or public space, one connection shall be provided for each 300 feet (91 140 mm) of exterior building wall or fraction thereof facing upon each such parallel street or public space.

912.2.1.3 Where a building faces upon two intersecting streets or public spaces and the total length of the exterior building walls facing upon such streets or public spaces does not exceed 300 feet (91 140 mm), only one Fire Department connection need be installed provided the Fire Department connection is located within 15 feet (4572 mm) of the corner and on the street with the longest building frontage.

912.2.1.4 Where a building faces on three streets or public spaces, one Fire Department connection shall be provided for each 300 feet (91 140 mm) of building wall or fraction thereof facing upon such streets or public spaces provided that at least one Fire Department connection is installed on each of the parallel streets or public spaces, and further provided that the Fire Department connections shall be located so that the distance between them does not exceed 300 feet (91 140 mm).

912.2.1.5 Where a building faces upon four streets or public spaces, at least one Fire Department connection shall be provided on each street front or public space; however, only one Fire Department connection need be provided at the corner of two intersecting streets or public spaces if the Fire Department connection is located within 15 feet (4572 mm) of the corner and on the street with the longest building frontage or public space, and if the distances between Fire Department connections, in all cases, do not exceed 300 feet (91 140 mm).

912.2.1.6 In any case where the exterior building walls of a building facing a street or public space are obstructed in part by another building, one Fire Department connection shall be provided for each clear 300 feet (91 140 mm) of exterior building wall or fraction thereof facing upon such street or public space.

912.2.2 Existing buildings. On existing buildings, wherever the Fire Department connection is not visible to approaching fire apparatus, the Fire Department connection shall be indicated by an approved sign mounted on the street front or on the side of the building. Such sign shall have the letters “FDC” [at least] not less than 6 inches (152 mm) high and words in letters [at least] not less than 2 inches (51 mm) high or an arrow to indicate the location. [All such] Such signs shall be subject to the approval of the Fire Department.

912.3 Fire hose threads. Fire hose threads used in connection with standpipe, sprinkler and combination standpipe-sprinkler systems shall be approved and shall be compatible with New York City Fire Department hose threads.

[912.3] 912.4 Access. Immediate access to Fire Department connections shall be maintained at all times and without obstruction by fences, bushes, trees, walls or any other object. [A working space of not less than 36 inches (762 mm) in width, 36 inches (914 mm) in depth and 78 inches (1981 mm) in height shall be provided and maintained in front of and to the sides of wall-mounted Fire Department connections and around the circumference of free-standing Fire Department connections, except as otherwise required or approved.]

Exception: Fences, where provided with an access gate and a means of emergency operation that shall be maintained operational at all times in accordance with the New York City Fire Code.

912.4.1 Locking Fire Department connection caps. The Fire Department may require locking caps on Fire Department connections in accordance with the New York City Fire Code.

912.4.2 Clear space around connections. A working space of not less than 36 inches (914 mm) in width, 36 inches (914 mm) in depth and 78 inches (1981 mm) in height shall be provided and maintained in front of and to the sides of wall-mounted Fire Department connections and around the circumference of free-standing Fire Department connections, except as otherwise required or approved by the Fire Commissioner.

912.4.3 Physical protection. Where Fire Department connections are subject to impact by a motor vehicle, vehicle impact protection shall be provided in accordance with the New York City Fire Code.

[912.4] 912.5 Signs. Fire Department connections shall be provided with signage in accordance with Section 912 of the New York City Fire Code.

[912.5] 912.6 Backflow protection. The potable water supply to automatic sprinkler and standpipe systems shall be protected against backflow as required by the New York City Plumbing Code.

SECTION BC 913
FIRE PUMPS

913.1 General. Where provided or required, fire pumps shall be installed in accordance with this section, NFPA 20[, Appendix Q] and other applicable sections of this code.

913.2 Protection against interruption of service. The fire pump, driver and controller shall be protected in accordance with NFPA 20 against possible interruption of service.

913.2.1 Protection of fire pump rooms. Fire pumps shall be located in rooms that are separated from all other areas of the building by 2-hour fire barriers constructed in accordance with Section 707 or 2-hour horizontal assemblies constructed in accordance with Section [712] 711, or both.

Exceptions:

1.	In other than high-rise buildings, separation by 1-hour fire barriers constructed in accordance with Section 707 or 1-hour horizontal assemblies constructed in accordance with Section [712] 711, or both, shall be permitted in buildings equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1 or 903.3.1.2.

2.	Separation is not required for fire pumps physically separated in accordance with NFPA 20.

3.	Separation is not required for a fire pump, other than an automatic standpipe fire pump, where such fire pump is located in a mechanical equipment room, as defined by the New York City Mechanical Code, enclosed by 2-hour fire barriers constructed in accordance with Section 707 or 2-hour horizontal assemblies constructed in accordance with Section [712] 711, or both. Refrigerants, gas piping, gas consumption devices, gas meters or any other gas equipment and fuel storage or fuel consuming appliances shall not be installed in any space housing a fire pump.

913.2.2 Circuits supplying fire pumps. Cables used for survivability of circuits supplying fire pumps shall be in accordance with the New York City Electrical Code. Electrical circuit protective systems shall be installed in accordance with their listing requirements, and the New York City Electrical Code.

913.3 Temperature of pump room. Suitable means shall be provided for maintaining the temperature of a pump room or pump house, where required, above 40°F (5°C).

913.3.1 Engine manufacturer’s recommendation. Temperature of the pump room, pump house or area where engines are installed shall never be less than the minimum recommended by the engine manufacturer. The engine manufacturer’s recommendations for oil heaters shall be followed.

913.4 Valve supervision. Where provided, the fire pump suction, discharge and bypass valves, and isolation valves on the backflow prevention device or assembly shall be supervised open as required by Section 907.

913.4.1 Test outlet control valve supervision. Fire pump test outlet control valves shall be supervised in the closed position. Individual hose valves on the test header are not required to be monitored.

913.5 Acceptance test. Acceptance testing shall be done in accordance with the requirements of Section 1705.30 of this code, the New York City Fire Code and NFPA 20. Refurbished or repaired fire pumps shall be tested in accordance with Section 1705.30 of this code, the New York City Fire Code and NFPA 20. All such tests shall be scheduled to include a department representative as a witness, if required.

SECTION BC 914
EMERGENCY RESPONDER SAFETY FEATURES

914.1 Shaftway markings. Vertical shafts shall be identified as required by the New York City Fire Code and Sections 914.1.1 and 914.1.2 of this code.

914.1.1 Exterior access to shaftways. Outside openings accessible to the Fire Department and that open directly on a hoistway or shaftway communicating between two or more floors in a building shall be plainly marked with the word “SHAFTWAY” in red letters [at least] not less than 6 inches (152 mm) high on a white background. Such warning signs shall be placed so as to be readily discernible from the outside of the building.

914.1.2 Interior access to shaftways. Door or window openings to a hoistway or shaftway from the interior of the building shall be plainly marked with the word “SHAFTWAY” in red letters [at least] not less than 6 inches (152 mm) high on a white background. Such warning signs shall be placed so as to be readily discernible.

Exception: Markings shall not be required on shaftway openings that are readily discernible as openings onto a shaftway by the construction or arrangement.

914.2 Equipment room identification. Fire protection equipment shall be identified in an approved manner. Rooms containing controls for air-conditioning systems, sprinkler risers and valves or other fire detection, suppression or control elements shall be identified for the use of the Fire Department. Approved signs required to identify fire protection equipment and equipment location shall be constructed of durable materials, permanently installed and readily visible.

SECTION BC 915
[RESERVED]
CARBON MONOXIDE DETECTION

915.1 Carbon monoxide alarms and detectors. Carbon monoxide alarms and detectors shall be provided and installed in accordance with Sections 915.1.1 through 915.7.

915.1.1 Group I-1 and R occupancies. Listed carbon monoxide alarms or detectors shall be installed as follows:

1.	Group I-1, Group R-1, and Group R-2 where the main use or dominant occupancy of a building is classified as Group R-2 student apartments. Carbon monoxide detectors and audible notification appliances shall be installed in affected dwelling units in accordance with Section 915.1.1.1 and shall be annunciated by dwelling unit at a constantly attended location from which the fire alarm system is capable of being manually activated.

2.	Groups R-2 (other than occupancies covered by Item 1) and R-3. Carbon monoxide alarms shall be installed in affected dwelling units in accordance with Section 915.1.1.1.

915.1.1.1 Affected dwelling units. Carbon monoxide alarms or detectors shall be required within the following dwelling units:

1.	Units on the same story where carbon monoxide-producing equipment or enclosed parking is located.

2.	Units on the stories immediately above and below the floor where carbon monoxide-producing equipment or enclosed parking is located.

3.	Units in a building containing a carbon monoxide-producing furnace, boiler, or water heater as part of a central system.

4.	Units in a building served by a carbon monoxide-producing furnace, boiler, or water heater as part of a central system that is located in an adjoining or attached building.

915.1.1.1.1 Required locations within dwelling units. Carbon monoxide alarms or detectors shall be located within dwelling units as follows:

1.	Outside of any room used for sleeping purposes, within 15 feet (4572 mm) of the entrance to such room.

2.	In any room used for sleeping purposes.

3.	On any story within a dwelling unit, including below-grade stories and penthouses of any area, but not including crawl spaces and uninhabitable attics.

915.1.1.1.2 Exhaust of Carbon Monoxide in Group R-3 Occupancy (One- and Two-Family dwellings and townhouses). Means of exhausting carbon monoxide from garages shall be provided when a carbon monoxide alarm or detector is activated in a Group R-3 occupancy, provided such garage is attached within the Group R-3 occupancy. Such exhaust system shall be arranged to operate automatically upon detection of a concentration of carbon monoxide of 35 parts per million (ppm) or greater by approved automatic detection device. The system shall be capable of producing an exhaust rate of 1.5 cfm per square foot of floor area of the garage. Removal of sensor, interruption of power or cut wires shall cause the relay circuit to open and start fan. The relay contact shall close and the fan may shut off when the carbon monoxide level is below 35 ppm. Carbon monoxide exhausting means shall be connected to a separate circuit and provided with a lock and identified at the power source. Such circuit shall not be connected to a power source through an arc-fault or Ground Fault Circuit Interrupter (GFCI) devices. Additionally, when the carbon monoxide exhausting means is connected to the plug-in-type overcurrent protection device, such device shall be secured in place by an additional fastener.

915.1.2 Buildings that are equipped with a fire alarm system and that contain Group A-1, A-2, A-3, Group B or Group M occupancies. Listed carbon monoxide detectors shall be installed in buildings that are equipped with a fire alarm system and that contain Group A-1, A-2 or A-3, Group B or Group M occupancies.  Such carbon monoxide detectors installed pursuant to this section shall have built-in sounder bases, shall transmit a carbon monoxide alarm signal to a central supervising station and shall be permitted to initiate an audible and visual supervisory signal at a constantly attended location.  The department shall adopt rules and/or reference standards (i) governing the installation and location of carbon monoxide detectors provided such detectors shall be required within rooms containing carbon monoxide-producing equipment and (ii) addressing the installation of such detectors or any alternative means of compliance in existing buildings.

915.1.2.1 Retroactive provisions for existing buildings. Notwithstanding any other provision of law, listed carbon monoxide detectors shall be installed in existing buildings that are equipped with a fire alarm system and that contain group A-1, A-2, A-3, Group B or Group M occupancies in accordance with Section 915.1.2 by January 1, 2021.

915.2 Group E, I-2 and I-4 occupancies. Listed carbon monoxide detectors with built-in sounder bases shall transmit a carbon monoxide alarm signal to a central supervising station and shall be permitted to initiate an audible and visual supervisory signal at a constantly attended location.

1.	Carbon monoxide detectors with built-in sounder bases shall be installed within any room containing carbon monoxide-producing equipment.

2.	Carbon monoxide detectors with built-in sounder bases shall be installed in corridors on the story where carbon monoxide-producing equipment unit is located, as well as one story above and one story below.

3.	Carbon monoxide detectors with built-in sounder bases shall be installed in all corridors on the story where enclosed parking or a loading dock is located, as well as one story above and one story below.

915.3 Installation requirement for all occupancies. Where a fire alarm system is required or provided, carbon monoxide detectors with sounder bases shall be installed within any room containing carbon monoxide-producing equipment.

915.3.1 Equipment shutdown. Activation of a carbon monoxide detector located at the source of carbon monoxide-producing equipment shall shut down that source.

Exception: This provision does not apply where the source is a generator.

915.4 Detection equipment. Carbon monoxide detection required by Sections 915.1 through 915.2 shall be provided by carbon monoxide alarms complying with Section 915.5 or carbon monoxide detection systems complying with Section 915.6, unless otherwise specified in this code.

915.5 Carbon monoxide alarms. Carbon monoxide alarms shall comply with Sections 915.5.1 through 915.5.4.

915.5.1 Power source. Carbon monoxide alarms shall receive their primary power from the building wiring where such wiring is served from a commercial source, and when primary power is interrupted, shall receive power from a battery. Wiring shall be permanent and without a disconnecting switch other than that required for overcurrent protection.

Exception: Where installed in buildings without commercial power, battery-powered carbon monoxide alarms shall be an acceptable alternative.

915.5.2 Listings. Carbon monoxide alarms shall be listed in accordance with UL 2034.

915.5.3 Combination alarms. Combination carbon monoxide/smoke alarms shall be an acceptable alternative to carbon monoxide alarms. Combination carbon monoxide/smoke alarms shall be listed in accordance with UL 2034 and UL 217.

915.5.4 Interconnection of alarms. When two or more alarms are installed, they shall be interconnected in accordance with NFPA 720.

915.6 Carbon monoxide detection systems. Carbon monoxide detection systems shall be an acceptable alternative to carbon monoxide alarms and shall comply with Sections 915.6.1 through 915.6.4.

915.6.1 General. Carbon monoxide detection systems shall comply with NFPA 720. Carbon monoxide detectors shall be listed in accordance with UL 2075.

915.6.2 Locations. Carbon monoxide detectors shall be installed in the locations specified in Section 915.2. These locations supersede the locations specified in NFPA 720.

915.6.3 Combination detectors. Combination carbon monoxide/smoke detectors installed in carbon monoxide detection systems shall be an acceptable alternative to carbon monoxide detectors, provided they are listed in accordance with UL 2075 and UL 268.

915.6.4 Wiring and power supply. Wiring and power supply for carbon monoxide detectors shall comply with Sections 907.6.1 and 907.6.2, respectively.

915.7 Inspection, testing and maintenance. Carbon monoxide alarms and carbon monoxide detection systems shall be inspected, tested and maintained in accordance with NFPA 720 and the New York City Fire Code.

SECTION BC 916
FIRE DEPARTMENT IN-BUILDING AUXILIARY 
RADIO COMMUNICATION SYSTEM (ARCS)

916.1 General. This section covers the design, installation and performance criteria of Fire Department In-Building Auxiliary Radio Communication System (ARCS). Such systems shall be designed and installed by the New York City Fire Code, Sections 403 and 907 of this code, or where installed voluntarily, such systems shall be designed and installed in accordance with this section, NFPA 72, the New York City Electrical Code and in accordance with Fire Department requirements.

916.1.1 Construction documents. Construction documents for ARCS shall be submitted for approval to the Fire Department prior to system installation. Construction documents shall include, but need not be limited to, all of the following:

1.	Type of radio equipment and antenna.

2.	Riser diagram and floor plans showing location of elements of the ARCS, including but not limited to building fire command center or fire alarm control panel, dedicated radio console, base station/s and all other critical system components such as antennas, amplifiers, cables as applicable.

3.	Legend of all ARCS symbols and abbreviations used.

4.	Location of primary and secondary power source.

5.	Specification and listing details for all equipment, devices and cables.

916.1.2 Acceptance testing, maintenance and operational testing. Acceptance testing, maintenance and operational testing of the ARCS shall be performed in accordance with the New York City Fire Code and rules promulgated by the Fire Department.

916.2 Instructions. Operating, testing and maintenance instructions and record drawings (“as-builts”) and detailed specifications of all the components shall be provided at an approved location.

916.3 Where required. ARCS, which shall be in accordance with this section, shall be required in the following:

1.	High-rise buildings constructed in accordance with Section 403.

2.	Underground buildings constructed in accordance with Section 405.

3.	Buildings having a total gross area exceeding 250,000 square feet (23 226 m2).

Exceptions:

1.	Group R-2 buildings that meet all of the following requirements:

a.	The highest occupied floor is less than 125 feet (38 100 mm) above the lowest level of Fire Department vehicle access;

b.	The building has no more than 1 story below grade; and

c.	The floor area of the building does not exceed 250,000 square feet (23 226 m2).

2.	Where it is determined by the Fire Department that a radio communication system is not required.

SECTION BC 917
POST-FIRE SMOKE PURGE SYSTEMS

[916.1] 917.1 Scope and purpose. The purpose of this section is to establish minimum requirements for the design and installation of post-fire smoke purge systems, which are intended for the timely restoration of operations and overhaul activities once a fire is extinguished. Post-fire smoke purge systems are not intended or designed as life safety systems and are not required to meet the provisions of Section 909. Post-fire smoke purge systems shall be required in:

1.	High-rise buildings subject to Section 403.

2.	Buildings with any story exceeding 50,000 square feet (4645 m2) in floor area.

3.	Building with spaces exceeding 100 feet (30 480 mm) from natural ventilation openings. Natural ventilation openings shall consist of operable windows and doors of at least 5 percent of the floor area or roof vents per Section 910.

4.	High-piled stock or rack storage in accordance with the New York City Fire Code.

Exceptions: A post-fire smoke purge system is not required in Group R-2 occupancies where either of the following conditions exists:

1.	Openable windows. A [postfire] post-fire smoke purge system is not required where every habitable room located in dwelling units is provided with windows complying with Chapter 12 and all of the following:

1.1.	Minimum window area. Each required window shall provide at least 12 square feet (1.1 m2) of glazed area. The total area of all such windows shall not be less than 10 percent of the floor area of the room or space served.

1.2.	Minimum openable area. Each required window shall provide a minimum of 6 square feet (0.56 m2) of openable area. The total area of all such openings shall not be less than 5 percent of the floor area of the room or space served. In addition, each required openable area shall be:

1.2.1.	Located wholly at least 30 inches (762 mm) above the finished floor; and

1.2.2.	Fully openable to the minimum 6 square feet (0.56 m2), at all times and without limiting stops or devices. Such openings may be achieved through the use of double-hung, sliding, or similar types of windows. However, in the event of the use of casement-, hopper-, pivot-, or awning-type windows, such windows shall satisfy the requirements of this section only when they open to at least 75 degrees(1.22 rad).

1.3	Window guards.  This exception shall not apply where the type of window guards installed in compliance with Section 27-2043.1 of the Administrative Code and Section 131.15 of the New York City Health Code requires the installation of limiting devices or stops.

2.	Smokeproof enclosures. A post-fire smoke purge system is not required where all exits are constructed as smokeproof enclosures in accordance with Section [1022.9] 1023.11.

[916.2] 917.2 Post-fire smoke purge systems in occupancy groups other than R-2.

[916.2.1] 917.2.1 General design requirements. [Postfire] Post-fire smoke purge systems are permitted to use dedicated equipment, the normal building HVAC system or other openings and shall have the capability to exhaust smoke from occupied spaces. Smoke removal may be by either mechanical or natural ventilation, but shall be capable of removing cold smoke. Smoke removed from a space must be discharged to a safe location outside the building and shall not be recirculated into the building in accordance with the New York City Mechanical Code.

[916.2.2] 917.2.2 Exhaust capability. The system shall have an air supply and smoke exhaust capability that will provide a minimum of 6 air changes per hour or 1 cubic foot per minute per square foot (cfm/ft2) [[0.00508 m3/s·• m2)]] (0.00508 m3/s·• m2), whichever is greater. The system need not exhaust from all areas at the same time, but is permitted to be zoned based on the largest fire area served. For the purpose of calculating system size, the height of a compartment shall be considered to run from slab to slab and include the volume above suspended ceilings. Provisions shall be made for sufficient make-up air. The provisions may include operable windows, doors, building leakage, or mechanical systems. In buildings having occupied floors located less than 75 feet (22 860 mm) above the lowest level of Fire Department vehicle access, breakable windows may be utilized.

[916.2.3] 917.2.3 Operation. The post-fire smoke purge system shall be operated by manual controls that are part of the fire command center, in accordance with Section 911, or fire alarm control unit when a fire command center is not required. Such control center or panel shall display a graphic indicating the portions of the building served by each [postfire] post-fire smoke purge system. When a system is zoned into areas of operation less than the entire building, each zone shall have an individual control. Fire Department manual controls of [postfire] post-fire smoke purge systems shall not override the manual or automatic operation of the smoke control system. Such Fire Department manual controls shall override the fire shutdown signal from the fire alarm system.

917.2.4 Interior exit stairways or ramps or exit passageways in occupancies other than Group R-2. Interior exit stairways or ramps or exit passageways shall not be used as a portion of the post-fire smoke purge system in occupancies other than Group R-2. Doors in interior exit stairways or ramps or exit passageways shall not be permitted to be used as a portion of the post-fire smoke purge system. Air transfer and duct openings associated with the post-fire smoke purge system shall not be permitted in the interior exit stairway or ramp or exit passageway.

[916.3] 917.3 Post-fire smoke purge systems in occupancy Group R-2. Post-fire smoke purge systems in Group R-2 occupancies shall comply with either Section [916.3.1 or 916.3.2] 917.3.1 or 917.3.2. Smoke removed must be discharged to a safe location outside the building and shall not be recirculated into the building in accordance with the New York City Mechanical Code.

[916.3.1] 917.3.1 Stair ventilation. The top of all enclosed exit stairs shall be provided with a reversible fan system capable of introducing fresh air or exhausting air at a rate of 6 air changes per hour or 1 cubic foot per minute per square foot (cfm/ft2) [[0.00508 m3/s·• m2)]] (0.00508 m3/s·• m2), whichever is greater, based on the area of the largest floor. Such system shall be operated by manual controls that are part of the fire command center, as per Section 911, or fire alarm panel when a fire command center is not required. Such control center or panel shall display a graphic indicating the portions of the building served by each post-fire smoke purge system. The operation of such system shall be controlled by Fire Department personnel by manually opening stair doors at the appropriate story.

[916.3.2] 917.3.2 Corridor ventilation. The ducts and fans that provide fresh air supply to the public corridors in accordance with the New York City Mechanical Code shall be provided with reversible fans and duct sizes capable of introducing fresh air to or exhausting air from the corridor at a rate of 6 air changes per hour or 1 cubic foot per minute per square foot (cfm/ft2) [[0.00508 m3/s·• m2)]] (0.00508 m3/s·• m2), whichever is greater, based on the area of the largest apartment plus the area of the public corridor. Such system shall be operated by manual controls that are part of the fire command center, as per Section 911, or fire alarm panel when a fire command center is not required. Each floor to be ventilated shall be by individual controls. Such control center or panel shall display a graphic indicating the portions of the building served by each postfire smoke purge system.

[916.4] 917.4 Maintenance. The building owner shall maintain [postfire] post-fire smoke exhaust systems in good operational condition. Records of testing shall be maintained on the premises for inspection by the department and Fire Department personnel.

[SECTION BC 917]
[FIRE DEPARTMENT IN-BUILDING AUXILIARY 
RADIO COMMUNICATION SYSTEM (ARCS)]

[917.1 General. This section covers the design, installation and performance criteria of Fire Department In-Building Auxiliary Radio Communication System (ARCS). Where required to be installed by Section 403, Section 907, or the New York City Fire Code or where installed voluntarily, such systems shall be designed and installed in accordance with this section, NFPA 72 as modified in Appendix Q, the New York City Electrical Code and as per requirements set forth by the Fire Department.]

[917.1.1 Construction documents. Construction documents for ARCS shall be submitted for review and approval to the Fire Department prior to system installation. Construction documents shall include, but need not be limited to, all of the following:]

[1.	Type of radio equipment and antenna.]

[2.	Riser diagram and floor plans showing location of elements of the ARCS, including but not limited to building fire command center or fire alarm control panel, dedicated radio console, base station/s and all other critical system components such as antennas, amplifiers, cables as applicable.]

[3.	Legend of all ARCS symbols and abbreviations used.]

[4.	Location of primary and secondary power source.]

[5.	Specification and listing details for all equipment, devices and cables.]

[917.1.2 Acceptance testing, maintenance and operational testing. Acceptance testing, maintenance and operational testing of the ARCS shall be performed in accordance with the New York City Fire Code and rules promulgated by the Fire Department.]

[917.2 Instructions. Operating, testing and maintenance instructions and record drawings (“as-builts”) and detailed specifications of all the components shall be provided at an approved location.]

SECTION BC 918
GAS DETECTION SYSTEMS

918.1 Gas detection systems. Gas detection systems, including systems designed to detect flammable, toxic, asphyxiants and other gases, required by the New York City Construction Codes or the New York City Fire Code, shall comply with Sections 918.2 through 918.10 of this code.

918.2 Design and installation. Gas detection systems shall be designed and installed in accordance with this code, the New York City Electrical Code, and manufacturer’s instructions. Such systems shall be inspected, tested and maintained in accordance with the New York City Fire Code.

918.2.1 Construction documents. Construction documents for gas detection systems shall be submitted for review and approval to the Fire Department prior to system installation. Construction documents shall include, but not be limited to, the following:

1.	Gas detection system devices and equipment.

2.	Engineering evaluation.

3.	Items required by Section 907.1.1, as applicable.

918.3 Equipment. Gas detection system devices and equipment shall be designed for use with the particular gas being detected.

918.4 Reserved.

918.5 Emergency power. Gas detection systems shall be provided with emergency power in accordance with the New York City Fire Code and Chapter 27 of this code.

918.6 Sensor locations. Where leaking gases are expected to accumulate, sensors shall be installed in approved locations in accordance with the New York City Fire Code and NFPA 72.

918.7 Gas sampling. Gas detection systems shall perform continuous gas sampling. Sample analysis shall be processed immediately after sampling, except as follows:

1.	For HPM gases, sample analysis shall be performed at intervals not exceeding 30 minutes.

2.	For toxic gases, sample analysis shall be performed at intervals not exceeding 5 minutes in accordance with the Section 6004 of the New York City Fire Code.

3.	Where a less frequent or delayed sampling interval is approved by the Fire Commissioner.

918.8 System activation. Gas detection systems shall activate and initiate an alarm system in compliance with the requirements of Sections 918.8.1 and 918.8.2.

918.8.1 Activation thresholds. A gas detection system alarm shall be initiated when a sensor detects a concentration of gas exceeding the following thresholds unless otherwise specified in this code or the New York City Fire Code:

1.	For flammable gases, a gas concentration exceeding 25 percent of the lower flammability limit (LFL).

2.	For nonflammable gases, a gas concentration exceeding one-half of the immediately dangerous to life and health (IDLH) concentration.

918.8.2 Alarm signals. The gas detection system shall initiate a local alarm and transmit a signal to a constantly attended control station when a short-term hazard condition is detected. The alarm shall be both visible and audible and shall provide warning both inside and outside the area where gas is detected. The audible alarm shall be distinct from all other alarms.

918.8.3 Shutoff of gas supply. The gas detection system shall automatically close the shutoff valve at the source of gas supply piping and tubing related to the system being monitored for whichever gas is detected.

Exception: Automatic shutdown is not required for reactors utilized for the production of highly toxic or toxic compressed gases where such reactors comply with all of the following:

1.	Operated at pressures less than 15 pounds per square inch gauge (psig) (103.4 kPa).

2.	Constantly attended.

3.	Provided with readily accessible emergency shutoff valves.

918.8.4 Valve closure. The automatic closure of shutoff valves shall be in accordance with the following:

1.	When the gas-detection sampling point initiating the gas detection system alarm is within a gas cabinet or exhausted enclosure, the shutoff valve in the gas cabinet or exhausted enclosure for the specific gas detected shall automatically close.

2.	Where the gas-detection sampling point initiating the gas detection system alarm is within a gas room and compressed gas containers are not in gas cabinets or exhausted enclosures, the shutoff valves on all gas lines for the specific gas detected shall automatically close.

3.	Where the gas-detection sampling point initiating the gas detection system alarm is within a piping distribution manifold enclosure, the shutoff valve for the compressed container of specific gas detected supplying the manifold shall automatically close.

Exception: When the gas-detection sampling point initiating the gas detection system alarm is at a use location or within a gas valve enclosure of a branch line downstream of a piping distribution manifold, the shutoff valve in the gas valve enclosure for the branch line located in the piping distribution manifold enclosure shall automatically close.

918.9 Reserved.

918.10 Fire alarm system connections. Gas detection systems shall be connected to and monitored at the Fire Command Center or fire alarm control unit where required or provided. Where a Fire Command Center or fire alarm control unit is not required or provided, an approved gas detection system control panel or annunciator shall be installed at the building main front entrance. A gas detection system shall be monitored by a central supervising station. Gas detection supervisory and alarm signals shall be transmitted as separate and distinct signals to the central supervising station.

§11  Chapter 10 of the New York city building code, as amended by, sections BC 1012, BC 1017, BC 1019 and BC 1024 as added by, and sections BC 1013, BC 1014, BC 1015, BC 1016, BC 1018, BC 1020, BC 1021, BC 1022, BC 1023, BC 1025, BC 1026, BC 1027, BC 1028, BC 1029 and BC 1030 as renumbered and amended by local law number 141 for the year 2013, sections 28-1022.1 and 28-1022.8 as amended by and section 28-1022.8.5 as added by local law number 17 for the year 2014, and section 28-1009.4.2 as amended by local law number 51 for the year 2014, is amended to read as follows:

CHAPTER 10
MEANS OF EGRESS

SECTION BC 1001
ADMINISTRATION

1001.1 General. Buildings or portions thereof shall be provided with a means of egress system as required by this chapter. The provisions of this chapter shall control the design, construction and arrangement of means of egress components required to provide an approved means of egress from structures and portions thereof.

1001.2 Minimum requirements. It shall be unlawful to alter a building or structure in a manner that will reduce the number of exits or the minimum width or required capacity of the means of egress to less than required by this code.

1001.3 Maintenance. Means of egress shall be maintained in accordance with the New York City Fire Code.

1001.3.1 Workplace exits. Except as specifically provided for in this chapter, no employer or agent of such employer shall lock the doors of or otherwise prohibit exit from any workplace, when by so doing the health or safety of any employee, independent contractor or other individual working in such workplace may become endangered by fire or other hazardous condition. Refer to Article 307 of Title 28 of the Administrative Code.

[1001.4] 1001.3.2 Inadequate exits for existing structures. Every existing structure which is not provided with means of egress as required by this chapter and, in which the means of egress are, in the opinion of the commissioner, inadequate for the safety of the occupants, shall be provided with means of egress or fire protection as directed by the commissioner.

1001.4 Fire protection and emergency preparedness plans. Fire protection plans shall be provided for occupancies and buildings where required by Article 109 of the Administrative Code. Such fire protection plans shall comply with the applicable provisions of Section 28-109.3 of the Administrative Code. Emergency preparedness plans shall be provided for occupancies and buildings where required by the New York City Fire Code. Such emergency preparedness plans shall comply with the applicable provisions of Chapter 4 of the New York City Fire Code.

SECTION BC 1002
DEFINITIONS

1002.1 Definitions. [The following words and terms shall, for the purposes of this chapter and as used elsewhere in this code, have the meanings shown herein] This section contains terms defined elsewhere in the code, and terms with definitions that are specific to this section.

1002.1.1 Terms defined elsewhere in this code. The following terms are defined in Chapter 2:

ACCESSIBLE MEANS OF EGRESS. [A continuous and unobstructed way of egress travel from any accessible point in a building or facility to a public way. Such way of egress travel may include an assisted rescue path.]

AISLE. [An unenclosed exit access component that defines and provides a path of egress travel.]

AISLE ACCESSWAY.[That portion of an exit access that leads to an aisle.]

ALTERNATING TREAD DEVICE. [A device that has a series of steps between 50 and 70 degrees (0.87 and 1.22 rad) from horizontal, usually attached to a center support rail in an alternating manner so that the user does not have both feet on the same level at the same time.]

AREA OF RESCUE ASSISTANCE. [An area where persons unable to use stairways can remain temporarily to await instructions or assistance during emergency evacuation.]

ASSEMBLY SPACE.

ASSISTED RESCUE PATH. [A portion of the accessible means of egress which begins at the area of rescue assistance and terminates at the public way.]

BLEACHERS. [Tiered seating supported on a dedicated structural system and two or more rows high and is not a building element (see “Grandstand”).]

BREAKOUT.

[COLLECTING SAFE AREA. A safe area that receives occupants from the assembly space it serves, as well as from other safe areas.]

COMMON PATH OF EGRESS TRAVEL. [That portion of exit access which the occupants are required to traverse before two separate and distinct paths of egress travel to two exits are available. Paths that merge are common paths of travel. Common paths of egress travel shall be included within the permitted travel distance.]

CORRIDOR. [An enclosed exit access component that defines and provides a path of egress travel to an exit. Corridors shall be either interior or public.]

Corridor, interior. [A corridor that serves only one tenant. In Group E occupancies, corridors serving only one institution shall be deemed as serving a single tenant.]

Corridor, public. [A corridor that serves more than one tenant.]

CROSS AISLE. [An unenclosed exit access component in a place of assembly usually parallel to rows of seats, connecting aisles or connecting an aisle and an exit. For the purposes of this chapter, a cross aisle is not an aisle.]

DEAD END. [A portion of a corridor in which the travel to an exit is in one direction only.]

DOOR, BALANCED. [A door equipped with double-pivoted hardware so designed as to cause a semicounterbalanced swing action when opening.]

EGRESS COURT.[A court or yard which provides access to a public way for one or more exits.]

EMERGENCY ESCAPE AND RESCUE OPENING.[An operable window, door or other similar device that provides for a means of escape and access for rescue in the event of an emergency.]

EXIT. [That portion of a means of egress system, which is separated from other interior spaces of a building or structure by fire-resistance-rated construction and opening protectives as required to provide a protected path of egress travel between the exit access and the exit discharge. Exits include exterior exit doors at the level of exit discharge, vertical exit enclosures, exit passageways, exterior exit stairways, exterior exit ramps and horizontal exits, but do not include access stairs, aisles, exit access doors opening to corridors, or corridors.]

EXIT ACCESS. [That portion of a means of egress system that leads from any occupied portion of a building or structure to an exit.]

EXIT ACCESS DOORWAY. [A door or access point along the path of egress travel from an occupied room, area or space where the path of egress enters an intervening room, corridor, unenclosed exit access stair or unenclosed exit access ramp.]

EXIT ACCESS RAMP.

EXIT ACCESS STAIRWAY.

EXIT DISCHARGE. [That portion of a means of egress system between the termination of an exit and a public way.]

EXIT DISCHARGE, LEVEL OF.[The story at the point at which an exit terminates and an exit discharge begins.]

[EXIT ENCLOSURE. An exit component that is separated from other interior spaces of a building or structure by fire-resistance-rated construction and opening protectives, and provides for a protected path of egress travel in a vertical or horizontal direction to the exit discharge or the public way.]

EXIT, HORIZONTAL. [An exit that provides a path of egress travel from one building to an area in another building on approximately the same level, or a path of egress travel through or around a wall or partition to an area on approximately the same level in the same building, or a bridge or tunnel between two buildings, which affords safety from fire and smoke from the area of incidence and areas communicating therewith.]

EXIT PASSAGEWAY. [An exit component that is separated from other interior spaces of a building or structure by fire-resistance-rated construction and opening protectives, and provides for a protected path of egress travel in a horizontal direction to the exit discharge or the public way.]

EXTERIOR EXIT RAMP.

EXTERIOR EXIT STAIRWAY.

FIRE EXIT HARDWARE. [Panic hardware that is listed for use on fire door assemblies.]

FIXED SEATING.

FLIGHT. [A continuous run of rectangular treads, winders or combination thereof from one landing to another.]

FLOOR AREA, GROSS. [The floor area within the inside perimeter of the exterior walls of the building under consideration, exclusive of courts, without deduction for corridors, stairways, closets, the thickness of interior walls, columns or other features. The floor area of a building, or portion thereof, not provided with surrounding exterior walls shall be the usable area under the horizontal projection of the roof or floor above. The gross floor area shall not include interior courts.]

FLOOR AREA, NET. [The actual occupied area not including the thickness of walls, partitions, columns, furred-in spaces, fixed cabinets, equipment, and unoccupied accessory areas such as corridors, stairways, toilet rooms, mechanical rooms and closets.]

FOLDING AND TELESCOPIC SEATING.[Tiered seating having an overall shape and size that is capable of being reduced for purposes of moving or storing and is not a building element.]

GRANDSTAND. [Tiered seating supported on a dedicated structural system and two or more rows high and is not a building element (see “Bleachers”).]

GUARD. [A building component or a system of building components located at or near the open sides of elevated walking surfaces that minimizes the possibility of a fall from the walking surface to a lower level.]

HANDRAIL. [A horizontal or sloping rail intended for grasping by the hand for guidance or support.]

INTERIOR EXIT RAMP.

INTERIOR EXIT STAIRWAY.

LOW ENERGY POWER-OPERATED DOOR.

MEANS OF EGRESS. [A continuous and unobstructed path of vertical and horizontal egress travel from any occupied portion of a building or structure to a public way. A means of egress consists of three separate and distinct parts: the exit access, the exit and the exit discharge.]

MERCHANDISE PAD. [A merchandise pad is an area for display of merchandise surrounded by aisles, permanent fixtures or walls. Merchandise pads contain elements such as nonfixed and moveable fixtures, cases, racks, counters and partitions from which customers browse or shop.]

NOSING. [The leading edge of treads of stairs and of landings at the top of stairway flights.]

OCCUPANT LOAD. [The number of persons for which the means of egress of a building or portion thereof is designed.]

OPEN-ENDED CORRIDOR.

[OPEN EXTERIOR SPACE. A street or other public space; or a yard, court, or plaza open on one or more sides and unroofed or open on all sides, which provides egress to a street or public space.]

PANIC HARDWARE. [A door-latching assembly incorporating a device that releases the latch upon the application of a force in the direction of egress travel.] [Having the property of emitting light that continues for a length of time after excitation by visible or invisible light has been removed.]

POWER-ASSISTED DOOR.

POWER-OPERATED DOOR.

PUBLIC WAY. [A street, alley or other parcel of land open to the outside air leading to a street, that has been deeded, dedicated or otherwise permanently appropriated to the public for public use and which has a clear width and height of not less than 10 feet (3048 mm).]

RAMP. [A walking surface that has a running slope steeper than one unit vertical in 20 units horizontal (5-percent slope).]

REFUGE AREA. [A floor area to which egress is made through a horizontal exit.]

[SAFE AREA. An interior or exterior space that serves as a means of egress by providing a transitional area from, and that also serves as a normal means of entry to, an assembly space.]

SCISSOR [STAIR] STAIRWAY. [Two interlocking stairways providing two separate paths of egress located within one stairwell enclosure.]

[SEATING SECTION. An area of seating bounded on all sides by aisles, cross aisles, walls or partitions.]

SELF-LUMINOUS. [Illuminated by a self-contained power source, other than batteries, and operated independently of external power sources.]

SMOKE-PROTECTED ASSEMBLY SEATING.[Seating served by means of egress that is not subject to smoke accumulation within or under a structure.]

STAIR.[A change in elevation, consisting of two or more risers.]

STAIRWAY. [One or more flights of stairs, either exterior or interior, with the necessary landings and platforms connecting them, to form a continuous and uninterrupted passage from one level to another.]

[Stairway, exterior. A stairway that is open on at least one side, except for required structural columns, beams, handrails and guards. The adjoining open areas shall be either yards, courts or public ways. The other sides of the exterior stairway need not be open.]

[Stairway, interior. A stairway not meeting the definition of an exterior stairway.]

[Stairway, spiral. A stairway having a closed circular form in its plan view with uniform section-shaped treads attached to and radiating from a minimum-diameter-supporting column.]

STAIRWAY, SPIRAL.

[SUITE. A group of patient treatment rooms or patient sleeping rooms within Group I-2 occupancies where staff are in attendance within the suite, for supervision of all patients within the suite and the suite is in compliance with the requirements of Sections 1014.2.2 through 1014.2.7.]

WINDER.[A stair tread with nonparallel edges.]

1002.1.2 Definitions specific to this chapter. The following terms shall, for the purposes of this chapter, have the meanings shown herein:

COLLECTING SAFE AREA. A safe area that receives occupants from the assembly space it serves, as well as from other safe areas.

OPEN EXTERIOR SPACE. A street or other public space; or a yard, court, or plaza open on one or more sides and unroofed or open on all sides, which provides egress to a street or public space.

SAFE AREA. An interior or exterior space that serves as a means of egress by providing a transitional area from, and that also serves as a normal means of entry to, an assembly space.

SEATING SECTION. An area of seating bounded on all sides by aisles, cross aisles, walls or partitions.

SECTION BC 1003
GENERAL MEANS OF EGRESS

1003.1 Applicability. The general requirements specified in Sections 1003 through [1013] 1015 shall apply to all three elements of the means of egress system, in addition to those specific requirements for the exit access, the exit and the exit discharge detailed elsewhere in this chapter.

1003.2 Ceiling height. The means of egress shall have a ceiling height of not less than 7 feet, 6 inches (2286 mm).

Exceptions:

1.	Ceilings that are permitted to be less than 7 feet, 6 inches (2286 mm) in accordance with Section 1208.2.

2.	Ceilings of dwelling units and sleeping units within residential occupancies in accordance with Section 1208.2.

3.	Allowable projections in accordance with Section 1003.3.

4.	Stair headroom in accordance with Section [1009.2] 1011.3.

5.	Door height in accordance with Section [1008.1.1.3] 1010.1.3.

6.	Ramp headroom in accordance with Section [1010.5.2] 1012.5.2.

7.	The clear height of floor levels in vehicular and pedestrian traffic areas [in] of public and private parking garages in accordance with Section [406.2.2] 406.4.1.

8.	Areas above and below mezzanine floors in accordance with Section [505.1] 505.2.

1003.3 Protruding objects. Protruding objects on circulation paths shall comply with the requirements of Sections 1003.3.1 through 1003.3.4.

1003.3.1 Headroom. Protruding objects are permitted to extend below the minimum ceiling height required by Section 1003.2 [provided] where a minimum headroom of 84 inches (2134 mm) [shall be] is provided [for] over any walking surface, including walks, corridors, aisles and passageways. Not more than 50 percent of the ceiling area of a means of egress shall be reduced in height by protruding objects.

Exception: Door closers and stops shall not reduce headroom to less than 78 inches (1981 mm).

A barrier shall be provided where the vertical clearance is less than 80 inches (2032 mm) high. The leading edge of such a barrier shall be located 27 inches (686 mm) maximum above the floor.

1003.3.2 Post-mounted objects. A free-standing object mounted on a post or pylon shall not overhang that post or pylon more than 4 inches (102 mm) where the lowest point of the leading edge is more than 27 inches (686 mm) and less than 80 inches (2032 mm) above the walking surface. Where a sign or other obstruction is mounted between posts or pylons and the clear distance between the posts or pylons is greater than 12 inches (305 mm), the lowest edge of such sign or obstruction shall be 27 inches (686 mm) maximum or 80 inches (2032 mm) minimum above the finished floor or ground.

Exception: These requirements shall not apply to sloping portions of handrails between the top and bottom riser of stairs and above the ramp run.

1003.3.3 Horizontal projections.[Structural elements, fixtures or furnishings shall not project horizontally from either side] Objects with leading edges more than [4 inches (102 mm) over any walking surface between the heights of] 27 inches ([686] 685 mm) and not more than 80 inches ([2032] 2030 mm) above the [walking surface] floor shall not project horizontally more than 4 inches (102 mm) into the circulation path.

Exception: Handrails are permitted to protrude [4.5] 4½ inches (114 mm) from the wall.

1003.3.4 Clear width. Protruding objects shall not reduce the minimum clear width of accessible routes.

1003.4 Floor surface. Walking surfaces of the means of egress shall have a slip-resistant surface and be securely attached.

1003.5 Elevation change. Where changes in elevation of less than 12 inches (305 mm) exist in the means of egress, sloped surfaces shall be used. Where the slope is greater than one unit vertical in 20 units horizontal (5-percent slope), ramps complying with Section [1010] 1012 shall be used. Where the difference in elevation is 6 inches (152 mm) or less, the ramp shall be equipped with handrails or floor finish materials that contrast with adjacent floor finish materials.

Exceptions: At locations that are not required to be accessible by Chapter 11:

1.	A single step with a maximum riser height of 7 inches (178 mm) is permitted for buildings with occupancies in Groups F, H, R-2, R-3, S and U at exterior doors.

2.	A step with a single riser or a stair with two risers and a tread is permitted [provided that] where the risers and treads comply with Section [1009.4] 1011.5, the minimum depth of the tread is 13 inches (330 mm) and [at least] not less than one handrail complying with Section [1012] 1014 is provided within 30 inches (762 mm) of the centerline of the normal path of egress travel on the step or stair.

3.	A step is permitted in aisles serving seating that has a difference in elevation less than 12 inches (305 mm) provided that the risers and treads comply with Section [1028] 1029.13 and the aisle is provided with a handrail complying with Section [1028.13] 1029.15.

Throughout a story in a Group I-2 occupancy, any change in elevation in portions of the [exit access] means of egress that serve nonambulatory persons shall be by means of a ramp or sloped walkway.

1003.6 Means of egress continuity. The path of egress travel along a means of egress shall not be interrupted by [any] a building element other than a means of egress component as specified in this chapter. Obstructions shall not be placed in the minimum width or required [width] capacity of a means of egress component except projections permitted by this chapter. The minimum width or required capacity of a means of egress system shall not be diminished along the path of egress travel.

1003.7 Elevators, escalators and moving walks. Elevators, escalators and moving walks shall not be used as a component of a required means of egress from any other part of the building.

Exceptions:

1.	Elevators used as a component of an accessible means of egress in accordance with Section [1007.4] 1009.4.

2.	Elevators permitted to be used for occupant self-evacuation pursuant to Sections 403.5.2 and 403.6.2.

SECTION BC 1004
OCCUPANT LOAD

1004.1 Design occupant load. In determining means of egress requirements, the number of occupants for whom means of egress facilities shall be provided shall be established by the largest number computed in accordance with Section [1004.1.1] 1004.1.3, unless otherwise permitted by Section [1004.1.2] 1004.1.3.1, [1004.1.3] 1004.1.3.2 or 1004.2.[Where occupants from accessory areas egress through a primary space, the calculated occupant load for the primary space shall include the total occupant load of the primary space plus the number of occupants egressing through it from the accessory area.]

1004.1.1 Cumulative occupant loads. Cumulative occupant loads shall be determined in accordance with Sections 1004.1.1.1 and 1004.1.1.2.

1004.1.1.1 Cumulative occupant loads for interconnected spaces. Where the path of egress travel includes intervening rooms, areas or spaces, cumulative occupant loads shall be determined in accordance with this section.

1004.1.1.1.1 Intervening spaces or accessory areas. Where occupants egress from one or more rooms, areas or spaces through others, the design occupant load shall be the combined occupant load of interconnected accessory or intervening spaces. Design of egress path capacity shall be based on the cumulative portion of occupant loads of all rooms, areas or spaces to that point along the path of egress travel.

1004.1.1.1.2. Adjacent levels for mezzanines. That portion of the occupant load of a mezzanine with required egress through a room, area or space on an adjacent level shall be added to the occupant load of that room, area or space.

1004.1.1.1.3 Adjacent stories. Other than for the egress components designed for convergence in accordance with Section 1005.6, the occupant load from separate stories shall not be added.

1004.1.1.2 Cumulative occupant loads in Group R-2 occupancies. Rooms, areas or spaces that are accessory to a Group R-2 occupancy and that comply with the conditions below may have occupant loads calculated individually per room, area, or space, and be classified as Occupancy Group R-2.

1004.1.1.2.1 Maximum occupant load per room. The occupant load in each individual room, area and space, including those subject to Section 1004.1.1.1.1 where applicable, shall not exceed 74 persons.

1004.1.1.2.2. Separated rooms. Each individual room, area and space shall be separated from others by minimum 1-hour fire-resistance-rated fire barriers constructed in accordance with Section 707.  Opening protectives in accordance with Exception 3 of Section 707.6 shall not be permitted.

1004.1.1.2.3. Group R-2 accessory spaces as primary function on a story. Where the aggregate Group R-2 occupancy accessory area of all rooms, areas or spaces, including outdoor spaces that are not provided with independent means of egress and that do not converge into interior means of egress, exceed 50 percent of the building area of the story in which they are located, and the total number of occupants on such story exceeds 150 persons, the following conditions shall apply:

1.	The interior corridors or portions thereof serving such accessory spaces shall be constructed as public corridors in accordance with Table 1020.1.2 with 1-hour fire-resistance-rated fire barriers, and 2-hour fire-resistance-rated fire barriers where a dead-end corridor exceeds 40 feet (12 192 mm) in length;

2.	Access to the corridors shall be limited to those necessary for exit access through the corridor from normally occupied spaces.  Direct openings from the mechanical, electrical and other storage spaces shall not be permitted, except that access to the corridor may be provided through a vestibule constructed with fire barriers, with a minimum fire-resistance rating consistent with the required hourly rating for the corridor;

3.	Corridors or portions thereof serving such accessory spaces shall be sufficient to accommodate a total occupant load on the basis of 3 square feet (0.28 m2) per person;

4.	The minimum dimension of such corridors shall be sufficient to accommodate the total occupant load discharging into such corridors, but shall in no case be less than 5 feet (1524 mm) in minimum dimension; and

5.	In addition to Conditions 1 through 4 above, one of the following conditions shall be met:

5.1.	Each of the interior exit stairways and ramps serving such story shall be protected by a smokeproof enclosure in accordance with Section 909.20;

5.2.	The corridor or portions of the corridor serving the rooms, areas or spaces that are accessory to the Group R-2 occupancy shall be pressurized in accordance with requirements that are applicable to interior exit stairways. Connecting interior exit stairways need not be pressurized unless otherwise required by this code;

5.3.	All passenger elevators serving the rooms, areas, or spaces that are accessory to the Group R-2 occupancy shall comply with occupant self-evacuation elevator requirements in Section 3008.1 through 3008.11; or

5.4.	One additional exit stairway meeting the requirements of Sections 1009 and 1023 shall be provided in addition to the minimum number of exits required by Section 1006. The total width of any combination of remaining exit stairways with one exit stairway removed shall not be less than the total width required by Section 1005.3.

Rooms, areas or spaces that do not comply with the conditions in Sections 1004.1.1.2.1 and 1004.1.1.2.2, or Section 1004.1.1.2.3 where applicable, shall have occupant loads calculated cumulatively per story and be classified as Occupancy Group A.

1004.1.2 Multiple function occupant load. Where an area under consideration contains multiple functions having different occupant load factors, the design occupant load for such area shall be based on the floor area of each function calculated independently.

1004.1.3 Areas without fixed seating. The number of occupants shall be computed at the rate of one occupant per unit of area as prescribed in Table [1004.1.1] 1004.1.3. For areas without fixed seating, the occupant load shall be not [be] less than that number determined by dividing the floor area under consideration by the occupant [per unit of area] load factor assigned to the [functions] function of the space as set forth in Table [1004.1.1] 1004.1.3.

[1004.1.2] 1004.1.3.1 Modifications. Where the actual number of occupants of any space will be significantly lower than listed in Table [1004.1.1] 1004.1.3, the commissioner may establish a lower basis for the determination of the number of occupants.

[1004.1.3] 1004.1.3.2 Unlisted functions. Where data regarding the square feet area per person for a function is not listed in Table [1004.1.1] 1004.1.3, the occupant load shall be established by a registered design professional, subject to the approval of the commissioner.

TABLE [1004.1.1] 1004.1.3
MAXIMUM FLOOR AREA ALLOWANCES PER OCCUPANT

| FUNCTION OF SPACE | [FLOOR AREA IN SQ. FT. PER OCCUPANT] OCCUPANT LOAD FACTORa |
| --- | --- |
| Accessory storage areas, mechanical equipment room | 300 gross |
| Agricultural building | 300 gross |
| Aircraft hangars | 500 gross |
| Assembly Gaming floors (keno, slots, etc.) Exhibit gallery and [museums] museum | 11 gross 30 net |
| Assembly with fixed seats | See Section [1004.7] 1004.3 |
| Assembly without fixed seats Concentrated (chairs only – not fixed) Dance floor Dance floor (ballroom) Standing space Unconcentrated (tables and chairs) | 7 net 5 net 10 net 5 net 15 net |
| Bowling centers, allow 5 persons for each lane including 15 feet of runway, and for additional areas | 7 net |
| Business areas, including accessory areas on terraces and rooftops | 100 grossb,d |
| Courtrooms – other than fixed seating areas | 40 net |
| Day Care: Age under 6 months Age 6 months – 2 years Age 2 years – 6 years Age above 6 years | 50 net 40 net 30 net 50 net |
| Dormitories | 50 gross |
| Educational Classroom area Shops and other vocational room areas Kindergarten, and pre-kindergarten | 20 net 50 net 30 net |
| Exercise rooms | 50 gross |
| Gymnasiums | 15 net |
| Group H-5 Fabrication and manufacturing areas | 200 gross |
| Industrial areas | 100 gross |
| Institutional areas Inpatient treatment areas Outpatient areas Sleeping areas | 240 gross 100 gross 120 gross |
| Kitchens, commercial | 200 gross |
| Library Reading rooms Stack area | 50 net 100 gross |
| Locker rooms | 50 gross |
| Mall buildings – covered and open | See Section 402.8.2 |
| Mercantile Areas on other floors Basement and grade floor areas Storage, stock, shipping areas | 60 gross 30 gross 300 gross |
| Parking garages | 200 gross |
| Passenger terminal Baggage claim Baggage handling Concourse Passenger terminal or platform Waiting area (Standing) Waiting areas (Seated) | 20 gross 300 gross 100 gross 1.5 X C* 15 gross 5 net |
| Residential Within dwelling units Rooftop and terrace accessory to Groups R-2 and R-3 Indoor residential amenity spaces accessory to Group R-2 (concentrated)e Indoor residential amenity spaces accessory to Group R-2 (unconcentrated)e | 200 gross [within dwelling units] 200 grossb,c,d 15 net 50 net |
| Skating rinks, swimming pools Rink and pool Decks | 50 gross 15 gross |
| Stages and platforms | 15 net for performing area and 50 net remaining area |
| [Accessory storage areas, mechanical equipment room] | [300 gross] |
| Warehouses | 500 gross |

C*-capacity of all passenger vehicles that can be unloaded simultaneously.

For SI: 1 square foot = 0.0929 m2, 1 foot = 304.8 mm.

a.	Floor area in square feet per occupant.

b.	For the purposes of occupant load calculation, permanent fixtures and amenities such as shrubs, decorative pools, non-walkable paving surfaces, etc. may be deducted from the total floor area.

c.	A rooftop or terrace in Group R-2 or R-3 occupancies that is provided for the incidental, recreational use by the residential tenants residing in the same residential building.

d.	Where the maximum occupant load of the rooftop or terrace exceeds 74 persons based on occupant load calculations, a Place of Assembly Certificate of Operation is required pursuant to Section 28-117.1 of the Administrative Code and Item 1 of Section 303.7 of this code.

e.	To be used only when the occupant load for the function of the space is not listed elsewhere in Table 1004.1.3.

1004.2 Increased occupant load. The occupant load permitted in any building, or portion thereof, is permitted to be increased from that number established for the functions in Table [1004.1.1] 1004.1.3, provided that all other requirements of the code are also met based on such modified number and the occupant load shall not exceed one occupant per 5 square feet (0.47 m2) of occupiable floor space, except for safe areas as specified in Section 1029.19.3 and standee areas as specified in Section 1029.18. Where required by the commissioner, an approved aisle, seating or fixed equipment diagram substantiating any increase in occupant load shall be submitted. Where required by the commissioner, such diagram shall be posted.  Capacity signs indicating the increased, stated occupant load in accordance with Sections 1029.1.3 and 1029.1.4 shall be posted where required by the commissioner.

[1004.3 Posting of occupant load. Every room or space that is an assembly occupancy shall have the occupant load of the room or space posted in a conspicuous place, near the main exit or exit access doorway from the room or space. Posted signs shall be of an approved legible permanent design and shall be maintained by the owner or authorized agent. Such sign shall also comply with Section 1028.1.2.]

[1004.4 Exiting from multiple levels. Where exits serve more than one floor, only the occupant load of each floor considered individually shall be used in computing the required capacity of the exits at that floor, provided that the exit capacity shall not decrease in the direction of egress travel.]

[1004.5 Egress convergence. Where means of egress from floors above and below converge at an intermediate level, the capacity of the means of egress from the point of convergence shall not be less than the sum of the two floors.]

[1004.6 Mezzanine levels. The occupant load of a mezzanine level with egress onto a room or area below shall be added to that room or area’s occupant load, and the capacity of the exits shall be designed for the total occupant load thus established.]

[1004.7] 1004.3 Fixed seating. For areas having fixed seats and aisles, the occupant load shall be determined by the number of fixed seats installed therein. The occupant load for areas in which fixed seating is not installed, such as waiting spaces [and wheelchair spaces], shall be determined in accordance with Section [1004.1.1] 1004.1.3 and added to the number of fixed seats.

The occupant load of wheelchair spaces and the associated companion seat shall be based on one occupant for each wheelchair space and one occupant for the associated companion seat provided in accordance with Section 1108.2.3.

For areas having fixed seating without dividing arms, the occupant load shall be not [be] less than the number of seats based on one person for each 18 inches (457 mm) of seating length.

The occupant load of seating booths shall be based on one person for each 24 inches (610 mm) of booth seat length measured at the backrest of the seating booth.

[1004.8] 1004.4 Outdoor areas. Yards, patios, courts and similar outdoor areas accessible to and usable by the building occupants shall be provided with means of egress as required by this chapter. The occupant load of such outdoor areas shall be determined by the design professional subject to the approval of the commissioner. Where outdoor areas are to be used by persons in addition to the occupants of the building, and the path of egress travel from the outdoor areas passes through the building, means of egress requirements for the building shall be based on the sum of the occupant loads of the building plus the outdoor areas.

Exceptions:

1.	Outdoor areas used exclusively for service of the building need only have one means of egress.

2.	Both outdoor areas associated with Group R-3 and individual dwelling units of Group R-2.

[1004.9] 1004.5 Multiple occupancies. Where a building contains two or more occupancies, the means of egress requirements shall apply to each portion of the building based on the occupancy of that space. Where two or more occupancies utilize portions of the same means of egress system, those egress components shall meet the more stringent requirements of all occupancies that are served.

SECTION BC 1005
MEANS OF EGRESS [WIDTH] SIZING

1005.1 General. All portions of the means of egress system shall be sized in accordance with this section.

Exception: Aisles and aisle accessways in rooms or spaces used for assembly purposes complying with Section 1029.

1005.2 Minimum [required egress] width based on component. The minimum width, in inches (mm), of any means of egress [width] components shall be not [be] less than that [required by this section] specified for such component, elsewhere in this code. [The total width of means of egress in inches (mm) shall not be less than the total occupant load served by the means of egress multiplied by 0.3 inches (7.62 mm) per occupant for stairways and by 0.2 inches (5.08 mm) per occupant for other egress components. The width shall not be less than specified elsewhere in this code. Multiple means of egress shall be sized such that the loss of any one means of egress shall not reduce the available capacity to less than 50 percent of the required capacity. The maximum capacity required from any story of a building shall be maintained to the termination of the means of egress.]

[Exception: Means of egress complying with Section 1028.]

1005.3 Required capacity based on occupant load. The required capacity, in inches (mm), of the means of egress for any room, area, space or story shall be not less than that determined in accordance with Sections 1005.3.1 and 1005.3.2.

1005.3.1 Stairways. The capacity, in inches, of means of egress stairways shall be calculated by multiplying the occupant load served by such stairways by a means of egress capacity factor of 0.3 inch (7.6 mm) per occupant. Where stairways serve more than one story, only the occupant load of each story considered individually shall be used in calculating the required capacity of the stairways serving that story.

Exceptions:

1.	Facilities with smoke-protected assembly seating shall be permitted to use the capacity factors in Table 1029.6.2 indicated for stepped aisles for exit access or exit stairways where the entire path for means of egress from the seating to the exit discharge is provided with a smoke control system complying with Section 909.

2.	Facilities with outdoor smoke-protected assembly seating shall be permitted to the capacity factors in Section 1029.6.3 indicated for stepped aisles for exit access or exit stairways where the entire path for means of egress from the seating to the exit discharge is open to the outdoors.

1005.3.2 Other egress components. The capacity, in inches, of means of egress components other than stairways shall be calculated by multiplying the occupant load served by such component by a means of egress capacity factor of 0.2 inch (5.1 mm) per occupant.

Exceptions:

1.	Facilities with smoke-protected assembly seating shall be permitted to use the capacity factors in Table 1029.6.2 indicated for level or ramped aisles for means of egress components other than stairways where the entire path for means of egress from the seating to the exit discharge is provided with a smoke control system complying with Section 909.

2.	Facilities with outdoor smoke-protected assembly seating shall be permitted to the capacity factors in Section 1029.6.3 indicated for level or ramped aisles for means of egress components other than stairways where the entire path for means of egress from the seating to the exit discharge is open to the outdoors.

1005.4 Continuity. The minimum width or required capacity of the means of egress required from any story of a building shall not be reduced along the path of egress travel until arrival at the public way.

1005.5 Distribution of minimum width and required capacity. Where more than one exit, or access to more than one exit, is required, the means of egress shall be configured such that the loss of any one exit, or access to one exit, shall not reduce the available capacity or width to less than 50 percent of the required capacity or width.

1005.6 Egress convergence. Where the means of egress from stories above and below converge at an intermediate level, the capacity of the means of egress from the point of convergence shall be not less than the largest minimum width or the sum of the required capacities for the stairways or ramps serving the two adjacent stories, whichever is larger.

1005.7 Encroachment. Encroachments into the required means of egress width shall be in accordance with the provisions of this section.

[1005.2 Door encroachment] 1005.7.1 Doors. Doors, when fully opened, [and handrails] shall not reduce the required [means of egress] width by more than 7 inches (178 mm). Doors in any position shall not reduce the required width by more than one-half.

Exceptions:

1.	Surface-mounted latch release hardware shall be exempt from inclusion in the 7-inch maximum (178 mm) encroachment where both of the following conditions exist:

1.1.	The hardware is mounted to the side of the door facing away from the adjacent wall where the door is in the open position.

1.2.	The hardware is mounted not less than 34 inches (865 mm) nor more than 48 inches (1219 mm) above the finished floor.

2.	The restrictions on door swing shall not apply to doors within individual dwelling units and sleeping units of Group R-2 occupancies and within individual dwelling units of Group R-3 occupancies.

1005.7.2 Other projections. Handrail projections shall be in accordance with the provisions of Section 1014.8. Other nonstructural projections such as trim and similar decorative features shall be permitted to project into the required width [a maximum of] not more than 1½ inches (38 mm) on each side.

Exception: [The restrictions on a door swing shall not apply to doors within individual dwelling units and sleeping units of Group R-2 and dwelling units of Group R-3] Projections are permitted in corridors within Group I-2 in accordance with Section 407.4.3.

[1005.3 Door hardware encroachment. Surface-mounted latch release hardware shall be exempt from inclusion in the 7-inch (178 mm) maximum projection requirement of Section 1005.2 when:]

[1.	The hardware is mounted to the side of the door facing the corridor width when the door is in the open position; and]

[2.	The hardware is mounted not less than 34 inches (865 mm) or more than 48 inches (1220 mm) above the finished floor.]

1005.7.3 Protruding objects. Protruding objects shall comply with the applicable requirements of Section 1003.3.

SECTION BC 1006
NUMBER OF EXITS AND EXIT ACCESS DOORWAYS

1006.1 General. The number of exits or exit access doorways required within the means of egress system shall comply with the provisions of Section 1006.2 for spaces, including mezzanines, and Section 1006.3 for stories.

1006.2 Egress from spaces. Rooms, areas or spaces, including mezzanines, within a story or basement shall be provided with the number of exits or access to exits in accordance with this section.

1006.2.1 Egress based on occupant load and common path of egress travel distance. Two exits or exit access doorways from any space shall be provided where the design occupant load or the common path of egress travel distance exceeds the values listed in Table 1006.2.1.

Exception: Care suites in Group I-2 occupancies complying with Section 407.4.

TABLE 1006.2.1
SPACES WITH ONE EXIT OR EXIT ACCESS DOORWAY

| OCCUPANCY | MAXIMUM OCCUPANT LOAD OF SPACE | MAXIMUM COMMON PATH OF EGRESS TRAVEL DISTANCE (feet) |
| --- | --- | --- |
|  |  | Without Sprinkler System (feet) | With Sprinkler System (feet) |
|  |  | Occupant Load |  |
|  |  | OL ≤ 30 | OL > 30 |  |
| Ac, Ef, M | 74 | 75 | 75 | 75a |
| B | 74 | 100 | 75 | 100a |
| F | 49 | 75 | 75 | 100a |
| H-1, H-2, H-3 | 3 | NP | NP | 25b |
| H-4b, H-5b, I-1, I-3, I-4 | 10 | NP | NP | 75a |
| I-2d | See Section 407 | NP | NP | 75a |
| R-1 | 20 | NP | NP | 75a |
| R-2 | 20g | NP | NP | 125a |
| S | 29 | 100 | 75e | 100a |
| U | 74 | 100 | 75 | 75a |

For SI: 1 foot = 304.8 mm.

NP = Not Permitted.

a.	Buildings equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1 or 903.3.1.2. See Section 903 for occupancies where automatic sprinkler systems are permitted in accordance with Section 903.3.1.2.

b.	Group H occupancies equipped throughout with an automatic sprinkler system in accordance with Section 903.2.5.

c.	For a room or space used for assembly purposes having fixed seating, see Section 1029.8.

d.	For the travel distance limitations in Group I-2, see Section 407.4.

e.	The length of common path of egress travel distance in a Group S-2 open parking garage shall be not more than 100 feet (30 480 mm).

f.	Day care maximum occupant load is 10.

1006.2.1.1 Three or more exits or exit access doorways. Three exits or exit access doorways shall be provided from any space with an occupant load of 501 to 1,000. Four exits or exit access doorways shall be provided from any space with an occupant load greater than 1,000.

1006.2.2 Egress based on use. The numbers of exits or access to exits shall be provided in the uses described in Sections 1006.2.2.1 through 1006.2.2.5.

1006.2.2.1 Boiler, incinerator and furnace rooms. Two exit access doorways are required in boiler, incinerator and furnace rooms where the area is over 500 square feet (46 m2) and any fuel-fired equipment exceeds 400,000 British thermal units (Btu) (422 000 KJ) input capacity. Where two exit access doorways are required, one such doorway is permitted to be served by a fixed ladder or an alternating tread device. Exit access doorways shall be separated by a horizontal distance equal to one-half the length of the maximum overall diagonal dimension of the room.

1006.2.2.2 Refrigeration machinery rooms. Machinery rooms larger than 1,000 square feet (93 m2) with refrigeration units or systems having a refrigerant circuit containing more than 220 pounds (100 kg) of Group A1 refrigerant, or more than 30 pounds (14 kg) of any other group refrigerant, as classified in Section 1103.1 of the New York City Mechanical Code, shall have not less than two exits or exit access doors. Where two exit access doorways are required, one such doorway is permitted to be served by a fixed ladder or an alternating tread device. Exit access doorways shall be separated by a horizontal distance equal to one-half the maximum horizontal dimension of the room.

All portions of machinery rooms shall be within 150 feet (45 720 mm) of an exit or exit access doorway. An increase in exit access travel distance is permitted in accordance with Section 1017.1.

Doors shall swing in the direction of egress travel and shall be equipped with panic hardware, regardless of the occupant load served. Doors shall be tight fitting and self-closing.

1006.2.2.3 Refrigerated rooms or spaces. Rooms or spaces having a floor area larger than 1,000 square feet (93 m2) containing a refrigerant evaporator and maintained at a temperature below 68°F (20°C), shall have access to not less than two exits or exit access doorways.

Exit access travel distance shall be determined as specified in Section 1017.1, but all portions of a refrigerated room or space shall be within 150 feet (45 720 mm) of an exit or exit access doorway where such rooms are not protected by an approved automatic sprinkler system. Egress is allowed through adjoining refrigerated rooms or spaces.

Exception: Where using refrigerants in quantities limited to the amounts based on the volume set forth in the New York City Mechanical Code.

1006.2.2.4 Day care means of egress. Day care facilities, rooms or spaces that are classified under Occupancy Group E providing care for more than 10 children shall have access to not less than two exits or exit access doorways.

1006.2.2.5 Vehicular ramps. Vehicular ramps shall not be considered as an exit access ramp unless provided with pedestrian facilities along the ramp in accordance with Section 1012.1.

1006.3 Egress from stories or occupied roofs. The means of egress system serving any story, or occupied roof designed for human occupancy or use, shall be provided with the number of exits or access to exits based on the aggregate occupant load served in accordance with this section. The path of egress travel to an exit shall not pass through more than one adjacent story.

Each story or occupied roof designed for human occupancy or use above the second story of a building shall have not less than one interior or exterior exit stairway, or interior or exterior exit ramp. Where three or more exits or access to exits are required, not less than 50 percent of the required exits shall be interior or exterior exit stairways or ramps.

Exceptions:

1.	Interior exit stairways and interior exit ramps are not required in open parking garages where the means of egress serves only the open parking garage.

2.	Interior exit stairways and interior exit ramps are not required in outdoor facilities where all portions of the means of egress are essentially open to the outside.

1006.3.1 Egress based on occupant load. Each story or occupied roof designed for human occupancy or use shall have the minimum number of exits, or access to exits, as specified in Table 1006.3.1. A single exit or access to a single exit shall be permitted in accordance with Section 1006.3.2. The required number of exits, or exit access stairways or ramps providing access to exits, from any such story or occupied roof shall be maintained until arrival at the exit discharge or a public way.

TABLE 1006.3.1
MINIMUM NUMBER OF EXITS OR ACCESS TO EXITS PER STORY

| OCCUPANT LOAD (persons per story) | MINIMUM NUMBER OF EXITS (per story) |
| --- | --- |
| 1-500 | 2 |
| 501-1,000 | 3 |
| More than 1,000 | 4 |

1006.3.2 Single exits. A single exit or access to a single exit shall be permitted from any story or occupied roof designed for human occupancy or use where one of the following conditions exists:

1.	The occupant load, number of dwelling units and exit access travel distance do not exceed the values in Table 1006.3.2.

2.	Rooms, areas and spaces complying with Section 1006.2.1 with exits that discharge directly to the exterior at the level of exit discharge are permitted to have one exit or access to a single exit.

3.	Open or enclosed parking garages where vehicles are mechanically parked shall be permitted to have one exit provided such exit shall not be a vehicle ramp.

4.	Group R-3 occupancies shall be permitted to have one exit or access to a single exit.

5.	Individual single-story or multistory dwelling units shall be permitted to have a single exit or access to a single exit from the dwelling unit provided that both of the following criteria are met:

5.1.	The dwelling unit complies with Section 1006.2.1 as a space with one means of egress.

5.2.	Either the exit from the dwelling unit discharges directly to the exterior at the level of exit discharge, or the exit access outside the dwelling unit’s entrance door provides access to not less than two approved independent exits.

6.	Buildings of Occupancy Group R-2 where all of the following conditions are met:

6.1.	The building does not exceed four stories;

6.2.	The building contains not more than three dwelling units per story;

6.3.	The building is of construction Type I or II;

6.4.	The building does not exceed 2,500 square feet (232 m2) per story;

6.5.	Each dwelling unit has at least one window facing the street, or facing a lawful yard with open, unobstructed, and direct access to the street. Such yard or direct access shall be a minimum width equal to 25% of the vertical distance from the windowsill of the highest operable window, facing such yard or direct access, to the grade of such yard or direct access directly below such window, but shall in no case be less than 36 inches (914 mm) wide;

6.6.	The stairway extends to the roof surface through a stairway bulkhead complying with Section 1509.2, provided the roof has a slope not steeper than 20 degrees (0.35 rad), or the stairway is constructed against the street wall, with one window facing the street at each landing and access to the roof is provided via a scuttle with a stationary, noncombustible access ladder;

6.7.	The stairway is enclosed in 2-hour fire-rated walls with all exit doors leading into the stairway having at least 1½-hour fire rating; and

6.8.	The building is equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.2.

7.	Buildings of Occupancy Group R-2 of construction Type I or II not exceeding six stories and not exceeding 2,000 square feet (186 m2) per story.

TABLE 1006.3.2
STORIES WITH ONE EXIT OR ACCESS TO ONE EXIT

| STORY | OCCUPANCY | MAXIMUM OCCUPANT LOAD PER FLOOR | MAXIMUM TRAVEL DISTANCE (feet) |
| --- | --- | --- | --- |
| First story above grade plane or cellarf | A, Bb, Ec, Fb, M, U, Sb | 49 | 75 |
|  | H-2, H-3 | 3 | 25 |
|  | H-4, H-5, I, Re | 10 | 75 |
|  | Sa | 29 | 100 |
| Second story above grade plane | B, F, M, Sa | 29 | 75 |
|  | R-2d,e | NA | 50 |
| Third story above grade plane | R-2d,e | NA | 50 |

For SI: 1 foot = 304.8 mm.

NP = Not Permitted.

NA = Not Applicable.

a.	For the required number of exits for open or enclosed parking garages, see Section 1006.3.2, Item 3.

b.	Group B, F and S occupancies in buildings equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1 shall have a maximum travel distance of 100 feet.

c.	Day care occupancies shall have a maximum occupant load of 10.

d.	Maximum four dwelling units per floor.

e.	Buildings classified as Occupancy Group R-2 equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1 or 903.3.1.2 and provided with emergency escape and rescue openings in accordance with Section 1030.

f.	Limited to the cellar closest to grade plane.

1006.3.2.1 Mixed occupancies. Where one exit, or exit access stairway or ramp providing access to exits at other stories, is permitted to serve individual stories, mixed occupancies shall be permitted to be served by single exits provided each individual occupancy complies with the applicable requirements of Table 1006.3.2 for that occupancy. Where applicable, cumulative occupant loads from adjacent occupancies shall be considered in accordance with the provisions of Section 1004.1. In each story of a mixed occupancy building, the maximum number of occupants served by a single exit shall be such that the sum of the ratios of the calculated number of occupants of the space divided by the allowable number of occupants indicated in Table 1006.3.2 for each occupancy does not exceed one. Where dwelling units are located on a story with other occupancies, the actual number of dwelling units divided by four plus the ratio from the other occupancy does not exceed one.

1006.4 Open or enclosed parking garages. Open or enclosed parking garages shall not have less than two exits from each parking tier. An unenclosed vehicle ramp constructed in accordance with Section 1012.1 may serve as one of the required exits when provided with pedestrian facilities along the ramp. Such ramps serving as part of a nonaccessible means of egress in open or enclosed parking garages three stories or less in height and serving not more than one level below grade is permitted to comply with Section 1012.2, Exception 2.

Exception: One exit shall be permitted in parking garages complying with Item 3 of Section 1006.3.2.

SECTION BC 1007
EXIT AND EXIT ACCESS DOORWAY CONFIGURATION

1007.1 General. Exits, exit access doorways, and exit access stairways and ramps serving spaces, including individual building stories, shall be separated in accordance with the provisions of this section.

1007.1.1 Two exits or exit access doorways. Where two exits, exit access doorways, exit access stairways or ramps, or any combination thereof, are required from any portion of the exit access, they shall be placed a distance apart equal to not less than one-half of the length of the maximum overall diagonal dimension of the building or area to be served measured in a straight line between them. Stairs sharing any common wall, floor, ceiling, scissor stair assembly, or other enclosure shall be counted as one exit stairway.

Exceptions:

1.	Corridor measurements. Where interior exit stairways or ramps are interconnected by a 1-hour fire-resistance-rated corridor conforming to the requirements of Section 1020, the required exit separation shall be measured along the shortest direct line of travel within the corridor.

2.	Remote location in sprinklered buildings. Where a building is equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1 or 903.3.1.2, the separation distance shall be not less than one-third of the length of the maximum overall diagonal dimension of the area served.

3.	Group R-2 occupancies. In Group R-2 occupancies, where stairs are enclosed in walls having at least a 2-hour fire resistance rating and constructed of masonry or masonry equivalent in accordance with department rules:

3.1.	The exit doors to such stairs shall be placed a distance apart equal to no less than 15 feet (4572 mm); and

3.2.	Such stairs shall be permitted to share common walls, floors, ceilings or scissor stairs assemblies or other enclosures provided that the construction separating the stairs is also of at least a 2-hour fire-resistance rating and constructed of masonry or masonry equivalent in accordance with department rules.

4.	Group B occupancies. In Group B occupancies of construction Type I or II not exceeding 60 feet (18 288 mm) in height, not exceeding 2,000 square feet (186 m2) on any story and not exceeding a travel distance of 50 feet (15 240 mm) on any story, where stairs are enclosed in walls having at least a 2-hour fire-resistance rating and constructed of masonry or masonry equivalent in accordance with department rules:

4.1.	The exit doors to such stairs shall be placed a distance apart equal to no less than 15 feet (4572 mm); and

4.2.	Such stairs shall be permitted to share common walls, floors, ceilings or scissor stairs assemblies.

1007.1.1.1 Measurement point. The separation distance required in Section 1007.1.1 shall be measured in accordance with the following:

1.	The separation distance to exit or exit access doorways shall be measured to the center point of the required doorway.

2.	The separation distance to exit access stairways shall be measured to the center point of the closest riser.

3.	The separation distance to exit access ramps shall be measured to the center point of the start of the ramp run.

1007.1.2 Three or more exits or exit access doorways. Where access to three or more exits is required, not less than two exit or exit access doorways shall be arranged in accordance with the provisions of Section 1007.1.1. Additional required exit or exit access doorways shall be arranged a reasonable distance apart so that if one becomes blocked, the others will be available.

1007.1.3 Remoteness of exit access stairways or ramps. Where two exit access stairways or ramps provide the required means of egress to exits at another story, the required separation distance shall be maintained for all portions of such exit access stairways or ramps.

1007.1.3.1 Three or more exit access stairways or ramps. Where more than two exit access stairways or ramps provide the required means of egress, not less than two shall be arranged in accordance with Section 1007.1.3.

SECTION BC [1006] 1008
MEANS OF EGRESS ILLUMINATION

[1006.1] 1008.1 Means of egress illumination. Illumination shall be provided in the means of egress in accordance with Section 1008.2. Under emergency power, means of egress illumination shall comply with Section 1008.3.

1008.2 Illumination required. Exits, exit discharges and public corridors shall be illuminated at all times by either daylight or electric lighting fixtures. Exit access components shall be illuminated by either daylight or electric lighting fixtures at all times that the space served by the exit access component is occupied.

Exceptions:

1.	Occupancies in Group U.

2.	Aisle accessways in Group A.

3.	Dwelling units and sleeping units in Groups I-1, R-1, R-2 and R-3.

4.	Sleeping units of Group I occupancies.

5.	Areas beyond safe dispersal area where such areas are provided, and designed in accordance with Section [1027.6] 1028.5, Exceptions 1 through 5.

[1006.2] 1008.2.1 Illumination level under normal power. The means of egress illumination level shall be not [be] less than 1 [foot-candle] footcandle (11 lux) at the walking surface.

Exceptions:

1.	For auditoriums, theaters, concert or opera halls and similar assembly occupancies, the [illumination at the] externally illuminated walking surface is permitted to be reduced during performances to not less than 0.5 [foot-candle] footcandle (5.38 lux) for aisles and cross aisles, and 0.2 [foot-candle] footcandle (2.15 lux) for other portions of the space, provided that the required illumination is automatically restored upon activation of a premise’s fire alarm system where such system is provided. [Step lights shall be provided in accordance with Section 1028.11.4.]

2.	Safe areas in assembly occupancies shall be illuminated in accordance with Section [1028.17.3.2] 1029.19.3.2.

3.	Open exterior spaces used to receive occupants as Class 1 or 2 exits in assembly occupancies shall be illuminated in accordance with Section [1028.17.4] 1029.19.4.

4.	In exits in buildings that contain existing photoluminescent exit path markings tested in laboratory conditions with 2 [foot-candles] footcandles (22 lux) of activating illumination, the illumination level shall not be less than 2 [foot-candles] footcandles (22 lux).

1008.2.2 Exit discharge. In Group I-2 occupancies where two or more exits are required, on the exterior landings required by Section 1010.1.6, means of egress illumination levels for the exit discharge shall be provided such that failure of any single lighting unit shall not reduce the illumination level on that landing to less than 1 footcandle (11 lux).

[1006.2.1] 1008.2.3 Sensors and controls. Automatic, occupant sensor or photosensor lighting controls shall be permitted within means of egress, provided that the illumination level is not reduced to a level below the minimum requirements of Section [1006.2] 1008.2.1, and the switch controllers are equipped for fail-safe operation ensuring that if the sensor or control fails, the lighting levels will be at the levels required by Section [1006.2] 1008.2.1.

[1006.3 Illumination emergency power] 1008.3 Emergency power for illumination. The power supply for means of egress illumination shall normally be provided by the premise’s electrical supply.

1008.3.1 Rooms and spaces that require two or more means of egress. In the event of power supply failure in rooms and spaces that require two or more means of egress, an emergency electrical system shall automatically illuminate all of the following areas:

1.	Aisles.

2.	Corridors.

3.	Exit access stairways and ramps.

4.	Safe areas in assembly occupancies where required by Section 1029.19.3.2.

1008.3.2 Buildings that require two or more means of egress. In the event of power supply failure in buildings that require two or more means of egress, an emergency electrical system shall automatically illuminate all of the following areas:

1.	[Aisles and unenclosed egress] Interior exit access stairways [in rooms and spaces that require two or more means of egress] and ramps.

2.	[Corridors, exit enclosures and exit passageways.] Interior and exterior exit stairways and ramps.

3.	[Exterior egress components at other than their levels of exit discharge until exit discharge is accomplished for buildings required to have two or more exits.] Exit passageways.

4.	[Interior exit] Vestibules and areas on the level of discharge [elements, as permitted in Section 1027.1, in buildings required to have two or more exits] used for exit discharge in accordance with Section 1028.1.

5.	Exterior landings as required by Section [1008.1.6] 1010.1.6 for exit [discharge] doorways [in buildings required] that lead directly to [have two or more exits] the exit discharge.

1008.3.3 Specific rooms and spaces. In the event of power supply failure, an emergency electrical system shall automatically illuminate all of the following areas:

1.	Electrical equipment rooms containing electrical point of entry or building service disconnect.

2.	Fire command centers.

3.	Fire pump rooms.

4.	Generator rooms.

5.	Public restrooms with an area greater than 300 square feet (27.87 m2).

[1006.3.1 Emergency power source.] 1008.3.4 Duration. The emergency power system shall provide power for a duration of not less than 90 minutes and shall consist of storage batteries, unit equipment or an on-site generator. The installation of the emergency power system shall be in accordance with [Chapter 27] Section 2702.

[1006.3.2] 1008.3.5 [Performance of system] Illumination level under emergency power. Emergency lighting facilities shall be arranged to provide initial illumination that is [at least] not less than an average of 1 [foot-candle] footcandle (11 lux) and a minimum at any point of 0.1 [foot-candle] footcandle (1 lux) measured along the path of egress at floor level. Illumination levels shall be permitted to decline to 0.6 [foot-candle] footcandle [(6.46 lux)] (6 lux) average and a minimum at any point of 0.06 [foot-candle] footcandle [(0.646 lux)] (0.6 lux) at the end of the emergency lighting time duration. A maximum-to-minimum illumination uniformity ratio of 40 to 1 shall not be exceeded. In buildings that contain existing photoluminescent exit path markings tested in laboratory conditions with greater than 1 [foot-candle] footcandle (11 lux) of activating, the initial illumination shall not be less than that required for activating the approved photoluminescent illumination. In Group I-2 occupancies, failure of any single lighting unit shall not reduce the illumination level to less than 0.2 footcandle (2.2 lux).

[1006.4 Reserved.]

SECTION BC [1007] 1009
ACCESSIBLE MEANS OF EGRESS

[1007.1] 1009.1 Accessible means of egress required. Accessible means of egress shall comply with this section. Accessible spaces shall be provided with not less than one accessible means of egress. Where more than one means of egress are required by Section [1015.1] 1006.2 or [1021.1] 1006.3 from any accessible space, each accessible portion of the space shall be served by not less than two accessible means of egress.

Exceptions:

1.	Accessible means of egress are not required in alterations to prior code buildings where the level of alterations does not trigger full compliance of accessibility pursuant to Section 28-101.4 of the Administrative Code.

2.	One accessible means of egress is required from an accessible mezzanine level in accordance with Section [1007.3] 1009.3, [1007.4] 1009.4 or [1007.5] 1009.5.

3.	In assembly areas with [sloped] ramped aisles or stepped aisles, one accessible means of egress is permitted where the common path of egress travel is accessible and meets the requirements in Section [1028.8] 1029.8.

[1007.2] 1009.2 Continuity and components. Each required accessible means of egress shall be continuous to a public way and shall consist of one or more of the following components:

1.	Interior accessible routes complying with Section 1104.

2.	Area of rescue assistance complying with Section [1007.6] 1009.6.

3.	Interior exit stairways complying with Sections [1007.3] 1009.3 and [1022.1] 1023.

4.	Exit access stairways complying with Sections 1009.3 and 1019.3 or 1019.4.

[4.] 5.	Exterior exit stairways complying with Sections [1007.3] 1009.3 and [1026] 1027 and serving levels other than the level of exit discharge.

[5.] 6.	Elevators complying with Section [1007.4] 1009.4.

[6.] 7.	Platform lifts complying with Section [1007.5] 1009.5.

[7.] 8.	Horizontal exits complying with Section [1025] 1026.

[8.] 9.	Ramps complying with Section [1010] 1012.

[9.] 10.	Exit discharges complying with Section [1027] 1028.

[10.] 11.	Exterior accessible routes complying with Section 1104.

[11.] 12.	Exterior areas for assisted rescue complying with Section [1007.7] 1009.7 serving exits at the level of exit discharge.

13.	Unenclosed vertical exits serving safe areas in assembly occupancies permitted by Section 1029.19.3.1.

[1007.2.1] 1009.2.1 High-rise buildings. In high-rise buildings subject to Section 403, at least one required accessible means of egress shall be an elevator complying with Section [1007.4] 1009.4.

Exceptions:

1.	In buildings equipped throughout with an automatic sprinkler system installed in accordance with Section 903.3.1.1 or 903.3.1.2, the elevator shall not be required on floors provided with a horizontal exit and located at or above the level of exit discharge.

2.	In buildings equipped throughout with an automatic sprinkler system installed in accordance with Section 903.3.1.1 or 903.3.1.2, the elevator shall not be required on floors provided with a ramp conforming to the provisions of Section [1010] 1012.

3.	In buildings of [occupancy] Occupancy Group R-2 not subject to the requirements of emergency power in Section 403 of this code.

[1007.2.2] 1009.2.2 Exit discharge. Where an exit discharge is not accessible, an exterior area for assisted rescue shall be provided in accordance with Section [1007.7] 1009.7. An exterior area for assisted rescue shall not be required where an exit discharge is on an assisted rescue path from a stairway or an elevator.

[1007.2.3] 1009.2.3 Exterior exit stairway. Where an exit stairway is open to the exterior, the accessible means of egress shall include either an area of rescue assistance in accordance with Section [1007.6] 1009.6 or an exterior area for assisted rescue in accordance with Section [1007.7] 1009.7.

[1007.3 Exit stairways] 1009.3 Stairways. To be considered part of an accessible means of egress, [an exit access] a stairway [as permitted by Section 1016.1 or exit stairway] between stories shall have a clear width of 48 inches (1219 mm) minimum between handrails and shall either incorporate an area of rescue assistance within an enlarged floor-level landing or shall be accessed from [either] an area of rescue assistance complying with Section [1007.6 or a horizontal exit] 1009.6. Exit access stairways that connect levels in the same story are not permitted as part of an accessible means of egress.

[Unenclosed exit stairways as permitted by Section 1022.1 are permitted to be considered part of an accessible means of egress.]

Exceptions: The following exceptions apply to the requirements of clear width and area of rescue assistance, and do not supersede the other requirements of the accessible means of egress:

1.	[The area of rescue assistance is not required for open exit access or exit stairways as permitted by Sections 1016.1 and 1022.1 in buildings that are equipped throughout with an automatic sprinkler system installed in accordance with Section 903.3.1.1 or 903.3.1.2] Exit access stairways providing means of egress from mezzanines are permitted as part of an accessible means of egress.

2.	The clear width of 48 inches (1219 mm) between handrails and the area of rescue assistance is not required at exit access stairways as permitted by Section [1016.1] 1017 or exit stairways in buildings equipped throughout with an automatic sprinkler system installed in accordance with Section 903.3.1.1 or 903.3.1.2.

3.	[Areas of rescue assistance are not required at exit stairways in buildings equipped throughout with an automatic sprinkler system installed in accordance with Section 903.3.1.1 or 903.3.1.2.]

[4.]	The clear width of 48 inches (1219 mm) between handrails is not required for [enclosed] interior exit stairways accessed from a refuge area in conjunction with a horizontal exit.

4.	Areas of rescue assistance are not required at exit access stairways where two-way communication is provided at the elevator landing in accordance with Section 1009.8.

5.	Areas of rescue assistance are not required at stairways in buildings equipped throughout with an automatic sprinkler system installed in accordance with Section 903.3.1.1 or 903.3.1.2.

[5.] 6.	Areas of rescue assistance are not required at [exit] stairways serving open parking garages.

[6.] 7.	Areas of rescue assistance are not required for [smoke protected] smoke-protected assembly seating areas complying with Section [1028.6.2] 1029.6.2.

[7.] 8.	[The areas] Areas of rescue assistance are not required in Group R-2 occupancies.

9.	Areas of rescue assistance are not required for stairways accessed from a refuge area in conjunction with a horizontal exit.

[1007.4] 1009.4 Elevators. To be considered part of an accessible means of egress, an elevator shall comply with the emergency operation and signaling device requirements of Section 2.27 of ASME A17.1 as modified by Appendix K, and Section [1109.6] 1109.7 of this code. Standby power shall be provided in accordance with Chapter 27 and Section 3003. The elevator shall be accessed from [either] an area of rescue assistance complying with Section [1007.6 or a horizontal exit complying with Section 1025] 1009.6.

Exceptions:

1.	[Elevators] Areas of rescue assistance are not required [to be accessed from an area of rescue assistance or horizontal exit] at the elevator in open parking garages.

2.	[Elevators] Areas of rescue assistance are not required [to be accessed from an area of rescue assistance or horizontal exit] in buildings and facilities equipped throughout with an automatic sprinkler system installed in accordance with Section 903.3.1.1 or 903.3.1.2.

3.	[Elevators] Areas of rescue assistance are not required at elevators not required to be located in a shaft in accordance with Section [708.2 are not required to be accessed from an area of rescue assistance or horizontal exit] 712.

4.	[Elevators] Areas of rescue assistance are not required [to be accessed from an area of rescue assistance or horizontal exit for smoke] at elevators serving smoke-protected assembly seating areas complying with Section [1028.6.2] 1029.6.2.

5.	Areas of rescue assistance are not required for elevators accessed from a refuge area in conjunction with a horizontal exit.

[1007.5] 1009.5 Platform lifts. Platform (wheelchair) lifts shall [not] be permitted to serve as part of an accessible means of egress[, except] where allowed as part of a required accessible route in Section [1109.7] 1109.8, except for Item 10. Platform lifts shall be installed in accordance with ASME A18.1. Standby power for the platform lift shall be provided in accordance with Chapter 27 for platform lifts permitted to serve as part of an accessible means of egress.

[1007.5.1] 1009.5.1 Openness. Platform lifts on an accessible means of egress shall not be installed in a fully enclosed hoistway.

[1007.6] 1009.6 Areas of rescue assistance. Every required area of rescue assistance shall be accessible from the space it serves by one or more accessible means of egress components as listed in Section [1007.2] 1009.2.

1009.6.1 Travel distance. The maximum travel distance from any accessible space to an area of rescue assistance shall not exceed the exit access travel distance permitted for the occupancy in accordance with Section [1016.1] 1017.1.

1009.6.2 Stairway or elevator access. Every required area of rescue assistance shall have direct access to a stairway [within an exit enclosure] complying with Sections [1007.3] 1009.3 and [1022] 1023, or an elevator complying with Section [1007.4] 1009.4.

1009.6.2.1 Elevator lobby. Where an elevator lobby [is used] serves as an area of rescue assistance, the shaft and lobby shall comply with Section [1022.9 for smokeproof enclosures except where the elevators are in an area of rescue assistance, such lobby shall be part of a horizontal exit or protected by a smoke barrier] 713.14 and Chapter 30.

[Exceptions:]

[1.	A stairway serving an area of rescue assistance is not required to be enclosed where permitted in Sections 1016.1 and 1022.1.]

[2.	Smokeproof enclosure is not required for an elevator lobby used as an area of rescue assistance where the elevator is not required to be enclosed.]

[1007.6.1] 1009.6.3 Size. Each area of rescue assistance shall be sized to accommodate one wheelchair space of 30 inches by 48 inches (762 mm by 1219 mm) for each 200 occupants or portion thereof, based on the occupant load of the area of rescue assistance and areas served by the area of rescue assistance. Such wheelchair spaces shall not reduce the [required] means of egress minimum width or required capacity. Access to any of the required wheelchair spaces in an area of rescue assistance shall not be obstructed by more than one adjoining wheelchair space.

[1007.6.2] 1009.6.4 Separation. Each area of rescue assistance shall be separated from the remainder of the story by a smoke barrier complying with Section [710] 709 or a horizontal exit complying with Section [1025] 1026. Each area of rescue assistance shall be designed to minimize the intrusion of smoke.

[Exception:] Exceptions:

1.	Areas of rescue assistance located within an [exit] enclosure for interior exit stairways complying with Section 1023.

2.	Areas of rescue assistance in outdoor facilities where exit access is essentially open to the outside.

[1007.6.3] 1009.6.5 Two-way communication. Areas of rescue assistance shall be provided with a two-way communication system complying with Sections [1007.8.1] 1009.8.1 and [1007.8.2] 1009.8.2.

[1007.7] 1009.7 Exterior [area] areas for assisted rescue. [The exterior area] Exterior areas for assisted rescue [must be open to the outside air and meet the requirements of Section 1007.6.1. Separation walls shall comply with the requirements of Section 705 for exterior walls] shall be accessed by an accessible route from the area served.

Where [walls or openings are between the area for assisted rescue and the interior of the building, the building exterior walls within 10 feet (3048 mm) horizontally of a nonrated wall or unprotected opening shall have a fire-resistance rating of not less than 1 hour. Openings within such exterior walls shall be protected by opening protectives having a fire protection rating of not less than ¾ hour. This construction shall extend vertically from the ground to a point 10 feet (3048 mm) above the floor level of the area for assisted rescue or to the roof line, whichever is lower] the exit discharge does not include an accessible route from an exit located on the level of exit discharge to a public way, an exterior area of assisted rescue shall be provided on the exterior landing in accordance with Sections 1009.7.1 through 1009.7.4.

1009.7.1 Size. Each exterior area for assisted rescue shall be sized to accommodate wheelchair spaces in accordance with Section 1009.6.3.

1009.7.2 Separation. Exterior walls separating the exterior area of assisted rescue from the interior of the building shall have a minimum fire-resistance rating of 1 hour, rated for exposure to fire from the inside. The fire-resistance-rated exterior wall construction shall extend horizontally 10 feet (3048 mm) beyond the landing on either side of the landing or equivalent fire-resistance-rated construction is permitted to extend out perpendicular to the exterior wall 4 feet (1220 mm) minimum on the side of the landing. The fire-resistance-rated construction shall extend vertically from the ground to a point 10 feet (3048 mm) above the floor level of the area for assisted rescue or to the roof line, whichever is lower. Openings within such fire-resistance-rated exterior walls shall be protected in accordance with Section 716.

[1007.7.1] 1009.7.3 Openness. The exterior area for assisted rescue shall be [at least] open to the outside air. The sides other than the separation walls shall be not less than 50 percent open, and the open area [above the guards] shall be [so] distributed so as to minimize the accumulation of smoke or toxic gases.

[1007.7.2 Exterior exit stairway] 1009.7.4 Stairways. [Exterior exit stairways] Stairways that are part of the accessible means of egress for the exterior area for assisted rescue shall provide a clear width of 48 inches [(1219 mm)] (1220 mm) between handrails.

Exception: The clear width of 48 inches (1220 mm) between handrails is not required at stairways serving buildings equipped throughout with an automatic sprinkler system installed in accordance with Section 903.3.1.1 or 903.3.1.2.

[1007.8] 1009.8 Two-way communication. A two-way communication system complying with Sections 1009.8.1 and 1009.8.2 shall be provided at the landing serving each elevator [landing] or bank of elevators on each accessible floor that is one or more stories above or below the [story] level of exit discharge [complying with Sections 1007.8.1 and 1007.8.2].

Exceptions:

1.	Two-way communication systems are not required at the landing serving each elevator [landing] or bank of elevators where the two-way communication system is provided within areas of rescue assistance in accordance with Section [1007.6.3] 1009.6.5.

2.	Two-way communication systems are not required on floors provided with [exit] ramps conforming to the provisions of Section [1010] 1012.

3.	Two-way communication systems are not required at the landings serving only service elevators that are not designated as part of the accessible means of egress or serve as part of the required accessible route into a facility.

4.	Two-way communication systems are not required at the landings serving only freight elevators that are not designated as part of the accessible means of egress or serve as part of the required accessible route into a facility.

5.	Two-way communication systems are not required at the landing serving a private residence elevator.

[1007.8.1] 1009.8.1 System requirements. Two-way communication systems shall provide communication between each required location and the fire command center or a central control point location approved by the Fire Department. Where the central control point is not a constantly attended location, a two-way communication system shall have a timed automatic telephone dial-out capability to a monitoring location or 911. The two-way communication system shall include both audible and visible signals.

[1007.8.2] 1009.8.2 Directions. Directions for the use of the two-way communication system, instructions for summoning assistance via the two-way communication system and written identification of the location shall be posted adjacent to the two-way communication system. Signage shall comply with the ICC A117.1 requirements for visual characters.

[1007.9] 1009.9 Signage. Signage indicating special accessibility provisions shall be provided as shown:

1.	Each door providing access to an area of rescue assistance from an adjacent floor area shall be identified by a sign stating: AREA OF RESCUE ASSISTANCE.

2.	Each door providing access to an exterior area for assisted rescue shall be identified by a sign stating: EXTERIOR AREA FOR ASSISTED RESCUE.

Signage shall comply with the ICC A117.1 requirements for visual characters and include the International Symbol of Accessibility. Where exit sign illumination is required by Section [1011.2] 1013.3, the signs shall be illuminated. Additionally, [tactile] visual character, raised character and braille signage complying with ICC A117.1 shall be located at each door to an area of rescue assistance and exterior area for assisted rescue in accordance with Section [1011.3] 1013.4 of this code.

[1007.10] 1009.10 Directional signage. [Direction] Directional signage indicating the location of [the] all other means of egress and which of those are accessible means of egress shall be provided at the following:

1.	At exits serving a required accessible space but not providing an approved accessible means of egress.

2.	At elevator landings.

3.	Within areas of rescue assistance.

[1007.11] 1009.11 Instructions. In areas of rescue assistance and exterior areas for assisted rescue, instructions on the use of the area under emergency conditions shall be posted. Signage shall comply with the ICC A117.1 requirements for visual characters. The instructions shall include all of the following:

1.	Persons able to use the exit stairway do so as soon as possible, unless they are assisting others.

2.	Information on planned availability of assistance in the use of stairs or supervised operation of elevators and how to summon such assistance.

3.	Directions for use of the two-way communication system where provided.

SECTION BC [1008] 1010
DOORS, GATES AND TURNSTILES

[1008.1] 1010.1 Doors. Means of egress doors shall meet the requirements of this section. Doors serving a means of egress system shall meet the requirements of this section and Section [1020.2] 1022.2. Doors provided for egress purposes in numbers greater than required by this code shall meet the requirements of this section.

Means of egress doors shall be readily distinguishable from the adjacent construction and finishes such that the doors are easily recognizable as doors. Mirrors or similar reflecting materials shall not be used on means of egress doors. Means of egress doors shall not be concealed by curtains, drapes, decorations or similar materials.

[1008.1.1] 1010.1.1 Size of doors. The minimum width and height of each door opening shall be in accordance with this section.

[1008.1.1.1] 1010.1.1.1 Door width. The required capacity [minimum width] of each door opening shall be sufficient for the occupant load thereof and shall provide a minimum clear width of [not less than] 32 inches (813 mm). Clear openings of doorways with swinging doors shall be measured between the face of the door and the stop, with the door open 90 degrees (1.57 rad). Where this section requires a minimum clear width of 32 inches (813 mm) and a door opening includes two door leaves without a mullion, one leaf shall provide a clear opening width of 32 inches (813 mm). The maximum width of a swinging door leaf shall be 48 inches (1219 mm) nominal. Means of egress doors in a Group I-2 occupancy used for the movement of beds shall provide a clear width not less than 41½ inches (1054 mm).

Exceptions:

1	The minimum and maximum width shall not apply to door openings that are not part of the required means of egress in Group R-2 and R-3 occupancies.

2.	Door openings to resident sleeping units in Group I-3 occupancies shall have a clear width of not less than 28 inches (711 mm).

3.	Door openings to storage closets less than 10 square feet (0.93 m2) in area shall not be limited by the minimum width.

4.	Width of door leaves in revolving doors that comply with Section [1008.1.4.1] 1010.1.4.1 shall not be limited.

5.	[Except for] In other than Group R-1 occupancies, the minimum widths shall not apply to interior egress doors within a dwelling unit or sleeping unit that is not required to be an Accessible unit, Type B+NYC or Type B unit.

6.	Doors to walk-in freezers and coolers less than 1,000 square feet (93 m2) in area shall have a maximum width of 60 inches (1524 mm).

7.	In Group R-1 dwelling units or sleeping units not required to be Accessible units, the minimum width shall not apply to doors for showers or saunas.

[1008.1.1.2] 1010.1.1.2 Projections into clear width. There shall not be projections into the required clear width lower than 34 inches (864 mm) above the floor or ground. Projections into the clear opening width between 34 inches (864 mm) and 80 inches (2032 mm) above the floor or ground shall not exceed 4 inches (102 mm).

Exception: Door closers and door stops shall be permitted to be 78 inches (1980 mm) minimum above the floor.

[1008.1.1.3] 1010.1.1.3 Height. The height of doors shall be not [be] less than 80 inches (2032 mm).

Exceptions:

1.	Door openings within a dwelling unit or sleeping unit shall be not [be] less than 78 inches (1981 mm) in height.

2.	Exterior door openings in dwelling units and sleeping units, other than the required exit door, shall be not [be] less than 76 inches (1930 mm) in height.

[1008.1.2] 1010.1.2 Door swing. Egress doors shall be installed in accordance with this section.

[1008.1.2.1] 1010.1.2.1 Mounting. Egress doors shall be of the pivoted or side-hinged swinging type.

Exceptions:

1.	Private garages, office areas, factory and storage areas with an occupant load of 10 or less.

2.	Group I-3 occupancies used as a place of detention.

3.	Critical or intensive care patient rooms within suites of health care facilities.

4.	Doors within or serving a single dwelling unit in Groups R-2 and R-3.

5.	In other than Group H occupancies, revolving doors complying with Section [1008.1.4.1] 1010.1.4.1.

6.	In other than Group H occupancies, special purpose horizontal sliding [doors], accordion or folding door assemblies complying with Section [1008.1.4.3] 1010.1.4.3[are permitted in a means of egress].

7.	Power-operated doors in accordance with Section [1008.1.4.2] 1010.1.4.2.

8.	Doors serving a bathroom within an individual sleeping unit in Group R-1.

9.	In other than Group H occupancies, manually operated horizontal sliding doors are permitted in a means of egress from spaces with an occupant load of 10 or less.

[1008.1.2.2] 1010.1.2.2 Direction of swing. Doors shall swing in the direction of egress travel where serving:

1.	Group F or H occupancies.

2.	Rooms or spaces with an occupant load of [50] 75 or more persons.

3.	Rooms or spaces requiring more than one exit door.

4.	Automatic teller machines in accordance with Section 10-160 of the Administrative Code.

Exception: Doors need not swing in the direction of egress travel for exterior street floor exit doors from lobbies serving only Group R-2 or R-3 occupancies.

[1008.1.3] 1010.1.3 Door opening force. The force for pushing or pulling open interior swinging egress doors, other than fire doors, shall not exceed [5 pound] 5-pounds (22 N). These forces do not apply to the force required to retract latch bolts or disengage other devices that hold the door in a closed position. For other swinging doors, as well as sliding and folding doors, the door latch shall release when subjected to a 15-pound (67 N) force. The door shall be set in motion when subjected to a 30-pound (133 N) force. The door shall swing to a full-open position when subjected to a 15-pound (67 N) force.

1010.1.3.1 Location of applied forces. Forces shall be applied to the latch side of the door.

[1008.1.4] 1010.1.4 Special doors. Special doors and security grilles shall comply with the requirements of Sections [1008.1.4.1] 1010.1.4.1 through [1008.1.4.5] 1010.1.4.4.

[1008.1.4.1] 1010.1.4.1 Revolving doors. Revolving doors shall comply with the following:

1.	Revolving doors shall comply with BHMA A156.27 and shall be installed in accordance with the manufacturer’s instructions.

[1.] 2.	Each revolving door shall be capable of [collapsing into a book fold position with parallel egress paths providing] breakout in accordance with BHMA A156.27 and shall provide an aggregate width of not less than 36 inches (914 mm).

[2.] 3.	A revolving door shall not be located within 10 feet (3048 mm) of the foot [of] or top of [stairs] stairways or escalators. A dispersal area shall be provided between the [stairs] stairways or escalators and the revolving doors.

[3.] 4.	The revolutions per minute (rpm) for a revolving door shall not exceed [those shown in] the maximum rpm as specified in BHMA A156.27. Manual revolving doors shall comply with Table [1008.1.4.1] 1010.1.4.1(1). Automatic or power-operated revolving doors shall comply with Table 1010.1.4.1(2).

5.	An emergency stop switch shall be provided near each entry point of power or automatic operated revolving doors within 48 inches (1220 mm) of the door and between 24 inches (610 mm) and 48 inches (1220 mm) above the floor. The activation area of the emergency stop switch button shall be not less than 1 inch (25 mm) in diameter and shall be red.

[4.] 6.	Each revolving door shall have a side-hinged swinging door [which] that complies with Section [1008.1] 1010.1 in the same wall and within 10 feet (3048 mm) of the revolving door.

[5.] 7.	Revolving doors shall not be part of an accessible route required by Section [1007] 1009 and Chapter 11.

TABLE [1008.1.4.1] 1010.1.4.1(1)
MAXIMUM [REVOLVING] DOOR [SPEEDS] SPEED MANUAL REVOLVING DOORS

| [INSIDE DIAMETER (feet-inches)] REVOLVING DOOR MAXIMUM NORMINAL DIAMETER (FT-IN) | [POWER-DRIVEN-TYPE SPEED CONTROL (rpm)] | [MANUAL-TYPE SPEED CONTROL (rpm)] MAXIMUM ALLOWABLE REVOLVING DOOR SPEED (RPM) |
| --- | --- | --- |
| [6-6] 6-0 | [11] | 12 |
| 7-0 | [10] | 11 |
| [7-6] | [9] | [11] |
| 8-0 | [9] | 10 |
| [8-6] | [8] | [9] |
| 9-0 | [8] | 9 |
| [9-6] | [7] | [8] |
| 10-0 | [7] | 8 |

For SI: 1 inch = 25.4 mm, 1 foot = 304.8 mm.

TABLE 1010.1.4.1(2)
MAXIMUM DOOR SPEED AUTOMATIC OR 
POWER-OPERATED REVOLVING DOORS

| REVOLVING DOOR MAXIMUM NOMINAL DIAMETER (FT-IN) | MAXIMUM ALLOWABLE REVOLVING DOOR SPEED (RPM) |
| --- | --- |
| 8-0 | 7.2 |
| 9-0 | 6.4 |
| 10-0 | 5.7 |
| 11-0 | 5.2 |
| 12-0 | 4.8 |
| 12-6 | 4.6 |
| 14-0 | 4.1 |
| 16-0 | 3.6 |
| 17-0 | 3.4 |
| 18-0 | 3.2 |
| 20-0 | 2.9 |
| 24-0 | 2.4 |

For SI: 1 inch = 25.4 mm, 1 foot = 304.8 mm.

[1008.1.4.1.1.1] 1010.1.4.1.1 Egress component. A revolving door used as a component of a means of egress shall comply with Section [1008.1.4.1] 1010.1.4.1 and the following three conditions:

1.	Revolving doors shall not be given credit for more than 50 percent of the minimum width or required [egress] capacity.

2.	Each revolving door shall be credited with [no] a capacity based on not more than a 50-person [capacity] occupant load.

3.	Each revolving door shall [be capable of being collapsed when a] provide for egress in accordance with BHMA A156.27 with a breakout force of not more than 130 pounds (578 N) [is applied within 3 inches (76 mm) of the outer edge of a wing].

[1008.1.4.1.2] 1010.1.4.1.2 Other than egress component. A revolving door used as other than a component of a means of egress shall comply with Section [1008.1.4.1] 1010.1.4.1. The [collapsing] breakout force of a revolving door not used as a component of a means of egress shall not be more than 180 pounds (801 N).

Exception: A [collapsing] breakout force in excess of 180 pounds (801 N) is permitted if the collapsing force is reduced to not more than 130 pounds (578 N) when [at least] not less than one of the following conditions is satisfied:

1.	There is a power failure or power is removed to the device holding the door wings in position.

2.	There is an actuation of the automatic sprinkler system where such system is provided.

3.	There is an actuation of a smoke detection system [which] that is installed in accordance with Section 907 to provide coverage in areas within the building [which] that are within 75 feet (22 860 mm) of the revolving doors.

4.	There is an actuation of a manual control switch, in an approved location and clearly [defined, which] identified, that reduces the [holding] breakout force to [below the] not more than 130[-pound] pounds (578 N)[force level].

[1008.1.4.2] 1010.1.4.2 Power-operated doors. Where means of egress doors are operated or assisted by power,[such as doors with a photoelectric-actuated mechanism to open the door upon the approach of a person, or doors with power-assisted manual operation,] the design shall be such that in the event of power failure, the door is capable of being opened manually to permit means of egress travel or closed where necessary to safeguard means of egress. The forces required to open these doors manually shall not exceed those specified in Section [1008.1.3] 1010.1.3, except that the force to set the door in motion shall not exceed 50 pounds (220 N). The door shall be capable of swinging open from any position to the full width of the opening in which such door is installed when a force is applied to the door on the side from which egress is made. [Full-] Power-operated swinging doors, power-operated sliding doors and power-operated folding doors shall comply with BHMA A156.10. Power-assisted swinging doors and low-energy power-operated swinging doors shall comply with BHMA A156.19.

Exceptions:

1.	Occupancies in Group I-3.

2.	Horizontal sliding doors complying with Section [1008.1.4.3] 1010.1.4.3.

3.	For a biparting door in the emergency breakout mode, a door leaf located within a multiple-leaf opening shall be exempt from the minimum 32-inch (813 mm) single-leaf requirement of Section [1008.1.1] 1010.1.1, provided a minimum 32-inch (813 mm) clear opening is provided when the two biparting leaves meeting in the center are broken out.

[1008.1.4.3] 1010.1.4.3 [Horizontal] Special purpose horizontal sliding, accordion or folding doors. In other than Group H occupancies, special purpose horizontal sliding [doors], accordion or folding door assemblies permitted to be a component of a means of egress in accordance with Exception 6 to Section [1008.1.2.1] 1010.1.2.1 shall comply with all of the following criteria:

1.	The doors shall be power operated and shall be capable of being operated manually in the event of power failure.

2.	The doors shall be openable by a simple method from both sides without special knowledge or effort.

3.	The force required to operate the door shall not exceed 30 pounds (133 N) to set the door in motion and 15 pounds (67 N) to close the door or open it to the minimum required width.

4.	The door shall be openable with a force not to exceed 15 pounds (67 N) when a force of 250 pounds (1100 N) is applied perpendicular to the door adjacent to the operating device.

5.	The door assembly shall comply with the applicable fire protection rating and, where rated, shall be self-closing or [automatic-closing] automatic closing by smoke detection in accordance with Section [715.4.8.3] 716.5.9.3, shall be installed in accordance with NFPA 80 and shall comply with Section [715] 716 of this code.

6.	The door assembly shall have an integrated standby power supply.

7.	The door assembly power supply shall be electrically supervised.

8.	The door shall open to the minimum required width within 10 seconds after activation of the operating device.

9.	The door shall not be provided with a latch or lock other than panic hardware or fire exit hardware complying with Section 1010.1.10.

[1008.1.4.4 Access-controlled entrance doors. The exterior building entrance doors serving occupancies in Group A, B, E, M, R-1 or R-2 and entrance doors to tenant spaces in occupancies in Groups A, B, E, M, R-1 and R-2 are permitted to be equipped with an approved entrance and egress access control system which shall be installed in accordance with all of the following criteria:]

[1.	A sensor shall be provided on the egress side arranged to detect an occupant approaching the doors. The doors shall be arranged to unlock by a signal from or loss of power to the sensor.]

[2.	Loss of power to that part of the access control system which locks the doors shall automatically unlock the doors.]

[3.	The doors shall be arranged to unlock from a manual unlocking device located 40 inches to 48 inches (1016 mm to 1219 mm) vertically above the floor and within 5 feet (1524 mm) of the secured doors. Ready access shall be provided to the manual unlocking device and the device shall be clearly identified by a sign that reads “PUSH TO EXIT.” When operated, the manual unlocking device shall result in direct interruption of power to the lock—independent of the access control system electronics—and the doors shall remain unlocked for a minimum of 30 seconds.]

[4.	Activation of the building fire alarm system, if provided, shall automatically unlock the doors, and the doors shall remain unlocked until the fire alarm system has been reset.]

[5.	Activation of the building automatic sprinkler or fire detection system, if provided, shall automatically unlock the doors. The doors shall remain unlocked until the fire alarm system has been reset.]

[6.	Entrance doors in buildings with an occupancy in Group A, B, E or M shall not be secured from the egress side during periods that the building is open to the general public.]

[1008.1.4.5] 1010.1.4.4 Security grilles. In Groups B, M and S, horizontal sliding or vertical security grilles are permitted at the main entrance where the opening of such grilles are essential to the operation of the establishments. Such grilles shall be installed in accordance with the following criteria:

1.	Security grilles shall be openable from the inside without the use of a key or special knowledge or effort during periods that the space is occupied.

2.	The security grilles shall remain secured in the full-open position during the period of occupancy by the general public.

3.	Except as to buildings or structures classified in occupancy Group S, buildings or structures that have been designated as a landmark by the landmarks preservation commission or located in a historic district designated by such commission, on or after July 1, 2011, no security grille may be installed or replaced, nor shall the owner of a structure classified as a Group B or M occupancy or the operator of the business occupying such structure allow to be installed or replaced, a security grille to secure such property where the grille abuts the sidewalk, unless the grille, when closed, permits visibility from the sidewalk of at least 70 percent of the area covered by such grille.

4.	No later than July 1, 2026, all security grilles installed on buildings or structures classified in occupancy Groups B or M shall comply with the provisions of [paragraph] Item 3 of this section.

5.	Where two or more means of egress are required, not more than one-half of the exits or exit access doorways shall be equipped with horizontal sliding or vertical security grilles.

[1008.1.5] 1010.1.5 Floor elevation. There shall be a floor or landing on each side of a door. Such floor or landing shall be at the same elevation on each side of the door. Landings shall be level except for exterior landings, which are permitted to have a slope not to exceed 0.25 unit vertical in 12 units horizontal (2-percent slope).

Exceptions:

1.	Doors serving individual dwelling units in Groups R-2 and R-3 where the following apply:

1.1.	A door is permitted to open at the top step of an interior flight of stairs within the dwelling unit, provided the door does not swing over the top step.

1.2.	Screen doors and storm doors are permitted to swing over stairs or landings.

2.	Exterior doors as provided for in Section 1003.5, Exception 1, and Section [1020.2] 1022.2, which are not on an accessible route.

3.	In Group R-3 occupancies not required to be Accessible units, Type B+NYC units or Type B units, the landing at an exterior doorway shall be not [be] more than 7¾ inches (197 mm) below the top of the threshold, provided the door, other than an exterior storm or screen door, does not swing over the landing.

4.	Variations in elevation due to differences in finish materials, but not more than [0.5]½ inch (12.7 mm).

5.	Exterior spaces of Type B+NYC units and Type B units where permitted pursuant to the exception to Section 1107.4.

6.	Doors serving equipment spaces not required to be accessible in accordance with Section 1103.2.9 and serving an occupant load of five or less shall be permitted to have a landing on one side to be not more than 7 inches (178 mm) above or below the landing on the egress side of the door.

[1008.1.6] 1010.1.6 Landings at doors. Landings shall have a width not less than the width of the stairway or the door, whichever is greater. Doors in the fully open position shall not reduce a required dimension by more than 7 inches (178 mm). At any stairway landing, or when a door landing serves an occupant load of 50 or more, doors in any position shall not reduce the landing to less than 75 percent of its required width. Landings shall have a length measured in the direction of travel of not less than 44 inches (1118 mm).

Exceptions:

1.	Landing length in the direction of travel in Groups R-3 and U and within individual units of Group R-2 need not exceed 36 inches (914 mm).

2.	In Group R-2 occupancies, where 36 inches wide stairways are permitted pursuant to Section [1009.1] 1011.2, Exception 1.2, such stairway landing length in the direction of travel shall be permitted to be not less than 36 inches (914 mm) or the width of the stairway, whichever is greater. Doors opening onto such stairway landings shall not reduce the landing width.

[1008.1.7] 1010.1.7 Thresholds. Thresholds at doorways shall not exceed [0.75]¾ inch (19.1 mm) in height above the finished floor or landing for sliding doors serving dwelling units or [0.5]½ inch (12.7 mm) above the finished floor or landing for other doors. Raised thresholds and floor level changes greater than [0.25]¼ inch (6.4 mm) at doorways shall be beveled with a slope not greater than one unit vertical in two units horizontal (50-percent slope).

[Exception:] Exceptions:

1.	[The threshold height shall be limited to 7.75 inches (197 mm) where the] In occupancy [is] Group R-2 or R-3[; the door is an], threshold heights for sliding and side-hinged exterior [door that is not a component] doors shall be permitted to be up to 7¾ inches (197 mm) in height if all of the following apply:

1.1.	The door is not part of the required means of egress[; the door, other than an exterior storm or screen door, does].

1.2.	The door is not [swing over the landing or step; and the doorway is not on] part of an accessible route as required by Chapter 11 [and].

1.3.	The door is not part of an Accessible unit, Type B+NYC unit or Type B unit.

1.4.	The exterior door, other than a storm or screen door,  does not swing over the landing or step.

2.	In Type B+NYC units and Type B units, where permitted pursuant to the exception to Section 1107.4, the threshold height on the exterior side of the door shall not exceed 4¾ inches (120 mm) in height above the exterior deck, patio or balcony for sliding doors or 4½ inches (114 mm) above the exterior deck, patio or balcony for other doors.

[1008.1.8] 1010.1.8 Door arrangement. Space between two doors in a series shall be 48 inches (1219 mm) minimum plus the width of a door swinging into the space. Doors in series shall swing either in the same direction or away from the space between the doors.

Exceptions:

1.	The minimum distance between horizontal sliding power-operated doors in a series shall be 48 inches (1219 mm).

2.	Storm and screen doors serving individual dwelling units in Groups R-2 and R-3 need not be spaced 48 inches (1219 mm) from the other door.

3.	Doors within individual dwelling units in Group R-3.

4.	Doors within individual dwelling units in Group R-2 that are not required to comply with Section 1107.

5.	Exterior doors in vestibules in Group R-2 occupancies shall not be required to swing either in the same direction or away from the space between doors provided that the 48-inch (1219 mm) minimum space between door swings is maintained.

[1008.1.9] 1010.1.9 Door operations. Except as specifically permitted by this section, egress doors shall be readily openable from the egress side without the use of a key or special knowledge or effort.

[1008.1.9.1] 1010.1.9.1 Hardware. Door handles, pulls, latches, locks and other operating devices on doors required to be accessible by Chapter 11 shall not require tight grasping, tight pinching or twisting of the wrist to operate.

[1008.1.9.2] 1010.1.9.2 Hardware height. Door handles, pulls, latches, locks and other operating devices shall be installed 34 inches (864 mm) minimum and 48 inches (1219 mm) maximum above the finished floor. Locks used only for security purposes and not used for normal operation are permitted at any height.

Exception: Access doors or gates in barrier walls and fences protecting pools, spas and hot tubs shall be permitted to have operable parts in compliance with Section 3109.4.2 or 3109.5.1.7, as applicable.

[1008.1.9.3] 1010.1.9.3 Locks and latches. Locks and latches shall be permitted to prevent operation of doors where any of the following [exists] exist:

1.	Places of detention or restraint.

2.	Places where extra safeguards are required such as banks, museums, and jewelry stores subject to the approval of the commissioner and provided the locks are equipped with electrical release devices for remote control in case of emergencies. However, museums shall be subject to further special review by the commissioner and Fire Commissioner.

3.	Main entrances in Occupancy Groups B, M, and S as permitted by Section [1008.1.3.5] 1010.1.4.4.

4.	Doors from individual dwelling or sleeping units of Group R occupancies having an occupant load of 10 or less are permitted to be equipped with a night latch, dead bolt or security chain, provided such devices are openable from the inside without the use of a key or tool.

5.	Doors serving Group R-2 occupancies as required by Section [1008.4] 1010.4.

6.	In educational occupancies classified in Occupancy Group B or E, and college or student dormitories in Group R-1, [Stairways] stairways leading from the top floor to a roof may be provided with locked wire mesh gates openable by key [in Occupancy Group E].

7.	On roofs that are not intended to be accessed by occupants other than building maintenance personnel, the [The] use of a hook and eye closing device or other similar non-self-locking devices on the [inside] stairway side of all doors openable without the use of a key or special knowledge to roofs shall be permitted.

[7] 8.	Fire doors after the minimum elevated temperature has disabled the unlatching mechanism in accordance with listed fire door test procedures.

[1008.1.9.4] 1010.1.9.4 Bolt locks. Manually operated flush bolts or surface bolts are not permitted.

Exceptions:

1.	On doors not required for egress in individual dwelling units or sleeping units.

2.	Where a pair of doors serves a storage or equipment room, manually operated edge- or surface-mounted bolts are permitted on the inactive leaf.

3.	Where a pair of doors serves an occupant load of less than 75 persons in a Group B, F or S occupancy, manually operated edge- or surface-mounted bolts are permitted on the inactive leaf. The inactive leaf shall not contain [no] doorknobs, panic bars or similar operating hardware.

4.	Where a pair of doors serves a Group B, F or S occupancy, manually operated edge- or surface-mounted bolts are permitted on the inactive leaf provided such inactive leaf is not needed to meet egress [width] capacity requirements and the building is equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1. The inactive leaf shall [contain no] not contain doorknobs, panic bars or similar operating hardware.

5.	Where a pair of doors serves patient care rooms in Group I-2 occupancies, self-latching edge- or surface-mounted bolts are permitted on the inactive leaf provided that the inactive leaf is not needed to meet egress [width] capacity requirements and the inactive leaf [contains no] shall not contain doorknobs, panic bars or similar operating hardware.

[1008.1.9.5] 1010.1.9.5 Unlatching. The unlatching of any door or leaf shall not require more than one operation.

Exception: More than one operation is permitted for unlatching doors in the following locations:

1.	Places of detention or restraint.

2.	Where manually operated bolt locks are permitted by Section [1008.1.9.4] 1010.1.9.4.

3.	Doors from individual dwelling units and sleeping units of Group R occupancies as permitted by Section [1008.1.9.3] 1010.1.9.3, Items 4 and 5.

[1008.1.9.5.1] 1010.1.9.5.1 Closet and bathroom doors in certain Group R occupancies. In community residences or intermediate-care facilities classified as Group R-1, R-2 or R-3 occupancies pursuant to Section [308.2.2] 308.3.2, Exception 1, 2 or 3, within such facilities, closet doors that latch in the closed position shall be openable from inside the closet, and bathroom doors that latch in the closed position shall be capable of being unlocked from the ingress side.

[1008.1.9.6 Special locking arrangements in Group I-2. Subject to special review and approval by the commissioner, approved, listed, delayed approved, listed, delayed egress locks may be permitted on doors serving spaces in a Group I-2 occupancy where the clinical needs of persons receiving care require such locking.]

1010.1.9.6 Controlled egress doors in Groups I-1 and I-2. Electric locking systems, including electro-mechanical locking systems and electromagnetic locking systems, shall be permitted to be locked in the means of egress in Group I-1 or I-2 occupancies where the clinical needs of persons receiving care require their containment. [Delayed] Controlled egress [locks may] doors shall be permitted in such occupancies where the building is equipped throughout with an [automatic] automatic sprinkler system in accordance with Section 903.3.1.1 or an approved automatic smoke or heat [detection] detection system installed in accordance with Section 907, provided that the doors [unlock] are installed and operate in accordance with [Items 1 through 6 below. A building occupant shall not be required to pass through more than one door equipped with a delayed egress lock before entering an exit.] all of the following:

1.	The [doors] door locks shall unlock [upon] on actuation of the automatic sprinkler system or automatic fire detection system.

2.	The [doors] door locks shall unlock [upon] on loss of power controlling the lock or lock mechanism.

3.	The door [locks] locking system shall be installed to have the capability of being unlocked by a [signal from] switch located at the fire command center, a nursing station or other approved location. The switch shall directly break power to the lock.

4.	A building occupant shall not be required to pass through more than one door equipped with a controlled egress locking system before entering an exit.

5.	The procedures for [the operation(s) of the unlocking system] unlocking the doors shall be described and approved as part of the emergency planning and preparedness required by [Chapter 4 of] the New York City Fire Code.

[5.] 6.	All clinical staff shall have the keys, codes or other means necessary to operate the locking [devices] systems.

[6.] 7.	Emergency lighting shall be provided at the door.

8.	The door locking system units shall be listed in accordance with UL 294.

[Exception:] Exceptions:

1.	Items 1 through [3] 4 shall not apply to doors to areas [where] occupied by persons who, because of clinical needs, require restraint or containment as part of the function of a [mental hospital] psychiatric treatment area.

2.	Items 1 through 4 shall not apply to doors to areas where a listed egress control system is utilized to reduce the risk of child abduction from nursery and obstetric areas of a Group I-2 hospital.

[1008.1.9.7] 1010.1.9.7 Delayed egress [locks] locking systems. Subject to special review and approval by the commissioner, approved, listed, delayed egress [locks] locking systems may be permitted on doors serving spaces where extra safeguards are required in buildings that are equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1 or an approved automatic smoke or heat detection system installed in accordance with Section 907, provided that the doors unlock in accordance with Items 1 through [6] 8 below.[A building occupant shall not be required to pass through more than one door equipped with a delayed egress lock before entering an exit.]

1.	The [doors unlock] delay electronics of the delayed egress locking system shall deactivate upon actuation of the automatic sprinkler system or automatic fire detection system, allowing immediate, free egress.

2.	The [doors unlock] delay electronics of the delayed egress locking system shall deactivate upon loss of power controlling the lock or lock mechanism, allowing immediate free egress.

3.	The [door locks] delayed egress locking system shall have the capability of being [unlocked by a signal from] deactivated at the fire command center and other approved locations.

4.	[The initiation of] An attempt to egress shall initiate an irreversible process [which will release the latch] that shall allow such egress in not more than 15 seconds when a [force of] physical effort of 15 pounds (67N) is applied to the egress side door hardware for not more than 3 seconds [15 pounds (67 N) is applied for 1 second to the release device]. Initiation of the irreversible process shall activate an audible signal in the vicinity of the door. Once the [door lock has] delay electronics have been [released by] deactivated, rearming the [application of force to the releasing device, relocking] delay electronics shall be by manual means only. Except [that] where approved by the department, a delay [in releasing the latch] of not more than 30 seconds is permitted on a delayed egress door.

5.	The egress path from any point shall not pass through more than one delayed egress locking system. Except where approved by the department, in Group I-2 or I-3 occupancies, the egress path from any point in the building shall pass through not more than two delayed egress locking systems provided the combined delay does not exceed 30 seconds.

6.	A sign shall be provided on the door and shall be located above and within 12 inches (305 mm) of the [release device reading] door exit hardware.[:] Except where approved by the department, in Group I occupancies, the installation of a sign is not required where care recipients who because of clinical needs require restraint or containment as part of the function of the treatment  area.

6.1.	For doors that swing in the direction of egress, the sign shall read: PUSH UNTIL ALARM SOUNDS. DOOR CAN BE OPENED IN 15 SECONDS. Except [that] where [a delay in releasing the latch of] not more than 30 seconds is permitted on a delayed egress door is approved by the department, such sign shall read: PUSH UNTIL ALARM SOUNDS. DOOR CAN BE OPENED IN [15] 30 SECONDS.

6.2.	For doors that swing in the opposite direction of egress, the sign shall read: PULL UNTIL ALARM SOUNDS. DOOR CAN BE OPENED IN 15 SECONDS. Except where not more than 30 seconds is permitted on a delayed egress door is approved by the department, such sign shall read: PULL UNTIL ALARM SOUNDS. DOOR CAN BE OPENED IN 30 SECONDS.

6.3.	The sign shall comply with the visual character requirements in ICC A117.1.

[6.] 7.	Emergency lighting shall be provided [at] on the egress side of the door.

8.	The delayed egress locking system units shall be listed in accordance with UL 294.

Exceptions:

1.	Delayed egress [locks] locking systems shall not be permitted in buildings or spaces in Group A, E, F and H occupancies. However, in museums, delayed egress locks may be installed on exit doors subject to special review by the commissioner and Fire Commissioner.

2.	Places of detention or restraints in Group I-3 are permitted to install delayed egress [locks] locking systems without the special review by the commissioner, provided that the installation complies with all of the other requirements of this section.

1010.1.9.8 Sensor release of electrically locked egress doors. The electric locks on sensor released doors located in a means of egress in buildings with an occupancy in Group A, B, E, M, R-1 or R-2 and entrance doors to tenant spaces in occupancies in Group A, B, E, M, R-1 or R-2 are permitted where installed and operated in accordance with all of the following criteria:

1.	The sensor shall be installed on the egress side, arranged to detect an occupant approaching the doors. The doors shall be arranged to unlock by a signal from or loss of power to the sensor.

2.	Loss of power to the lock or locking system shall automatically unlock the doors.

3.	The doors shall be arranged to unlock from a manual unlocking device located 40 inches to 48 inches (1016 mm to 1219 mm) vertically above the floor and within 5 feet (1524 mm) of the secured doors. Ready access shall be provided to the manual unlocking device and the device shall be clearly identified by a sign that reads “PUSH TO EXIT.” When operated, the manual unlocking device shall result in direct interruption of power to the lock—independent of other electronics—and the doors shall remain unlocked for not less than 30 seconds.

4.	Activation of the building fire alarm system, where provided, shall automatically unlock the doors, and the doors shall remain unlocked until the fire alarm system has been reset.

5.	Activation of the building automatic sprinkler system or fire detection system, where provided, shall automatically unlock the doors. The doors shall remain unlocked until the fire alarm system has been reset.

6.	The door locking system units shall be listed in accordance with UL 294.

[1008.1.9.8] 1010.1.9.9 Electromagnetically locked egress doors. Doors in the means of egress [that are not otherwise required to have panic hardware] in buildings with an occupancy in Group A, B, E, M, R-1 or R-2 and doors to tenant spaces in Group A, B, E, M, R-1 or R-2 shall be permitted to be [electromagnetically] locked [if] with an electromagnetic locking system where equipped with [listed] hardware that incorporates a built-in switch and [meet the requirements below] where installed and operated in accordance with all of the following:

1.	The [listed] hardware that is affixed to the door leaf has an obvious method of operation that is readily operated under all lighting conditions.

2.	The [listed] hardware is capable of being operated with one hand.

3.	Operation of the [listed] hardware [releases to] directly interrupts the power to the electromagnetic lock and unlocks the door immediately.

4.	Loss of power to the [listed hardware] electromagnetic locking system automatically unlocks the door to permit egress.

5.	Where panic or fire exit hardware is required by Section 1010.1.10, operation of the panic or fire exit hardware also releases the electromagnetic lock.

6.	The locking system units shall be listed in accordance with UL 294.

[1008.1.9.9] 1010.1.9.10 Locking arrangements in correctional facilities. In occupancies in Groups A-2, A-3, A-4, B, E, F, I-2, I-3, M and S within correctional and detention facilities, doors in means of egress serving rooms or spaces occupied by persons whose movements are controlled for security reasons shall be permitted to be locked [when] where equipped with egress control devices [which ] that shall unlock manually and by [at least] not less than one of the following means:

1.	Activation of an automatic sprinkler system installed in accordance with Section 903.3.1.1[;].

2.	Activation of an approved manual fire alarm box[; or].

3.	A signal from a constantly attended location.

[1008.1.9.10] 1010.1.9.11 Stairway doors. Interior stairway means of egress doors shall be openable from both sides without the use of a key or special knowledge or effort.

Exceptions:

1.	Stairway discharge doors shall be openable from the egress side and shall only be locked from the opposite side.

2.	This section shall not apply to doors arranged in accordance with Section 403.5.3.

3.	In stairways serving not more than four stories, doors are permitted to be locked from the side opposite the egress side, provided they are openable from the egress side and capable of being unlocked simultaneously without unlatching upon a signal from the fire command center, if present, or a signal by emergency personnel from a single location inside the main entrance to the building.

4.	This section shall not apply to buildings permitted to be served by one exit in accordance with Item [4 or] 5 or 6 of Section [1021.2] 1006.3.2.

5.	In schools classified as Group E occupancies that require lockdown drills as per New York State Education Law 807, stairway egress doors from occupied spaces are permitted to be locked from the side opposite the egress side for the duration of the lockdown drill, provided that they are openable from the occupied side for egress and are unlocked upon directions from the school administrative personnel following the completion of the lockdown drill.

[1008.1.10] 1010.1.10 Panic and fire exit hardware. Doors serving [a Group H occupancy and doors serving rooms or spaces with an occupant load of 50 or more in a Group A or E occupancy] the following shall not be provided with a latch or lock [unless it is] other than panic hardware or fire exit hardware[.]:

1.	Group H occupancies;

2.	A room or space with an occupant load of 75 or more in a Group A or E occupancy;

3.	A building or nonaccessory tenant space used for assembly purposes that is permitted to be classified as a Group B occupancy pursuant to Section 303.1.2; and

4.	An accessory room or space used for assembly purposes where permitted to be classified as a Group B occupancy or as part of the occupancy it is accessory to, pursuant to Section 303.1.3.

[Exception:] Exceptions:

1.	A main exit of a Group A occupancy shall be permitted to be locking in [compliance] accordance with Section [1008.1.9.3] 1010.1.9.3, Item 2.

2.	Doors serving a Group A or E occupancy shall be permitted to be electromagnetically locked in accordance with Section 1010.1.9.9.

[Electrical rooms with equipment rated 1,200 amperes or more and over 6 feet (1829 mm) wide that contain overcurrent devices, switching devices or control devices with exit or exit access doors shall be equipped with panic hardware or fire exit hardware. The doors shall swing in the direction of egress travel.]

1010.1.10.1 Rooms with electrical equipment. Exit or exit access doors serving transformer vaults, rooms designated for batteries or energy storage systems, or modular data centers shall be equipped with panic hardware or fire exit hardware. Where rooms contain electrical rooms with equipment rated 800 amperes or more that contain overcurrent devices, switching devices or control devices and where the exit or exit access door is less than 25 feet from the equipment working space, shall be equipped with panic hardware or fire exit hardware. The doors shall swing in the direction of egress travel.

1010.1.10.2 Refrigeration machinery room. Swinging doors in refrigeration machinery rooms, where required by Section 1006.2.2.3, shall not be provided with a latch or lock other than panic hardware or fire exit hardware.

[1008.1.10.1] 1010.1.10.3 Installation. Where panic or fire exit hardware is installed, it shall comply with the following:

1.	Panic hardware shall be listed in accordance with UL 305[;].

2.	Fire exit hardware shall be listed in accordance with UL 10C and UL 305[;].

3.	The actuating portion of the releasing device shall extend [at least] not less than one-half of the door leaf width[; and].

4.	The maximum unlatching force shall not exceed 15 pounds (67 N).

[1008.1.10.2] 1010.1.10.4 Balanced doors. If balanced doors are used and panic hardware is required, the panic hardware shall be the push-pad type and the pad shall not extend more than one-half the width of the door measured from the latch side.

[1008.2] 1010.2 Gates. Gates serving the means of egress system shall comply with the requirements of this section. Gates used as a component in a means of egress shall conform to the applicable requirements for doors.

Exception: Horizontal sliding or swinging gates exceeding the 4-foot (1219 mm) maximum leaf width limitation are permitted in fences and walls surrounding a stadium.

[1008.2.1] 1010.2.1 Stadiums. Panic hardware is not required on gates surrounding stadiums where such gates are under constant immediate supervision while the public is present, and where safe dispersal areas based on 3 square feet (0.28 m2) per occupant are located between the fence and enclosed space. Such required safe dispersal areas shall not be located less than 50 feet (15 240 mm) from the enclosed space. See Section [1027.6] 1028.5 for means of egress from safe dispersal areas.

[1008.3] 1010.3 Turnstiles. Turnstiles or similar devices that restrict travel to one direction shall not be placed so as to obstruct any required means of egress. Where portable turnstiles are installed for ticketing purposes, such turnstiles shall be moved from the egress path for proper exiting.

Exceptions:

1.	Manually-operated turnstiles. Manually-operated turnstiles that consist of revolving devices that turn freely in the direction of exit travel may be used in any occupancy where revolving doors are permitted. Each manually-operated turnstile or similar device shall be credited with no more than a 50-person capacity where all of the following provisions are met:

1.1.	Each device shall turn free manually in the direction of egress travel when primary power is lost, and upon the manual release by an employee in the area.

1.2.	Such devices are not given credit for more than 50 percent of the required egress capacity or width.

1.3.	Each device is not more than 39 inches (991 mm) high.

1.4.	Each device has [at least 16.5] not less than 16½ inches (419 mm) clear width at and below a height of 39 inches (991 mm) and [at least] not less than 22 inches (559 mm) clear width at heights above 39 inches (991 mm).

1.5	Where located as part of an accessible route, turnstiles shall have [at least] not less than 36 inches (914 mm) clear at and below a height of 34 inches (864 mm), [at least] not less than 32 inches (813 mm) clear width between 34 inches (864 mm) and 80 inches (2032 mm) and shall consist of a mechanism other than a revolving device.

2.	Automatic turnstiles. Automatic turnstiles that consist of mechanisms other than revolving devices, and are operated by power, such as turnstiles with a photoelectric-actuated mechanism to open the turnstile upon the approach of a person, may be used in any occupancy where revolving doors are permitted. Automatic turnstiles may serve a means of egress system where all of the following provisions are met:

2.1.	Each automatic turnstile shall have minimum widths sufficient for the occupant load served and shall provide at least 32 inches (813 mm) of clear width at and below a height of 80 inches (2032 mm).

2.2.	The design shall be such that in the event of power failure, each automatic turnstile is capable of breaking away manually to permit means of egress travel. The force required to break away these turnstiles manually shall not exceed 13 pounds (57 N). The turnstile shall be capable of swinging from any position to the full, clear opening width of the turnstile when a force is applied to the turnstile on the side from which egress is made.

2.3.	Each automatic turnstile shall be operable from the egress side without special knowledge or effort.

2.4.	Each automatic turnstile shall be connected to the building fire alarm system. Activation of the building fire alarm system shall automatically release each such turnstile to its full, clear opening width, and each such turnstile shall remain in its open position until the fire alarm system has been reset.

2.5	Each automatic turnstile shall, upon actuation of a manual release device, automatically open to its full, clear opening width, and shall remain in its open position until the automatic turnstile’s access control system is reset.  The manual release device shall be clearly identified with ready access that results in direct interruption of power to each turnstile.  The manual release device shall be positioned at the fire command center or, if a fire command center is not required, at an approved location near the building entrance where the automatic turnstiles are located.

[2.5.] 2.6	Each automatic turnstile shall have an integrated emergency power supply.

[2.6.] 2.7	Each automatic turnstile power supply shall be electrically supervised.

[2.7.] 2.8	Turnstiles provided for egress purposes in numbers greater than the egress capacity required by this code shall meet the requirements of this section.

[2.8.] 2.9	Where located as part of an accessible route, such turnstiles shall have at least 36 inches (914 mm) clear width at and below a height of 34 inches (864 mm), at least 32 inches (813 mm) clear width between 34 inches (864 mm) and 80 inches (2032 mm).

[1008.3.1] 1010.3.1 High turnstile. Turnstiles more than 39 inches (991 mm) high shall meet the requirements for revolving doors.

[1008.3.2] 1010.3.2 Additional door. Where serving an occupant load greater than 300, each manually-operated turnstile and automatic turnstile that is not portable shall have a side-hinged swinging door [which] that conforms to Section [1008.1] 1010.1 within 50 feet (15 240 mm).

[1008.4] 1010.4 Security requirements for doors and windows. The provisions of Sections [1008.4.1] 1010.4.1 through [1008.4.4] 1010.4.4 shall apply to Group R-2 occupancies.

[1008.4.1] 1010.4.1 Entrance doors. Building entrance doors and other exterior exit doors shall be equipped with heavy duty lock sets with auxiliary latch bolts to prevent the latch from being manipulated by means other than a key. Latch sets shall have stop-work in the inside cylinder controlled by a master key only. Outside cylinders of main entrance door locks shall be operated by the tenants’ key, which shall not be keyed to also open the tenants’ apartment door. A light or lights shall be provided at or near the outside of the front entranceway of the building providing not less than 5-foot candles (53.82 lux) intensity measured at the floor level for the full width of the entranceway.

[1008.4.2] 1010.4.2 Doors to dwelling units. Doors to dwelling units shall be equipped with a heavy duty latch set and a heavy duty dead bolt operable by a key from the outside and a thumb-turn from the inside. Those doors shall also be equipped with a chain guard so as to permit partial opening of the door. Dwelling unit entrance doors shall also be equipped with a viewing device located so as to enable a person on the inside of the entrance door to view a person immediately outside.

[1008.4.3] 1010.4.3 Windows. All openable windows shall be equipped with sash locks designed to be openable from the inside only. Grilles lockable from the inside only may be placed on the inside or outside of windows that are accessible from grade but that do not serve to provide access to exits.

[1008.4.4] 1010.4.4 Intercommunication system. Buildings containing eight or more dwelling units shall be provided with an intercommunication system located at the door giving access to the main entrance lobby, consisting of a device or devices for voice communication between the occupant of each dwelling unit and a person outside the door to the main entrance lobby, and permitting such dwelling unit occupant to release the locking mechanism of said door from the dwelling unit. In buildings provided with a full-time lobby attendant, the intercommunication system may be between each dwelling unit and the attendant’s station.

SECTION BC [1009] 1011
STAIRWAYS

1011.1 General. Stairways serving occupied portions of a building shall comply with the requirements of Sections 1011.2 through 1011.13. Alternating tread devices shall comply with Section 1011.14. Ships ladders shall comply with Section 1011.15. Ladders shall comply with Section 1011.16.

Exception: Within rooms or spaces used for assembly purposes, stepped aisles shall comply with Section 1029.

[1009.1 Stairway width] 1011.2 Width and capacity. The [width] required capacity of stairways shall be determined as specified in Section [1005.1] 1005, but [such] the minimum width shall be not [be] less than 44 inches (1118 mm). See Section [1007.3] 1009.3 for accessible means of egress stairways.

Exceptions:

1.	A width of not less than 36 inches (914 mm) shall be permitted in:

1.1.	A stairway that serves an occupant load of 50 or less cumulative for all stories; or

1.2.	A stairway that provides egress to the exit discharge solely for the use of Group R-2 occupancies, provided the building it serves is 125 feet (38 100 mm) or less in height, and provided such a stairway serves not more than 30 occupants per floor.

2.	Spiral stairways as provided for in Section [1009.9] 1011.10.

3.	[Aisle stairs complying with Section 1028.]

[4.	] Where an inclined platform lift or a stairway chairlift is installed on stairways serving occupancies in Group R-3, or within dwelling units in occupancies in Group R-2, a clear passage width not less than 20 inches (508 mm) shall be provided. [If] Where the seat and platform can be folded when not in use, the distance shall be measured from the folded

[1009.2] 1011.3 Headroom. Stairways shall have a [minimum] headroom clearance of not less than 84 inches (2134 mm) measured vertically from a line connecting the edge of the nosings. Such headroom shall be continuous above the stairway to the point where the line intersects the landing below, one tread depth beyond the bottom riser. The minimum clearance shall be maintained the full width of the stairway and landing. Projections into the required width shall not be limited above the minimum headroom height.

Exceptions:

1.	In Group R-2 and R-3 occupancies stairways shall have a [minimum] headroom clearance of not less than 80 inches (2032 mm).

2.	Spiral stairways complying with Section [1009.9] 1011.10 are permitted a 78-inch (1981 mm) headroom clearance.

3.	In Group R-3 occupancies; within dwelling units in Group R-2 occupancies; and in Group U occupancies that are accessory to a Group R-3 occupancy or accessory to individual dwelling units in Group R-2 occupancies; where the nosings of treads at the side of a flight extend under the edge of a floor opening through which the stair passes, the floor opening shall be allowed to project horizontally into the required headroom [a maximum of] not more than 4¾ inches (121 mm).

[1009.3] 1011.4 Walkline. The walkline across winder treads shall be concentric to the direction of travel through the turn and located 12 inches (305 mm) from the side where the winders are narrower. The 12-inch (305 mm) dimension shall be measured from the widest point of the clear stair width at the walking surface of the winder. [If] Where winders are adjacent within the flight, the point of the widest clear stair width of the adjacent winders shall be used.

[1009.4] 1011.5 Stair treads and risers. Stair treads and risers shall comply with Sections [1009.4.1] 1011.5.1 through [1009.4.5] 1011.5.5.3.

[1009.4.1] 1011.5.1 Dimension reference surfaces. For the purpose of this section, all dimensions are exclusive of carpets, rugs or runners.

[1009.4.2] 1011.5.2 Riser height and tread depth. Stair riser heights shall be 7 inches (178 mm) maximum and 4 inches (102 mm) minimum. The riser height shall be measured vertically between the [leading edges] nosings of adjacent treads. Rectangular tread depths shall be 11 inches (279 mm) minimum measured horizontally between the vertical planes of the foremost projection of adjacent treads and at a right angle to the tread’s [leading edge] nosing. The greatest tread depth within any flight of stairs shall not exceed the smallest by more than ⅜ inch (9.5 mm). Winder treads shall have a minimum tread depth of 11 inches (279 mm)[measured] between the vertical planes of the foremost projection of adjacent treads at the intersections with the walkline and a minimum tread depth of 10 inches (254 mm) within the clear width of the stair.

Exceptions:

[1.	Alternating tread devices in accordance with Section 1009.10.]

[2.	Ship ladders in accordance with Section 1009.11.]

[3.] 1.	Spiral stairways in accordance with Section [1009.9] 1011.10.

[4.] 2.	[Aisle stairs in assembly seating areas where the stair pitch or slope is set, for sightline reasons, by the slope of the adjacent seating area in accordance with Section 1028.11.2.] Stairways connecting stepped aisles to cross aisles or concourses shall be permitted to use the riser/tread dimension in Section 1029.13.2.

[5.] 3.		In Group R-2 occupancies:

[5.1.] 3.1.	Sum of treads and risers. The sum of two risers plus one tread exclusive of nosing shall be not less than 24 inches (610 mm) nor more than 25½ inches (648 mm).

[5.2.] 3.2.	Dimensions of treads and risers. The maximum riser height shall be 7¾ inches (197 mm) and the minimum tread depth shall be 9½ inches (241 mm) plus nosing. Treads may be undercut a distance equal to the nosing. A nosing not less than ¾ inch (19 mm) but not more than 1¼ inches (32 mm) shall be provided on stairways with solid risers where the tread depth is less than 11 inches (279 mm).

[5.3.] 3.3.	Tolerances. The greatest riser height, tread depth, and nosing projection, within any flight of stairs shall not exceed the smallest by more than ⅜ inch (9.5 mm).

[6.] 4.	In Group R-3 occupancies;[within dwelling units in Group R-2 occupancies not subject to accessibility provisions in Section 1107.2.5, Exception 2;] and in Group U occupancies that are accessory to Group R-3 occupancy or accessory to individual dwelling units in Group R-2 occupancies:

[6.1.] 4.1.	Sum of treads and risers. The sum of two risers plus one tread exclusive of nosing shall be not less than 24 inches (610 mm) nor more than 25½ inches (648 mm).

[6.2.] 4.2.	Dimensions of treads and risers. The maximum riser height shall be 8¼ inches (210 mm) and the minimum tread depth shall be 9 inches (229 mm) plus nosing. Treads may be undercut a distance equal to the nosing. A 1¼ -inch (32 mm) nosing shall be provided on stairways with solid risers where the tread depth is less than 11 inches (279 mm).

[6.3.] 4.3.	Tolerances. The greatest riser height, tread depth, and nosing projection, within any flight of stairs shall not exceed the smallest by more than 3/8 inch (9.5 mm).

[7.] 5.	In Group R-3 occupancies; and within dwelling units in Group R-2 occupancies; winders shall have a minimum tread depth of 10 inches (254 mm) measured horizontally between the vertical planes of the foremost projection of adjacent treads and at a right angle to the tread’s leading edge, when measured at a point 12 inches (305 mm) from the side where the treads are narrower. Winder treads shall have a minimum tread depth of 6 inches (152 mm) at any point. Within any flight of stairs, the greatest winder tread depth at the 12-inch (305 mm) walk line shall not exceed the smallest by more than ⅜ inch (9.5 mm).

[8.] 6.	In Group I-3 facilities, stairways providing access to guard towers, observation stations and control rooms, not more than 250 square feet (23 m2) in area, shall be permitted to have a maximum riser height of 8 inches (203 mm) and a minimum tread depth of 9 inches (229 mm).

[1009.4.3] 1011.5.3 Winder treads. Winder treads are not permitted in means of egress stairways except within a dwelling unit.

Exceptions:

1.	Curved stairways in accordance with Section [1009.8] 1011.9.

2.	Spiral stairways in accordance with Section [1009.9] 1011.10.

[1009.4.4] 1011.5.4 Dimensional uniformity. Stair treads and risers shall be of uniform size and shape. The tolerance between the largest and smallest riser height or between the largest and smallest tread depth shall not exceed [0.375]⅜inch (9.5 mm) in any flight of stairs. The greatest winder tread depth at the walkline within any flight of stairs shall not exceed the smallest by more than ⅜ inch (9.5 mm).

Exceptions:

1.	[Nonuniform riser dimensions of aisle stairs complying with Section 1028.11.2.] Stairways connecting stepped aisles to cross aisles or concourses shall be permitted to comply with the dimensional nonuniformity in Section 1029.13.2.

2.	Consistently shaped winders, complying with Section [1009.4.2] 1011.5, differing from rectangular treads in the same flight of stairs.

3.	Where the bottom or top riser adjoins a sloping public way, walkway or driveway having an established grade and serving as a landing, the bottom or top riser is permitted to be reduced along the slope to less than 4 inches (102 mm) in height, with the variation in height of the bottom or top riser not to exceed one unit vertical in 12 units horizontal (8-percent slope) of [stairway] stair width. The nosings or leading edges of treads at such nonuniform height risers shall have a distinctive marking stripe, different from any other nosing marking provided on the stair flight. The distinctive marking stripe shall be visible in descent of the stair and shall have a slip-resistant surface. Marking stripes shall have a width of [at least] not less than 1 inch (25 mm) but not more than 2 inches (51 mm).

[1009.4.5 Profile] 1011.5.5 Nosing and riser profile. [The radius of curvature at the leading edge of the tread shall be not greater than 9/16 inch (14.3 mm). Beveling of nosings shall not exceed 9/16inch (14.3 mm).] Nosings shall have a curvature or bevel of not less than 1/16 inch (1.6 mm) but not more than 9/16 inch (14.3 mm) from the foremost projection of the tread. Risers shall be solid and vertical or sloped under the tread above from the underside of the nosing above at an angle not more than 30 degrees (0.52 rad) from the vertical.

1011.5.5.1 Nosing projection size. The leading edge (nosings) of treads shall project not more than 1¼ inches (32 mm) beyond the tread below [and all].

1011.5.5.2 Nosing projection uniformity. Nosing projections of the leading edges shall be of uniform size, including the projections of the nosing’s leading edge of the floor at the top of a flight.

1011.5.5.3 Solid risers. Risers shall be solid. Perforated risers with openings not exceeding ¼ inch (6.4 mm) shall be considered solid risers.

Exceptions:

1.	Solid risers are not required for stairways that are not serving as exits or that are not required to comply with Section [1007.3] 1009.3, provided that the opening between treads does not permit the passage of a sphere with a diameter of 4 inches (102 mm).

2.	Solid risers are not required for occupancies in Group I-3 or in Group F, H and S occupancies other than areas accessible to the public. There are no restrictions on the size of the opening in the riser.

3.	In Group R-3 occupancies, the following shall apply:

3.1.	The radius of curvature at the leading edge of the tread shall be no greater than 9/16 inch (14.3 mm).

3.2.	Solid risers are not required provided that the opening between treads does not permit the passage of a sphere with a diameter of 4 inches (102 mm). However, the opening between treads is not limited on stairways with a total rise of 30 inches (762 mm) or less.

4.	Solid risers are not required for spiral stairways constructed in accordance with Section [1009.9] 1011.10.

5.	Solid risers are not required for alternating tread devices constructed in accordance with Section [1009.10] 1011.14.

[1009.5] 1011.6 Stairway landings. There shall be a floor or landing at the top and bottom of each stairway. The width of landings shall be not [be] less than the width of stairways [they serve] served. Every landing shall have a minimum [dimension] width measured [in] perpendicular to the direction of travel equal to the width of the stairway. [Such dimension] Where the stairway has a straight run, the depth need not exceed 48 inches (1219 mm) [where the stairway has a straight run]. Doors opening onto a landing shall not reduce the landing to less than one-half the required width. When fully open, the door shall not project more than 7 inches (178 mm) into a landing. When wheelchair spaces are required on the stairway landing in accordance with Section [1007.6.1] 1009.6.3, the wheelchair space shall not be located in the required width of the landing and doors shall not swing over the wheelchair spaces.[Where doors open onto a stairway landing, such landing shall also comply with Section 1008.1.6.]

Exception: [Aisle stairs complying with Section 1028] Where stairways connect stepped aisles to cross aisles or concourses, stairway landings are not required at the transition between stairways and stepped aisles constructed in accordance with Section 1029.

[1009.6] 1011.7 Stairway construction. [All stairways] Stairways shall be built of materials consistent with the types permitted for the type of construction of the building, except that wood handrails shall be permitted for all types of construction.

[1009.6.1] 1011.7.1 Stairway walking surface. The walking surface of treads and landings of a stairway shall not be sloped steeper than one unit vertical in 48 units horizontal (2-percent slope) in any direction. Stairway treads and landings shall have a solid surface. Finish floor surfaces shall be securely attached.

Exceptions:

1.	Openings in stair walking surfaces shall be a size that does not permit the passage of ½-inch-diameter (12.7 mm) sphere. Elongated [opening] openings shall be placed so that the long dimension is perpendicular to the direction of travel.

2.	In Group F, H and S occupancies, other than areas of parking structures accessible to the public, openings in treads and landings shall not be prohibited provided a sphere with a diameter of 1⅛ inches (29 mm) cannot pass through the opening.

[1009.6.2] 1011.7.2 Outdoor conditions. Outdoor stairways and outdoor approaches to stairways shall be designed so that water will not accumulate on walking surfaces. In [other than] occupancies [in] other than Group R-3[,] and occupancies in Group U that are accessory to an occupancy in Group R-3, treads, platforms and landings that are part of exterior stairways in climates subject to snow or ice shall be protected to prevent the accumulation of same.

[1009.6.3] 1011.7.3 Enclosures under interior stairways. The walls and soffits within enclosed usable spaces under enclosed and unenclosed stairways shall be protected by 1-hour fire-resistance-rated construction or the fire-resistance rating of the stairway enclosure, whichever is greater. Access to the enclosed space shall not be directly from within the [stair] stairway enclosure.

Exception: Spaces under stairways serving and contained within a single residential dwelling unit in Group R-2 or R-3 shall be permitted to be protected on the enclosed side with ½-inch (12.7 mm) gypsum board.

1011.7.4 Enclosures under exterior stairways. There shall not be [no] enclosed usable space under exterior exit stairways unless the space is completely enclosed in 1-hour fire-resistance-rated construction. The open space under exterior stairways shall not be used for any purpose.

[1009.7] 1011.8 Vertical rise. A flight of stairs shall not have a vertical rise greater than 12 feet (3658 mm) between floor levels or landings.

Exceptions:

1.	Aisle stairs [comply] complying with Section [1028] 1029.

2.	Alternating tread devices [used as means of egress shall not have a rise greater than 20 feet (6096 mm) between floor levels or landings] complying with Section 1011.14.

3.	Spiral stairways used as a means of egress from technical production areas.

[1009.8] 1011.9 Curved stairways. Curved stairways with winder treads shall have treads and risers in accordance with Section [1009.4] 1011.5 and the smallest radius shall [not] be not less than twice the minimum width or required [width] capacity of the stairway, whichever is greater.

Exception: The radius restriction shall not apply to curved stairways [for occupancies] in Group R-3 and within individual dwelling units in [occupancies in] Group R-2.

[1009.9] 1011.10 Spiral stairways. Spiral stairways are permitted to be used as a component in the means of egress only within dwelling units or from a space not more than 250 square feet (23 m2) in area and serving not more than five occupants, or from [galleries, catwalks and gridirons] technical production areas in accordance with Section [1015.6] 410.6.

A spiral stairway shall have a [7.5] 7½-inch (191 mm) minimum clear tread depth at a point 12 inches (305 mm) from the narrow edge. The risers shall be sufficient to provide a headroom of 78 inches (1981 mm) minimum, but riser height shall not be more than [9.5] 9½ inches (241 mm). The minimum stairway clear width at and below the handrail shall be 26 inches (660 mm).

1011.11 Handrails. Stairways shall have handrails on each side and shall comply with Section 1014. Where glass is used to provide the handrail, the handrail shall also comply with Section 2407.

Exceptions:

1.	Stairways within dwelling units and spiral stairways are permitted to have a handrail on one side only.

2.	Decks, patios and walkways that have a single change in elevation where the landing depth on each side of the change of elevation is greater than what is required for a landing do not require handrails.

3.	In Group R-3 occupancies, a change in elevation consisting of a single riser at an entrance or egress door does not require handrails.

4.	Changes in room elevations of only one riser within dwelling units and sleeping units in Group R-2 and R-3 do not require handrails.

5.	One handrail shall be allowed in enclosed interior exit stairways less than 44 inches (1118 mm) wide that do not serve as an accessible means of egress.

6.	Handrails for ramped aisles and stepped aisles shall comply with Section 1029.15.

1011.12 Stairway to roof and roof access. In buildings four or more stories or more than 40 feet (12 192 mm) in height above grade, one stairway shall extend to the roof surface through a stairway bulkhead complying with Section 1510.2, unless the roof has a slope steeper than 20 degrees (0.35 rad). Access to setback roof areas may be through a door or window opening to the roof. Stairways terminating at the level of a setback shall provide access to the setback roof areas, except where the setback is less than 4 feet (1219 mm) in width and 10 feet (3048 mm) in length, measured from the inside of the parapet wall.

1011.12.1 Occupancy Groups I-1, R-1 and R-2. In buildings in Occupancy Groups I-1, R- 1 and R-2 two stories or more in height, with roofs having a slope of 15 degrees (0.26 rad) or less, all interior exit stairways, except those terminating at the level of a setback roof, shall extend to the roof surface.

Exceptions:

1.	In buildings in Occupancy Groups R- 1 and R-2 that are two stories in height and in Occupancy Group R-2 that are three stories in height with not more than one dwelling unit per story, access to the roof shall be permitted to be a noncombustible roof hatch or trap door not less than 21 inches (533 mm) in width and 28 inches (711 mm) in length. Such hatches shall be located within the interior exit stairway enclosure and be provided with a stationary, noncombustible access ladder or alternating tread device.

2.	In buildings in Occupancy Group R-2 complying with Item 6 of Section 1006.3.2, roof access shall be governed by Item 6.6 of such section.

1011.12.2 Stairway to elevator equipment. Roofs and penthouses containing elevator equipment that must be accessed for maintenance are required to be accessed by a stairway.

1011.13 Guards. Guards shall be provided along stairways and landings where required by Section 1015 and shall be constructed in accordance with Section 1015. Where the roof hatch opening providing the required access is located within 10 feet (3049 mm) of the roof edge, such roof access or roof edge shall be protected by guards installed in accordance with Section 1015.

[1009.10] 1011.14 Alternating tread devices. Alternating tread devices are limited to an element of a means of egress in buildings of Groups F, H and S from a mezzanine not more than 250 square feet (23 m2) in area and [which] that serves not more than five occupants; in buildings of Group I-3 from a guard tower, observation station or control room not more than 250 square feet (23 m2) in area and for access to unoccupied roofs. Alternating tread devices used as a means of egress shall not have a rise greater than 20 feet (6096 mm) between floor levels or landings.

[1009.10.1] 1011.14.1 Handrails of alternating tread devices. Handrails shall be provided on both sides of alternating tread devices and shall comply with Section [1012] 1014.

[1009.10.2] 1011.14.2 Treads of alternating tread devices. Alternating tread devices shall have a minimum [projected] tread depth of 5 inches (127 mm), a minimum projected tread depth of [8.5] 8½ inches (216 mm), a minimum tread width of 7 inches (178 mm) and a maximum riser height of [9.5] 9½ inches (241 mm). The [projected] tread depth shall be measured horizontally between the vertical planes of the foremost projections of adjacent treads. The riser height shall be measured vertically between the leading edges of adjacent treads. The [combination of] riser height and [projected] tread depth provided shall result in an [alternating tread device] angle [that complies with Section 1002] of ascent from the horizontal of between 50 and 70 degrees (0.87 and 1.22 rad). The initial tread of the device shall begin at the same elevation as the platform, landing or floor surface.

Exception: Alternating tread devices used as an element of a means of egress in buildings from a mezzanine area not more than 250 square feet (23 m2) in [an] area [which] that serves not more than five occupants shall have a minimum tread depth of 3 inches (76 mm) with a minimum projected tread [of 8.5 inches (216 mm) with a minimum tread] depth of [10.5] 10½inches (267 mm). The rise to the next alternating tread surface [should] shall not [be more than] exceed 8 inches (203 mm).

[1009.11 Ship] 1011.15 Ships ladders. [Ship] Ships ladders are permitted to be used in Group I-3 as a component of a means of egress to and from control rooms or elevated facility observation stations not more than 250 square feet (23 m2) with not more than three occupants and for access to unoccupied roofs. The minimum clear width at and below the handrails shall be 20 inches (508 mm).

1011.15.1 Handrails of ships ladders. Handrails shall be provided on both sides of ships ladders.

1011.15.2 Treads of ships ladders. [Ship] Ships ladders shall have a minimum tread depth of 5 inches (127 mm). The tread shall be projected such that the total of the tread depth plus the nosing projection is [no] not less than 8½ inches (216 mm). The maximum riser height shall be 9½ inches (241 mm).

[Handrails shall be provided on both sides of ship ladders. The minimum clear width at and below the handrails shall be 20 inches (508 mm).]

1011.16 Ladders. Permanent ladders shall not serve as a part of the means of egress from occupied spaces within a building. Permanent ladders constructed in accordance with Section 306.5 of the New York City Mechanical Code shall be permitted to provide access to the following areas:

1.	Spaces frequented only by personnel for maintenance, repair or monitoring of equipment.

2.	Nonoccupiable spaces accessed only by catwalks, crawl spaces, freight elevators or very narrow passageways.

3.	Raised areas used primarily for purposes of security, life safety or fire safety including, but not limited to, observation galleries, prison guard towers, fire towers or lifeguard stands.

4.	Elevated levels in Group U not open to the general public.

5.	Roofs that are permitted to have noncombustible access ladders in accordance with Section 1011.12.1.

6.	Technical production areas in assembly occupancies.

[1009.12 Handrails. Stairways shall have handrails on each side and shall comply with Section 1012. Where glass is used to provide the handrail, the handrail shall also comply with Section 2407.]

[1.	Handrails for aisle stairs are not required where permitted by Section 1028.13.]

[2.	Stairways within dwelling units, spiral stairways and aisle stairs serving seating only on one side are permitted to have a handrail on one side only.]

[3.	Decks, patios and walkways that have a single change in elevation where the landing depth on each side of the change of elevation is greater than what is required for a landing do not require handrails.]

[4.	In Group R-3 occupancies, a change in elevation consisting of a single riser at an entrance or egress door does not require handrails.]

[5.	Changes in room elevations of only one riser within dwelling units and sleeping units in Group R-2 and R-3 occupancies do not require handrails.]

[6.	One handrail shall not be allowed in enclosed exit stairs less than 44 inches (1118 mm) wide that do not serve as an accessible means of egress.]

[1009.13 Stairway to roof and roof access. In buildings four or more stories or more than 40 feet (12 192 mm) in height above grade, one stairway shall extend to the roof surface through a stairway bulkhead complying with Section 1509.2, unless the roof has a slope steeper than 20 degrees (0.35 rad). Access to setback roof areas may be through a door or window opening to the roof. Stairs terminating at the level of a setback shall provide access to the setback roof areas, except where the setback is less than 4 feet (1219 mm) in width and 10 feet (3048 mm) in [length, measured from the inside of the parapet wall.]

[1009.13.1 Occupancy Groups I-1, R-1 and R-2. In buildings in Occupancy Groups I-1, R-1 and R-2 two stories or more in height, with roofs having a slope of 15 degrees (0.26 rad) or less, all interior stairs, except those terminating at the level of a setback roof, shall extend to the roof surface.]

[1.	In buildings in Occupancy Groups R-1 and R-2 two stories in height and in Occupancy Group R-2 three stories in height with not more than one dwelling unit per story, access to the roof shall be permitted to be a noncombustible roof hatch or trap door not less than 21 inches (533 mm) in width and 28 inches (711 mm) in length. Such hatches shall be located within the stair enclosure and be provided with a stationary, noncombustible access ladder or alternating tread device.]

[2.	In buildings in Occupancy Group R-2 complying with Item 4 of Section 1021.2, roof access shall be governed by Item 4.6 of such section.]

[1009.13.2 Protection at roof hatch openings. Where the roof hatch opening providing the required access is located within 10 feet (3049 mm) of the roof edge, such roof access or roof edge shall be protected by guards installed in accordance with the provisions of Section 1013.]

[1009.14 Stairway to elevator equipment. Roofs and penthouses containing elevator equipment that must be accessed for maintenance are required to be accessed by a stairway.]

SECTION BC [1010] 1012
RAMPS

[1010.1] 1012.1 Scope. The provisions of this section shall apply to ramps used as a component of a means of egress.

Exceptions:

1.	Other than ramps that are part of the accessible routes providing access in accordance with Sections 1108.2 through 1108.2.4 and 1108.2.6, ramped aisles within assembly rooms or spaces shall [conform] comply with the provisions in Section [1028.11] 1029.

2.	Curb ramps shall comply with ICC A117.1.

3.	Vehicle ramps in parking garages for pedestrian exit access shall not be required to comply with Sections [1010.3] 1012.3 through [1010.9 when] 1012.10 where they are not an accessible route serving accessible parking spaces, other required accessible elements or part of an accessible means of egress.

[1010.2] 1012.2 Slope. Ramps used as part of a means of egress or part of an accessible route shall have a running slope not steeper than one unit vertical in 12 units horizontal (8-percent slope). The slope of other pedestrian ramps shall not be steeper than one unit vertical in eight units horizontal (12.5-percent slope).

Exceptions:

1.	Aisle ramp slope in occupancies of Group A shall comply with Section [1028.11] 1029.13.

2.	In garages three stories or less in height and serving not more than one level below grade, ramps with a maximum slope of one unit vertical in seven units horizontal (14-percent slope) may serve as part of a nonaccessible means of egress.

[1010.3] 1012.3 Cross slope. The slope measured perpendicular to the direction of travel of a ramp shall not be steeper than one unit vertical in 48 units horizontal (2-percent slope).

[1010.4] 1012.4 Vertical rise. The rise for any ramp run shall be 30 inches (762 mm) maximum.

[1010.5] 1012.5 Minimum dimensions. The minimum dimensions of means of egress ramps shall comply with Sections [1010.5.1] 1012.5.1 through [1010.5.3] 1012.5.3.

[1010.5.1] 1012.5.1 Width and capacity. The minimum width and required capacity of a means of egress ramp shall be not [be] less than that required for corridors by Section [1018.2] 1020.2. The clear width of a ramp between handrails, if provided, or other permissible projections shall be 36 inches (914 mm) minimum.

[1010.5.2] 1012.5.2 Headroom. The minimum headroom in all parts of the means of egress ramp shall be not [be] less than 84 inches (2134 mm).

[1010.5.3] 1012.5.3 Restrictions. Means of egress ramps shall not reduce in width in the direction of egress travel. Projections into the required ramp and landing width are prohibited. Doors opening onto a landing shall not reduce the clear width to less than 42 inches (1067 mm).

[1010.6] 1012.6 Landings. Ramps shall have landings at the bottom and top of each ramp, points of turning, entrance, exits and at doors. Landings shall comply with Sections [1010.6.1] 1012.6.1 through [1010.6.5] 1012.6.5.

[1010.6.1] 1012.6.1 Slope. Landings shall have a slope not steeper than one unit vertical in 48 units horizontal (2-percent slope) in any direction. Changes in level are not permitted.

[1010.6.2] 1012.6.2 Width. The landing width shall be [at least as wide as] not less than the width of the widest ramp run adjoining the landing.

[1010.6.3] 1012.6.3 Length. The landing length shall be 60 inches (1525 mm) minimum.

Exceptions:

1.	In Group R-2 and R-3 individual dwelling and sleeping units that are not required to be Accessible units, Type B+NYC units or Type B units in accordance with Section 1107, landings are permitted to be 36 inches (914 mm) minimum.

2.	Where the ramp is not a part of an accessible route, the length of the landing shall not be required to be more than 48 inches (1220 mm) in the direction of travel.

[1010.6.4] 1012.6.4 Change in direction. Where changes in direction of travel occur at landings provided between ramp runs, the landing shall be 60 inches by 60 inches (1524 mm by 1524 mm) minimum.

Exception: In Group R-2 and R-3 individual dwelling or sleeping units that are not required to be Accessible units, Type B+NYC units or Type B units in accordance with Section 1107, landings are permitted to be 36 inches by 36 inches (914 mm by 914 mm) minimum.

[1010.6.5] 1012.6.5 Doorways. Where doorways are located adjacent to a ramp landing, maneuvering clearances required by ICC A117.1 are permitted to overlap the required landing area.

[1010.7] 1012.7 Ramp construction. [All ramps] Ramps shall be built of materials consistent with the types permitted for the type of construction of the building[;], except that wood handrails shall be permitted for all types of construction. [Ramps used as an exit shall conform to the applicable requirements of Sections 1022.1 and 1022.3 through 1022.5 for vertical exit enclosures.]

[1010.7.1] 1012.7.1 Ramp surface. The surface of ramps shall be of slip-resistant materials that are securely attached.

[1010.7.2] 1012.7.2 Outdoor conditions. Outdoor ramps and outdoor approaches to ramps shall be designed so that water will not accumulate on walking surfaces. In other than occupancies in Group R-3, and occupancies in Group U that are accessory to an occupancy in Group R-3, surfaces and landings which are part of exterior exit ramps in climates subject to snow or ice shall be designed to minimize the accumulation of same.

[1010.8] 1012.8 Handrails. Ramps with a rise greater than 6 inches (152 mm) shall have handrails on both sides. Handrails shall comply with Section [1012] 1014.

Exception: Handrails for ramped aisles are not required where permitted by Section [1028.13] 1029.15.

1012.9 Guards. Guards shall be provided where required by Section 1015 and shall be constructed in accordance with Section 1015. Such guards may be used to satisfy the requirement of edge protection of Section 1012.10.

[1010.9] 1012.10 Edge protection. Edge protection complying with Section [1010.9.1] 1012.10.1 shall be provided on each side of ramp runs and at each side of ramp landings not adjoining another ramp run or stairway.

Exceptions:

1.	Edge protection is not required on ramps that are not required to have handrails, provided they have flared sides that comply with the ICC A117.1 curb ramp provisions.

2.	Edge protection is not required on the sides of ramp landings having a vertical dropoff of not more than [0.5]½ inch [(13 mm)] (12.7 mm) within 10 inches (254 mm) horizontally of the required landing area.

3.	Edge protection is not required where the floor or ground surface of the ramp run or landing extends 12 inches (305 mm) minimum beyond the inside face of handrail complying with Section [1012] 1014.

[1010.9.1] 1012.10.1 Curb, rail, wall or barrier. A curb, rail, wall or barrier serving as edge protection shall be provided as follows:

1.	Solid barriers. Solid barriers shall extend at least 4 inches (102 mm) from the floor or ground surface.

2.	Other types of barriers. Other types of barriers shall prevent the passage of a 4-inch-diameter (102 mm) sphere, where any portion of the sphere is within 4 inches (102 mm) of the floor or ground surface.

[1010.10 Guards. Guards shall be provided where required by Section 1013 and shall be constructed in accordance with Section 1013. Such guards may be used to satisfy the requirement of edge protection of Section 1010.9.]

SECTION BC [1011] 1013
EXIT SIGNS

[1011.1] 1013.1 Where required. Exits and exit access doors shall be marked by an approved exit sign readily visible from any direction of egress travel. The path of egress travel to exits and within exits shall be marked by readily visible exit signs to clearly indicate the direction of egress travel in cases where the exit or the path of egress travel is not immediately visible to the occupants. Intervening means of egress doors within exits shall be marked by exit signs. Exit sign placement shall be such that no point in an exit access corridor or exit passageway is more than 100 feet (30 480 mm) or the listed viewing distance for the sign, whichever is less, from the nearest visible exit sign.

Exceptions:

1.	Exit signs are not required in rooms or areas that require only one exit or exit access.

2.	Exit signs are not required in occupancies in Group U and individual sleeping units or dwelling units in Group I-1 or R. However, in a congregate living unit where the occupancy of such unit exceeds four people, exit signs shall be provided.

3.	Exit signs are not required in dayrooms, sleeping rooms or dormitories in occupancies in Group I-3.

4.	In occupancies in Groups A-4 and A-5, exit signs are not required on the seating side of vomitories or openings into seating areas where exit signs are provided in the concourse that are readily apparent from the vomitories. Such vomitories shall be provided with emergency egress lighting to identify each vomitory or opening within the seating area.

[1011.1.1] 1013.1.1 Signs within exits in high-rise buildings. In high-rise buildings subject to Section 403, exit signs shall be placed within exits at horizontal extensions to indicate the transition from vertical to horizontal direction an at turns along the horizontal path.

1013.2 Floor-level exit signs in Group R-1. Where exit signs are required in Group R-1 occupancies by Section 1013.1, additional low-level exit signs shall be provided in all areas serving guest rooms in Group R-1 occupancies and shall comply with Section 1013.5.

The bottom of the sign shall be not less than 10 inches (254 mm) nor more than 12 inches (305 mm) above the floor level. The sign shall be flush mounted to the door or wall. Where mounted on the wall, the edge of the sign shall be within 4 inches (102 mm) of the door frame on the latch side.

[1011.2] 1013.3 Illumination. Exit signs shall be internally or externally illuminated.

Exception: Tactile signs required by Section [1011.3] 1013.4 need not be provided with illumination.

[1011.3 Tactile] 1013.4 Raised character and braille exit signs. A [tactile] sign stating EXIT in visual characters, raised characters and braille and complying with ICC A117.1 shall be provided adjacent to each door to an area of rescue assistance, an exterior area for assisted rescue, [an exit stairway,] an exit stairway or ramp, an exit passageway, a horizontal exit and the exit discharge.

[1011.4] 1013.5 Internally illuminated exit signs. Electrically powered exit signs shall be listed and labeled in accordance with UL 924, except that letters of exit signs shall be red. Exit signs shall be installed in accordance with the manufacturer’s instructions and Chapter 27 of this code. Exit signs shall be illuminated at all times. The letters of exit signs shall be red.

[1011.4.1] 1013.5.1 Graphics. The height of letters shall be not less than 6 inches (152 mm), except that in Group A and Group R-1 occupancies letters shall be not less than 8 inches (203 mm) high. Graphics shall have letter widths, strokes and spacing in proportion to their height.

[1011.5] 1013.6 Externally illuminated exit signs. Externally illuminated exit signs shall comply with Sections [1011.5.1] 1013.6.1 through [1011.5.3] 1013.6.3.

[1011.5.1] 1013.6.1 Graphics. Every exit sign and directional exit sign shall have plainly legible letters not less than 6 inches (152 mm) high with the principal strokes of the letters not less than [0.75]¾ inch (19.1 mm) wide. The word “EXIT” shall have letters having a width not less than 2 inches (51 mm) wide, except the letter “I,” and the minimum spacing between letters shall be not less than [0.375]⅜ inch (9.5 mm). In Group A and R-1 occupancies letters shall be not less than 8 inches (203 mm) high. Signs larger than the minimum established in this section shall have letter widths, strokes and spacing in proportion to their height.

The word “EXIT” shall be in high contrast with the background and shall be clearly discernible when the means of exit sign illumination is or is not energized. The letters of exit signs shall be red. If a chevron directional indicator is provided as part of the exit sign, the construction shall be such that the direction of the chevron directional indicator cannot be readily changed.

[1011.5.2] 1013.6.2 Exit sign illumination. The face of an exit sign illuminated from an external source shall have an intensity of not less than 25 [foot-candles] footcandles (269.1 lux).

[1011.5.3] 1013.6.3 Power source. Exit signs shall be illuminated at all times. To ensure continued illumination for a duration of not less than 90 minutes in case of primary power loss, the sign illumination means shall be connected to an emergency power system provided from storage batteries, unit equipment or an on-site generator. The installation of the emergency power system shall be in accordance with Chapter 27.

SECTION BC [1012] 1014
HANDRAILS

[1012.1] 1014.1 Where required. Handrails [for stairways and ramps] serving stairways, ramps, stepped aisles and ramped aisles shall be adequate in strength and attachment in accordance with Section [1607.7] 1607.8. Handrails required for stairways by Section [1009.12] 1011.11 shall comply with Sections [1012.2] 1014.2 through [1012.9] 1014.9. Handrails required for ramps by Section [1010.8] 1012.8 shall comply with Sections [1012.2] 1014.2 through [1012.8] 1014.8. Handrails for stepped aisles and ramped aisles required by Section 1029.15 shall comply with Sections 1014.2 through 1014.8.

[1012.2] 1014.2 Height. Handrail height, measured above stair tread nosings, or finish surface of ramp slope, shall be uniform, not less than 34 inches (864 mm) and not more than 38 inches (965 mm). Handrail height of alternating tread devices and [ship] ships ladders, measured above tread nosings, shall be uniform, not less than 30 inches (762 mm) and not more than 34 inches (864 mm).

Exceptions:

1.	Where handrail fittings or bendings are used to provide continuous transition between flights, the fittings or bendings shall be permitted to exceed the maximum height.

2.	In Group R-3 occupancies; within dwelling units in Group R-2 occupancies; and in Group U occupancies that are associated with a Group R-3 occupancy or associated with individual dwelling units in Group R-2 occupancies; where handrail fittings or bendings are used to provide continuous transition between flights, transition at winder treads, transition from handrail to guard, or where used at the start of a flight, the handrail height at the fittings or bendings shall be permitted to exceed the maximum height.

3.	Top surface of a guard where permitted to be used as a handrail along stepped aisles and ramped aisles in accordance with Section 1029.15.

[1012.3] 1014.3 Handrail graspability. [All required] Required handrails shall comply with Section [1012.3.1] 1014.3.1 or shall provide equivalent graspability.

Exception: In Group R-3 occupancies; within dwelling units in Group R-2 occupancies; and in Group U occupancies that are accessory to a Group R-3 occupancy or accessory to individual dwelling units in Group R-2 occupancies; handrails shall be Type I in accordance with Section [1012.3.1] 1014.3.1, Type II in accordance with Section [1012.3.2] 1014.3.2, or shall provide equivalent graspability.

[1012.3.1] 1014.3.1 Type I. Handrails with a circular cross section shall have an outside diameter of [at least] not less than 1¼ inches (32 mm) and not greater than 2 inches (51 mm). [If] Where the handrail is not circular, it shall have a perimeter dimension of [at least] not less than 4 inches (102 mm) and not greater than 6¼ inches (160 mm) with a maximum cross-[section] sectional dimension of 2¼ inches (57 mm) and minimum cross-sectional dimension of 1 inch (25 mm). Edges shall have a minimum radius of 0.01 inch (0.25 mm).

[1012.3.2] 1014.3.2 Type II. Handrails with a perimeter greater than 6¼ inches (160 mm) shall provide a graspable finger recess area on both sides of the profile. The finger recess shall begin within a distance of ¾ inch (19 mm) measured vertically from the tallest portion of the profile and achieve a depth of [at least] not less than 5/16 inch (8 mm) within ⅞ inch (22 mm) below the widest portion of the profile. This required depth shall continue for [at least] not less than ⅜ inch (10 mm) to a level that is not less than 1¾ inches (45 mm) below the tallest portion of the profile. The [minimum] width of the handrail above the recess shall be not less than 1¼ inches (32 mm) to [a maximum] not greater than of 2¾ inches (70 mm). Edges shall have a minimum radius of 0.01 inch (0.25 mm).

[1012.4] 1014.4 Continuity. [Handrail-gripping] Handrail gripping surfaces shall be continuous, without interruption by newel posts or other obstructions.

Exceptions:

1.	Handrails within dwelling units are permitted to be interrupted by a newel post at a turn or landing.

2.	Within a dwelling unit, the use of a volute, turnout, starting easing or starting newel is allowed over the lowest tread.

3.	Handrail brackets or balusters attached to the bottom surface of the handrail that do not project horizontally beyond the sides of the handrail within 1½ inches (38 mm) of the bottom of the handrail shall not be considered obstructions. For each ½ inch (12.7 mm) of additional handrail perimeter dimension above 4 inches (102 mm), the vertical clearance dimension of 1½ inches (38 mm) shall be permitted to be reduced by ⅛ inch [(3 mm)] (3.2 mm).

4.	Where handrails are provided along walking surfaces with slopes not steeper than 1:20 (5-percent slope), the bottoms of the handrail gripping surfaces shall be permitted to be obstructed along their entire length where they are integral to crash rails or bumper guards.

5.	Handrails serving stepped aisles or ramped aisles are permitted to be discontinuous in accordance with Section 1029.15.1.

[1012.5] 1014.5 Fittings. Handrails shall not rotate within their fittings.

[1012.6] 1014.6 Handrail extensions. Handrails shall return to a wall, guard or the walking surface or shall be continuous to the handrail of an adjacent [stair] flight of stairs or ramp run. Where handrails are not continuous between flights, the handrails shall extend horizontally [at least] not less than 12 inches (305 mm) beyond the top riser and continue to slope for the depth of one tread beyond the bottom riser. At ramps where handrails are not continuous between runs, the handrails shall extend horizontally above the landing 12 inches (305 mm) minimum beyond the top and bottom of ramp runs. The extensions of handrails shall be in the same direction of the [stair] flights of stairs at stairways and the ramp runs at ramps.

Exceptions:

1.	Handrails within a dwelling unit that is not an Accessible unit, Type B+NYC unit, or Type B unit need extend only from the top riser to the bottom riser.

2.	Handrails within a Type B+NYC multistory dwelling unit that complies with Section 1107.2.5, Items 1 through 3, need extend only from the top riser to the bottom riser.

3.	[Aisle handrails in Group A and E occupancies in accordance with Section 1028.13.] Handrails serving aisles in rooms or spaces used for assembly purposes are permitted to comply with the handrail extensions in accordance with Section 1029.15.

4.	Handrails for alternating tread devices and [ship] ships ladders are permitted to terminate at a location vertically above the top and bottom risers. Handrails for alternating tread devices and ship ladders are not required to be continuous between flights or to extend beyond the top or bottom risers.

[1012.7] 1014.7 Clearance. Clear space between a handrail and a wall or other surface shall be [a minimum of] not less than 1½ inches (38 mm). A handrail and a wall or other surface adjacent to the handrail shall be free of any sharp or abrasive elements.

[1012.8] 1014.8 Projections. On ramps and on ramped aisles that are part of an accessible route, the clear width between handrails shall be 36 inches (914 mm) minimum. Projections into the required width of aisles, stairways and ramps at each [handrail] side shall not exceed 4½ inches (114 mm) at or below the handrail height. Projections into the required width shall not be limited above the minimum headroom height required in Section [1009.2.] 1011.3. Projections due to intermediate handrails shall not constitute a reduction in the egress width.

Exception: The available egress width shall be reduced by the distance between the closest edges of a pair of intermediate handrails where:

1.	Such pair of intermediate handrails are provided within the stairway width without a walking surface between the pair; and

2.	The distance between the closest edges of such pair of intermediate handrails is greater than 6 inches (152 mm).

[1012.9] 1014.9 Intermediate handrails. Stairways shall have intermediate handrails located in such a manner that all portions of the stairway minimum width or required [for egress] capacity are within 30 inches (762 mm) of a handrail. On monumental stairs, handrails shall be located along the most direct path of egress travel.

SECTION BC [1013] 1015
GUARDS

1015.1 General. Guards shall comply with the provisions of Sections 1015.2 through 1015.7. Operable windows with sills located more than 72 inches (1829 mm) above finished grade or other surface below shall comply with Section 1015.8.

[1013.1] 1015.2 Where required. Guards adequate in strength and attachment in accordance with Section 1607.8 shall be located along open-sided walking surfaces that are more than 30 inches (762 mm) measured vertically to the floor or grade below at any point within 36 inches (914 mm) horizontally to the edge of the open side. Such open-sided walking surfaces shall[, including] include, but not be limited to, the following:

1.	Roofs and setback roofs such as terraces accessible by a stairway, including those required by Section 1011.12;

2.	Where protective guards are required on building roofs pursuant to Section 1510.8;

3.	[mezzanines,] Mezzanines;

4.	Balconies;

5.	[equipment] Equipment platforms[,];

6.	Aisles;

7.	[stairs,] Stairs;

8.	[ramps,] Ramps; and

9.	[landings that are located more than 30 inches (762 mm) measured vertically to the floor or grade below at any point within 36 inches (914 mm) horizontally to the edge of the open side. Guards shall be adequate in strength and attachment in accordance with Section 1607.7] Landings.

Exception: Guards are not required for the following locations:

1.	On the loading side of loading docks or piers.

2.	On the audience side of stages and raised platforms, including [steps] stairs and ramps leading up to the stage and raised platforms.

3.	On raised stage and platform floor areas, such as runways, ramps and side stages used for entertainment or presentations.

4.	At vertical openings in the performance area of stages and platforms.

5.	At elevated walking surfaces appurtenant to stages and platforms for access to and utilization of special lighting or equipment.

6.	Along vehicle service pits not accessible to the public.

7.	In assembly seating [where guards] areas at cross aisles in accordance with Section [1028.14 are permitted and provided] 1029.16.2.

[1013.1.1] 1015.2.1 Glazing. Where glass is used to provide a guard or as a portion of the guard system, the guard shall [also] comply with Section 2407. Where the glazing provided does not meet the strength and attachment requirements of Section [1607.7] 1607.8, complying guards shall [also] be located along glazed sides of open-sided walking surfaces.

[1013.2] 1015.3 Height. Required guards shall be not less than 42 inches (1067 mm) high, measured vertically [above the adjacent walking surfaces, adjacent fixed seating or the line connecting the leading edges of the treads.] as follows:

1.	From the adjacent walking surfaces.

2.	Where any portion of fixed seating, fixed planters or similar fixed elements are located within 21 inches (533 mm) horizontally of the guards, from the upper most surface of such portion of the fixed seating or fixed element.

3.	On stairways and stepped aisles, from the line connecting the leading edges of the tread nosings.

4.	On ramps and ramped aisles, from the ramp surface at the guard.

Exceptions:

1.	For occupancies in Group R-3, and within individual dwelling units in occupancies in Group R-2, guards on the open sides of stairs shall have a height not less than 34 inches (864 mm) measured vertically from a line connecting the leading edges of the treads.

2.	For occupancies in Group R-3, and within individual dwelling units in occupancies in Group R-2, where the top of the guard also serves as a handrail on the open sides of stairs, the top of the guard shall be not [be] less than 34 inches (864 mm) and not more than 38 inches (965 mm) measured vertically from a line connecting the leading edges of the treads.

3.	The guard height in assembly seating areas shall [be in accordance] comply with Section [1028.14] 1029.16 as applicable.

4.	Along alternating tread devices and [ship] ships ladders, guards [whose] where the top rail also serves as a handrail[,] shall have height not less than 30 inches (762 mm) and not more than 34 inches (864 mm), measured vertically from the leading edge of the device tread nosing.

[1013.3] 1015.4 Opening limitations. Required guards shall not have openings [which] that allow passage of a sphere 4 inches (102 mm) in diameter from the walking surface to the required guard height.

Exceptions:

1.	From a height of 36 inches (914 mm) to 42 inches (1067 mm), guards shall not have openings [which] that allow passage of a sphere 4⅜ inches (111 mm) in diameter.

2.	The triangular openings at the open sides of a stair, formed by the riser, tread and bottom rail, shall not allow passage of a sphere 6 inches (152 mm) in diameter.

3.	At elevated walking surfaces that are not open to the public for access to and use of electrical, mechanical or plumbing systems or equipment, guards shall not have openings [which] that allow passage of a sphere 21 inches (533 mm) in diameter.

4.	In areas that are not open to the public within occupancies in Group I-3, F, H or S, and for alternating tread devices and [ship] ships ladders, guards shall not have openings [which] that allow passage of a sphere 21 inches (533 mm) in diameter.

5.	In assembly seating areas, guards required at the end of aisles [where they terminate at a fascia of boxes, balconies and galleries] in accordance with Section 1029.16.4 shall not have openings [which] that allow passage of a sphere 4 inches (102 mm) in diameter [(102 mm)] up to a height of 26 inches (660 mm). From a height of 26 inches (660 mm) to 42 inches (1067 mm) above the adjacent walking surfaces, guards shall not have openings [which] that allow passage of a sphere 8 inches (203 mm) in diameter.

6.	Within individual dwelling units and sleeping units in Group R-2 and R-3 occupancies, guards on the open sides of stairs shall not have openings [which] that allow passage of a sphere 4⅜ inches (111 mm) [inches] in diameter.

[1013.4] 1015.5 Screen porches. Porches and decks [which] that are enclosed with insect screening shall be provided with guards where the walking surface is located more than 30 inches (762 mm) above the floor or grade below.

[1013.5] 1015.6 Mechanical equipment, systems and devices. Guards shall be provided where [appliances, equipment, fans, roof hatch openings or other] various components that require service are located within 10 feet (3048 mm) of a roof edge or open side of a walking surface and such edge or open side is located more than 30 inches (762 mm) above the floor, roof or grade below. The guard shall extend not less than 30 inches (762 mm) beyond each end of such components. The guard shall be constructed so as to prevent the passage of a sphere 21 inches (533 mm) in diameter.[The guard shall extend not less than 30 inches (762 mm) beyond each end of such appliance, equipment, fan or component.]

[1013.6] 1015.7 Roof access. Guards shall be provided where the roof hatch opening is located within 10 feet (3048 mm) of a roof edge or open side of a walking surface and such edge or open side is located more than 30 inches (762 mm) above the floor, roof or grade below. The guard shall be constructed so as to prevent the passage of a sphere 21 inches (533 mm) in diameter.

1015.8 Window sills in Group R-3 occupancies. In one- and two-family dwellings, where the opening of the sill portion of an operable window is located more than 72 inches (1829 mm) above the finished grade or other surface below, the lowest part of the clear opening of the window shall be at a height not less than 36 inches (915 mm) above the finished floor surface of the room in which the window is located. Glazing between the floor and a height of 36 inches (915 mm) shall be fixed or have openings through which a 4-inch (102 mm) diameter sphere cannot pass.

Exception: Openings that are provided with window guards that comply with ASTM F 2090.

1015.9 Windows and openings in Group R-2 occupancies. Windows and openings that do not allow passageway onto grade, balcony, terrace, setback, roof or other walking surfaces in Group R-2 occupancies shall be subject to the applicable requirements of the New York City Department of Health and Mental Hygiene with regard to window guards.

SECTION BC [1014] 1016
EXIT ACCESS

[1014.1] 1016.1 General. The exit access shall comply with the applicable provisions of Sections 1003 through [1013] 1015. Exit access arrangement shall comply with Sections [1014] 1016 through [1019] 1021.

[1014.2] 1016.2 Egress through intervening spaces. Egress through intervening spaces shall comply with this section.

1.	Exit access through an enclosed elevator lobby is permitted. Access to not less than one of the required exits shall be provided without travel through the enclosed elevator lobbies required by Section 3006. Where the path of exit access travel passes through an enclosed elevator lobby, the level of protection required for the enclosed elevator lobby is not required to be extended to the exit unless direct access to an exit is required by other sections of this code.

2.	Egress from a room or space shall not pass through adjoining or intervening rooms or areas, except where such adjoining rooms or areas and the area served are accessory to[;] one or the other, are not a Group H occupancy and provide a discernible path of egress travel to an exit.

Exception: Means of egress are not prohibited through adjoining or intervening rooms or spaces in a Group H, S or F occupancy [when] where the adjoining or intervening rooms or spaces are the same or a lesser hazard occupancy group.

[2.] 3.	An exit access shall not pass through a room that can be locked to prevent egress.

[3.] 4.	Means of egress from dwelling units or sleeping areas shall not lead through other sleeping areas, toilet rooms or bathrooms.

[4.] 5.	Egress shall not pass through kitchens, storage rooms, closets or spaces used for similar purposes.

Exceptions:

1.	Means of egress are not prohibited through a kitchen area serving adjoining rooms constituting part of the same dwelling unit or sleeping unit.

2.	Means of egress are not prohibited through stockrooms in Group M [when] where all of the following are met[.]:

2.1.	The stock is of the same hazard classification as that found in the main retail area [;].

2.2.	Not more than 50 percent of the exit access is through the stockroom[;].

2.3.	The stockroom is not subject to locking from the egress side[; and].

2.4.	There is a demarcated, minimum 44-inch-wide (1118 mm) aisle defined by full- or partial-height fixed walls or similar construction that will maintain the required width and lead directly from the retail area to the exit without obstructions.

[1014.2.1] 1016.2.1 Multiple tenants. Where more than one tenant occupies any one floor of a building or structure, each tenant space, dwelling unit and sleeping unit shall be provided with access to the required exits without passing through adjacent tenant spaces, dwelling units and sleeping units.

Exception: The means of egress from a smaller tenant space shall not be prohibited from passing through a larger adjoining tenant space where the following conditions are met:

1.	Such rooms or spaces of the smaller tenant occupy less than 10 percent of the area of the larger tenant space through which they pass;

2.	The larger tenant is a Group M occupancy and the smaller tenant space is of the same or similar occupancy group;

3.	A [discernable] discernible path of egress travel is provided from the smaller tenant space to an exit;

4.	The means of egress into the adjoining space is not subject to locking from the egress side of the smaller tenant space; and

5.	The smaller tenant space serves the same occupants, customers, or patrons as the larger tenant space.

[1014.2.2 Group I-2. Habitable rooms or suites in Group I-2 occupancies shall have an exit access door leading directly to a corridor.]

[Exception: Rooms with exit doors opening directly to the outside at ground level to a public way.]

[1014.2.3 Suites in patient sleeping areas. Patient sleeping areas in Group I-2 occupancies shall be permitted to be divided into suites with one intervening room if one of the following conditions is met:]

[1.	The intervening room within the suite is not used as an exit access for more than eight patient beds.]

[2.	The arrangement of the suite allows for direct and constant visual supervision by nursing personnel.]

[1014.2.3.1 Area. Suites of sleeping rooms shall not exceed 5,000 square feet (465 m2).]

[1014.2.3.2 Exit access. Any patient sleeping room, or any suite that includes patient sleeping rooms, of more than 1,000 square feet (93 m2) shall have at least two exit access doors remotely located from each other.]

[1014.2.3.3 Travel distance. The travel distance between any point in a suite of sleeping rooms and an exit access door of that suite shall not exceed 100 feet (30 480 mm).]

[1014.2.4 Suites in areas other than patient sleeping areas. Areas other than patient sleeping areas in Group I-2 occupancies shall be permitted to be divided into suites.]

[1014.2.4.1 Area. Suites of rooms, other than patient sleeping rooms, shall not exceed 10,000 square feet (929 m2).]

[1014.2.4.2 Exit access. Any room or suite of rooms, other than patient sleeping rooms, of more than 2,500 square feet (232 m2) shall have at least two exit access doors remotely located from each other.]

[1014.2.4.3 One intervening room. For rooms other than patient sleeping rooms, suites of rooms are permitted to have one intervening room if the travel distance within the suite to the exit access door is not greater than 100 feet (30 480 mm).]

[1014.2.4.4 Two intervening rooms. For rooms other than patient sleeping rooms located within a suite, exit access travel from within the suite shall be permitted through two intervening rooms where the travel distance to the exit access door is not greater than 50 feet (15 240 mm).]

[1014.2.5 Exit access through suites. Exit access from all other portions of a building not classified as a suite in a Group I-2 occupancy shall not pass through a suite.]

[1014.2.6 Travel distance. The travel distance between any point in a Group I-2 occupancy patient sleeping room and an exit access door in that room shall not exceed 50 feet (15 240 mm).]

[1014.2.7 Separation. Suites in Group I-2 occupancies shall be separated from other portions of the building by a smoke partition complying with Section 711.]

[1014.3 Common path of egress travel. In occupancies other than Groups H-1, H-2 and H-3, the common path of egress travel shall not exceed 75 feet (22 860 mm). In Group H-1, H-2 and H-3 occupancies, the common path of egress travel shall not exceed 25 feet (7620 mm). For common path of egress travel in Group A occupancies having fixed seating, see Section 1028.8.]

[Exceptions:]

[1.	The length of a common path of egress travel in Group B, F and S occupancies shall not be more than 100 feet (30 480 mm), provided that the building is equipped throughout with an automatic sprinkler system installed in accordance with Section 903.3.1.1.]

[2.	Where a tenant space in Group B, S and U occupancies has an occupant load of not more than 30, the length of a common path of egress travel shall not be more than 100 feet (30 480 mm).]

[3.	The length of a common path of egress travel in a Group I-3 occupancy shall not be more than 100 feet (30 480 mm).]

[4.	The length of a common path of egress travel in a Group R-2 occupancy shall not be more than 125 feet (38 100 mm), provided that the building is protected throughout with an approved automatic sprinkler system in accordance with Section 903.3.1.1 or 903.3.1.2.]

[5.	The length of a common path of egress travel in Group I-2 occupancies between any point in a suite of sleeping rooms and an exit access door of that suite shall not be more than 100 feet (30 480 mm) in accordance with Section 1014.2.3.3.]

[1014.4] 1016.3 Intervening public hall in Group R-2 occupancies. Buildings in Occupancy Group R-2 shall comply with the intervening public hall requirements in accordance with Sections [1014.4.1] 1016.3.1 and [1014.4.2] 1016.3.2.

[1014.4.1] 1016.3.1 Group R-2 nonhigh-rise occupancies. In buildings in Occupancy Group R-2 not subject to Section 403, a door from a dwelling unit shall open into an intervening public hall. Such public hall shall be constructed as a public corridor in accordance with Section [1018] 1020. Opening protectives in accordance with Exception 3 of Section 707.6 shall not be permitted.

Exceptions:

1.	No intervening public hall shall be required for any of the following:

1.1.	A building that is both three stories or less in height, and contains two or fewer dwelling units per story; or

1.2.	A building that complies with Item [4] 6 of Section [1021.2] 1006.3.2.

2.	No intervening public hall shall be required where the doors opening to the apartments are smoke and draft controlled doors complying with UL 1784 without artificial bottom seals, in accordance with [Section] Sections [715.3] 716.5 and [715.3.5.3] 716.5.7.3, and the building is equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1. This exception shall not apply to any building that complies with Item [5] 7 of Section [1021.2] 1006.3.2 where there is more than one apartment per story.

[1014.4.2] 1016.3.2 Group R-2 high-rise occupancies. In high-rise buildings in Occupancy Group R-2, all doors from a dwelling unit shall open into an intervening public hall. Such public hall shall be constructed as a public corridor in accordance with Section [1018] 1020. Opening protectives in accordance with Exception 3 of Section 707.6 shall not be permitted.  Such public hall shall provide access to at least two exits.

Exception: Where the only dwelling units on a story of a building are the upper stories of multi-story (duplex) dwelling units;

1.	Any public halls shall be permitted to provide access to only one exit; or

2.	No such public hall shall be required where smoke and draft controlled doors complying with UL 1784 without artificial bottom seals, in accordance with Sections [715.4] 716.5 and [715.4.6.3] 716.5.7.3, are provided. This exception shall not be construed to effect, alter, or change any requirement of this code to provide two means of egress from each apartment on each story.

[SECTION BC 1015
EXIT AND EXIT ACCESS DOORWAYS]

[1015.1 Exits or exit access doorways from spaces. Two exits or exit access doorways from any space shall be provided where one of the following conditions exists:]

[1.	The occupant load of the space exceeds one of the values in Table 1015.1.]

[2.	The common path of egress travel exceeds one of the limitations of Section 1014.3.]

[3.	Where required by Section 1015.3, 1015.4, 1015.5, 1015.6 or 1015.6.1.

Exception: Group I-2 occupancies shall comply with Sections 1014.2.2 through 1014.2.7.]

[Where a building contains mixed occupancies, each individual occupancy shall comply with the applicable requirements for that occupancy. Where applicable, cumulative occupant loads from adjacent occupancies shall be considered in accordance with the provisions of Section 1004.1.]

[TABLE 1015.1

SPACES WITH ONE EXIT OR EXIT ACCESS DOORWAY

| OCCUPANCY | MAXIMUM OCCUPANT LOAD |
| --- | --- |
| A, B, Ea, M, U | 74 |
| F | 49 |
| H-1, H-2, H-3 | 3 |
| H-4, H-5, I-1, I-3, I-4 | 10 |
| I-2 | See Sections 1014.2.2 through 1014.2.7 |
| R | 20 |
| S | 29 |

[a. Day care maximum occupant load is 10.]

[1015.1.1 Three or more exits or exit access doorways. Three exits or exit access doorways shall be provided from any space with an occupant load of 501 to 1,000. Four exits or exit access doorways shall be provided from any space with an occupant load greater than 1,000.]

[1015.2 Exit or exit access doorway arrangement. Required exits shall be located in a manner that makes their availability obvious. Exits shall be unobstructed at all times. Exit and exit access doorways shall be arranged in accordance with Sections 1015.2.1 and 1015.2.2.]

[1015.2.1 Two exits or exit access doorways. Where two exits or exit access doorways are required from any portion of the exit access, the exit doors or exit access doorways shall be placed a distance apart equal to not less than one-half of the length of the maximum overall diagonal dimension of the building or area to be served measured in a straight line between exit doors or exit access doorways. Stairs sharing any common wall, floors, ceilings, scissor stair assemblies, or other enclosures shall be counted as one exit stairway.]

[Exceptions:]

[1.	Corridor measurements. Where exit enclosures are provided as a portion of the required exit and are interconnected by a 1-hour fire-resistance-rated corridor conforming to the requirements of Section 1018, the required exit separation shall be measured along the shortest direct line of travel within the corridor.]

[2.	Remote location in sprinklered buildings. Where a building is equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1 or 903.3.1.2, the separation distance of the exit doors or exit access doorways shall not be less than one-third of the length of the maximum overall diagonal dimension of the area served.]

[3.	R-2 occupancies. In Group R-2 occupancies, where stairs are enclosed in walls having at least a 2-hour fire-resistance rating and constructed of masonry or masonry equivalent in accordance with department rules.]

[3.1.	The exit doors to such stairs shall be placed a distance apart equal to no less than 15 feet (4572 mm); and]

[3.2.	Such stairs shall be permitted to share common walls, floors, ceilings or scissor stairs assemblies or other enclosures provided that the construction separating the stairs is also of at least a 2-hour fire-resistance rating and constructed of masonry or masonry equivalent in accordance with department rules.]

[4.	B occupancies. In Group B occupancies of construction Type I or II not exceeding 60 feet (18 288 mm) in height, not exceeding 2,000 square feet (186 m2) on any story and not exceeding a travel distance of 50 feet (15 240 mm) on any story, where stairs are enclosed in walls having at least a 2-hour fire-resistance rating and constructed of masonry or masonry equivalent in accordance with department rules.]

[4.1.	The exit doors to such stairs shall be placed a distance apart equal to no less than 15 feet (4572 mm); and]

[4.2.	Such stairs shall be permitted to share common walls, floors, ceilings or scissor stairs assemblies.]

[1015.2.2 Three or more exits or exit access doorways. Where access to three or more exits is required, at least two exit doors or exit access doorways shall be arranged in accordance with the provisions of Section 1015.2.1.]

[1015.3 Boiler, incinerator and furnace rooms. Two exit access doorways are required in boiler, incinerator and furnace rooms where the area is over 500 square feet (46 m2) and any fuel-fired equipment exceeds 400,000 British thermal units (Btu) (422 000 KJ) input capacity. Where two exit access doorways are required, one is permitted to be a fixed ladder or an alternating tread device. Exit access doorways shall be separated by a horizontal distance equal to one-half the length of the maximum overall diagonal dimension of the room.]

[1015.4 Refrigeration machinery rooms. Machinery rooms larger than 1,000 square feet (93 m2) with refrigeration units or systems having a refrigerant circuit containing more than 220 pounds (100 kg) of Group A1 refrigerant or 30 pounds (14 kg) of any other group refrigerant, as classified in Section 1103.1 of the New York City Mechanical Code, shall have not less than two exits or exit access doors. Where two exit access doorways are required, one such doorway is permitted to be served by a fixed ladder or an alternating tread device. Exit access doorways shall be separated by a horizontal distance equal to one-half the maximum horizontal dimension of room.]

[All portions of machinery rooms shall be within 150 feet (45 720 mm) of an exit or exit access doorway. An increase in travel distance is permitted in accordance with Section 1016.1.]

[Doors shall swing in the direction of egress travel, regardless of the occupant load served. Doors shall be tight fitting and self-closing.]

[1015.5 Refrigerated rooms or spaces. Rooms or spaces having a floor area larger than 1,000 square feet (93 m2), containing a refrigerant evaporator and maintained at a temperature below 68°F (20°C), shall have access to not less than two exits or exit access doors.]

[Travel distance shall be determined as specified in Section 1016.1, but all portions of a refrigerated room or space shall be within 150 feet (45 720 mm) of an exit or exit access door where such rooms are not protected by an approved automatic sprinkler system. Egress is allowed through adjoining refrigerated rooms or spaces.]

[Exception: Where using refrigerants in quantities limited to the amounts based on the volume set forth in the New York City Mechanical Code.]

[1015.6 Stage means of egress. Where a minimum of two means of egress are required pursuant to Section 410.5.3, one means of egress shall be provided on each side of the stage.]

[1015.6.1 Gallery, gridiron and catwalk means of egress. The means of egress from lighting and access catwalks, galleries and gridirons shall meet the requirements for occupancies in Group F-2.]

[Exceptions:]

[1.	A minimum width of 22 inches (559 mm) is permitted for lighting and access catwalks.]

[2.	Stairways required by this subsection need not be enclosed.]

[3.	Stairways with a minimum width of 22 inches (559 mm), ladders or spiral stairs are permitted in the means of egress.]

[4.	A second means of egress is not required from these areas where a means of escape to a floor or to a roof is provided.]

SECTION BC [1016] 1017
EXIT ACCESS TRAVEL DISTANCE

[1016.1Travel distance limitations. Exits shall be so located on each story such that the maximum length of exit access travel, measured from the most remote point within a story along the natural and unobstructed path of egress travel to an exterior exit door at the level of exit discharge, an entrance to a vertical exit enclosure, an exit passageway, a horizontal exit, an exterior exit stairway or an exterior exit ramp, shall not exceed the distances given in Table 1016.1.]

1017.1 General. Travel distance within the exit access portion of the means of egress system shall be in accordance with this section.

[Exceptions:]

[1.	Travel distance in open parking garages is permitted to be measured to the closest riser of open exit stairways.]

[2.	In outdoor facilities with open exit access components and open exterior exit stairways or exit ramps, travel distance is permitted to be measured to the closest riser of an exit stairway or the closest slope of the exit ramp.]

[3.	In all occupancies other than occupancy Groups H and I, the exit access travel distance to a maximum of 50 percent of the exits is permitted to be measured from the most remote point within a building to an exit using unenclosed exit access stairways or ramps when connecting a maximum of two stories. Each such interconnected story shall have access to the minimum number of approved independent exits as required by Section 1021.1, but in no case shall there be less than two means of egress. Such interconnected stories shall not be open to other stories. Unenclosed exit stairways shall be remotely located in accordance with Section 1015.2.]

[4.	In all occupancies other than occupancy Groups H and I, exit access travel distance is permitted to be measured from the most remote point within a building to an exit using unenclosed exit access stairways or ramps in the first and second stories above grade plane in buildings equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1. The first and second stories above grade plane shall have access to the minimum number of approved independent exits as required by Section 1021.1, but in no case shall there be less than two means of egress. Such interconnected stories shall not be open to other stories. Unenclosed exit stairways shall be remotely located in accordance with Section 1015.2.]

[Where applicable, travel distance on unenclosed exit access stairways or ramps and on connecting stories shall also be included in the travel distance measurement. The measurement along stairways shall be made on a plane parallel and tangent to the stair tread nosings in the center of the stairway.]

1017.2 Limitations. Exit access travel distance shall not exceed the values given in Table 1017.2.

TABLE [1016.1] 1017.2
EXIT ACCESS TRAVEL DISTANCEa

| OCCUPANCY | WITHOUT SPRINKLER SYSTEM (feet) | WITH SPRINKLER SYSTEM (feet) |
| --- | --- | --- |
| A | See Section [1028.7] 1029.7 |
| E, F-1, M, R, S-1 | 150 | 200b |
| B | 200 | 300c |
| F-2, S-2, U | 200 | 250[b]c |
| H-1 | Not Permitted | 75[c]d |
| H-2 | Not Permitted | 100[c]d |
| H-3 | Not Permitted | 150[c]d |
| H-4 | Not Permitted | 175[c]d |
| H-5 | Not Permitted | 200c |
| I-1, I-2, I-3, I-4 | Not Permitted | 200c |

For SI: 1 foot = 304.8 mm.

- See the following sections for modifications to exit access travel distance requirements:

Section [402.4] 402.8: For the distance limitation in malls.

Section 404.9: For the distance limitation through an atrium space.

Section 407.4: For the distance limitation in Group I-2.

Sections 408.6.1 and 408.8.1: For the distance limitations in Group I-3.

Section 411.4: For the distance limitation in special amusement buildings.

Section 412.7: For the distance limitations in aircraft manufacturing facilities.

[Sections 1014.2.2 through 1014.2.7] Section 407.4.2: For the distance limitation in Group I-2 hospital suites.

Section [1015.4] 1006.2.2.2: For the distance limitation in refrigeration machinery rooms.

Section [1015.5] 1006.2.2.3: For the distance limitation in refrigerated rooms and spaces.

Section [1021.2] 1006.3.2: For buildings with one exit.

Section [1028.7] 1029.7: For increased limitation in assembly seating.

[Section 1028.7: For increased limitation for assembly open-air seating.]

Section 3103.4: For temporary structures.

Section 3104.9: For pedestrian walkways.

- Buildings equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1 or 903.3.1.2. See Section 903 for occupancies where sprinkler systems [according to] are permitted in accordance with Section 903.3.1.2[are permitted].

- Buildings equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1.

d.	Group H occupancies equipped throughout with an automatic sprinkler system in accordance with Section 903.2.5.1.

[1016.2] 1017.2.1 Exterior egress balcony increase. [Travel] Exit access travel distances specified in [Section 1016.1] Table 1017.2 shall be increased up to an additional 100 feet (30 480 mm) provided the last portion of the exit access leading to the exit occurs on an exterior egress balcony constructed in accordance with Section [1019] 1021. The length of such balcony shall be not [be] less than the amount of the increase taken.

1017.3 Measurement. Exit access travel distance shall be measured from the most remote point within a story along the natural and unobstructed path of horizontal and vertical egress travel to the entrance to an exit.

Exceptions:

1.	In open parking garages, exit access travel distance is permitted to be measured to the closest riser of an exit access stairway or the closest slope of an exit access ramp.

2.	In buildings of Group A-5 with open-air seating served by exit access stairways and ramps, exit access travel distance is permitted to be measured to the closest riser of an exit access stairway or the closest slope of an exit access ramp.

3.	Exit access travel distance in assembly occupancies shall be measured in accordance with Section 1029.

1017.3.1 Exit access stairways and ramps. Travel distance on exit access stairways or ramps shall be included in the exit access travel distance measurement. The measurement along stairways shall be made on a plane parallel and tangent to the stair tread nosings in the center of the stair and landings. The measurement along ramps shall be made on the walking surface in the center of the ramp and landings.

SECTION BC [1017] 1018
AISLES

[1017.1] 1018.1 General. Aisles and aisle accessways serving as a portion of the exit access in the means of egress system shall comply with the requirements of this section. Aisles or aisle accessways shall be provided from all occupied portions of the exit access [which] that contain seats, tables, furnishings, displays and similar fixtures or equipment. [Aisles serving assembly areas shall comply with Section 1028. Aisles serving reviewing stands, grandstands and bleachers shall also comply with Section 1028.] The minimum width or required [width] capacity of aisles shall be unobstructed.

Exception: [Doors] Encroachments complying with Section [1005.2] 1005.7.

1018.2 Aisles in assembly spaces. Aisles and aisle accessways serving a room or space used for assembly purposes shall comply with Section 1029.

[1017.2] 1018.3 Aisles in Groups B and M. In Group B and M occupancies, the minimum clear aisle width shall be determined by Section [1005.1] 1005 for the occupant load served, but shall be not [be] less than 36 inches (914 mm).

Exception: Nonpublic aisles serving less than 50 people and not required to be accessible by Chapter 11 need not exceed 28 inches (711 mm) in width.

[1017.3] 1018.4 Aisle accessways in Group M. An aisle accessway shall be provided on [at least] not less than one side of each element within the merchandise pad. The minimum clear width for an aisle accessway not required to be accessible shall be 30 inches (762 mm). The required clear width of the aisle accessway shall be measured perpendicular to the elements and merchandise within the merchandise pad. The 30-inch (762 mm) minimum clear width shall be maintained to provide a path to an adjacent aisle or aisle accessway. The common path of egress travel shall not exceed 30 feet (9144 mm) from any point in the merchandise pad.

Exception: For areas serving not more than 50 occupants, the common path of egress travel shall not exceed 75 feet [(22 880 mm)] (22 860 mm).

[1017.4 Seating at tables. Where seating is located at a table or counter and is adjacent to an aisle or aisle accessway, the measurement of required clear width of the aisle or aisle accessway shall be made to a line 19 inches (483 mm) away from and parallel to the edge of the table or counter. The 19-inch (483 mm) distance shall be measured perpendicular to the side of the table or counter. In the case of other side boundaries for aisle or aisle accessways, the clear width shall be measured to walls, edges of seating and tread edges, except that handrail projections are permitted.]

[Exception: Where tables or counters are served by fixed seats, the width of the aisle accessway shall be measured from the back of the seat.]

[1017.4.1 Aisle accessway for tables and seating. Aisle accessways serving arrangements of seating at tables or counters shall have sufficient clear width to conform to the capacity requirements of Section 1005.1 but shall not have less than the appropriate minimum clear width specified in Section 1017.4.2.]

[1017.4.2 Table and seating accessway width. Aisle accessways shall provide a minimum of 12 inches (305 mm) of width plus ½ inch (12.7 mm) of width for each additional 1 foot (305 mm), or fraction thereof, beyond 12 feet (3658 mm) of aisle accessway length measured from the center of the seat farthest from an aisle.]

[Exception: Portions of an aisle accessway having a length not exceeding 6 feet (1829 mm) and used by a total of not more than four persons.]

[1017.4.3 Table and seating aisle accessway length. The length of travel along the aisle accessway shall not exceed 30 feet (9144 mm) from any seat to the point where a person has a choice of two or more paths of egress travel to separate exits.]

SECTION BC 1019
EXIT ACCESS STAIRWAYS AND RAMPS

1019.1 General. Exit access stairways and ramps serving as an exit access component in a means of egress system shall comply with the requirements of this section. The number of stories connected by exit access stairways and ramps shall include basements, but not mezzanines.

1019.2 All occupancies. Exit access stairways and ramps that serve floor levels within a single story are not required to be enclosed.

1019.3 Occupancies other than Groups H, I-2 and I-3. In other than Group H, I-2 and I-3 occupancies, exit access stairways or ramps shall be enclosed with a shaft enclosure constructed in accordance with Section 713.

Exception: In other than Group H, I-2 and I-3 occupancies, exit access stairways or ramps that comply with one of the following conditions need not be enclosed:

1.	A maximum of 50 percent of the exit access stairways and ramps that serve only two consecutive stories need not be enclosed, provided each such interconnected story has access to the minimum number of approved independent exits as required by Section 1006, and in no case be less than two means of egress. Such interconnected stories shall not be open to other stories. Unenclosed exit access stairways and ramps shall be remotely located in accordance with Section 1007.

2.	In buildings equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1, exit access stairways and ramps that serve between only the first and second stories above grade, provided the first and second stories have access to the minimum number of approved independent exits as required by Section 1006, and in no case be less than two means of egress. Such interconnected stories shall not be open to other stories. Unenclosed exit access stairways and ramps shall be remotely located in accordance with Section 1007.

3.	In Group R-1, R-2 or R-3 occupancies that are fully sprinklered in accordance with Section 903.3.1.1, 903.3.1.2 or 903.3.1.3, exit access stairways and ramps connecting four stories or less and contained within an individual residential dwelling unit.

4.	Exit access stairways and ramps in buildings equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1, where the area of the vertical opening between stories does not exceed twice the horizontal projected area of the stairway or ramp and the opening is protected by a draft curtain and closely spaced sprinklers in accordance with NFPA 13 as modified by Appendix Q. In other than Group B and M occupancies, this provision is limited to openings that do not connect more than four stories.

5.	Exit access stairways and ramps within an atrium complying with the provisions of Section 404.

6.	Exit access stairways and ramps in open parking garages that serve only the parking garage.

7.	Exit access stairways and ramps serving open-air seating in buildings of Group A-5, where all portions of the means of egress are essentially open to the outside.

8.	Exit access stairways and ramps serving the balcony, gallery or press box and the main assembly floor in occupancies such as theaters, places of religious worship, auditoriums and sports facilities.

1019.4 Group I-2 and I-3 occupancies. In Group I-2 and I-3 occupancies, floor openings between stories containing exit access stairways or ramps are required to be enclosed with a shaft enclosure constructed in accordance with Section 713.

Exception: In Group I-3 occupancies, exit access stairways or ramps constructed in accordance with Section 408 are not required to be enclosed.

SECTION BC [1018] 1020
CORRIDORS

[1018.1] 1020.1 Construction. Corridors shall be constructed in accordance with this section. Interior corridor walls required to be fire-resistance rated shall comply with Section [709] 708 for fire partitions. Public corridor walls shall comply with Section 707 for fire barriers.

[1018.1.1] 1020.1.1 Interior corridors. Interior corridors shall be fire-resistance rated in accordance with Table [1018.1.1] 1020.1.1.

Exceptions:

1.	A fire-resistance rating is not required for corridors in an occupancy in Group E where each room that is used for instruction has [at least] not less than one door opening directly to the exterior and rooms for assembly purposes have [at least] not less than one-half of the required means of egress doors opening directly to the exterior. Exterior doors specified in this exception are required to be at ground level.

2.	A fire-resistance rating is not required for corridors contained within a dwelling unit or sleeping unit in an occupancy in Group R.

3.	A fire-resistance rating is not required for corridors in open parking garages.

4.	A fire-resistance rating is not required for corridors in an occupancy in Group B [which] that is a space requiring only a single means of egress complying with Section [1015.1] 1006.2.

5.	Corridors adjacent to the exterior walls of buildings shall be permitted to have unprotected openings on unrated exterior walls where unrated walls are permitted by Table 602 and unprotected openings are permitted by Table 705.8.

TABLE [1018.1.1] 1020.1.1
INTERIOR CORRIDOR FIRE-RESISTANCE RATING

| OCCUPANCY | OCCUPANT LOAD SERVED BY INTERIOR CORRIDOR | REQUIRED FIRE-RESISTANCE RATING (hours) |
| --- | --- | --- |
|  |  | Without sprinkler system | With sprinkler systemc |
| H-1, H-2, H-3 | All | Not Permitted | 1 |
| H-4, H-5 | Greater than 30 | Not Permitted | 1 |
| A, B, E, F, M, S, U | Greater than 30 | 1 | 0 |
| R | Greater than 10 | 1d | 0 |
| I-2a, I-4 | All | Not Permitted | 0 |
| I-1, I-3 | All | Not Permitted | 1b |

a.	For requirements for occupancies in Group I-2, see Sections 407.2 and 407.3.

b.	For a reduction in the fire-resistance rating for occupancies in Group I-3, see Section 408.8.

c.	Buildings equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1 or 903.3.1.2 where allowed.

d.	Interior corridors within dwelling or sleeping units in Group R occupancies pursuant to Section [1018.1.1] 1020.1.1, Exception 2 shall not require fire-resistance rating.

[1018.1.2] 1020.1.2 Public corridors. Public corridors shall be fire-resistance rated in accordance with Table [1018.1.2] 1020.1.2.

TABLE [1018.1.2] 1020.1.2
PUBLIC CORRIDOR FIRE-RESISTANCE RATING

| OCCUPANCY | REQUIRED FIRE-RESISTANCE RATING (hours) |
| --- | --- |
| H-1, H-2, H-3 | 2 |
| H-4, H-5 | 1 |
| A, E, F, M, S, U | 1 |
| B | 1a |
| R (Noncombustible) | 1c |
| R (Combustible) | 2b |
| I-1, I-2, I-3, I-4 | 1 |

a.	Public corridors need not be fire rated in high-rise buildings in Occupancy Group B equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1, where such building is provided with smokeproof enclosures in stairways in accordance with Section 403.5.4.

b.	Public corridors in buildings not exceeding two stories in height, or that are three stories in height and occupied by not more than one family on each story, may be constructed with 1-hour fire-resistance rating.

c.	Corridors serving accessory rooms or spaces in Group R-2 occupancies pursuant to Section 1004.1.1.2.3 shall be constructed with fire barriers with 1-hour fire-resistance rating, and 2-hour fire-resistance rating where the dead-end distance exceeds 40 feet (12 192 mm) in length.

[1018.2 Corridor width] 1020.2 Width and capacity. The [minimum corridor width] required capacity of corridors shall be [as] determined as specified in Section [1005.1] 1005, but the minimum width shall be not less than [44 inches (1118 mm)] that specified in Table 1020.2.

[Exceptions:]

[1.	Twenty-four inches (610 mm)—For access to and utilization of electrical, mechanical or plumbing systems or equipment.]

[2.	Thirty-six inches (914 mm)—With a required occupant capacity of 50 or less, except as otherwise required by Chapter 11.]

[3.	Thirty-six inches (914 mm)—Within a dwelling unit in Occupancy Groups I-1 and R-1, except as otherwise required by Section 1107.]

[4.	Thirty inches (762 mm) —Within a dwelling unit in Occupancy Groups R-2 and R-3, except as otherwise required by Section 1107.]

[5.	Sixty-six inches (1676 mm)—In Group E serving classrooms.]

[6.	Seventy-two inches (1829 mm)—In corridors and areas serving gurney traffic in occupancies where patients receive outpatient medical care, which causes the patient to be not capable of self-preservation.]

[7.	Ninety-six inches (2438 mm)—In Group I-2 in areas where required for bed movement.]

Exception: In Group I-2 occupancies, corridors are not required to have a clear width of 96 inches (2438 mm) in areas where there will not be stretcher or bed movement for access to care or as part of the defend-in-place strategy.

TABLE 1020.2
MINIMUM CORRIDOR WIDTH

| OCCUPANCY | MINIMUM WIDTH (inches) |
| --- | --- |
| Any facilities not listed below | 44 |
| Access to and utilization of mechanical, plumbing or electrical systems or equipment | 24 |
| With an occupant load of 50 or less, except as otherwise required by Chapter 11 | 36 |
| Within a dwelling unit, in Occupancy Groups I-1 and R-1, except as otherwise required by Section 1107 | 36 |
| Within a dwelling unit, in Occupancy Groups R-2 and R-3, except as otherwise required by Section 1107 | 30 |
| In Group E serving classrooms | 66 |
| In corridors and areas serving stretcher traffic in occupancies where patients receive outpatient medical care that causes the patients to be incapable of self-preservation | 72 |
| Group I-2 in areas where required for bed movement | 96 |

For SI: 1 inch = 25.4 mm.

[1018.3 Corridor obstruction] 1020.3 Obstruction. The [required] minimum width or required capacity of corridors shall be unobstructed.

Exception: [Doors] Encroachments complying with Section [1005.2] 1005.7.

[1018.4] 1020.4 Dead ends. Where more than one exit or exit access doorway is required, the exit access shall be arranged such that there are no dead ends in corridors more than 20 feet (6096 mm) in length.

Exceptions:

1.	In occupancies in Group I-3 of [Occupancy] Condition 2, 3 or 4 [(see Section 308.4)], the dead end in a corridor shall not exceed 50 feet (15 240 mm).

2.	In occupancies in Groups B, E, F, I-1, M, R-1, S and U, where the building is equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1, the length of the dead-end corridors shall not exceed 50 feet (15 240 mm).

3.	Dead-end length not exceeding 2.5 times the least width of the dead-end corridor.

4.	In occupancies in Group R-2, the dead end in a corridor shall not exceed 40 feet (12 192 mm). However, where the corridors are completely enclosed in construction having a 2-hour fire-resistance rating with all doors opening into the corridor being self-closing and having a fire-resistance rating of 1½ hours, the length of dead-end corridor shall not exceed 80 feet (24 384 mm).

[1018.5] 1020.5 Air movement in corridors. Use of corridors as part of direct supply, return, or exhaust air system shall be subject to the limitations of the New York City Mechanical Code.

[1018.5.1] 1020.5.1 Corridor ceiling. Use of the space between the corridor ceiling and the floor or roof structure above as a return air plenum shall be in accordance with the New York City Mechanical Code.

[1018.6] 1020.6 Corridor continuity. Fire-resistance-rated corridors shall be continuous from the point of entry to an exit, and shall not be interrupted by intervening rooms. Where the path of egress travel within a fire-resistance-rated corridor to the exit includes travel along unenclosed exit access stairways or ramps, the fire-resistance rating shall be continuous for the length of the stairway or ramp and for the length of the connecting corridor on the adjacent floor leading to the exit.

[Exception:] Exceptions:

1.	Foyers, lobbies or reception rooms constructed as required for corridors shall not be construed as intervening rooms.

2.	Enclosed elevator lobbies as permitted by Item 1 of Section 1016.2 shall not be construed as intervening rooms.

SECTION BC [1019] 1021
EGRESS BALCONIES

[1019.1] 1021.1 General. Balconies used for egress purposes shall conform to the same requirements as corridors for minimum width, required capacity, headroom, dead ends and projections.

[1019.2] 1021.2 Wall separation. Exterior egress balconies shall be separated from the interior of the building by walls and opening protectives as required for corridors.

Exception: Separation is not required where the exterior egress balcony is served by [at least] not less than two [stairs] stairways and a dead-end travel condition does not require travel past an unprotected opening to reach a [stair] stairway.

[1019.3] 1021.3 Openness. The long side of an egress balcony shall be at least 50 percent open, and the open area above the guards shall be so distributed as to minimize the accumulation of smoke or toxic gases.

1021.4 Location. Exterior egress balconies shall have a minimum fire separation distance of 10 feet (3048 mm) measured at right angles from the exterior edge of the egress balcony to the following:

1.	Adjacent lot lines.

2.	Other portions of the building.

3.	Other buildings on the same lot unless the adjacent building exterior walls and openings are protected in accordance with Section 705 based on fire separation distance.

For the purposes of this section, other portions of the building shall be treated as separate buildings.

[1019.4] 1021.5 Outdoor conditions. Exterior egress balconies shall be designed to minimize accumulation of snow and ice that impedes the means of egress.

SECTION BC [1020] 1022
EXITS

[1020.1] 1022.1 General. Exits shall comply with Sections [1020] 1022 through [1026] 1027 and the applicable requirements of Sections 1003 through [1013] 1015. An exit shall not be used for any purpose that interferes with its function as a means of egress. Once a given level of exit protection is achieved, such level of protection shall not be reduced until arrival at the exit discharge. Exits shall be continuous from the point of entry into the exit to the exit discharge.

Exception: Interior exit stairways with doors that are automatic-closing by smoke detection pursuant to the exception set forth in Section 713.7 may be used for travel between floors and this use shall not be deemed to interfere with function as a means of egress.

[1020.2] 1022.2 Exterior exit doors. Buildings or structures used for human occupancy shall have [at least] not less than one exterior door that meets the requirements of Section [1008.1.1] 1010.1.1.

[1020.2.1] 1022.2.1 Detailed requirements. Exterior exit doors shall comply with the applicable requirements of Section [1008.1] 1010.1.

[1020.2.2] 1022.2.2 Arrangement. Exterior exit doors shall lead directly to the exit discharge or the public way.

[SECTION BC 1021
NUMBER OF EXITS AND CONTINUITY]

[1021.1 Exits from stories. All spaces within each story shall have access to the minimum number of approved independent exits as specified in Table 1021.1 based on the occupant load of such story. For the purposes of this chapter, occupied roofs shall be provided with exits as required for stories.]

[Exceptions:]

[1.	As modified by Section 403.5.2.]

[2.	As modified by Section 1021.2.]

[3.	Exit access stairways and ramps that comply with Exception 3 or 4 of Section 1016.1 shall be permitted to provide the minimum number of approved independent exits required by Table 1021.1 on each story.]

[4.	Unless otherwise required by other provisions of this chapter, the number of exits from rooms and spaces within a story discharging directly to the exterior at the level of exit discharge shall be determined in accordance with Table 1015.1.]

[TABLE 1021.1
MINIMUM NUMBER OF EXITS FOR OCCUPANT LOAD

| OCCUPANT LOAD (persons per story) | MINIMUM NUMBER OF EXITS (per story) |
| --- | --- |
| 1-500 | 2 |
| 501-1,000 | 3 |
| More than 1,000 | 4 |

[1021.1.1 Exits maintained. The required number of exits from any story shall be maintained until arrival at grade or the public way.]

[1021.1.2 Open or enclosed parking garages. Open or enclosed parking garages shall not have less than two exits from each parking tier. An unenclosed vehicle ramp constructed in accordance with Section 1010.2 may serve as one of the required exits when provided with pedestrian facilities along the ramp. Such ramps serving open or enclosed parking garages three stories or less in height and serving not more than one level below grade shall further comply with Section 1010.2, Exception 2.]

[Exception: Where vehicles are mechanically parked, only one exit is required but such exit shall not be a vehicle ramp.]

[1021.2 Single exits. Only one exit shall be required in buildings or from stories of buildings as described below:]

[1.	Stories in buildings as described in Table 1021.2.]

[2.	Buildings of Group R-3 occupancy.]

[3.	Single-level buildings with the occupied space at the level of exit discharge provided that the story or space complies with Section 1015.1 as a space with one means of egress.]

[4.	Buildings of Group R-2 occupancy where all of the following conditions are met:]

[4.1.	The building does not exceed four stories;]

[4.2.	The building contains not more than three dwelling units per story;]

[4.3.	The building is of construction Type I or II;]

[4.4.	The building does not exceed 2,500 square feet (232 m2) per story;]

[4.5.	Each dwelling unit has at least one window facing the street, or facing a lawful yard with open, unobstructed, and direct access to the street;]

[4.6.	The stairway extends to the roof surface through a stairway bulkhead complying with Section 1509.2 provided the roof has a slope not steeper than 20 degrees (0.35 rad). In lieu of the stairway bulkhead, the stair may be constructed against the street wall with one window facing the street at every landing and access to the roof is provided via a scuttle with a stationary, noncombustible access ladder;]

[4.7.	The stairway is enclosed in 2-hour fire-rated walls with all exit doors leading into the stairway having at least 1½-hour fire rating; and]

[4.8.	The building shall be equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.2.]

[5.	Buildings of Group R-2 occupancy of construction Type I or II not exceeding six stories and not exceeding 2,000 square feet (186 m2) per story.]

| [TABLE 1021.2 STORIES WITH ONE EXITe, f, g |
| --- |
| STORY | OCCUPANCY | MAXIMUM OCCUPANTS (OR DWELLING UNITS) PER FLOOR AND TRAVEL DISTANCE |
| First story or basement | A, Bc, Ed, Fc, M, U, Sc | 49 occupants and 75 feet travel distance |
|  | H-2, H-3 | 3 occupants and 25 feet travel distance |
|  | H-4, H-5, I, R | 10 occupants and 75 feet travel distance |
|  | Sa | 29 occupants and 100 feet travel distance |
| Second story | B, F, M, Sa | 29 occupants and 75 feet travel distance |
|  | R-2 | 4 dwelling units and 50 feet travel distance |
| Third story | R-2b | 4 dwelling units and 50 feet travel distance |

For SI: 1 foot = 304.8 mm.

a.	For the required number of exits for open or enclosed parking garages, see Section 1021.1.2.

b.	Buildings classified as Group R-2 equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1 or 903.3.1.2 and provided with emergency escape and rescue openings in accordance with Section 1029.

c.	Group B, F and S occupancies in buildings equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1 shall have a maximum travel distance of 100 feet.

d.	Day care occupancies shall have a maximum occupant load of 10.

e.	Mixed occupancies shall be permitted to be served by single exits provided each individual occupancy complies with the applicable requirements of Table 1021.2 for that occupancy.

f.	Where applicable, cumulative occupant loads from adjacent occupancies shall be considered in accordance with the provisions of Section 1004.1.

g.	Basements with a single exit shall not be located more than one story below grade plane.]

[1021.3 Exit continuity. Exits shall be continuous from the point of entry into the exit to the exit discharge.]

[1021.4 Exit door arrangement. Exit door arrangement shall meet the requirements of Sections 1015.2 through 1015.2.2.]

SECTION BC [1022] 1023
[EXIT ENCLOSURES] INTERIOR EXIT STAIRWAYS AND RAMPS

[1022.1 Enclosures required. Interior exit stairways and interior exit ramps shall be enclosed with] 1023.1 General. Interior exit stairways and ramps serving as an exit component in a means of egress system shall comply with the requirements of this section. Interior exit stairways and ramps shall be enclosed and lead directly to the exterior of the building or shall be extended to the exterior of the building with an exit passageway conforming to the requirements of Section 1024, except as permitted in Section 1028.1. An interior exit stairway or ramp shall not be used for any purpose other than as a means of egress and a circulation path.

1023.2 Construction. Enclosures for interior exit stairways and ramps shall be constructed as fire barriers [constructed] in accordance with Section 707 or horizontal assemblies constructed in accordance with Section [712] 711, or both. [Exit enclosures] Interior exit stairway and ramp enclosures shall have a fire-resistance rating of not less than 2 hours where connecting four stories or more and not less than 1 hour where connecting less than four stories. The number of stories connected by the interior exit [enclosure] stairways or ramps shall include any basements, but not any mezzanines. [Exit enclosures] Interior exit stairways and ramps shall have a fire-resistance rating not less than the floor assembly penetrated, but need not exceed 2 hours. In Group R-1 and R-2 occupancies, where interior exit [enclosures] stairways and ramps are required to have a fire-resistance rating of 2 hours, such enclosures shall be constructed of masonry or masonry equivalent. Wall assemblies constituting masonry equivalent shall be constructed in accordance with department rules. [Exit enclosures shall lead directly to the exterior of the building or shall be extended to the exterior of the building with an exit passageway conforming to the requirements of Section 1023, except as permitted in Section 1027.1. An exit enclosure shall not be used for any purpose other than means of egress.]

Exceptions:

1.	[In all occupancies, other than Group H and I occupancies, a stairway is not required to be enclosed when the stairway serves an occupant load of less than 10 and stairway complies with either Item 1.1 or 1.2. In all cases, the maximum number of connecting open stories shall not exceed two.] Interior exit stairways and ramps in Group I-3 occupancies in accordance with the provisions of Section 408.3.8.

[1.1	The stairway is open to not more than one story above its level of exit discharge; or]

[1.2	The stairway is open to not more than one story below its level of exit discharge.]

2.	[Exits in buildings of Group A-5 where all portions of the means of egress are essentially open to the outside need not be enclosed.] Interior exit stairways within an atrium enclosed in accordance with Section 404.6.

[3.	Stairways serving and contained within a single residential dwelling unit or sleeping unit in  Group R-1, R-2 or R-3 occupancies are not required to be enclosed.]

[4.	Stairways in open parking structures that serve only the parking structure are not required to be enclosed.]

[5.	Stairways in Group I-3 occupancies as provided for in Section 408.3.8 are not required to be enclosed.]

[6.	Means of egress stairways as required by Sections 410.5.3 and 1015.6.1 are not required to be enclosed.]

[7.	Means of egress stairways from balconies, galleries or press boxes as provided for in Section 1028.5.1 are not required to be enclosed.]

[8.	Vertical exit enclosures with doors that are automatic-closing by smoke detection pursuant to the exception set forth in Section 708.7 may be used for travel between floors and this use shall not be deemed to interfere with function as a means of egress.]

[1022.2] 1023.3 Termination. [Exit enclosures] Interior exit stairways and ramps shall terminate at an exit discharge or a public way.

Exception: [An] A combination of interior exit [enclosure] stairways, interior exit ramps and exit passageways, constructed in accordance with Sections 1023.2, 1023.3.1 and 1024, respectively, and forming a continuous protected enclosure, shall be permitted to [terminate at] extend an [exit passageway complying with Section 1023, provided the exit passageway terminates at an] interior exit stairway or ramp to the exit discharge or a public way.

[1022.2.1] 1023.3.1 Extension. Where [an] interior exit [enclosure is] stairways and ramps are extended to an exit discharge or a public way by an exit passageway, the interior exit [enclosure] stairway and ramp shall be separated from the exit passageway by a fire barrier constructed in accordance with Section 707 or a horizontal assembly constructed in accordance with Section [712] 711, or both. The fire-resistance rating shall be [at least equal to] not less than that required for the interior exit [enclosure] stairway and ramp. A fire door assembly complying with Section [715.4] 716.5 shall be installed in the fire barrier to provide a means of egress from the interior exit [enclosure] stairway and ramp to the exit passageway. Openings in the fire barrier other than the fire door assembly are prohibited. Penetrations of the fire barrier are prohibited.

[Exception:] Exceptions:

1.	Penetrations of the fire barrier in accordance with Section [1022.4] 1023.5 shall be permitted.

2.	Separation between an interior exit stairway or ramp and the exit passageway extension shall not be required where there are no openings into the exit passageway extension.

[1022.3] 1023.4 Openings. Interior exit stairway and [penetrations. Exit enclosure] ramp opening protectives shall be in accordance with the requirements of Section [715] 716.

Openings in interior exit [enclosures] stairways and ramps other than unprotected exterior openings shall be limited to those necessary for exit access to the enclosure from normally occupied spaces and for egress from the enclosure.

Elevators shall not open into [an] interior exit [enclosure] stairways and ramps.

[1022.4] 1023.5 Penetrations. Penetrations into [and openings] or through [an] interior exit [enclosure] stairways and ramps are prohibited except for [required exit doors,] equipment and ductwork necessary for independent ventilation or pressurization, hydronic piping and related heating equipment limited to serving the interior exit [enclosure] stairway or ramp in which such piping and equipment is located, sprinkler piping, standpipes, electrical raceway for Fire Department communication systems and electrical raceway serving the interior exit [enclosure] stairway and ramp and terminating at a steel box not exceeding 16 square inches (0.010 m2). Such penetrations shall be protected in accordance with Section [713] 714. There shall not be [no] penetrations or communication openings, whether protected or not, between adjacent interior exit [enclosures] stairways and ramps.

Exception: Membrane penetrations shall be permitted on the outside of the interior exit stairway and ramp. Such penetrations shall be protected in accordance with Section 714.3.2.

[1022.5] 1023.6 Ventilation. Equipment and ductwork for interior exit [enclosure] stairway and ramp ventilation [necessary for independent ventilation or pressurization] as permitted by Section [1022.4] 1023.5 shall comply with one of the following items:

1.	Such equipment and ductwork shall be located exterior to the building and shall be directly connected to the interior exit [enclosure] stairway and ramp by ductwork enclosed in construction as required for shafts.

2.	Where such equipment and ductwork is located within the interior exit [enclosure] stairway and ramp, the intake air shall be taken directly from the outdoors and the exhaust air shall be discharged directly to the outdoors, or such air shall be conveyed through ducts enclosed in construction as required for shafts.

3.	Where located within the building, such equipment and ductwork shall be separated from the remainder of the building, including other mechanical equipment, with construction as required for shafts.

In each case, openings into the fire-resistance-rated construction shall be limited to those needed for maintenance and operation and shall be protected by opening protectives in accordance with Section [715] 716 for shaft enclosures.[Exit enclosure ventilation systems shall be independent of other building ventilation systems].

The interior exit stairway and ramp ventilation systems shall be independent of other building ventilation systems.

[1022.6 Exit enclosure] 1023.7 Interior exit stairway and ramp exterior walls. Exterior walls of [an] the interior exit [enclosure] stairway or ramp shall comply with the requirements of Section 705 for exterior walls. Where nonrated walls or unprotected openings enclose the exterior of the stairway or ramps and the walls or openings are exposed [to] by other parts of the building at an angle of less than 180 degrees (3.14 rad), the building exterior walls within 10 feet (3048 mm) horizontally of a nonrated wall or unprotected opening shall have a fire-resistance rating of not less than 1 hour. Openings within such exterior walls shall be protected by opening protectives having a fire protection rating of not less than ¾ hour. This construction shall extend vertically from the ground to a point 10 feet (3048 mm) above the topmost landing of the stairway or ramp, or to the roof line, whichever is lower.

[1022.7] 1023.8 Discharge identification. [A] An interior exit stairway [in an exit enclosure] and ramp shall not continue below its level of exit discharge unless an approved barrier is provided at the level of exit discharge to prevent persons from unintentionally continuing into levels below. Directional exit signs shall be provided as specified in Section [1011] 1013. An approved barrier shall consist of partitions, doors, or gates separating the portion of the [vertical exit] interior exit stairway above grade from the portion below grade. Where doors or gates are provided as approved barriers, such doors or gates shall be self-closing [and], opening in the direction of exit travel from the floors below grade, and provided with landings in accordance with Sections 1010.1.5 and 1010.1.6.

Exceptions:

1.	Such barrier separating the above-grade portion of the [vertical exit] interior exit stairways and ramps from the portion below grade shall not be required in Group E and R-3 occupancies.

2.	Such barrier separating the above-grade portion of the [vertical exit] interior exit stairways and ramps from the portion below grade shall not be required  where the stairway or ramp design is intended to continue the path of egress through a below grade level.

[1022.8] 1023.9 Stairway identification and floor level signs. Signs identifying stairways shall comply with Section 1023.9.1. Signs identifying [and] floor levels shall comply with Sections [1022.8.1] 1023.9.2 through [1022.8.5] 1023.9.5.

[1022.8.1] 1023.9.1 Stairway identification signs. A stairway identification sign indicating each stair by alphabetic letter shall be posted on both sides of each stair door. The alphabetic letters designating the identification of the interior exit stairway and ramp shall be not less than 3 inches (76 mm) in height. Such sign shall comply with Items 2, 5 and 6 of Section 1023.9.4.

[1022.8.2] 1023.9.2 Floor identification signs. A floor identification sign shall be provided at each floor landing [within] in an interior exit [enclosures] stairway and ramp connecting more than three stories. Such sign shall designate:

1.	The floor level;

2.	The terminus of the top and bottom of the interior exit [enclosure] stairway and ramp;

3.	The identification of the [stair or] interior exit stairway and ramp;

4.	The story of the exit discharge; and

5.	The availability of roof access from the [enclosure] interior exit stairway and ramp for the Fire Department.

[The signs shall be located 5 feet (1524 mm) above the floor landing in a position that is readily visible when the doors are in the open and closed positions.]

[1022.8.3 Tactile] 1023.9.3 Accessible floor level identification signs. Floor level identification signs in [tactile] visual characters, raised characters and braille complying with ICC A117.1 shall be located at each floor level landing adjacent to the door on the stair side.

[1022.8.4] 1023.9.4 Signage requirements. [Stairway and floor] Floor identification signs required by [Sections 1022.8.1 and 1022.8.2] Section 1023.9.2 shall comply with all of the following requirements:

1.	The signs shall be a minimum size of 18 inches (457 mm) by 12 inches (305 mm).

2.	[The alphabetic letters designating the identification of the stair enclosure shall be a minimum of 1½ inches (38 mm) in height.] The top of the signs shall be located 5 feet (1524 mm) above the floor landing in a position that is readily visible when the doors are in the open and closed positions.

3.	The number designating the floor level shall be [a minimum of] not less than 5 inches (127 mm) in height and located in the center of the sign.

4.	[All other] Other lettering and numbers shall be [a minimum of] not less than 1 inch (25 mm) in height.

5.	Characters and their background shall have a nonglare finish. Characters shall contrast with their background, with either light characters on a dark background or dark characters on a light background.

6.	[When] Where signs required by Section [1022.8] 1023.9 are installed in the interior exit [enclosures] stairways and ramps of buildings subject to Section [1024] 1025, the signs shall be made of the same luminous materials as required by Section [1024.4] 1025.4.

[1022.8.5] 1023.9.5 Directions to openable doors. Where doors serving [vertical] interior exit [enclosures] stairways are locked on the stair side, signage shall be posted in compliance with Sections [1030.4.1] 1031.4.1, [1030.4.2] 1031.4.2 and [1030.4.3] 1031.4.3.

[1022.9] 1023.10 Elevator lobby identification signs. At landings in interior exit stairways where two or more doors lead to the floor level, any door with direct access to an enclosed elevator lobby shall be identified by signage located on the door or directly adjacent to the door stating “Elevator Lobby.” Signage shall be in accordance with Section 1023.9.4, Items 4, 5 and 6.

1023.11 Smokeproof enclosures and [pressurized stairways] pressurization alternative. In buildings required to comply with Section 403 or 405, each of the [exit enclosures] interior exit stairways and ramps serving a story with a floor surface located more than 75 feet (22 860 mm) above the lowest level of Fire Department vehicle access or more than 30 feet (9144 mm) below the finished floor of a level of exit discharge serving such stories shall be protected by a smokeproof enclosure or [pressurized stairway] pressurization alternative in accordance with Section 909.20.

[1022.9.1] 1023.11.1 Termination and extension. A smokeproof enclosure or [pressurized stairway] pressurization alternative shall terminate at an exit discharge or a public way. The smokeproof enclosure or [pressurized stairway] pressurization alternative shall be permitted to be extended by an exit passageway in accordance with Section [1022.2] 1023.3. The exit passageway shall be without openings other than the fire door assembly required by Section [1022.2] 1023.3.1 and those necessary for egress from the exit passageway. The exit passageway shall be separated from the remainder of the building by 2-hour fire barriers constructed in accordance with Section 707 or horizontal assemblies constructed in accordance with Section [712] 711, or both.

Exceptions:

1.	Openings in the exit passageway serving a smokeproof enclosure are permitted where the exit passageway is protected and pressurized in the same manner as the smokeproof enclosure, and openings are protected as required for access from other floors.

2.	Openings in the exit passageway serving a [pressurized stairway] pressurization alternative are permitted where the exit passageway is protected and pressurized in the same manner as the [pressurized stairway] pressurization alternative.

3.	The fire barrier separating the smokeproof enclosure or [pressurized stairway] pressurization alternative from the exit passageway is not required, provided the exit passageway is protected and pressurized in the same manner as the smokeproof enclosure or [pressurized stairway] pressurization alternative.

4.	A smokeproof enclosure or [pressurized stairway] pressurization alternative shall be permitted to egress through areas on the level of exit discharge or vestibules as permitted by Section [1027] 1028.

[1022.9.2] 1023.11.2 Enclosure access. Access to the stairway or ramp within a smokeproof enclosure shall be by way of a vestibule or an open exterior balcony.

Exception: Access is not required by way of a vestibule or exterior balcony for stairways and ramps using the pressurization alternative complying with Section 909.20.5.

SECTION BC [1023] 1024
EXIT PASSAGEWAYS

[1023.1] 1024.1 Exit [passageway] passageways. Exit passageways serving as an exit component in a means of egress system shall comply with the requirements of this section. An exit passageway shall not be used for any purpose other than as a means of egress and a circulation path.

[1023.2] 1024.2 Width. The [width] required capacity of exit passageways shall be determined as specified in Section [1005.1] 1005 but [such] the minimum width shall be not [be] less than 44 inches (1118 mm), except that exit passageways serving an occupant load of less than 50 shall be not [be] less than 36 inches (914 mm) in width. The minimum width or required capacity of exit passageways shall be unobstructed.

[The required width of exit passageways shall be unobstructed.]

Exception: [Doors] Encroachments complying with Section [1005.2] 1005.7.

[1023.3] 1024.3 Construction. Exit passageway enclosures shall have walls, floors and ceilings of not less than a 1-hour fire-resistance rating, and not less than that required for any connecting interior exit [enclosure] stairway or ramp. Exit passageways shall be constructed as fire barriers in accordance with Section 707 or horizontal assemblies constructed in accordance with Section [712] 711, or both.

[1023.4] 1024.4 Termination. Exit passageways on the level of exit discharge shall terminate at an exit discharge [or a public way]. Exit passageways on other levels shall terminate at an exit component.

[1023.5] 1024.5 Openings [and penetrations]. Exit passageway opening protectives shall be in accordance with the requirements of Section [715] 716.

Except as permitted in Section [402.4.6] 402.8.7, openings in exit passageways other than unprotected exterior openings shall be limited to those necessary for exit access to the exit passageway from normally occupied spaces and for egress from the exit passageway.

Where an interior exit [enclosure] stairway or ramp is extended to an exit discharge or a public way by an exit passageway, the exit passageway shall [also] comply with Section [1022.2.1] 1023.3.1.

Elevators shall not open into an exit passageway.

[1023.6] 1024.6 Penetrations. Penetrations into [and openings] or through an exit passageway are prohibited except for [required exit doors,] equipment and ductwork necessary for independent pressurization, hydronic piping and related heating equipment limited to serving the exit passageway in which such piping and equipment is located, sprinkler piping, standpipes, electrical raceway for fire department communication and electrical raceway serving the exit passageway and terminating at a steel box not exceeding 16 square inches (0.010 m2). Such penetrations shall be protected in accordance with Section [713] 714. There shall not be [no] penetrations or communicating openings, whether protected or not, between adjacent exit passageways.

Exception: Membrane penetrations shall be permitted on the outside of the exit passageway. Such penetrations shall be protected in accordance with Section 714.3.2.

1024.7 Ventilation. Equipment and ductwork for exit passageway ventilation as permitted by Section 1024.6 shall comply with one of the following:

1.	The equipment and ductwork shall be located exterior to the building and shall be directly connected to the exit passageway by ductwork enclosed in construction as required for shafts.

2.	Where the equipment and ductwork is located within the exit passageway, the intake air shall be taken directly from the outdoors and the exhaust air shall be discharged directly to the outdoors, or the air shall be conveyed through ducts enclosed in construction as required for shafts.

3.	Where located within the building, the equipment and ductwork shall be separated from the remainder of the building, including other mechanical equipment, with construction as required for shafts.

In each case, openings into the fire-resistance-rated construction shall be limited to those needed for maintenance and operation and shall be protected by opening protectives in accordance with Section 716 for shaft enclosures.

Exit passageway ventilation systems shall be independent of other building ventilation systems.

SECTION BC [1024] 1025
LUMINOUS EGRESS PATH MARKINGS

[1024.1] 1025.1 General. Approved luminous egress path markings delineating the exit path shall be provided in all high-rise buildings subject to Section 403.5 having occupied floors located more than 75 feet (22 860 mm) above the lowest level of Fire Department vehicle access in accordance with Sections [1024.1] 1025.1 through [1024.9] 1025.9.

Exceptions:

1.	Luminous egress path markings shall not be required on the level of exit discharge in lobbies that serve as part of the exit path in accordance with Section [1027.1] 1028.1, Exception 1.

2.	[Luminous] In open parking garages, luminous egress path markings shall not be required in [areas of] open exit stairways serving only the open parking [garages] garage, and areas of open parking garages that serve [as] such part of the exit path [in accordance with Section 1027.1, Exception 3].

3.	Luminous egress path markings shall not be required on egress paths serving Group R-2.

[1024.2] 1025.2 Required [Markings] markings. Egress path markings shall be provided in interior exit [enclosures, including vertical] stairways, interior exit [enclosures, horizontal exits,] ramps and exit passageways, in accordance with Sections [1024.2.1] 1025.2.1 through [1024.2.9] 1025.2.9. Entrances to interior exit [enclosure] stairways, interior exit ramps and exit passageways shall be provided with exit signs in compliance with Section [1024.2.6.1] 1025.2.6.1.

[1024.2.1] 1025.2.1 Steps. A solid and continuous stripe shall be applied to the horizontal leading edge of each step and shall extend for the full length of the step. Outlining stripes shall have a minimum horizontal width of 1 inch (25 mm) and a maximum width of 2 inches (51 mm). The leading edge of the stripe shall be placed [at a maximum of] not more than ½ inch ([13] 12.7 mm) from the leading edge of the step and the stripe shall not overlap the leading edge of the step by [not] more than ½ inch [(13 mm)] (12.7 mm) down the vertical face of the step. Outlining stripes on steps shall comply with Figure S101.1(2) of Appendix S.

Exception: The minimum width of 1 inch (25 mm) shall not apply to outlining stripes listed in accordance with UL 1994.

[1024.2.2] 1025.2.2 Landings. The leading edge of landings shall be marked with a stripe consistent with the dimensional requirements for steps. Stripes on landings shall comply with Figure S101.1(3) of Appendix S.

[1024.2.3] 1025.2.3 Handrails. [All handrails] Handrails and handrail extensions shall be marked with a solid and continuous stripe having a minimum width of 1 inch (25 mm). The stripe shall be placed on the top surface of the handrail for the entire length of the handrail, including extensions and newel post caps. Where handrails or handrail extensions bend or turn corners, the stripe shall not have a gap of more than 4 inches (102 mm). Stripes on handrails shall comply with Figure S101.1(4) of Appendix S.

Exception: The minimum width of 1 inch (25 mm) shall not apply to outlining stripes listed in accordance with UL 1994.

[1024.2.4] 1025.2.4 Perimeter demarcation lines. Stair landings and other floor areas within interior exit [enclosures] stairways, interior exit ramps and exit passageways, with the exception of the sides of steps, shall be provided with solid and continuous demarcation lines on the floor or on the walls or a combination of both. The stripes shall be 1 to 2 inches (25 mm to 51 mm) wide with interruptions not exceeding 4 inches (102 mm).

Exception: The minimum width of 1 inch (25 mm) shall not apply to outlining stripes listed in accordance with UL 1994.

[1024.2.4.1] 1025.2.4.1 Floor-mounted demarcation lines. Perimeter demarcation lines shall be placed within 4 inches (102 mm) of the wall and shall extend to within 2 inches (51 mm) of the markings on the leading edge of landings. The demarcation lines shall continue across the floor in front of all doors. Perimeter demarcation lines shall comply with Figure S101.1(5) of Appendix S.

Exceptions:

1.	Demarcation lines shall not extend in front of exit discharge doors that lead out of an exit [enclosure] and through which occupants must travel to complete the exit path.

2.	Demarcation lines shall be continuous but need not extend into an area such as a dead end or an obstruction that is selected not to be outlined because it is not part of the egress path.

[1024.2.4.2] 1025.2.4.2 Wall-mounted demarcation lines. Perimeter demarcation lines shall be placed on the wall with the bottom edge of the stripe [no] not more than 4 inches (102 mm) above the finished floor. At the top or bottom of the stairs, demarcation lines shall drop vertically to the floor within 2 inches (51 mm) of the step or landing edge. Demarcation lines on walls shall transition vertically to the floor and then extend across the floor where a line on the floor is the only practical method of outlining the path. Where the wall line is broken by a door, demarcation lines on walls shall continue across the face of the door or transition to the floor and extend across the floor in front of such door. Wall-mounted demarcation lines shall comply with Figure S101.1(8) of Appendix S.

Exceptions:

1.	Demarcation lines shall not extend in front of exit discharge doors that lead out of an exit [enclosure] and through which occupants must travel to complete the exit path.

2.	Perimeter demarcation lines are not required on the sides of steps.

3.	Perimeter demarcation lines are not required where an area such as a dead end or an obstruction is selected not to be outlined because it is not part of the egress path, the demarcation lines shall not be required in such area provided that a demarcation line is continuous across the floor.

[1024.2.4.3] 1025.2.4.3 Transition. Where a wall-mounted demarcation line transitions to a floor-mounted demarcation line, or vice versa, the wall-mounted demarcation line shall drop vertically to the floor to meet a complementary extension of the floor-mounted demarcation line, thus forming a continuous marking. Transitioning demarcation lines shall comply with Figure S101.1(7) of Appendix S.

[1024.2.5] 1025.2.5 Obstacles. Obstacles at or below 6 feet 6 inches (1981 mm) in height and projecting more than 4 inches (102 mm) into the egress path shall be outlined with markings [no] not less than 1 inch (25 mm) in width comprised of a pattern of alternating equal bands, of [luminescent] luminous material and black, with the alternating bands [no] not more than 2 inches (51 mm) thick and angled at 45 degrees (0.79 rad). Obstacles shall include, but are not limited to, standpipes, hose cabinets, wall projections and restricted height areas. However, such markings shall not conceal any required information or indicators including[,] but not limited to[,] instructions to occupants for the use of standpipes. Markings on obstacles shall comply with Figure S101.1(6) of Appendix S.

[1024.2.6] 1025.2.6 Doors [from] within the exit [enclosures] path. Doors through which occupants [within an exit enclosure] must pass in order to complete the exit path, and doors serving horizontal exits, shall be provided with markings complying with Sections [1024.2.6.1] 1025.2.6.1 through [1024.2.6.3] 1025.2.6.3 of this chapter and Figures S101.1(11) and S101.1(12) of Appendix S. Exit discharge doors shall further comply with Section [1024.2.6.1.2] 1025.2.6.1.2.

[1024.2.6.1] 1025.2.6.1 Emergency exit symbol. The doors shall be identified by a low-location luminous emergency exit symbol complying with Section [1024.6.1] 1025.6.1. The exit symbol shall be [a minimum of] not less than 4 inches (102 mm) in height and shall be mounted on the door itself in accordance with Section [1024.2.6.1.1] 1025.2.6.1.1. Such signs shall be no higher than 18 inches (457 mm) above the finished floor.

[1024.2.6.1.1] 1025.2.6.1.1 Mounting location. The vertical centerline of the sign shall be centered with the door, or shall be in that half of the door, either the right or left, that contains the latch. In case of double-doors, both doors shall be marked and the signs shall be centered with the doors. Arrows may be omitted on door-mounted signs. Door-mounted signs shall comply with Figure S101.1(1) in Appendix S.

[1024.2.6.1.2] 1025.2.6.1.2 Exit discharge doors. At doors serving as exit discharge, a sign in compliance with Section [1024.2.6.1.1] 1025.2.6.1.1 shall contain supplemental directional text such as “FINAL EXIT,” “EXIT THROUGH LOBBY,” or “EXIT TO STREET” in sans serif letters one-half as high as the word EXIT. Exit discharge door sign shall comply with Figure S101.1(13) in Appendix S.

[1024.2.6.2] 1025.2.6.2 Door hardware markings. Door hardware shall be marked with [no] not less than 16 square inches [(406 mm2)] (0.01 m2) of luminous material. This marking shall be located behind, immediately adjacent to, or on the door handle [and/] or escutcheon. Where a panic bar is installed, such material shall not be [no] less than 1 inch (25 mm) wide for the entire length of the actuating bar or touchpad. Additional hardware markings may include ANSI Z 535.1 safety green graphics such as arrows indicating door handle turning directions, or emergency egress symbols as per NFPA 170, the word “EXIT,” the word “PUSH,” and similar egress-related symbols, provided the minimum 16 square inches [(406 mm2)] (0.01 m2) of luminous materials is maintained.

[1024.2.6.3] 1025.2.6.3 Door frame markings. The top and sides of the door frame shall be marked with a solid and continuous [1 inch] 1-inch- to [2 inch] 2-inch-wide (25 mm to 51 mm) [wide] stripe. Where the door molding does not provide sufficient flat surface on which to locate the stripe, the stripe shall be permitted to be located on the wall surrounding the frame.

[1024.2.7] 1025.2.7 Directional signage upon entering an interior exit [enclosures] stairway or ramp. Luminous directional signs designed in compliance with Section [1024.6.1] 1025.6.1 shall be placed in the interior exit [enclosure] stairway or ramp at every entrance thereto such that they are readily visible when the doors are in the open and closed positions. Such directional sign shall include an arrow indicating the direction of travel. The word “EXIT” shall not be required. The signs shall be located such that their top edge is within 18 inches (457 mm) above the finished floor. Directional signs shall comply with Figure S101.1(9) in Appendix S.

[1024.2.8] 1025.2.8 Directional signage at transfer levels and where egress direction is not clear. Luminous directional signs designed in compliance with Section [1024.6.1] 1025.6.1 and installed at heights indicated in Section [1024.2.7] 1025.2.7 shall be placed on the wall at transfer levels and wherever egress direction is not clear; including at turns along horizontal extensions, at transitions from vertical to horizontal direction and at a “T” intersection. These directional signs shall include arrows indicating the direction of travel. The word “EXIT” shall not be required. Directional signs at transfer levels shall comply with Figure S101.1(9) in Appendix S.

[1024.2.9] 1025.2.9 “No Exit” sign. Luminous signs shall be placed on doors along the egress path that lead to dead ends (mechanical rooms, storage closets, etc.). Such signs shall contain sans serif lettering at least 1 inch (25 mm) high reading “NO EXIT,” with the “NO” centered above the “EXIT.” The “NO” may be a larger size than the “EXIT” for clarity. The nonluminous portion of such signs shall not be green. No-exit signs shall comply with Figure S101.1(10) in Appendix S.

[1024.3] 1025.3 Uniformity. Placement and dimensions of markings shall be consistent and uniform throughout the same [exit] enclosure.

[1024.3.1] 1025.3.1 Solid and continuous. For the purposes of this section, solid and continuous means without gaps or interruption, except as required for the control of expansion and contraction. A series of dashes, chevrons, dots, or other similar patterns is not solid and continuous. Luminous materials shall be considered solid and continuous if they occasionally contain the following safety green (ANSI Z 535.1) symbols or text:

1.	The word “EXIT”;

2.	Egress symbol as per NFPA 170;

3.	Direction arrows as per NFPA 170; or

4.	Other text or symbols as approved by the commissioner.

[1024.4] 1025.4 Self-luminous and photoluminescent. Luminous egress path markings shall be permitted to be made of any material, including paint, provided that an electrical charge is not required to maintain the required luminance. Such materials shall include, but [are] not be limited to, self-luminous materials and photoluminescent materials. Materials shall comply with either[:] of the following standards:

1.	UL 1994[; or].

2.	ASTM E 2072, except that the charging source shall be 1 [foot-candle] footcandle (11 lux) of fluorescent illumination for 60 minutes, and the minimum luminance shall be 30 millicandelas per square meter at 10 minutes and 5 millicandelas per square meter after 90 minutes.

[1024.4.1] 1025.4.1 Labeling. All approved materials shall be labeled and identified with the manufacturer’s name, model number and the name of the approved agency in a minimum of 6 point type with at least one such identification on each piece of material installed. However, labeling is not required for pieces of material less than 1 foot (305 mm) in length that are placed in immediate proximity of an identical model that is labeled. Materials may include supplemental identifying information such as the trade name or “NYC.”

[1024.5] 1025.5 Reserved.

[1024.6] 1025.6 General standards. Luminous materials shall comply with the design standards of Sections [1024.6.1] 1025.6.1 and [1024.6.2] 1025.6.2.

[1024.6.1] 1025.6.1 Design of door and directional signs. Unless otherwise specified, all photoluminescent door signs and directional signs:

1.	May be either positive or negative image;

2.	Shall be made with the non-photoluminescent portions of the signs in safety green as per ANSI Z535.1; and

3.	Shall include three components:

3.1.	The word “EXIT” printed in sans serif letters at least 4 inches high (102 mm) with strokes no less than ½ inch (13 mm);

3.2.	An emergency exit symbol at least 4 inches high (102 mm), complying with NFPA 170; and

3.3.	An arrow at least 2¾ inches (70 mm) high, complying with NFPA 170.

Design of door and directional sign shall comply with Figures S101.1(9), S101.1(13), S101.1(14) and S101.1(15) of Appendix S.

[1024.6.1.1] 1025.6.1.1 Additional text for sign subject to this section. Additional descriptive text is permitted, provided such words are in sans serif letters and, where the word “EXIT” or the emergency symbol is required on such sign, such a descriptive text is no more than one-half as high as the word “EXIT” or the emergency exit symbol.

[1024.6.2] 1025.6.2 Figures. The figures in Appendix S are intended only for illustration, and where there is a conflict between the figures and this section, this section shall govern.

[1024.7] 1025.7 Voluntary installation. Where luminous egress path markings are not required but are voluntarily installed in the exit path, such markings shall comply with Section [1024] 1025.

[1024.8] 1025.8 Special inspection. Luminous exit path markings shall be subject to special inspection in accordance with Sections [1024.8.1] 1025.8.1 through [1024.8.3] 1025.8.3.

[1024.8.1] 1025.8.1 Inspection. A registered design professional shall verify by visual inspection that all components have been installed in accordance with Section [1024] 1025, both with the normal lighting turned on and with the normal and emergency lighting turned off.

[1024.8.2] 1025.8.2 Product identification. A registered design professional shall review the manufacturer product literature and information from the testing agency and verify that the products installed are labeled as meeting the standards in Section [1024.4] 1025.4. The registered design professional shall verify which particular products were installed in which parts of the building.

[1024.8.3] 1025.8.3 Paints. Where in situ painting was utilized, a registered design professional shall field-verify that the specified paint was utilized in accordance with the manufacturer recommended methods of application.

[1024.9] 1025.9 Maintenance program. Owners shall keep the required luminous egress path markings in good repair. At a minimum, owners shall, every 12 months, perform a visual inspection of the markings with the normal lighting turned on. Markings that are missing, damaged, loose, or that show signs of wear or missing labels shall be noted and promptly repaired. The log of such inspections, including the results and any corrective measures taken, shall be kept and maintained on the premises for inspection by the department and the Fire Department. The log shall contain the date of inspection and the printed name and signature of the person performing the inspection.

SECTION BC [1025] 1026
HORIZONTAL EXITS

[1025.1] 1026.1 Horizontal exits. Horizontal exits serving as an exit in a means of egress system shall comply with the requirements of this section. A horizontal exit shall not serve as the only exit from a portion of a building, and where two or more exits are required, not more than one-half of the total number of exits or total exit minimum width or required capacity shall be horizontal exits.

Exceptions:

1.	Horizontal exits are permitted to comprise two-thirds of the required exits from any building or floor area for occupancies in Group I-2.

2.	Horizontal exits are permitted to comprise 100 percent of the exits required for occupancies in Group I-3. [At least] Not less than 6 square feet (0.6 m2) of accessible space per occupant shall be provided on each side of the horizontal exit for the total number of people in adjoining compartments.

3.	Horizontal exits are permitted to serve as the only exits from a portion of a building serving as an intermediate refuge area in accordance with Section 1026.4.2, Exception.

[1025.2] 1026.2 Separation. The separation between buildings or refuge areas connected by a horizontal exit shall be provided by a fire wall complying with Section 706; or [it shall be provided] by a fire barrier complying with Section 707 or a horizontal assembly complying with Section [712] 711, or both. The minimum fire-resistance rating of the separation shall be 2 hours. Opening protectives in horizontal exits shall also comply with Section [715] 716. Duct and air transfer openings in a fire wall or fire barrier that serves as a horizontal exit shall also comply with Section [716] 717. The horizontal exit separation shall extend vertically through all levels of the building unless floor assemblies have a fire-resistance rating of not less than 2 hours with no unprotected openings.

Exception: A fire-resistance rating is not required at horizontal exits between a building area and an above-grade pedestrian walkway constructed in accordance with Section 3104, provided that the distance between connected buildings is more than 20 feet (6096 mm).

Horizontal exits constructed as fire barriers shall be continuous from exterior wall to exterior wall so as to divide completely the floor served by the horizontal exit.

[1025.3] 1026.3 Opening protectives. Fire doors in horizontal exits shall be self-closing or automatic-closing when activated by a smoke detector in accordance with Section [715.4.8.3] 716.5.9.3. Doors, where located in a cross-corridor condition, shall be automatic-closing by activation of a smoke detector installed in accordance with Section [715.4.8.3] 716.5.9.3.

[1025.4 Capacity of refuge area] 1026.4 Refuge area. The refuge area of a horizontal exit shall be a space occupied by the same tenant or a public area and each such refuge area shall be adequate to accommodate the original occupant load of the refuge area plus the occupant load anticipated from the adjoining compartment. The anticipated occupant load from the adjoining compartment shall be based on the capacity of the horizontal exit doors entering the refuge area.

1026.4.1 Capacity. The capacity of the refuge area shall be computed based on a net floor area allowance of 3 square feet (0.2787 m2) for each occupant to be accommodated therein.

[Exception] Exceptions: The net floor area allowable per occupant shall be as follows for the indicated occupancies:

1.	Six square feet (0.6 m2) per occupant for occupancies in Group I-3.

2.	Fifteen square feet (1.4 m2) per occupant for ambulatory occupancies in Group I-2.

3.	Thirty square feet (2.8 m2) per occupant for nonambulatory occupancies in Group I-2.

1026.4.2 Number of exits. The refuge area into which a horizontal exit leads shall be provided with exits adequate to meet the occupant requirements of this chapter, but not including the added occupant load imposed by persons entering [it] the refuge area through horizontal exits from [other areas] the adjoining compartment. [At least] Not less than one refuge area exit shall lead directly to the exterior or to an interior exit [enclosure] stairway or ramp. In addition to such refuge area exit, in buildings more than 420 feet (128 m) in height that are subject to Section 403.5.2, at least one other exit from each refuge area shall lead directly to the additional exit stairway required by Section 403.5.2, or shall provide access to occupant self-evacuation elevators where such elevators are permitted by Exception 1 or 2 of Section 403.5.2 in lieu of an additional exit stairway.

Exception: [The] A single intermediate refuge area between the adjoining compartment from which egress originates and the final refuge area shall not be required to have a stairway or door leading directly outside, provided the final refuge area into which a horizontal exit leads has stairways or doors leading directly outside and are so arranged that egress shall not require the occupants to return through the intermediate refuge area and the adjoining compartment from which egress originates.

SECTION BC [1026] 1027
EXTERIOR EXIT [RAMPS AND] STAIRWAYS AND RAMPS

[1026.1] 1027.1 Exterior exit [ramps and] stairways and ramps. Exterior exit [ramps and] stairways and ramps serving as an element of a required means of egress shall comply with this section.

[Exception: Exterior exit ramps and stairways for outdoor stadiums complying with Section 1022.1, Exception 2.]

[1026.2] 1027.2 Use in a means of egress. Exterior exit stairways shall not be used as an element of a required means of egress for Group I-2 occupancies. For all occupancies other than Group I-2, exterior exit [ramps and] stairways and ramps shall be permitted as an element of a required means of egress for buildings not exceeding six stories above grade plane or [having occupied floors more than 75 feet (22 860 mm) above the lowest level of Fire Department vehicle access] that are not high-rise buildings.

[1026.3] 1027.3 Open side. Exterior exit [ramps and] stairways and ramps serving as an element of a required means of egress shall be open on [at least] not less than one side[.], except for required structural columns, beams, handrails and guards. An open side shall have [a minimum of] not less than 35 square feet (3.3 m2) of aggregate open area adjacent to each floor level and the level of each intermediate landing. The required open area shall be located not less than 42 inches (1067 mm) above the adjacent floor or landing level.

[1026.4] 1027.4 Adjoining open areas.  The open areas adjoining exterior exit [ramps or] stairways or ramps shall be either yards, courts or public ways; the remaining sides are permitted to be enclosed by the exterior walls of the building.

[1026.5] 1027.5 Location. Exterior exit [ramps and] stairways [shall be located in accordance with Section 1027.3.] and ramps shall have a minimum fire separation distance of 10 feet (3048 mm) measured at right angles from the exterior edge of the stairway or ramps, including landings, to:

1.	Adjacent lot lines.

2.	Other portions of the building.

3.	Other buildings on the same lot unless the adjacent building exterior walls and openings are protected in accordance with Section 705 based on fire separation distance.

For the purposes of this section, other portions of the building shall be treated as separate buildings.

Exception: Noncombustible stoops and ramps not exceeding one story above grade plane located at the street wall and terminating at the street are permitted to be located within 10 feet (3048 mm) of adjacent lot lines or buildings on the same lot when serving:

1.	Group R-2 occupancies in buildings of noncombustible construction not exceeding four stories in height and a total of four dwelling units.

2.	Group R-3 occupancies.

[1026.6] 1027.6 Exterior [ramps and] exit stairway and ramp protection. Exterior exit [ramps and] stairways and ramps shall be separated from the interior of the building as required in Section [1022.1] 1023.2. Openings shall be limited to those necessary for egress from normally occupied spaces.  Where a vertical plane projecting from the edge of an exterior exit stairway or ramp and landings is exposed by other parts of the building at an angle of less than 180 degrees (3.14 rad), the exterior wall shall be rated in accordance with Section 1023.7.

Exceptions:

1.	In all occupancies other than Group R-1 or R-2, separation from the interior of the building is not required in buildings that are [no] not more than two stories above grade plane where a level of exit discharge serving such occupancies is the first story above grade plane.

2.	Separation from the interior of the building is not required where the exterior [ramp or] exit stairway or ramp is served by an exterior exit ramp or balcony that connects two remote exterior exit stairways or other approved exits, with a perimeter that is not less than 50 percent open. To be considered open, the opening shall be [a minimum of] not less than 50 percent of the height of the enclosing wall, with the top of the openings [no] not less than 7 feet (2134 mm) above the top of the balcony.

3.	Separation from the [interior] open-ended corridor of the building is not required for [an exterior ramp or stairway located in a building or structure that is permitted to have unenclosed interior stairways in accordance with Section 1022.1] exterior exit stairways or ramps, provided that Items 3.1 through 3.5 are met.

[4.	Separation from the interior of the building is not required for exterior ramps or stairways connected to open-ended corridors, provided that Items 4.1 through 4.4 are met:]

[4.1.] 3.1.	The building, including open-ended corridors, and stairways and ramps [and stairs], shall be equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1 or 903.3.1.2.

[4.2.] 3.2.	The open-ended corridors comply with Section [1018] 1020.

[4.3.] 3.3.	The open-ended corridors are connected on each end to an exterior exit [ramp or] stairway or ramp complying with Section [1026] 1027.

[4.4.] 3.4.	The exterior walls and openings adjacent to the exterior exit stairway or ramp comply with Section 1023.7.

3.5.	At any location in an open-ended corridor where a change of direction exceeding 45 degrees (0.79 rad) occurs, a clear opening of not less than 35 square feet (3.3 m2) or an exterior [ramp or] stairway or ramp shall be provided. Where clear openings are provided, they shall be located so as to minimize the accumulation of smoke or toxic gases.

[1026.7] 1027.7 Fire towers. Fire towers may be used as exits in lieu of interior stairs provided they comply with all of the requirements for stairways as per Section [1009] 1011, except as modified below.

[1026.7.1] 1027.7.1 Enclosure. The enclosing walls of fire towers shall be of noncombustible materials or assemblies having a fire-resistance rating of at least 4 hours. Such walls shall be without openings, except for doors serving as means of egress.

[1026.7.2] 1027.7.2 Access. At each story served by a fire tower, access to the stairways of such fire tower shall be provided through outside balconies or fireproof vestibules. Such balconies or vestibules shall be at least 44 inches (1118 mm) in width and shall have unpierced floors of noncombustible materials and shall be provided with substantial guard railings at least 4 feet (1219 mm) high, without any openings greater than 5 inches (127 mm) in width.

[1026.7.3] 1027.7.3 Balconies and vestibules. Such balconies or vestibules of fire towers shall be level with the floors of the structure and the platforms of the stairs connected by such balconies. Such balconies or vestibules shall be separated from the structure and the stairs by self-closing swinging doors with a one and ½-hour fire protection rating, capable of being opened from both sides without the use of a key or other unlocking device.

Balconies or vestibules of fire towers shall open on a street or yard, or on a court open vertically to the sky for its full height, having a minimum net area of 105 square feet (9.7 m2) and a minimum dimension of 7 feet (2134 mm). The opening from the vestibule to the street, yard or court shall have a minimum area of 18 square feet (1.7 m2) and a minimum dimension of 30 inches (762 mm). It shall be unlawful to leave openings in the court walls surrounding an interior fire tower, other than the openings from the vestibules, within 15 feet (4572 mm) of the balcony, except that self-closing windows with a ¾-hour fire protection rating may be used if such windows are at least 10 feet (3048 mm) from the balcony, provided that the area of the court is at least 12 feet by 24 feet (3658 mm by 7315 mm).

[1026.7.4] 1027.7.4 Termination. Fire towers shall terminate at grade level and shall exit directly to the street independently of corridors serving other stairways, except when the fire tower terminates in the ground floor corridor outside of the inner vestibule and within 10 feet (3048 mm) of the building line.

SECTION BC [1027] 1028
EXIT DISCHARGE

[1027.1] 1028.1 General. Exits shall discharge directly to the exterior of the building. The exit discharge shall be at grade or shall provide a direct [access] path of egress travel to grade. The exit discharge shall not reenter a building. The combined use of Exceptions 1 and 2 below shall not exceed 50 percent of the number and minimum width or required capacity of the required exits.

Exceptions:

1.	[A maximum of] Not more than 50 percent of the number and minimum width or required capacity of [the] interior exit [enclosures] stairways and ramps is permitted to egress through protected areas on the level of discharge provided all of the following conditions are met:

1.1.	Such protected area shall [provide] be provided with a free and unobstructed path of travel to an exterior exit door and such exit is readily visible and identifiable within 40 feet from the point of termination of the [exit] enclosure.

1.2.	The protected area [shall be] of the level of exit discharge is separated from areas below by construction conforming to the fire-resistance rating for the [exit] enclosure.

1.3.	The protected area shall be provided with an approved automatic sprinkler system. [All portions] Portions of the level of exit discharge with access to the egress path shall be either [be protected] equipped throughout with an automatic sprinkler system installed in accordance with Section 903.3.1.1 or 903.3.1.2, or separated from the egress path in accordance with the requirements for the enclosure of [exits] interior exit stairways or ramps.

1.4.	Where a required interior exit stairway or ramp and an exit access stairway or ramp serve the same floor level and terminate at the same level of exit discharge, the termination of the exit access stairway or ramp and the exit discharge door of the interior exit stairway or ramp shall be separated by a distance of not less than 30 feet (9144 mm) or not less than one-fourth the length of the maximum overall diagonal dimension of the building, whichever is less. The distance shall be measured in a straight line between the exit discharge door from the interior exit stairway or ramp and the last tread of the exit access stairway or termination of slope of the exit access ramp.

1.5.	The capacity of the protected area shall not be less than required by Section [1027.2] 1028.2 in addition to the occupant load of all exits serving communication spaces.

2.	[A maximum of] Not more than 50 percent of the number and minimum width or required capacity of the interior exit [enclosures] stairways and ramps is permitted to egress through a vestibule provided all of the following conditions are met:

2.1.	The entire area of the vestibule is separated from areas below by construction conforming to the fire-resistance rating [for] of the interior exit [enclosure] stairway or ramp enclosure.

2.2.	The depth from the exterior of the building is not greater than 10 feet (3048 mm) and the length is not greater than 30 feet (9144 mm).

2.3.	The area is separated from the remainder of the level of exit discharge by [construction providing protection at least the equivalent of approved wired glass in steel frames] a fire partition constructed in accordance with Section 708.

Exception: The maximum transmitted temperature rise is not required.

2.4	The area is used only for means of egress and exits directly to the outside.

3.	[Stairways in open parking garages complying with Section 1022.1, Exception 4, are permitted to egress through the open parking garage at their levels of exit discharge.]

[4.	] In buildings in occupancy Group R-2, up to 100 percent of the number and minimum width and required capacity of the interior exit [enclosures is] stairways and ramps are permitted to egress through a protected area on the level of discharge, if all of the following conditions are met:

[4.1.] 3.1.	Egress is provided in two different directions from the discharge points of all interior exit [enclosures] stairways and ramps to the exterior of the building that are remote from each other.

[4.2.] 3.2.	The exit discharges are arranged and constructed so as to minimize the possibility that all exit discharges would be compromised by smoke, fire or other emergency condition[,and].

[4.3.] 3.3.	Such protected areas shall comply with all requirements of Exception 1 above.

[5.] 4.	Horizontal exits complying with Section [1025] 1026 shall not be required to discharge directly to the exterior of the building.

1028.1.1 Fire Department access. Where Exception 1 or 2 to Section 1028.1 is not applied, not less than one exit that discharges directly to the exterior shall be accessible to the Fire Department:

1.	Through an exit access door directly from the protected area or vestibule, as applicable. Such exit access door shall only be used by the Fire Department and shall not be used as an exit. Signage indicating “No Exit. FDNY Access Only” shall be posted on both sides of the exit access door; or

2.	Within a maximum of 100 feet (30 480 mm) from the exit of the protected area or vestibule, as applicable. Such distance shall be measured along a natural and unobstructed path between the nearest points of the exit doors.

[1027.2] 1028.2 Exit discharge width or capacity. The minimum width or required capacity of the exit discharge shall be not less than the minimum width or required [discharge] capacity of the exits being served.

[1027.3 Exit discharge location. Exterior balconies, stairways and ramps shall be located at least 10 feet (3048 mm) from adjacent lot lines and from other buildings on the same lot unless the adjacent building exterior walls and openings are protected in accordance with Section 705 based on fire separation distance.]

[Exception: Noncombustible stoops and ramps not exceeding one story above grade plane located at the street wall and terminating at the street are permitted to be located within 10 feet (3048 mm) of adjacent lot lines or buildings on the same lot when serving:]

[1.	Group R-2 occupancies in buildings of noncombustible construction not exceeding four stories in height and a total of four dwelling units.]

[2.	Group R-3 occupancies.]

[1027.4] 1028.3 Exit discharge components. Exit discharge components shall be sufficiently open to the exterior so as to minimize the accumulation of smoke and toxic gases.

[1027.5] 1028.4 Egress courts. Egress courts serving as a portion of the exit discharge in the means of egress system shall comply with the requirements of [Section 1027] Sections 1028.4.1 and 1028.4.2.

[1027.5.1] 1028.4.1 Width or capacity. The [width] required capacity of egress courts shall be determined as specified in Section [1005.1] 1005, but [such] the minimum width shall be not [be] less than 44 inches (1118 mm), except as specified herein. Egress courts serving Group R-3 and U occupancies shall be not [be] less than 36 inches (914 mm) in width. The required capacity and width of egress courts shall be unobstructed to a height of 7 feet 6 inches (2286 mm).

Exception: [Doors] Encroachments complying with Section [1005.2] 1005.7.

Where an egress court exceeds the minimum required width and the width of such egress court is then reduced along the path of exit travel, the reduction in width shall be gradual. The transition in width shall be affected by a guard not less than 36 inches (914 mm) in height and shall not create an angle of more than 30 degrees (0.52 rad) with respect to the axis of the egress court along the path of egress travel. [In no case shall the] The width of the egress court shall not be less than the required [minimum] capacity.

[1027.5.1.1 Projections. Doors, when fully opened, and handrails shall not reduce the required width by more than 7 inches (178 mm). Doors in any position shall not reduce the required width by more than one-half. Other nonstructural projections such as trim and similar decorative features are permitted to project into the required width 1½ inches (38 mm) from each side.]

[1027.5.2] 1028.4.2 Construction and openings. Where an egress court serving a building or portion thereof is less than 10 feet (3048 mm) in width, the egress court walls shall have not less than 1-hour fire-resistance-rated construction for a distance of 10 feet (3048 mm) above the floor of the egress court. Openings within such walls shall be protected by opening protectives having a fire protection rating of not less than ¾ hour.

Exception: Protection of exterior walls shall not be required where:

1.	Egress courts serving an occupant load of less than 10.

2.	Egress courts serving Group R-3.

[1027.6] 1028.5 Access to a public way. The exit discharge shall provide a direct and unobstructed access to a public way.

Exception: Where access to a public way cannot be provided, a safe dispersal area shall be provided where all of the following are met:

1.	The area shall be of a size to accommodate [at least] not less than 5 square feet (0.46 m2) for each person.

2.	The area shall be located on the same lot [at least] not less than 50 feet (15 240 mm) away from the building requiring egress.

3.	The area shall be permanently maintained and identified as a safe dispersal area.

4.	The area shall be provided with a safe and unobstructed path of travel from the building.

5.	The area shall be illuminated in accordance with Section [1006.1] 1008.

SECTION BC [1028] 1029
ASSEMBLY

[1028.1] 1029.1 General. [Occupancies in Group] A room or space used for assembly purposes that contains seats, tables, displays, equipment or other material shall comply with this section.

1029.1.1 Bleachers. Bleachers, grandstands and folding and telescopic seating, that are not building elements, shall comply with ICC 300. Bleachers, folding and telescopic seating, and grandstands shall be permitted to be constructed of combustible or noncombustible materials in accordance with Section 302 of ICC 300 and the following:

1.	Where the number of seats or seating positions of the bleachers, grandstands, and folding and telescopic seating within an assembly space exceeds 300, the dedicated structural system supporting the bleachers, folding and telescopic seating, or grandstands shall be constructed of noncombustible materials.

2.	Where the space beneath the bleachers, grandstands, or folding and telescopic seating is used for placement of portable equipment, including but not limited to those for audio, video, data, lighting, motion control, and associated wiring, the decking on such bleachers, grandstands, or folding and telescopic seating shall be constructed of fire-retardant-treated wood complying with Section 2303.2 or other Class A materials.

3.	Where the number of seats or seating positions of the bleachers, grandstands, and folding and telescopic seating within an assembly space exceeds 1,500, the dedicated structural system supporting the bleachers, grandstands, or folding and telescopic seating, and the decking on such bleachers, grandstands, or folding and telescopic seating, shall be constructed of noncombustible materials.

[No place of assembly shall be located within 250 feet (76 200 mm) of any occupancy containing explosive contents.]

1029.1.1.1 Spaces under grandstands and bleachers. Where spaces under grandstands or bleachers are used for purposes other than means of egress, ticket booths less than 100 square feet (9.29 m2) and toilet rooms, such spaces shall be separated by fire barriers complying with Section 707 and horizontal assemblies complying with Section 711, with not less than 1-hour fire-resistance-rated construction. An automatic smoke detection system shall be installed in such separated spaces. The system shall be activated in accordance with Section 907.5.

[1028.1.1] 1029.1.2 Place of assembly Certificate of Operation. A Certificate of Operation shall be required for a place of assembly in accordance with Section [303.2] 303.7. It shall be unlawful to occupy any building or space as a place of assembly unless and until a Certificate of Operation therefore has been issued by the department pursuant to the provisions of Chapter 1 of Title 28 of the Administrative Code.

[1028.1.2] 1029.1.3 Posted capacity sign. Signs shall be posted in all assembly spaces, indicating the number of persons who may legally occupy the space. Every room or space in such places of assembly shall have the occupant load of the room or space posted in a conspicuous place, near the main exit or exit access doorway from the room or space. Posted signs shall be of an approved legible permanent design in accordance with Section 1029.1.4, and shall be maintained by the owner or the owner’s authorized agent.

Exception: Signs shall not be required where seating is fixed in place in accordance with an approved plan and no provision is made for standee spaces.

[Such] Posted capacity signs, where required, shall read as follows:

OCCUPANCY BY MORE THAN . . . . . . PERSONS IS DANGEROUS AND UNLAWFUL Certificate of Operation No . . . . . . Commissioner, Dept. of Buildings, City of New York

[1028.1.2.1] 1029.1.3.1 Multiple-occupant load sign. When a space is occupied for multiple purposes involving different occupant loads the sign shall read as follows:

OCCUPANCY BY MORE THAN

(number) . . . . .PERSONS AS (type of occupancy) . . .

OR BY

(number) . . . . .PERSONS AS (type of occupancy) . . .

OR BY

(number) . . . . .PERSONS AS (type of occupancy) . . .

IS DANGEROUS AND UNLAWFUL

Certificate of Operation No . . . . . .

Commissioner, Dept. of Buildings, City of New York

[1028.1.2.2] 1029.1.4 Design of capacity signs. Signs shall be at least 12 inches (305 mm) wide and 16 inches (406 mm) high. The lettering shall be red on a white background. The letters shall be at least 1 inch (25 mm) high and the numerals at least 1¼ inches (32 mm) high. Signs hall be framed under a transparent protective cover, and permanently mounted in a location that is conspicuously visible to a person entering the space. Signs shall be lighted by artificial illumination at all times during occupancy to maintain at least 5 foot-candles (54 lux) on the surface of the sign.

[1028.1.3] 1029.1.5 Approved plans. In every place of assembly providing seating or other moveable furnishings, copies of approved plans and approved alternate plans shall be kept on the premises. The plans shall be readily available for inspection, and shall provide the following information:

1.	For assembly spaces:

1.1.	The location of each seat of each tier of seating, along with the number of occupants of each seating section.

1.2.	The location and number of standees for each standee area.

1.3.	The total number of occupants of each tier and of the assembly space.

1.4.	The location and classification of all exits.

2.	For safe areas:

2.1.	The furniture and equipment arrangement and location.

2.2.	The number of occupants to be accommodated.

3.	For stage areas:

3.1.	The maximum number of occupants, including audience seating on the stage.

3.2.	Any conditions limiting the use of the stage area.

3.3.	The location of all exits.

These plans shall not be smaller in size than required for ⅛-inch scale plans.

[1028.2] 1029.2 Assembly with occupant load greater than 300. [Buildings or spaces occupied by Group A that have] A building, room or space used for assembly purposes that has an occupant load of greater than 300 [shall be] and is provided with a main exit[. Such], that main exit shall be of sufficient [width] capacity to accommodate not less than one-half of the occupant load, but such [width] capacity shall be not [be] less than the total required [width] capacity of all means of egress leading to the exit. Where the main use or dominant occupancy of the building is classified as a Group A occupancy, the main exit shall front on [at least] not less than one street or an unoccupied space of not less than 10 feet (3048 mm) in width that adjoins a street or public way. Other additional exits shall provide an egress capacity for at least one-half of the total occupant load served by that level and comply with Section [1015.2] 1007.1.

Exception: In a building, room or space used for assembly [occupancies] purposes where there is [no] not a well-defined main exit or where multiple main exits are provided, exits shall be permitted to be distributed around the perimeter of the building provided that the total [width] capacity of egress is not less than 100 percent of the required [width] capacity.

[1028.3] 1029.3 Reserved.

[1028.4] 1029.4 Foyers and lobbies. In Group A-1 occupancies, where persons are admitted to the building at times when seats are not available, such persons shall be allowed to wait in a lobby or similar space, provided such lobby or similar space shall not encroach upon the minimum width or required [clear width] capacity of the means of egress. Such foyer, if not directly connected to a public street by all the main entrances or exits, shall have a straight and unobstructed corridor or path of travel to every such main entrance or exit.

[1028.5] 1029.5 Interior balcony and gallery means of egress. For balconies, galleries or press boxes having a seating capacity of [50] 75 or more located in [Group A occupancies, at least] a building, room or space used for assembly purposes, not less than two means of egress shall be provided, with one from each side of every balcony, gallery[,] or press box[and at least one leading directly to an exit].

[1028.5.1 Enclosure of openings. Interior stairways and other vertical openings shall be enclosed in an exit enclosure as provided in Section 1022.1, except that stairways are permitted to be open between the balcony, gallery or press box and the main assembly floor in occupancies such as theaters, places of religious worship, auditoriums and sports facilities.]

1029.5.1 Accessible means of egress. At least one accessible means of egress is required from a balcony, gallery or press box level containing accessible seating locations in accordance with Section [1007.3] 1009.3 or [1007.4] 1009.4.

[1028.6] 1029.6 [Width of means] Capacity of [egress] aisle for assembly. The [clear width] required capacity of aisles [and other means of egress] shall [comply] be not less than that determined in accordance with Section [1028.6.1] 1029.6.1 where smoke-protected assembly seating is not provided and with Section [1028.6.2] 1029.6.2 or [1028.6.3] 1029.6.3 where smoke-protected assembly seating is provided. [The clear width shall be measured to walls, edges of seating and tread edges except for permitted projections.]

[1028.6.1] 1029.6.1 Without smoke protection. The [clear width] required capacity in inches (mm) of the aisles [and other means of egress shall provide sufficient capacity] for assembly seating without smoke protection shall be not less than the occupant load served by the egress element in accordance with all of the following, as applicable:

1.	[At least] Not less than 0.3 inch (7.6 mm) of [width] aisle capacity for each occupant served shall be provided on [stairs] stepped aisles having riser heights 7 inches (178 mm) or less and tread depths 11 inches (279 mm) or greater, measured horizontally between tread [nosing] nosings.

2.	[At least] Not less than 0.005 inch (0.127 mm) of additional [stair width] aisle capacity for each occupant shall be provided for each 0.10 inch (2.5 mm) of riser height above 7 inches (178 mm).

3.	Where egress requires [stair] stepped aisle descent, [at least] not less than 0.075 inch (1.9 mm) of additional [width] aisle capacity for each occupant shall be provided on those portions of [stair width] aisle capacity having no handrail within a horizontal distance of 30 inches (762 mm).

4.	Ramped [means of egress] aisles, where slopes are steeper than one unit vertical in 12 units horizontal (8-percent slope), shall have [at least] not less than 0.22 inch (5.6 mm) of clear [width] aisle capacity for each occupant served. Level or ramped [means of egress] aisles, where slopes are not steeper than one unit vertical in 12 units horizontal (8-percent slope), shall have [at least] not less than 0.20 inch (5.1 mm) of clear [width] aisle capacity for each occupant served.

[1028.6.2] 1029.6.2 Smoke-protected assembly seating. The [clear width] required capacity in inches (mm) of [aisles and other means of egress] the aisle for smoke-protected assembly seating shall be not [be] less than the occupant load served by the egress element multiplied by the appropriate factor in Table [1028.6.2] 1029.6.2. The total number of seats specified shall be those within the space and exposed to the same smoke-protected environment. Interpolation is permitted between the specific values shown. A life safety evaluation, complying with NFPA 101, shall be done for a facility utilizing the reduced width requirements of Table [1028.6.2] 1029.6.2 for smoke-protected assembly seating subject to the approval by the commissioner.

Exception: For [an] outdoor smoke-protected assembly seating with an occupant load not greater than 18,000, the [clear width] required capacity in inches (mm) shall be determined using the factors in Section [1028.6.3] 1029.6.3.

TABLE [1028.6.2] 1029.6.2
[WIDTH OF AISLES AND OTHER MEANS OF EGRESS] CAPACITY FOR AISLES FOR SMOKE-PROTECTED ASSEMBLY

| TOTAL NUMBER OF SEATS IN THE [SPACE EXPOSED TO THE SAME] SMOKE- PROTECTED [ENVIRONEMENT] ASSEMBLY SEATING | INCHES OF CLEAR WIDTH PER SEAT SERVED |
| --- | --- |
|  | [Stairs and aisle steps] Stepped aisles with handrails within 30 inches | [Stairs and aisle steps] Stepped aisles without handrails within 30 inches | [Passageways, doorways and ramps] Level aisles or ramped aisles not steeper than 1 in 10 in slope | [Ramps] Ramped aisles steeper than 1 in 10 in slope |
| Equal to or less than 5,000 | 0.200 | 0.250 | 0.150 | 0.165 |
| 10,000 | 0.130 | 0.163 | 0.100 | 0.110 |
| 15,000 | 0.096 | 0.120 | 0.070 | 0.077 |
| 20,000 | 0.076 | 0.095 | 0.056 | 0.062 |
| Equal to or greater than 25,000 | 0.060 | 0.075 | 0.044 | 0.048 |

For SI: 1 inch = 25.4 mm.

[1028.6.2.1] 1029.6.2.1 Smoke control. [Means of egress] Aisles and aisle accessways serving a smoke-protected assembly seating area shall be provided with a smoke control system complying with Section 909 or natural ventilation designed to maintain the smoke level [at least] not less than 6 feet (1829 mm) above the floor of the means of egress.

[1028.6.2.2] 1029.6.2.2 Roof height. A smoke-protected assembly seating area with a roof shall have the lowest portion of the roof deck not less than 15 feet (4572 mm) above the highest aisle or aisle accessway.

Exception: A roof canopy in an outdoor stadium shall be permitted to be less than 15 feet (4572 mm) above the highest aisle or aisle accessway provided that there are no objects less than 80 inches (2032 mm) above the highest aisle or aisle accessway.

[1028.6.2.3] 1029.6.2.3 Automatic sprinklers. Enclosed areas with walls and ceilings in buildings or structures containing smoke-protected assembly seating shall be protected with an approved automatic sprinkler system in accordance with Section 903.3.1.1.

Exceptions:

1.	The floor area used for contests, performances or entertainment, provided the roof construction is more than 50 feet (15 240 mm) above the floor level and the use is restricted to low fire hazard uses.

2.	Press boxes and storage facilities less than 1,000 square feet (93 m2) in area.

3.	Outdoor seating facilities where seating and the means of egress in the seating area are essentially open to the outside.

[1028.6.3] 1029.6.3 [Width of means of egress for outdoor] Outdoor smoke-protected assembly seating. The [clear width] required capacity in inches (mm) of aisles [and other means of egress] shall be not less than the total occupant load served by the egress element multiplied by 0.08 (2.0 mm) where egress is by [aisles and stairs] stepped aisle and multiplied by 0.06 (1.52 mm) where egress is by ramps, corridors, tunnels,[or] vomitories, level aisles or ramped aisles.

Exception: The [clear width] required capacity in inches (mm) of aisles [and other means of egress] shall be permitted to comply with Section [1028.6.2] 1029.6.2 for the number of seats in the outdoor smoke-protected assembly seating where Section [1028.6.2] 1029.6.2 permits less [width] capacity.

[1028.7] 1029.7 Travel distance. Exits and aisles shall be so located such that the travel distance to an exit door shall be provided in accordance with Table [1028.7] 1029.7. At least one exit [opening] door shall be available from every attached seat or standee space in an assembly space, or from the most remote point in the space when movable seats are provided or, when no seats are provided, within the primary travel distance limitation listed in Table [1028.7] 1029.7. In addition, an alternate exit [opening] door shall be available from every attached seat or standee space, or from the most remote point when attached seats are not provided within the secondary travel distance limitation listed in Table [1028.7] 1029.7. Such alternate exit [openings] door may serve to satisfy the requirements for primary travel distance for other seats or locations. Exit [openings] door satisfying the primary and secondary travel distance requirements for any one seat or location shall be separated [from each other by a distance of at least 25 feet (7620 mm)] in accordance with Section 1007.1. Where aisles are provided for seating, the distance shall be measured along the aisles and aisle accessway without travel over or on the seats.

[Exception] Exceptions: For the purposes of this section, travel distances may be measured in accordance with the following exceptions:

1.	Smoke-protected assembly seating: The primary travel distance shall be permitted to be measured from each seat or standee space to the nearest entrance to a vomitory or concourse, and shall not exceed 200 feet (60 960 mm). The secondary travel distance shall be permitted to be measured from each such seat or standee space to an alternate entrance to the vomitory or concourse, and shall not exceed 300 feet (91 440 mm). The travel distance from any such [entrance] entrances to the vomitory or concourse to a [stair] stairway, ramp or walk on the exterior of the building shall not exceed 200 feet (60 960 mm).

2.	Open-air seating served by exit access stairways and ramps: The primary travel distance shall be permitted to be measured from each seat or standee space to the closest riser of an exit access stairway or the closest slope of an exit access ramp that are outside the assembly space. The secondary travel distance shall be permitted to be measured to the closest riser of an alternate exit access stairway or the closest slope of an alternate exit access ramp that are outside the assembly space.

3.	Assembly with safe areas:  Where an assembly space is provided with an exit access doorway that opens directly to a safe area in accordance with Section 1029.19, the primary travel distance shall be permitted to be measured to such an exit access doorway.  The secondary travel distances shall also be permitted to be measured to an alternate exit access doorway that opens directly to a safe area.  The travel distance within safe areas shall be in accordance with Section 1017 based on the occupancy classification of the main occupancy of the building or portion thereof to which the assembly space is ancillary. Where a safe area contains other occupancies, travel distances within such safe area shall comply with Section 1017.

4.	Assembly with open exterior spaces:  Where an assembly space is provided with an exit that opens directly to an open exterior space in accordance with Section 1029.19, the primary and secondary travel distances shall be measured to such an exit.

TABLE [1028.7] 1029.7
TRAVEL DISTANCE

| OCCUPANCY | NON SPRINKLERED | SPRINKLERED |
| --- | --- | --- |
|  | PRIMARY | SECONDARY | PRIMARY | SECONDARY |
| A-1, A-2, A-3, A-4 | 100 | 150 | 150 | 250 |
| A-5 | 200 | 300 | 200 | 300 |

[1028.8] 1029.8 Common path of egress travel. The common path of egress travel shall not exceed 30 feet (9144 mm) from any seat to a point where an occupant has a choice of two paths of egress travel to two exits.

Exceptions:

1.	For areas, such as box seats, galleries or balconies, serving [not more] less than [50] 75 occupants, the common path of egress travel shall not exceed 75 feet (22 860 mm).

2.	For smoke-protected assembly seating, the common path of egress travel shall not exceed 50 feet (15 240 mm).

1029.8.1 Path through adjacent row. Where one of the two paths of travel is across the aisle through a row of seats to another aisle, there shall be not more than 24 seats between the two aisles, and the minimum clear width between rows for the row between the two aisles shall be 12 inches (305 mm) plus 0.6 inch (15.2 mm) for each additional seat above seven in the row between aisles.

Exception: For smoke-protected assembly seating there shall be not more than 40 seats between the two aisles and the minimum clear width shall be 12 inches (305 mm) plus 0.3 inch (7.6 mm) for each additional seat.

[1028.9] 1029.9 Assembly aisles are required. Every occupied portion of any [occupancy in Group A] building, room or space used for assembly purposes that contains seats, tables, displays, similar fixtures or equipment shall be provided with aisles leading to exits or exit access doorways in accordance with this section. [Aisle accessways for tables and seating shall comply with Section 1017.4.]

[1028.9.1] 1029.9.1 Minimum aisle width. The minimum clear width [of] for aisles shall [be as shown] comply with one of the following:

1.	Forty-eight inches (1219 mm) for [aisle stairs] stepped aisles having seating on each side.

Exception: Thirty-six inches (914 mm) where the [aisle does not] stepped aisles serve [more] less than [50] 51 seats.

2.	Thirty-six inches (914 mm) for [aisle stairs] stepped aisles having seating on only one side.

Exception: Twenty-three inches (584 mm) between a stepped aisle handrail and seating where a stepped aisle does not serve more than five rows on one side.

3.	Twenty-three inches (584 mm) between an aisle stair handrail or guard and seating where the stepped aisle is subdivided by a mid-aisle handrail.

4.	Forty-two inches (1067 mm) for level or ramped aisles having seating on both sides.

Exception: Thirty-six inches (914 mm) where the aisle [does not serve more] serves less than [50] 51 seats.

5.	Thirty-six inches (914 mm) for level or ramped aisles having seating on only one side.

6.	Thirty-six inches (914 mm) for aisles other than those listed above and cross-aisles serving less than 51 persons.

[1028.9.2] 1029.9.2 Aisle [width] catchment area. The aisle [width] shall provide sufficient [egress] capacity for the number of persons accommodated by the catchment area served by the aisle. The catchment area served by an aisle is that portion of the total space [that is] served by that section of the aisle. In establishing catchment areas, the assumption shall be made that there is a balanced use of all means of egress, with the number of persons in proportion to egress capacity.

[1028.9.3] 1029.9.3 Converging aisles. Where aisles converge to form a single path of egress travel, the required [egress] capacity of that path shall be not [be] less than the combined required capacity of the converging aisles.

[1028.9.4] 1029.9.4 Uniform width and capacity. Those portions of aisles, where egress is possible in either of two directions, shall be uniform minimum width or [in] required [width] capacity.

[1028.9.5] 1029.9.5 [Assembly aisle termination] Dead end aisles. Each end of an aisle shall [terminate at] be continuous to a cross aisle, foyer, doorway, vomitory, [or] concourse or stairway in accordance with Section 1029.9.7 having access to an exit. Travel through dead-end aisles shall be subject to Section 1029.8. Dead-end aisles shall be not greater than 20 feet (6096 mm) in length.

Exceptions:

1.	[Dead-end aisles shall not be greater than 20 feet (6096 mm) in length.]

[2.	For smoke-protected assembly seating, the dead-end aisle length of vertical aisles shall not exceed a distance of 50 feet (15 240 mm)] A dead-end aisle of up to 16 rows shall be permitted to exceed 20 feet (6096 mm) in length where seats served by the dead-end aisle are not more than 24 seats from another aisle, measured along a row of seats having a clear width of not less than 12 inches (305 mm) plus 0.6 inches (15.2 mm) for each additional seat over a total of 7 in the row.

2.	For smoke-protected assembly seating, dead end aisles of up to 21 rows may be permitted to exceed 20 feet (6096 mm) in length provided seats served by the dead-end aisle are not more than 40 seats from another aisle, measured along a row of seats having a clear width of not less than 12 inches (305 mm) plus 0.3 inches (7.6 mm) for each additional seat over a total of 7 in the row.

1029.9.6 Aisle measurement. The clear width for aisles shall be measured to walls, edges of seating and tread edges except for permitted projections.

Exception: The clear width of aisles adjacent to seating at tables shall be permitted to be measured in accordance with Section 1029.12.1.

[1028.9.6] 1029.9.6.1 Assembly aisle obstructions. There shall not be [no] obstructions in the minimum width or required [width of aisles except for handrails as provided in Section 1028.13] capacity of aisles.

Exception: Handrails are permitted to project into the required width of stepped aisles and ramped aisles in accordance with Section 1014.8.

1029.9.7 Stairways connecting to stepped aisles and vomitories. A stairway that connects a stepped aisle or a vomitory to a cross aisle, concourse, or to another aisle shall be permitted to comply with the assembly aisle walking surface requirements of Section 1029.13. Transitions between stairways and stepped aisles shall comply with Section 1029.10.

1029.10 Transitions. Transitions between stairways and stepped aisles shall comply with either Section 1029.10.1 or 1029.10.2.

1029.10.1 Transitions and stairways that maintain stepped aisle riser and tread dimensions. Stepped aisles, transitions and stairways that maintain riser and tread dimensions shall comply with Section 1029.13 as one exit access component.

1029.10.2 Transitions to stairways that do not maintain stepped aisle riser and tread dimensions. Transitions to stairways from stepped aisles with riser and tread dimensions that differ from the stairways shall comply with Sections 1029.10.2.1 through 1029.10.3.

1029.10.2.1 Stairways and stepped aisles in a straight run. Transitions where the stairway is a straight run from the stepped aisle shall have a minimum depth of 22 inches (559 mm) where the treads on the descending side of the transition have greater depth and 30 inches (762 mm) where the treads on the descending side of the transition have lesser depth.

1029.10.2.2 Stairways and stepped aisles that change direction. Transitions where the stairway changes direction from the stepped aisle shall have a minimum depth of 11 inches (280 mm) or the stepped aisle tread depth, whichever is greater, between the stepped aisle and stairway.

1029.10.3 Transition marking. A distinctive marking stripe shall be provided at each nosing or leading edge adjacent to the transition. Such stripe shall be not less than 1 inch (25 mm), and not more than 2 inches (51 mm), wide. The edge marking stripe shall be distinctively different from the stepped aisle contrasting marking stripe.

1029.11 Construction. Aisles, stepped aisles and ramped aisles shall be built of materials consistent with the types permitted for the type of construction of the building.

Exception: Wood handrails shall be permitted for all types of construction. Bleachers, grandstands and folding and telescopic seating shall be built of materials permitted by Section 1029.1.1.

1029.11.1 Walking surface. The surface of aisles, stepped aisles and ramped aisles shall be of slip-resistant materials that are securely attached. The surface for stepped aisles shall comply with Section 1011.7.1.

1029.11.2 Outdoor conditions. Outdoor aisles, stepped aisles and ramped aisles and outdoor approaches to aisles, stepped aisles and ramped aisles shall be designed so that water will not accumulate on the walking surface.

1029.12 Aisle accessways. Aisle accessways for seating at tables shall comply with Section 1029.12.1. Aisle accessways for seating in rows shall comply with Section 1029.12.2.

1029.12.1 Seating at tables. Where seating is located at a table or counter and is adjacent to an aisle or aisle accessway, the measurement of required clear width of the aisle or aisle accessway shall be made to a line 19 inches (483 mm) away from and parallel to the edge of the table or counter. The 19-inch (483 mm) distance shall be measured perpendicular to the side of the table or counter. In the case of other side boundaries for aisles or aisle accessways, the clear width shall be measured to walls, edges of seating and tread edges.

Exception: Where tables or counters are served by fixed seats, the width of the aisle or aisle accessway shall be measured from the back of the seat.

1029.12.1.1 Aisle accessway capacity and width for seating at tables. Aisle accessways serving arrangements of seating at tables or counters shall comply with the capacity requirements of Section 1005 but shall not have less than 12 inches (305 mm) of width plus 1/2 inch (12.7 mm) of width for each additional 1 foot (305 mm), or fraction thereof, beyond 12 feet (3658 mm) of aisle accessway length measured from the center of the seat farthest from an aisle.

Exception: Portions of an aisle accessway having a length not exceeding 6 feet (1829 mm) and used by a total of not more than four persons.

1029.12.1.2 Seating at table aisle accessway length. The length of travel along the aisle accessway shall not exceed 30 feet (9144 mm) from any seat to the point where a person has a choice of two or more paths of egress travel to separate exits.

[1028.10] 1029.12.2 Clear width of aisle accessways serving seating in rows. Where seating rows have 14 or fewer seats, the minimum clear aisle accessway width shall be not [be] less than 12 inches (305 mm) measured as the clear horizontal distance from the back of the row ahead and the nearest projection of the row behind. Where chairs have automatic or self-rising seats, the measurement shall be made with seats in the raised position. Where any chair in the row does not have an automatic or self-rising seat, the measurements shall be made with the seat in the down position. For seats with folding tablet arms, row spacing shall be determined with the tablet arm in the used position.

Exception: For seats with folding tablet arms, row spacing is permitted to be determined with the tablet arm in the stored position where the tablet arm when raised manually to vertical position in one motion automatically returns to the stored position by force of gravity.

[1028.10.1] 1029.12.2.1 Dual access. For rows of seating served by aisles or doorways at both ends, there shall be not [be] more than 100 seats per row. The minimum clear width of 12 inches (305 mm) between rows shall be increased by 0.3 inch (7.6 mm) for every additional seat beyond 14 seats[, but the] where seats have backrests or beyond 21 where seats are without backrests. The minimum clear width is not required to exceed 22 inches (559 mm).

Exception: For smoke-protected assembly seating, the row length limits for a 12-inch-wide (305 mm) aisle accessway, beyond which the aisle accessway minimum clear width shall be increased, are in Table [1028.10.1] 1029.12.2.1.

TABLE [1028.10.1] 1029.12.2.1
SMOKE-PROTECTED
ASSEMBLY AISLE ACCESSWAYS

| TOTAL NUMBER OF SEATS IN THE SMOKE- PROTECTED ASSEMBLY [OCCUPANCY] SEATING | MAXIMUM NUMBER OF SEATS PER ROW PERMITTED TO HAVE A MINIMUM 12-INCH CLEAR WIDTH AISLE ACCESSWAY |
| --- | --- |
|  | Aisle or doorway at both ends of row |
|  | Seats with backrests | Seats without backrests |
| Less than 4,000 | 14 | 21 |
| 4,000 | 15 | 22 |
| 7,000 | 16 | 23 |
| 10,000 | 17 | 24 |
| 13,000 | 18 | 25 |
| 16,000 | 19 | 26 |
| 19,000 | 20 | 27 |
| 22,000 and greater | 21 | 28 |

For SI: 1 inch = 25.4 mm.

[1028.10.2] 1029.12.2.2 Single access. For rows of seating served by an aisle or doorway at only one end of the row, the minimum clear width of 12 inches (305 mm) between rows shall be provided. Not more than eight chairs shall be provided in such row of seating.

[1028.11] 1029.13 Assembly aisle walking surfaces. Ramped aisles shall comply with Section 1029.13.1. Stepped aisles shall comply with Section 1029.13.2.

1029.13.1 Ramped aisles. Aisles [with a slope not exceeding] that are sloped more than one unit vertical in [eight] 20 units horizontal ([12.5] 5-percent slope) shall [consist] be considered a ramped aisle. Ramped aisles that serve as part of [a ramp having] an accessible route in accordance with Sections 1009 and 1108.2 shall have a [slip-resistant walking surface] maximum slope of one unit vertical in 12 units horizontal (8-percent slope). The slope of other ramped aisles shall not exceed one unit vertical in 8 units horizontal (12.5-percent slope).

1029.13.1.1 Cross slope. The slope measured perpendicular to the direction of travel of a ramped aisle shall not be steeper than one unit vertical in 48 units horizontal (2-percent slope).

1029.13.1.2 Landings. Ramped aisles shall have landings in accordance with Sections 1012.6 through 1012.6.5. Landings for ramped aisles shall be permitted to overlap required aisles or cross aisles.

1029.13.1.3 Edge protection. Ramped aisles shall have edge protection in accordance with Section 1012.10 and 1012.10.1.

Exception: In assembly spaces with fixed seating, edge protection is not required on the sides of ramped aisles where the ramped aisles provide access to the adjacent seating and aisle accessways.

1029.13.2 Stepped aisles. Aisles with a slope exceeding one unit vertical in eight units horizontal (12.5-percent slope) shall consist of a series of risers and treads that extends across the full width of aisles and complies with Sections [1028.11.1] 1029.13.2.1 through [1028.11.4] 1029.13.2.4.

[1028.11.1] 1029.13.2.1 Treads. Tread depths shall be [a minimum of] not less than 11 inches (279 mm) and shall have dimensional uniformity.

Exception: The tolerance between adjacent treads shall not exceed [0.188] 3/16 inch (4.8 mm).

[1028.11.2] 1029.13.2.2 Risers. Where the gradient of [aisle stairs] stepped aisles is to be the same as the gradient of adjoining seating areas, the riser height shall be not [be] less than 4 inches (102 mm) nor more than 8 inches (203 mm) and shall be uniform within each flight.

Exception: Riser height nonuniformity shall be limited to the extent necessitated by changes in the gradient of the adjoining seating area to maintain adequate sightlines. Where nonuniformities exceed [0.188] 3/16 inch (4.8 mm) between adjacent risers, the exact location of such nonuniformities shall be indicated with a distinctive marking stripe on each tread at the nosing or leading edge adjacent to the nonuniform risers. Such stripe shall be [a minimum of] not less than 1 inch (25 mm), and [a maximum of] not more than 2 inches (51 mm), wide. The edge marking stripe shall be distinctively different from the contrasting marking stripe.

1029.13.2.2.1 Construction tolerances. The tolerance between adjacent risers on a stepped aisle that were designed to be equal height shall not exceed 3/16 inch (4.8 mm). Where the stepped aisle is designed in accordance with the Exception of Section 1029.13.2.2, the stepped aisle shall be constructed so that each riser of unequal height, determined in the direction of descent, is not more than ⅜ inch (9.5 mm) in height different from adjacent risers where stepped aisle treads are less than 22 inches (560 mm) in depth and ¾ inch (19.1 mm) in height different from adjacent risers where stepped aisle treads are 22 inches (560 mm) or greater in depth.

[1028.11.3] 1029.13.2.3 Tread contrasting marking stripe. A contrasting marking stripe shall be provided on each tread at the nosing or leading edge such that the location of each tread is readily apparent when viewed in descent. Such stripe shall be [a minimum of] not less than 1 inch (25 mm), and [a maximum of] not more than 2 inches (51 mm), wide.

Exception: The contrasting marking stripe is permitted to be omitted where tread surfaces are such that the location of each tread is readily apparent when viewed in descent.

1029.13.2.4 Nosing and profile. Nosing and riser profile shall comply with Sections 1011.5.5 through 1011.5.5.3.

[1028.11.4 Step lighting. Each step shall have a steplight.]

[1028.11.5] 1029.13.3 Aisle illumination. Aisles, [and] cross aisles and stepped aisles shall be illuminated in accordance with Section [1006.2] 1008.2.1.

[1028.12] 1029.14 Seat stability. In [places of] a building, room or space used for assembly purposes, the seats shall be securely fastened to the floor.

Exceptions:

1.	In [places of] a building, room or space used for assembly purposes or portions thereof [without ramped or tiered floors] for seating and with 200 or fewer seats, the seats shall not be required to be fastened to the floor, provided that the seating area has a minimum net floor area of 12 square feet (1.11 m2) per person or all seats in a row shall be fastened together with a maximum of 12 seats between aisles where 12 square feet (1.11 m2) per person is not provided.

2.	In [places of] a building, room or space used for assembly purposes or portions thereof with seating at tables and without ramped or tiered floors for seating, the seats shall not be required to be fastened to the floor.

3.	In a building, room or space used for assembly purposes or portions thereof with seating at tables on ramped or tiered floors, the seats shall not be required to be fastened to the floor provided that the seating area has a minimum net floor area of 12 square feet (1.11 m2) per person.

[3.] 4.	In [places of] a building, room or space used for assembly purposes or portions thereof [without ramped or tiered floors] for seating and with greater than 200 seats, the seats shall be securely fastened to the floor, or all seats in a row shall be fastened together with a maximum of 12 seats between aisles.

[4.] 5.	In [places of] a building, room or space used for assembly purposes where flexibility of the seating arrangement is an integral part of the design and function of the space [and seating is on tiered levels], a [maximum] seating area of up to 200 seats shall not be required to be fastened to the floor, provided that the seating area has a minimum net floor area of 12 square feet (1.11 m2) per person or all seats in a row in such seating area shall be fastened together with a maximum of 12 seats between aisles where 12 square feet (1.11 m2) per person is not provided.

[5.] 6.	Groups of seats within a [place of] building, room or space used for assembly purposes separated from other seating by railings, guards, partial height walls or similar barriers with level floors and having [no] not more than 14 seats per group shall not be required to be fastened to the floor.

[6.] 7.	Seats intended for musicians or other performers and separated by railings, guards, partial height walls or similar barriers shall not be required to be fastened to the floor.

Where a building, room or space used for assembly purposes includes mixed seating arrangements and conditions, the seat stability requirements and allowances shall be applied respectively to each portion of the space containing such seating.

[1028.13] 1029.15 Handrails. Ramped aisles having a slope exceeding one unit vertical in 15 units horizontal (6.7-percent slope) and [aisle stairs] stepped aisles shall be provided with handrails in compliance with Section 1014 located either at one or both sides of the [side] aisle or within the aisle width.

Exceptions:

1.	Handrails are not required for ramped aisles [having a gradient no greater than one unit vertical in eight units horizontal (12.5-percent slope) and] with seating on both sides.

2.	Handrails are not required [if] where, at the side of the aisle, there is a guard with a top surface that complies with the graspability requirements of handrails in accordance with Section 1014.3.

3.	Handrail extensions are not required at the top and bottom of [aisle stairs] stepped aisles and [aisle ramp runs] ramped aisles to permit crossovers within the aisles.

[1028.13.1] 1029.15.1 Discontinuous handrails. Where there is seating on both sides of the aisle, the mid-aisle handrails shall be discontinuous with gaps or breaks at intervals not exceeding five rows to facilitate access to seating and to permit crossing from one side of the aisle to the other. These gaps or breaks shall have a clear width of [at least] not less than 22 inches (559 mm) and not greater than 36 inches (914 mm), measured horizontally, and the mid-aisle handrail shall have rounded terminations or bends.

1029.15.2 Handrail termination. Handrails located on the side of stepped aisles shall return to a wall, guard or the walking surface or shall be continuous to the handrail of an adjacent stepped aisle flight.

1029.15.3 Mid-aisle termination. Mid-aisle handrails shall not extend beyond the lowest riser and shall terminate within 18 inches (457 mm), measured horizontally, from the lowest riser. Handrail extensions are not required.

Exception: Mid-aisle handrails shall be permitted to extend beyond the lowest riser where the handrail extensions do not obstruct the width of the cross aisle.

[1028.13.2 Intermediate handrails.] 1029.15.4 Rails. Where mid-aisle handrails are provided in [the middle of aisle stairs] stepped aisles, there shall be an additional [intermediate handrail] rail located approximately 12 inches (305 mm) below the [main] handrail. The rail shall be adequate in strength and attachment in accordance with Section 1607.8.1.2.

[1028.14] 1029.16 Assembly guards. [Assembly guards shall comply with Sections 1028.14.1 through 1028.14.4.] Guards adjacent to seating in a building, room or space used for assembly purposes shall be provided where required by Section 1015 and shall be constructed in accordance with Section 1015 except where provided in accordance with Sections 1029.16.1 through 1029.16.5. At bleachers, grandstands and folding and telescopic seating, guards must be provided where required by ICC 300 and Section 1029.16.1.

1029.16.1 Perimeter guards. Perimeter guards shall be provided where the footboards or walking surface of seating facilities are more than 30 inches (762 mm) above the floor or grade below. Where the seatboards are adjacent to the perimeter, guard height shall be 42 inches (1067 mm) high minimum, measured from the seatboard. Where the seats are self-rising, guard height shall be 42 inches (1067 mm) high minimum, measured from the floor surface. Where there is an aisle between the seating and the perimeter, the guard height shall be measured in accordance with Section 1015.2.

Exceptions:

1.	Guards that impact sightlines shall be permitted to comply with Section 1029.16.3.

2.	Bleachers, grandstands and folding and telescopic seating shall not be required to have perimeter guards where the seating is located adjacent to a wall and the space between the wall and the seating is less than 4 inches (102 mm).

[1028.14.1] 1029.16.2 Cross aisles. Cross aisles located more than 30 inches (762 mm) above the floor or grade below shall have guards in accordance with Section [1013] 1015.

Where an elevation change of 30 inches (762 mm) or less occurs between a cross aisle and the adjacent floor or grade below, guards not less than 26 inches (660 mm) above the aisle floor shall be provided.

Exception: Where the backs of seats on the front of the cross aisle project 24 inches (610 mm) or more above the adjacent floor of the aisle, a guard need not be provided.

[1028.14.2] 1029.16.3 Sightline-constrained guard heights. Unless subject to the requirements of Section [1028.14.3] 1029.16.4, a fascia or railing system in accordance with the guard requirements of Section [1013] 1015 and having a minimum height of 26 inches (660 mm) shall be provided where the floor or footboard elevation is more than 30 inches (762 mm) above the floor or grade below and the fascia or railing would otherwise interfere with the sightlines of immediately adjacent seating.[At bleachers, a guard must be provided where required by ICC 300.]

[1028.14.3] 1029.16.4 Guards at the end of aisles. A fascia or railing system complying with the guard requirements of Section [1013] 1015 shall be provided for the full width of the aisle where the foot of the aisle is more than 30 inches (762 mm) above the floor or grade below. The fascia or railing shall be a minimum of 36 inches (914 mm) high and shall provide a minimum 42 inches (1067 mm) measured diagonally between the top of the rail and the nosing of the nearest tread.

[1028.14.4] 1029.16.5 Toe guard at balconies. An unperforated curb or toe guard at least 12 inches (305 mm) high above the level of the floor shall be provided at the fascia of all balconies.

[1028.15] 1029.17 Bench seating. Where bench seating is used, the number of persons shall be based on one person for each 18 inches (457 mm) of length of the bench.

[1028.16 Standee areas] 1029.18 Standing spaces. [Standee areas] Standing spaces may be permitted within assembly spaces [provide] provided each standee has a minimum of 5 square feet (0.47 m2) of occupiable floor space [width of 22 inches (559 mm) and a minimum depth of 21 inches (533 mm)]. [Standee areas] Standing spaces shall not encroach on the required exit facilities and shall be separated from the space to be left clear for passage [by tape, ribbon or other easily broken material, supported by lightweight posts fixed in stationary sockets].

[1028.17] 1029.19 Places of assembly with an occupant load of less than 12 square feet per person. Places of assembly in which the net floor area, exclusive of stage area, is less than 12 square feet (1.11 m2) per person shall have special egress provisions in accordance with this section.

[1028.17.1] 1029.19.1 Classification of exit [openings] access doorways and exits. For the purposes of Section [1028.17] 1029.19, exit [openings] access doorways and exits shall be classified as follows:

1.	Class 1—Exit [openings] access doorways and exits that are used for normal entry to the assembly space, and that open directly to a safe area or to an open exterior space.

2.	Class 2—Exit [openings] access doorways and exits that are not used for normal entry to the assembly space, and that open directly to a safe area or to an open exterior space.

3.	Class 3—Exit [openings] access doorways and exits that open from the assembly space into corridors, exit passageways or vertical exits.

[1028.17.2] 1029.19.2 Distribution of classes. The required exit capacity from assembly spaces in which the net floor area, exclusive of stage area, is less than 12 square feet (1.11 m2) per person shall be distributed so that exit [openings] access doorways and exits of each class are provided to comply with the following requirements:

1.	For assembly spaces in which the mean floor level is not more than 15 feet (4572 mm) above or below the adjoining grade elevation, the exit capacity shall be distributed as follows:

1.1.	Class 1—not less than 40 percent.

1.2.	Class 2—not more than 60 percent.

1.3.	Class 3—not more than 40 percent.

2.	For assembly spaces in which the mean floor level is more than 15 feet (4572 mm) above or below the adjoining grade elevation, the exit capacity shall be distributed as follows:

2.1.	Class 1—not less than 60 percent.

2.2.	Class 3—not more than 40 percent.

[1028.17.3] 1029.19.3 Safe areas. The capacity of exits from safe areas shall be provided for all occupants of the safe area. Safe areas shall comply with the following requirements:

1.	When provided to serve Class 1 or 2 exit [openings] access doorways, safe areas shall be separated from assembly spaces by fire barriers constructed in accordance with Section 707 or horizontal assemblies constructed in accordance with Section [712] 711, or both, each having a 2-hour fire-resistance rating. Such safe areas shall serve as transition areas in the line and direction of exit travel. They shall serve for normal entry to the assembly space and may be used as corridors, lobbies or lounges.

2.	No room or space classified in Occupancy Group H, S-1, F-1 or F-2 shall open upon a safe area.

3.	Safe areas shall be at a level not more than 6 feet (1829 mm) above or below the level at which egress is made from the assembly space.

4.	Ventilating systems for safe areas shall not be connected to systems serving any other spaces, unless separated from such systems by fire/smoke dampers actuated by smoke detectors.

5.	Collecting safe areas. Places of assembly having more than one assembly space may have a collecting safe area that receives the occupant load discharged into it by other safe areas. Collecting safe areas shall be located within 6 feet (1829 mm) above or below the assembly space nearest to grade.

6.	Occupant load. The occupant load of a safe area shall be the aggregate occupant load of all exit [openings] access doorways discharging directly into it. The occupant load of a collecting safe area shall be the aggregate occupant load of all exit [openings] access doorways discharging directly into it, plus 50 percent of the occupant load of other safe areas discharging into it.

7.	Dimensions. The clear unobstructed floor area of each safe area shall be sufficient to accommodate the total occupant load of the safe area on the basis of 3 square feet (0.28 m2) per person, not including space occupied by furniture or equipment. The minimum dimension of such unobstructed space shall be 8 feet (2438 mm). The width of the unobstructed space shall be measured at right angles to the direction of travel to an exit and shall not be less than required for the occupant load. The height of safe areas shall be at least 8 feet (2438 mm) at all points.

8.	Safe areas near grade. When a safe area provides egress to an open exterior space, either directly or through a vestibule, the safe area need not provide the floor area required by this section when the level of discharge from the safe area to the open exterior space is not more than 4 feet (1219 mm) above or below the grade of the open exterior space.

[1028.17.3.1] 1029.19.3.1 Unenclosed [vertical exits] exit access stairways and ramps. [Vertical exits] Where permitted by Section 1019, exit access stairways or ramps leading directly from one safe area to another, or leading from a safe area directly to an open exterior space, need not be enclosed.  Travel distance on such unenclosed exit access stairway or ramp shall be in accordance with the primary travel distance in Table 1029.7, and shall be measured in accordance with Section 1017.3.1.

[1028.17.3.2] 1029.19.3.2 Safe area lighting. In addition to requirements of Section [1006] 1008, safe areas shall be artificially lighted by electrical means at all times during occupancy of a place of assembly so as to provide illumination of at least 5 foot-candles (54 lux) at the level of the floor and on the surface of all stairs, steps, ramps, and escalators within the safe area.

[1028.17.4] 1029.19.4 Open exterior space. The following provisions shall apply when an open exterior space is used as an exit discharge:

1.	Capacity. Open exterior spaces shall be adequate in width and area to accommodate the accumulated occupant load of all exits discharging into them on the basis of 2 square feet (0.19 m2) per person.

2.	Minimum dimensions. The minimum dimension of open exterior spaces shall be 20 feet (6096 mm), except that when the principal entrance to the place of assembly is from an open exterior space, the minimum dimension of this space shall be 30 feet (9144 mm). No open exterior space shall have less than 400 square feet (37 m2) of floor area, and floor area shall be measured exclusive of the following:

2.1.	The area immediately outside any exit door from the place of assembly for a distance perpendicular to the exit doors of 10 feet (3048 mm) for the full width of the exit opening.

2.2.	The area of steps, platforms, stairs, or ramps within or leading to or from the space.

2.3.	The area of obstructions such as shrubs, trees, fixed furniture, signs, sculptures, pools, and similar obstructions to occupancy or exit travel.

3.	Above or below grade. When an open exterior space is more than 15 feet (4572 mm) above or below the grade of the street or public space to which it discharges, its required area shall be increased by one-third.

4.	Egress from open exterior spaces. Exterior exit passageways, ramps, or steps leading from open exterior spaces shall be not less in width than required for the occupant load of all exits discharging into the open exterior space. The width of such exit passageways shall be based on the capacities listed in Section [1005.1] 1005.1, but in no case less than 10 feet (3048 mm).

5.	Open exterior spaces. Yards or courts [which] that serve as open exterior spaces shall be artificially lighted by electrical means at all times between sunset and sunrise during occupancy of a place of assembly so as to provide illumination of at least 5 foot-candles (54 lux) at the level of the floor over at least the required area.

SECTION BC [1029] 1030
EMERGENCY ESCAPE AND RESCUE

[1029.1] 1030.1 General. In addition to the means of egress required by this chapter, provisions shall be made for emergency escape and rescue openings in Group [R and Group I-1] R-2 occupancies that are subject to Table 1006.3.2, and Group R-3 occupancies. Sleeping rooms below the fourth story above grade plane and below-grade stories shall have at least one exterior emergency escape and rescue opening in accordance with this section. Where below-grade stories contain one or more sleeping rooms, emergency escape and rescue openings shall be required in each sleeping room, but shall not be required in adjoining areas of such below-grade story. Such [opening] openings shall open directly into a public way or to a yard or court that opens to a public way.

Exceptions:

1.	[Buildings equipped throughout with an approved automatic sprinkler system in accordance with Section 903.3.1 or 903.3.1.2.]

[2.]	Sleeping rooms provided with a door to a fire-resistance-rated corridor having access to two remote exits in opposite directions.

[3.	The emergency escape and rescue opening is permitted to open onto a balcony within an atrium in accordance with the requirements of Section 404, provided the balcony provides access to an exit and the dwelling unit or sleeping unit has a means of egress that is not open to the atrium.]

[4.	High-rise buildings in accordance with Section 403.]

[5.] 2.	Emergency escape and rescue openings are not required from below-grade stories or sleeping rooms that have an exit door or exit access door that opens directly into a public way or to a yard, court or exterior exit balcony that opens to a public way.

[6.] 3.	Below-grade stories without habitable spaces and having [no] not more than 200 square feet (18.6 m2) in floor area shall not be required to have emergency escape [windows] and rescue openings.

[1029.2] 1030.2 Minimum size. Emergency escape and rescue openings shall have a minimum net clear opening of 6 square feet (0.56 m2).

Exception: The minimum net clear opening for grade-floor emergency escape and rescue [grade-floor] openings shall be 5 square feet (0.46 m2) unless such opening is required for natural ventilation in accordance with Chapter 12.

[1029.2.1] 1030.2.1 Minimum dimensions. The minimum net clear opening height dimension shall [not] be [less than] 30 inches (762 mm). The net clear opening width dimension shall not be less than 24 inches (610 mm). The final dimensions shall result in a net clear opening area as required above. The net clear opening dimensions shall be the result of normal operation of the opening.

[1029.3] 1030.3 Maximum height from floor. Emergency escape and rescue openings shall have the bottom of the clear opening not greater than 36 inches (914 mm) measured from the floor.

[1029.4] 1030.4 Operational constraints. Emergency escape and rescue openings shall be operational from the inside of the room without the use of keys or tools in accordance with the provisions of Chapter 10 of the New York City Fire Code.

[1029.5] 1030.5 Window wells. An emergency escape and rescue opening with a finished sill height below the adjacent ground level shall be provided with a window well in accordance with Sections [1029.5.1] 1030.5.1 and [1029.5.2] 1030.5.2.

[1029.5.1] 1030.5.1 Minimum size. The minimum horizontal area of the window well shall be 9 square feet (0.84 m2), with a minimum dimension of 36 inches (914 mm). The area of the window well shall allow the emergency escape and rescue opening to be fully opened.

[1029.5.2] 1030.5.2 Ladders or steps. Window wells with a vertical depth of more than 44 inches (1118 mm) shall be equipped with an approved permanently affixed ladder or steps. Ladders or rungs shall have an inside width of at least 12 inches (305 mm), shall project at least 3 inches (76 mm) from the wall and shall be spaced not more than 18 inches (457 mm) on center (o.c.) vertically for the full height of the window well. The ladder or steps shall not encroach into the required dimensions of the window well by more than 6 inches (152 mm). The ladder or steps shall not be obstructed by the emergency escape and rescue opening. Ladders or steps required by this section are exempt from the stairway requirements of Section [1009] 1011.

SECTION BC [1030] 1031
SIGNAGE

[1030.1] 1031.1 Signage. Signage shall be provided in accordance with this section and the rules of the department.

[1030.2] 1031.2 Exit signs. Exits signs shall be provided in accordance with Section [1011] 1013.

[1030.3] 1031.3 Stairway and elevator identification signs. Stairway floor number and stairway identification signs shall be provided in accordance with Section [1022.8] 1023.9. Elevator identification and emergency signs shall be provided in accordance with Section 3002.3.

[1030.4] 1031.4 Door signs. For the following buildings, signs shall be posted and maintained on exit stair doors in accordance with this section:

1.	Buildings or portions thereof occupied by Group B or arranged to be occupied by more than 100 persons above or below the street level or more than 500 persons in the entire building.

2.	High-rise buildings subject to Section 403.

3.	Buildings where any stair side door is locked pursuant to Section [1008.1.9.10] 1010.1.9.11.

Exception: Signs shall not be required on exit stair doors opening directly to dwelling or sleeping units in occupancy Group R where permitted by Section [1014.4] 1016.3.

[1030.4.1] 1031.4.1 Occupied side. Where reentry is not provided from a stair to every floor, a sign that reads, “NO REENTRY FROM THIS STAIR” shall be posted on the occupied side of the stair door at every floor.

[1030.4.2] 1031.4.2 Stair side. On the stair side, signs shall be posted and maintained at all stair doors at every floor. Such signs shall be either:

1.	Reentry. Where reentry is provided, a sign shall read, "REENTRY ON THIS FLOOR."

2.	No Reentry. Where reentry is not provided on that floor, the sign shall read:

2.1.	“NO REENTRY”; where reentry is not provided on any floor;

2.2.	“NO REENTRY, NEAREST REENTRY ON THE AND FLOORS”; where reentry is provided on other floors; and

2.3.	“NO REENTRY. REENTRY IS PROVIDED ONLY DURING FIRE EMERGENCIES. NEAREST TELEPHONE ON THE AND FLOORS”; where stair side doors are locked in accordance with Section 403.5.3.

[1030.4.3] 1031.4.3 Graphics. The lettering and numerals of the signs shall be at least 1/2 inch (12.7 mm) high of bold type. The lettering and background shall be contrasting colors and the signs shall be securely attached approximately 5 feet (1524 mm) above the floor. The signs may be either independent or combined with floor and stairway identification signs.

[1030.5] 1031.5 Wall signs, stair side. In high-rise buildings subject to Section 403, signs shall be posted and maintained on the wall as follows:

1.	Reentry. Where a reentry door is recessed, a supplementary sign complying with Section [1030.4.3] 1031.4.3, except that the lettering and numerals shall be at least 1 inch (25 mm) high, shall be securely attached on the wall of the landing and shall be readily visible to the evacuee on the stairs indicating the location of such recessed reentry door.

2.	No reentry. Where there is no reentry from the stair, an additional sign complying with [Subdivision 2 of Sections 1030.4.2] Item 2 of Section 1031.4.2, and [1030.4.3] Section 1031.4.3, except that the lettering and numerals shall be at least 1 inch (25 mm) high, shall be securely attached at the beginning of the descent into such portion of the stair on the wall of the landing and shall be readily visible to the evacuee on the stairs.

[1030.6] 1031.6 Accessible means of egress signs. Accessible means of egress shall be provided with signs in accordance with Section [1007.9] 1009.9.

[1030.7] 1031.7 Capacity sign. Occupant load signs shall be provided in accordance with Section [1004.3] 1029.1.3.

[1030.8] 1031.8 Access-controlled doors. Access-controlled doors shall be provided with signs in accordance with Section [1008.1.4.4] 1010.1.9.8.

[1030.9] 1031.9 Delayed egress locks. Doors equipped with delayed egress shall be provided with signs in accordance with [Sections] Section [1008.1.9.7] 1010.1.9.7.

[1030.10] 1031.10 Signs in sleeping rooms. A sign shall be posted on the inside of every door opening onto a corridor giving access to a sleeping room in all Group R-1 occupancies. The sign shall contain a diagram showing the location where it is posted and the location and letter identification of the exit stairs on the floor. The diagram shall indicate the number of doors opening onto the public corridor which must be passed to reach each exit stair. The sign shall be at least 8 inches by 10 inches (203 mm by 254 mm), located on the inside of the door and securely attached. The top of such sign shall not be more than 6 feet (1829 mm) from the floor level. Such sign shall contain such additional information as the Fire Department may require.

[1030.11] 1031.11 Luminous egress path markings. Luminous egress path markings in high-rise buildings subject to Section 403.5.5 shall be provided in accordance with Section [1024] 1025 and Appendix S.

[1030.12] 1031.12 Materials for signs. Signs required by this section shall be of metal or other durable material.

§ 12.  Chapter 11 of the New York city building code, as amended by local law number 141 for the year 2013, item 3 of section 1109.2, as added by local law number 51 for the year 2014, section 1109.2.4 as amended by local law number 34 for the year 2018, item 4 of section 1110.2 as amended by local law number 79 for the year 2016 and item 7 of section 1110.3 as amended by local law number 122 for the year 2019, is amended to read as follows:

CHAPTER 11
ACCESSIBILITY

SECTION BC 1101
GENERAL

1101.1 Scope. The provisions of this chapter and Appendices E[,] and N [and P] shall control the design and construction of facilities for accessibility [to persons] for individuals with [physical] disabilities.

1101.2 Design. Buildings and facilities shall be designed and constructed to be accessible in accordance with [this code and] ICC A117.1 and this code.

1101.3 Special provisions for prior code buildings. The provisions of this chapter shall apply to alterations, including minor alterations but excluding ordinary repairs, and changes of use or occupancy to prior code buildings, portions of such buildings, and spaces within such buildings in accordance with [Section] Sections 1101.3.1 through 1101.3.5. Alterations within prior code buildings affecting an area containing a primary function shall comply with the requirements of Section 1101.4. This section shall not impose a requirement for greater accessibility than that which would be required for new construction, nor shall it reduce or have the effect of reducing accessibility.

Exception: The provisions of this chapter are not applicable to:

1.	[Ordinary repairs.]

[2.]	 Group R-3 occupancies in buildings with first occupancy on or before March 13, 1991.

[3.] 2.	Group R-3 occupancies in buildings with first occupancy after March 13, 1991, and originally constructed in a single structure with fewer than [4] four dwelling or sleeping units.

1101.3.1 Requirements based on change of occupancy or how a space is used. Accessible features and construction governed by this chapter shall be provided:

1.	To the entire building, as if the building were hereafter erected, where a change is made in the main use or dominant occupancy of such building.

2.	Throughout a space, including the immediate entrance(s) thereto, where an alteration is made that is considered either: (i) a change in occupancy classification of such space in accordance with this code, or (ii) a change in the zoning use group of such space in accordance with the New York City Zoning Resolution.

[2.2.	Entrances within 18 inches (457.2 mm) of the sidewalk.]

2.1.	Where the [floor elevation of a space is within 18 inches (457.2 mm) of the sidewalk, and the] immediate entrance(s) to such space provides direct access to the sidewalk, such immediate entrance(s) shall be provided with an accessible route to the sidewalk. Where the immediate entrance(s) to such space are only through an adjacent space, such as a building lobby, such space shall be provided with an accessible route, through the adjacent space, to the sidewalk.

2.2.	Where elevator service is provided in the building, an accessible route shall be required to a rooftop, where prior to a change in use or occupancy, such rooftop was not intended for general public or occupant use.

[3.	To provide an accessible route to a space, including rooftops, where prior to a change in use of occupancy or in how such space is used, this chapter would not have required an accessible route for new construction.]

1101.3.2 Requirements based on value of alterations. Accessible features and construction governed by this chapter shall be provided:

1.	To the entire building undergoing alterations, as if the building were hereafter erected, where the value of alterations exceeds 50 percent of the value of the existing building.

2.	To the portion of the building being altered, to the extent of the alteration, including minor alterations but excluding ordinary repairs, where the value of the alteration does not exceed 50 percent of the value of the existing building.

2.1.	Within buildings with first occupancies on or before March 13, 1991, bathrooms and powder rooms located in dwelling units in such portion being altered shall comply with this chapter or [be permitted to comply] with prototype layouts established by rule.

1101.3.3 Directional accessibility signage. Directional signage shall be provided in accordance with Section [1110.2] 1111.2 at or in close proximity to inaccessible building entrances, inaccessible public toilets and bathing facilities, and elevators not serving an accessible route, indicating the route to the nearest like accessible element where such accessible element is provided, such that [a person] an individual with disabilities will not be required to retrace the approach route from the inaccessible element.

1101.3.4 Identifying accessibility signage. Identifying accessibility signage shall be provided in accordance with Item [7] 5 of Section [1110.1] 1111.1 at accessible building entrances where not all entrances are accessible.

1101.3.5 Waiver of requirements. The commissioner may waive the requirements of this chapter for the alteration of [existing] prior code buildings, provided [, however,] that such waiver would not significantly adversely affect provisions for health, safety and security and that equally safe and proper alternatives are prescribed and, [further,] that such waiver is based upon a specific finding that strict compliance with the requirement:

1.	Would create an undue economic burden;

2.	Would not achieve its intended objective;

3.	Would be physically or legally impossible;

4.	Would be unnecessary in light of alternatives which ensure the achievement of the intended objective or which, without a loss in the level of safety, achieve the intended objective more efficiently, effectively or economically; or

5.	Would entail a change so slight as to produce a negligible additional benefit consonant with the purposes of this chapter.

1101.3.5.1 Application process. Each application for a waiver shall be made to the commissioner in writing, setting forth each requirement sought to be waived and the specific reason or reasons therefore. The commissioner shall determine, under all of the circumstances presented by such application, which of such requirements may appropriately be waived. The commissioner shall render such determination in [a] writing, which shall set forth in detail, the commissioner’s findings and conclusions with respect to each requirement sought to be waived. A copy of such written determination shall be forwarded to the applicant. Such written determination shall be filed with the department and shall be available for public inspection.

1101.3.5.2 Waiver recommendation. The Mayor’s Office for People with Disabilities or its successor agency shall be consulted by and shall advise the commissioner concerning each application for a waiver under Section 1101.3.5.

1101.4 Alterations affecting an area containing a primary function. Where an alteration affects the accessibility to, or contains an area of primary function, the route to the primary function area shall be accessible. The costs of providing the accessible route are not required to exceed 20 percent of the value of the alterations affecting the area of primary function. The accessible route to the primary function area shall include toilet facilities and drinking fountains serving the area of primary function.

Exceptions:

1.	This provision does not apply to alterations limited solely to windows, hardware, operating controls, electrical outlets and signs.

2.	This provision does not apply to alterations limited solely to mechanical systems, electrical systems, installation or alteration of fire protection systems and abatement of hazardous materials.

3.	This provision does not apply to alterations undertaken for the primary purpose of increasing the accessibility of a facility.

4.	This provision does not apply to altered areas limited within a Type B or Type B+NYC dwelling unit.

SECTION BC 1102
DEFINITIONS

1102.1 Definitions. The following [words and] terms [shall, for the purposes of this chapter, applicable appendices and as used elsewhere in this code, have the meanings shown herein] are defined in Chapter 2:

ACCESSIBLE. [A site, building, facility or portion thereof that complies with this chapter.]

ACCESSIBLE UNIT. [A dwelling unit or sleeping unit that complies with this code and the provisions for Accessible units in ICC A117.1.]

#### AREA OF SPORT ACTIVITY.

CIRCULATION PATH. [An exterior or interior way of passage from one place to another for pedestrian travel.]

COMMON USE. [Interior or exterior circulation paths, rooms, spaces or elements that are made available for the shared use of two or more people but are not for public use.]

DETECTABLE WARNING. [A standardized surface feature built in or applied to walking surfaces or other elements to warn visually impaired persons of hazards on a circulation path.]

DWELLING UNIT (ACCESSIBILITY). [For the purposes of Chapter 11 and applicable appendices: A single unit providing complete, independent living facilities for one or more persons, including permanent provisions for living, sleeping, eating, cooking and sanitation.]

DWELLING UNIT OR SLEEPING UNIT, MULTI[-] STORY. [See “Multistory unit.”]

DWELLING UNIT OR SLEEPING UNIT, TYPE B. [See “Type B unit.”]

EMPLOYEE WORK AREA. [All or any portion of a space used only by employees and only for work. Corridors, toilet rooms, kitchenettes and break rooms are not employee work areas.]

FACILITY. [All or any portion of buildings, structure, site improvements, elements and pedestrian or vehicular routes located on a site.]

HALL CALL CONSOLE.

INTENDED TO BE OCCUPIED AS A RESIDENCE.[This refers to a dwelling unit or sleeping unit that can or will be used all or part of the time as the occupant’s place of abode.]

MULTILEVEL ASSEMBLY SEATING. [Seating that is arranged in distinct levels where each level is comprised of either multiple rows, or single row of box seats accessed from a separate level.]

MULTISTORY UNIT. [A dwelling unit or sleeping unit with habitable space located on more than one story.]

PRIMARY FUNCTION AREAS.

PUBLIC ENTRANCE.[An entrance that is not a service entrance.]

PUBLIC-USE AREAS.[Interior or exterior rooms or spaces that are made available to the general public.]

RESTRICTED ENTRANCE. [An entrance that is made available for public use but on a controlled basis, and that is not a service entrance.]

SELF-SERVICE STORAGE FACILITY. [Real property designed and used for the purpose of renting or leasing individual storage spaces to customers for the purpose of storing and removing personal property on a self-service basis.]

SERVICES. [Includes but is not limited to toilet rooms, drinking fountains, public telephones and food.]

SERVICE ENTRANCE. [An entrance solely for delivery of goods or services.]

SITE. [A parcel of land bounded by a lot line or a designated portion of a public right-of-way.]

SLEEPING UNIT (ACCESSIBILITY). [For the purposes of Chapter 11 and applicable appendices: A room or space in which people sleep, which can also include permanent provisions for living, eating, and either sanitation or kitchen facilities but not both. Such rooms and spaces that are also part of a dwelling unit are not sleeping units.]

TYPE B UNIT. [A dwelling unit or sleeping unit designed and constructed for accessibility in accordance with this code and the provisions for Type B units in ICC A117.1, consistent with the design and construction requirements of the federal Fair Housing Act.]

TYPE B+NYC UNIT. [A dwelling unit or sleeping unit designed and constructed for accessibility in accordance with this code, Section 1004 (Type B Units) of ICC A117.1 as modified by Sections 1107.2.1 through 1107.2.8, and Appendix P of this code.]

VALUE (OF EXISTING BUILDING OR SPACE). [See Section 202.]

VALUE (OF ALTERATIONS, TO DETERMINE REQUIRED ACCESSIBILITY). [The value of alterations shall be determined by adding the estimated cost of the proposed alteration, including minor alterations but excluding ordinary repairs, computed as of the time of submitting the application for construction document approval, or, where no permit is required, computed at the time of the work, to the actual cost of any and all alterations and minor alterations made in the preceding 12-month period. Where the alteration includes an enlargement, the value of the alteration shall include the cost of the enlargement.]

WHEELCHAIR SPACE.[A space for a single wheelchair and its occupant.]

SECTION BC 1103
SCOPING REQUIREMENTS

1103.1 Where required. Sites, buildings, structures, facilities, elements and spaces, temporary or permanent, shall be accessible to [persons] individuals with [physical] disabilities.

1103.2 General exceptions. Sites, buildings, structures, facilities, elements and spaces shall be exempt from this chapter to the extent specified in this section.

1103.2.1 Specific requirements. Accessibility is not required in buildings and facilities, or portions thereof, to the extent permitted by Sections 1104 through [1110] 1111.

1103.2.2 [Prior code buildings. Prior code buildings shall comply with Section 1101.3.3.]

[1103.2.3 Employee work areas. All or any portion of a space used exclusively by employees and only for work shall be required to comply only with Section 1103.2.3. However, common use circulation paths, located within employee work areas shall also comply with Section 1104.3.1.]

[1103.2.3.1] Employee work areas [and work stations]. Spaces and elements within employee work areas shall only be required to comply with Sections [907.5.2.3.2] 907.5.2.3.1, [1007] 1009 and 1104.3.1, and shall be designed and constructed so that individuals with disabilities can approach, enter and exit the work area. In addition, at least one [and] but not less than five percent of fixed seating, tables, desks, and/or work [stations] surfaces, if provided, within employee work areas shall be located on an accessible route and comply with [applicable sections] Section 902 (Dining Surfaces and Work Surfaces) of ICC A117.1. Work areas, or portions of work areas, other than raised courtroom stations in accordance with Section 1108.4.1.4, that are less than 300 square feet (30 m2) in area and located 7 inches (178 mm) or more above or below the ground or finished floor where the change in elevation is critical to the work operation shall be exempt from all requirements.

[1103.2.3.2 Elevated employee work areas. Where the elevation is critical to the proper work operations, work areas or portions of work areas, other than raised courtroom stations, that are less than 300 square feet (30 m2) in area and elevated 7 inches (178 mm) or more above the ground or finish floor shall be exempt from all requirements.]

[1103.2.4] 1103.2.3 Detached dwellings. Detached [one] one- and two-family dwellings [and], their accessory structures and their associated sites and facilities are not required to [be accessible] comply with this chapter.

[1103.2.5] 1103.2.4 Utility buildings. [Occupancies in] Group U [are exempt from the requirements of] occupancies are not required to comply with this chapter other than the following:

1.	In agricultural buildings and livestock shelters, access is required to paved work areas and areas open to the general public.

2.	Green houses and stables open to the public.

3.	Private garages or carports that contain required accessible parking.

[1103.2.6] 1103.2.5 Construction sites. Structures, sites and equipment directly associated with the actual processes of construction including, but not limited to, scaffolding, bridging, materials hoists, materials storage or construction trailers are not required to [be accessible] comply with this chapter.

[1103.2.7] 1103.2.6 Raised areas. Raised areas used for purposes of security, life safety or fire safety including, but not limited to, observation galleries, prison guard towers, fire towers or lifeguard stands are not required to [be accessible or to be on an accessible route] comply with this chapter.

[1103.2.8] 1103.2.7 Limited access spaces.[Nonoccupiable spaces] Spaces accessed only by ladders, catwalks, crawl spaces, freight elevators that are not part of an accessible route, or very narrow passageways are not required to [be accessible] comply with this chapter.

1103.2.8 Reserved.

1103.2.9 Equipment spaces. Spaces frequented only by service personnel for maintenance, repair or occasional monitoring of equipment are not required to [be accessible] comply with this chapter. Such spaces include, but are not limited to, elevator pits, elevator penthouses, mechanical, electrical or communications equipment rooms, piping or equipment catwalks, water or sewerage treatment pump rooms and stations, electrical substations and transformer vaults, and highway and tunnel utility facilities.

1103.2.10 [Nongrade single-occupant structures. Single-occupant structures that are accessed only by passageways below grade or above grade including, but not limited to, toll booths that are accessed only by bridges or underground tunnels, are not required to be accessible .] Reserved.

1103.2.11 Reserved.

1103.2.12 Reserved.

1103.2.13 [Reserved.]

[1103.2.14] Detention and correctional facilities. In detention and correctional facilities, common use areas that are used only by inmates or detainees and security personnel, and that do not serve holding cells or housing cells required to be [accessible pursuant to Section 1107.5.5] Accessible units, are not required to [be accessible or to be on an accessible route] comply with this chapter.

[1103.2.15] 1103.2.14 Walk-in coolers and freezers. Walk-in coolers and freezers intended for employee use only are not required to [be accessible] comply with this chapter.

SECTION BC 1104
ACCESSIBLE ROUTE

1104.1 Site arrival points. [Accessible routes] At least one accessible route within the site shall be provided from public transportation stops, accessible parking, accessible passenger loading zones, and public streets or sidewalks to the accessible building entrance served.

1104.2 Within a site. At least one accessible route shall connect accessible buildings, accessible facilities, accessible elements and accessible spaces that are on the same site and shall comply with Section 1104.5.

Exceptions:

1.	An accessible route is not required between accessible buildings, accessible facilities, accessible elements and accessible spaces that have, as the only means of access between them, a vehicular way not providing for pedestrian access.

2.	An accessible route to recreational facilities shall only be required to the extent specified in Section 1110.

1104.3 Connected spaces. When a building[,] or portion of a building[,] is required to be accessible, [an] at least one accessible route shall be provided to each portion of the building, to accessible building entrances connecting accessible pedestrian walkways and to the public way.

Exceptions:

1.	Stories and mezzanines exempted by Section 1104.4.

2.	In a building, room or space used for assembly [areas] purposes with fixed seating, an accessible route shall not be required to serve levels where wheelchair spaces are not provided as permitted by other sections of this chapter.

[2.	Accessible routes shall not be required where multiple levels are not required to be connected by an accessible route as permitted by Section 1104.4.]

3.	[In Group I-2 facilities, doors to sleeping units shall be exempted from the requirements for maneuvering clearance at the room side provided the door is a minimum of 44 inches (1118 mm) in width.] Vertical access to elevated employee work stations within a courtroom complying with Section 1108.4.1.4.

4.	An accessible route to recreational facilities shall only be required to the extent specified in Section 1110.

1104.3.1 [Circulation paths within employee] Employee work areas. Common use circulation paths within employee work areas shall be accessible routes.

Exceptions: The following exceptions apply only to the common use circulation paths within an employee work area and are not intended to remove the requirement of Section [1103.2.3] 1103.2.2 that employee work areas be designed and constructed so that individuals with disabilities can approach, enter and exit the employee work area.

- Common use circulation paths, located within employee work areas that are less than 300 square feet (27.9 m2) in size [,] and defined by permanently installed partitions, counters, casework or furnishings not serving accessible employee work stations that are required in Section [1103.2.3.1] 1103.2.2, shall not be required to be accessible routes.

- Common use circulation paths, located within employee work areas, that are an integral component of equipment, shall not be required to be accessible routes.

1104.3.2 Press boxes. Press boxes in a building, room or space used for assembly [areas] purposes shall be on an accessible route.

Exceptions:

- An accessible route shall not be required to press boxes in bleachers that have [points] a single point of entry [at only one level] from the bleachers, provided that the aggregate area of all press boxes for each area of sport activity is not more than 500 square feet (46.5 m2) [maximum].

- An accessible route shall not be required to free-standing press boxes that are [elevated above grade] more than 12 feet (3658 mm) [minimum] above grade provided that the aggregate area of all press boxes for each area of sport activity is not more than 500 square feet (46.5 m2) [maximum].

1104.4 Multilevel buildings and facilities. At least one accessible route shall connect each accessible level[, including mezzanines,] and mezzanine in multilevel buildings and facilities.

Exceptions:

- In [non-residential] nonresidential buildings, an accessible route is not required to levels and mezzanines above and below accessible levels where the aggregate area of all such levels and mezzanines that are not provided with accessible routes is not more than 2,500 square feet (232.3 m2). This exception shall not apply to:

1.1.	Multiple tenant facilities of Group M occupancies containing five or more tenant spaces where all such tenant spaces are located on the accessible levels;

1.2.	Levels or mezzanines containing offices of health care providers (Group B or I occupancies);

1.3.	Passenger transportation facilities and airports (Group A-3 or B occupancies); or

1.4.	Levels frequented by the public for assembly purposes other than levels where wheelchair spaces are not required to be provided as determined in accordance with Section 1108.2.4.[.]

1.5.	Levels frequented by the public for government, public utility or health facility purposes.

- Levels or mezzanines that do not contain accessible elements or other spaces as [permitted] determined by [Sections] Section 1107 or 1108 are not required to be served by an accessible route from an accessible level.

3.	In air traffic control towers, an accessible route is not required to serve the cab and the floor immediately below the cab.

[3.] 4.	Where a two-story building or facility has one story or mezzanine with an occupant load of five or fewer persons that does not contain public use space, that story or mezzanine shall not be required to be connected by an accessible route to the story above or below.

[4.	Vertical access to elevated employee work stations within a courtroom is not required at the time of initial construction, provided a ramp, lift or elevator complying with ICC A117.1 can be installed without requiring reconfiguration or extension of the courtroom or extension of the electrical system.]

The exemption of a level from accessible route requirements pursuant to the exceptions set forth in this section shall not be construed to automatically exempt such level from other accessibility provisions of this chapter including but not limited to requirements for accessible doors[, toilets and level floors] and toilet rooms. Such other accessibility provisions remain applicable to such level unless specifically exempted by other sections of this code.

1104.5 Location. Accessible routes shall coincide with or be located in the same area as a general circulation path. Where the circulation path is interior, the accessible route shall also be interior. Where only one accessible route is provided, the accessible route shall not pass through kitchens, storage rooms, restrooms, closets or similar spaces.

Exception: A single accessible route is permitted to pass through a kitchen in an Accessible unit, Type B+NYC unit, or Type B unit.

1104.6 Security barriers. Security barriers including, but not limited to, security bollards and security check points shall not obstruct a required accessible route or accessible means of egress.

Exception: Where security barriers incorporate elements that cannot comply with these requirements, such as certain metal detectors, fluoroscopes or other similar devices, the accessible route shall be permitted to be provided adjacent to security screening devices. The accessible route shall permit [persons] individuals with disabilities passing around security barriers to maintain visual contact with their personal items to the same extent provided others passing through the security barrier.

SECTION BC 1105
ACCESSIBLE ENTRANCES

1105.1 Public entrances. In addition to accessible entrances required by Sections 1105.1.1 through [1105.1.6] 1105.1.8, all public entrances shall be accessible.

Exceptions:

1.	An accessible entrance is not required to areas [that are] not required to be accessible by [this chapter or] Appendix E or this chapter.

2.	Loading and service entrances that are not the only entrance to a building or a tenant space.

3.	Revolving doors, revolving gates, or turnstiles shall not be required to be accessible provided that an accessible entrance is available adjacent to such revolving doors, revolving gates or turnstiles.

1105.1.1 Parking garage entrances. Where provided, direct access for pedestrians from parking structures to buildings or facility entrances shall be accessible.

1105.1.2 Entrances from tunnels or elevated walkways. Where direct access is provided for pedestrians from a pedestrian tunnel or elevated walkway to a building or facility, entrances from such access to the building or facility shall be accessible.

1105.1.3 Restricted entrances. Where restricted entrances are provided to a building or facility, all such restricted [entrances] entrances to the building or facility shall be accessible.

1105.1.4 Entrances for inmates and detainees. Where entrances used only by inmates or detainees and security personnel are provided at judicial facilities, detention facilities or correctional facilities, all such entrances shall be accessible.

1105.1.5 Service entrances. If a service entrance is the only entrance to a building or a tenant space in a facility, that entrance shall be accessible.

1105.1.6 Tenant spaces. All entrances to tenant spaces that are required to be accessible shall be accessible entrances.

Exception: An accessible entrance is not required to self-service storage units that are not required to be accessible.

[1105.1.6.1] 1105.1.7 Dwelling units and sleeping units. Doors and doorways at entrance(s) to Accessible units and Type B+NYC units, including hardware, shall comply with Section 404 (Doors and Doorways) of ICC A117.1. Doors and doorways, including hardware, at entrance(s) to Type B units shall comply with Section 1003.5 (Doors and doorways) of ICC A117.1.

Exceptions:

- An accessible entrance is not required to dwelling units and sleeping units that are not required to be Accessible units, Type B+NYC units, or Type B units.

- Entrances to multistory dwelling or sleeping units in Group R-2 [occupancy] occupancies as provided in Section 1107.2.5 that are not on the primary entry story to the unit and are not part of the accessible route required in Exception 1 of Section 1107.2.5 shall not be required to be accessible.

[3.	In Group I-2 facilities, doors to sleeping units shall be exempted from the requirements for maneuvering clearance at the room side provided the door is a minimum of 44 inches (1118 mm) in width.]

1105.1.8 Automatic doors. In facilities with the occupancies and building occupant loads indicated in Table 1105.1.8, at least one accessible public entrance shall be either a full power-operated door or a low-energy power-operated door.

Exception: For ground floor business or mercantile occupancies which are not yet demised for tenancy, the requirements of this section shall not apply until the occupant load for the tenant or tenants has been determined.

TABLE 1105.1.8
PUBLIC ENTRANCE WITH POWER-OPERATED DOORS

| Occupancy | Occupancy Load ≥ |
| --- | --- |
| A-1, A-2, A-3, A-4, B, R-1 | 200 |
| E, M | 300 |

SECTION BC 1106
PARKING AND PASSENGER LOADING FACILITIES

1106.1 Required. Where parking is provided, 5 percent of the total number of parking spaces provided for a facility, but not less than one parking space, shall be accessible parking spaces except as otherwise required by Sections 1106.2 through 1106.4. Van-accessible parking spaces shall be provided in accordance with Section 1106.5. Accessible parking spaces shall be designed and constructed in accordance with Section 502 (Parking Spaces) of ICC A117.1. Where more than one parking facility is provided on a site, the number of parking spaces required to be accessible shall be calculated separately for each parking facility. Where a determination of the minimum number of parking spaces results in a number containing a decimal of 0.5 or more, the next highest integer shall be used.

Exception: This section does not apply to parking spaces used exclusively for buses, trucks, other delivery vehicles, law enforcement vehicles or vehicular impound where lots accessed by the public are provided with an accessible passenger loading zone.

1106.2 Groups R-2 and R-3. Where parking is provided for occupancies in Groups R-2 and R-3, which are required to have Accessible, Type B+NYC, or Type B units, the number of accessible parking spaces shall be in compliance with Section 1106.1 and such number of accessible parking spaces shall be dispersed in accordance with Section 1106.6. Where parking is provided within or beneath a building, accessible parking spaces shall also be provided within or beneath the building.

1106.2.1 Lease, rental, or assignment of spaces. In a parking facility accessory to Occupancy Group R-2 or R-3 serving only the residents or employees of the management of such occupancy, or provided in compliance with Section 25-412 of the New York City Zoning Resolution, the accessible parking spaces in such facility may be leased, rented or assigned to [a person] an individual without [physical] disabilities on a no longer than month-to-month basis. Such leases, rentals, or assignments of the accessible parking spaces to [persons] individuals without [physical] disabilities shall be on written condition that such spaces be relinquished immediately at the end of the term of such lease, rental, or assignment to a resident or employee of the management of such occupancy who is [a person] an individual with [physical] disabilities.

1106.3 Hospital outpatient facilities. At least 10 percent, but not less than one, of [patient] care recipient and visitor parking spaces provided to serve hospital outpatient facilities shall be accessible.

1106.4 Rehabilitation facilities and outpatient physical therapy facilities. At least 20 percent, but not less than one, of the portion of [patient] care recipient and visitor parking spaces serving rehabilitation facilities specializing in treating conditions that affect mobility and outpatient physical therapy facilities shall be accessible.

1106.5 Van spaces. For every six or fraction of six accessible parking spaces, at least one [space] shall be a van-accessible parking space. Van-accessible parking spaces shall be designed and constructed in accordance with ICC A117.1, including Section 502 (Parking Spaces).

Exception: In Group R-2 and R-3 occupancies, van-accessible spaces located within private garages not exceeding 300 square feet (27.9 m2) shall be permitted to have vehicular routes, entrances, parking spaces and access aisles with a minimum vertical clearance of 7 feet (2134 mm).

1106.6 Location. Accessible parking spaces shall be located on the shortest accessible route of travel from adjacent parking to an accessible building entrance. In parking facilities that do not serve a particular building, accessible parking spaces shall be located on the shortest route to an accessible pedestrian entrance to the parking facility. Where buildings have multiple accessible entrances with adjacent parking, accessible parking spaces shall be dispersed and located near the accessible entrances. In Occupancy Groups R-2 and R-3, at least one of each type of parking space shall be accessible.

Exceptions:

1.	In multilevel parking structures, van-accessible parking spaces complying with Section 502 (Parking Spaces) of ICC A117.1 may be provided on one level.

2.	Accessible parking spaces shall be permitted to be located in different parking facilities if substantially equivalent or greater accessibility is provided in terms of distance from an accessible entrance or entrances, parking fee and user convenience.

3.	In an attended parking facility in which vehicles customarily are parked and later returned to their drivers by an attendant employed by the parking facility, [accessible parking spaces need not be designated by a sign or lines if all of the following conditions are met:] the number of accessible parking spaces shall be provided in accordance with Table 1106.7.3 and Section 1106.7.3.

[3.1.	Van-accessible parking spaces complying with Section 502 (Parking Spaces) of ICC A117.1 are provided;]

[3.2.	A passenger loading zone complying with Section 1106.7 is provided where an attendant shall take control of the vehicles. A vertical clearance of 98 inches (2489 mm) shall be permitted at such loading zone;]

[3.3.	At least one accessible parking space shall remain available unless all accessible parking spaces are occupied;]

[3.4.	The attendant shall park and retrieve all vehicles not equipped with special controls entering the facility in which a person with disabilities is either the driver or a passenger, provided accessible parking space is available;]

[3.5.	The attendant shall direct the drivers of vehicles equipped with special controls to accessible parking spaces. The attendant shall accompany such drivers to and from such space along an accessible route when they enter and exit the facility. If necessary, the accessible route and accessible parking space shall be created by the repositioning of vehicles parked previously by the attendant; and]

[3.6.	Each van-accessible parking space shall have two permanently and prominently posted signs. One shall include the International Symbol of Accessibility complying with Section 703.6.3.1 of ICC A117.1. The other sign shall note that vehicles parked in such spaces are subject to being moved by an attendant of the parking facility in order to accommodate a vehicle which cannot be accommodated in another accessible parking space. Such signs shall not be obstructed by a vehicle parked in the space.]

4.	Mechanical access parking garages shall comply with Section 1106.7.4.

1106.7 Passenger loading zones. Passenger loading zones shall be designed and constructed in accordance with ICC A117.1 including Section 503 (Passenger Loading Zones). [Where there are curbs between the access aisle and the vehicle pull-up space, a curb ramp complying with ICC A117.1 including Section 406 (Curb Ramps) shall be provided.]

1106.7.1 Continuous loading zones. Where passenger loading zones are provided, at least one accessible passenger loading zone shall be provided within each continuous 100 linear feet (30 400 mm) of loading zone space, or fraction thereof, so that travel between accessible passenger loading zones will not exceed 100 linear feet (30 400 m).

1106.7.2 Medical facilities. A passenger loading zone shall be provided at an accessible entrance to licensed medical and long-term care facilities where people receive physical or medical treatment or care and where the period of stay exceeds 24 hours.

1106.7.3 Valet and attended parking. The number of accessible parking spaces in facilities that utilize valet and attended parking services shall be provided in accordance with Table 1106.7.3, and Sections 1106.7.3.1 and 1106.7.3.2.

TABLE 1106.7.3
VALET AND ATTENDED ACCESSIBLE PARKING SPACES

| TOTAL PARKING SPACES PROVIDED IN PARKING FACILITIES | REQUIRED MINIMUM NUMBER OF ACCESSIBLE SPACES |
| --- | --- |
| 1 to 25 | 1 |
| 26 to 50 | 2 |
| 51 to 75 | 3 |
| 76 to 100 | 4 |
| 101 to 150 | 5 |
| 151 to 200 | 6 |
| 201 to 300 | 7 |
| 301 to 400 | 8 |
| 401 to 500 | 9 |
| 501 to 1,000 | 2% of total |
| 1,001 and over | 20, plus one for each 100, or fraction thereof, over 1,000 |

[1106.7.3] 1106.7.3.1 Valet parking. In a facility utilizing valet parking services in which vehicles are parked and later returned to their drivers by a valet employed by the facility, the number of accessible parking spaces shall be provided in accordance with Table 1106.7.3. A passenger loading zone complying with Section 1106.7 shall be provided at valet parking services where the valet shall take control of the vehicles. Passenger loading zones shall comply with Section 503 (Passenger Loading Zones) of ICC A117.1.

1106.7.3.2 Attended parking. In an attended parking facility in which vehicles customarily are parked and later returned to their drivers by an attendant employed by the parking facility, the number of accessible parking spaces shall be provided in accordance with Table 1106.7.3.

1106.7.3.2.1 Passenger loading zone. A passenger loading zone complying with Section 1106.7 shall be provided where an attendant shall take control of the vehicles. Passenger loading zones shall comply with Section 503 (Passenger Loading Zones) of ICC A117.1.

1106.7.3.2.2 Retrieval of vehicles. The attendant shall park and retrieve all vehicles not equipped with special controls entering the facility in which an individual with disabilities is either the driver or a passenger, provided accessible parking space is available.

1106.7.4 Mechanical access parking garages. Mechanical access parking garages shall provide at least one passenger loading zone in compliance with Section 1106.7 at vehicle drop-off and vehicle pick-up areas.

1106.8 Electrical vehicle charging stations. Electrical vehicle charging stations shall comply with Sections 1106.8.1 through 1106.8.5.

Exception: Electrical vehicle charging stations intended for use by a designated vehicle or driver shall not be required to comply with this section.

1106.8.1 Number of accessible vehicle charging stations. Where provided for common use, at least five percent of the total number of electrical vehicle charging stations per facility, but not less than one for each type of electric vehicle charging station, shall be accessible.  Where a multiport electric vehicle charging station can simultaneously charge more than one vehicle, the number of electric vehicle charging stations shall be counted as the number of electric vehicles that can be simultaneously charged. The number of accessible vehicle charging stations are in addition to the required accessible parking spaces.

1106.8.2 Electric vehicle charging space. At each electrical vehicle charging station required to be accessible, the charging space shall comply with the requirements for a van accessible parking space complying with Sections 502.2 through 502.5 of ICC A117.1.

1106.8.3 Accessible route. At each electric vehicle charging station required to be accessible, the charging station shall be located along an accessible route. An accessible route shall be provided between the charging station and the charging space.

Exception: In existing facilities with no accessible route, electrical vehicle charging stations are not required to be located along an accessible route.

1106.8.4 Obstructions. Electric vehicle charging stations shall be designed so accessible routes are not obstructed by cables or other elements.

1106.8.5 Electrical vehicle charging station controls. Electric vehicle charging stations and electric vehicle charging station controls shall comply with Sections 309.2 and 309.3 of ICC A117.1.

SECTION BC 1107
DWELLING UNITS AND SLEEPING UNITS

1107.1 General. In addition to the other requirements of this chapter, occupancies having dwelling units or sleeping units shall be provided with accessible features in accordance with this section.

1107.2 Design. Dwelling units and sleeping units which are required to be Accessible units, Type B+NYC units, or Type B units shall comply with this code [including Appendix P where applicable,] and the applicable provisions of Chapter 10 of ICC A117.1. [In addition,] Type B+NYC units shall further comply with Section 1004 (Type B Units) of ICC A117.1, including any modifications made by Sections 1107.2.1 through 1107.2.8. Units required to be Type B+NYC units or Type B units are permitted to be designed and constructed as Accessible units.

1107.2.1 Type B+NYC unit doors and doorways. Doors and doorways at the entrance(s) to Type B+NYC dwelling or sleeping units shall comply with Section [1105.1.6] 1105.1.7. All other doors and doorways within the dwelling or sleeping unit, and patio or balcony doors of such dwelling or sleeping unit, meant for human passage shall comply with Section 1003.5 (Doors and Doorways) of ICC A117.1. [In addition, doors] Doors and doorways serving toilet and bathing rooms [that are required to comply with Appendix P shall also comply with Section P102.3.] shall comply with Section 1003.5 of ICC A117.1.

Exceptions:

1.	Maneuvering clearance at doors.

1.1.	Where pull side, latch approach maneuvering clearance is required within the dwelling or sleeping unit for a door without a closer as per Figure 404.2.3.2(f) of ICC A117.1, the minimum maneuvering clearance perpendicular to the doorway shall be permitted to be reduced to 42 inches (1067 mm).

1.2.	Where exterior spaces are greater than 24 inches (610 mm) in clear depth such spaces shall comply with the required door maneuvering clearances on both the interior and exterior side of the door.

2.	Door hardware. Door hardware on doors within the dwelling or sleeping unit, except on entrance doors, shall not be required to comply with Section 404.2.6 (Door Hardware) of ICC A117.1 provided such hardware is readily replaceable without the removal or replacement of the door.

3.	Future reversibility for bedroom doors. Bedroom doors and frames shall be permitted to be provided with mortised hinge and latch blanks to permit future reversal of the door on the same frame using common hand tools and without further alterations to the door and frame, provided such future swing of the door will not obstruct the maneuvering clearances required at the door or doorway.

4.	Storage facility doors. Door maneuvering clearances are not required for doors that are accessed from the interior of a closet within a dwelling unit or sleeping unit.

5.	Supplemental toilet and bathing rooms. Where one Type A toilet and bathing room is provided in a Type B+NYC unit in accordance with the exception in Section 1107.2.2, the doors and doorways to all other toilet and bathing rooms in that dwelling unit or sleeping unit shall not be required to comply with maneuvering clearances on the interior side of the bathroom, but shall comply with Section 1004.5.2 (User Passage Doorways) of ICC A117.1 and shall provide clear opening width of 32 inches (813 mm) minimum.

6.	Bathroom and toilet room doors.

6.1.	Doors shall not swing into the required clear floor or ground space or clearance for any fixture unless a clear floor or ground space complying with Section 305.3 of ICC A117.1 is provided within the room, beyond the arc of the door swing.

6.2.	Bathroom and toilet room doors shall be provided with maneuvering clearances on the toilet room or bathroom side of the door in accordance with Section 404.2.3 of ICC A117.1.

1107.2.2 Type B+NYC unit toilet and bathing rooms. Where toilet and bathing rooms are provided in [the] a Type B+NYC dwelling unit or sleeping unit, all such toilet and bathing rooms shall comply with [Appendix P] Sections 1107.2.2.1 through 1107.2.2.9. Within each such toilet, at least one lavatory, and one water closet shall comply with Sections 1107.2.2.1 through 1107.2.2.7. Within each bathing room, at least one lavatory, one water closet, and either a bathtub or shower shall comply with Sections 1107.2.2.1 through 1107.2.2.8.  Toilet and bathing fixtures shall be in a single room, such that travel between fixtures does not require travel beyond the room in which the fixtures of such toilet or bathing room is located. Additional fixtures shall comply with Section 1107.2.2.9.

Exception for Type A toilet and bathing room: Where at least one toilet and bathing room complying with Sections 1003.11 (Toilet and Bathing Facility) and 1003.3.2 (Turning Space) of ICC A117.1 is provided within a Type B+NYC dwelling unit or sleeping unit in accordance with Items 1 through 3 of this exception, other toilet and bathing rooms in the same unit shall be required to comply only with Sections 1004.3 (Accessible route), 1004.4 (Walking Surfaces), 1004.5.2 (User Passage Doorways), 1004.9 (Operable Parts) and 1004.11.1 (Grab Bar and Shower Seat Reinforcement) of ICC A117.1. In addition, a vertical grab bar 18 inches (457 mm) minimum in length shall be mounted with the bottom of the bar located between 39 inches (991 mm) and 41 inches (1041 mm) above the floor, and with the center of the bar located at 30 inches (762 mm) from the rear wall. Doors and doorways to such toilet and bathing rooms shall be subject to Section 1107.2.1, Exception 5.

[1.	Where at least one toilet and bathing room in the Type B+NYC dwelling unit or sleeping unit is constructed in accordance with the Type A toilet and bathing facilities requirements of Section 1003.11 (Toilet and Bathing Facilities), including Section 1003.3.2 (Turning Space), of ICC A117.1 and is in compliance with the following:]

[1.1.] 1. 	At least one lavatory, one water closet and either a bathtub or shower within such toilet or bathing facility shall comply with Section 1003.11 of ICC A117.1. Such toilet and bathing fixtures shall be in a single toilet or bathing area, such that travel between fixtures does not require travel beyond the area in which the fixtures of such toilet or bathing room are located.

[1.2.] 2. 	Toilet paper dispensers within such rooms shall comply with Section 604.7 (Dispensers) of ICC A117.1.

[1.3.] 3. 	Medicine cabinets, if provided, must include a storage shelf no higher than 44 inches (1118 mm) above the floor.

[2.	Where at least one toilet and bathing room complying with Sections 1003.11 and 1002.3.2 of ICC A117.1 is provided within the Type B+NYC dwelling unit or sleeping unit in accordance with Item 1 of this exception, other toilet and bathing rooms in the same unit shall be required to comply only with Sections 1004.3 (Accessible route), 1004.4 (Walking Surfaces), 1004.5.2 (User Passage Doorways), 1004.9 (Operable Parts) and 1004.11.1 (Grab Bar and Shower Seat Reinforcement) of ICC A117.1. Doors and doorways to such toilet and bathing rooms shall be subject to Section 1107.2.1, Exception 5.]

1107.2.2.1 Accessible route. At least one accessible route shall connect all spaces and elements with each toilet and bathing room within a dwelling unit or sleeping unit unless as permitted in Section 1107.2.5, Item 3. Accessible routes shall comply with ICC A117.1.

1107.2.2.2 Operable parts. Lighting controls, electrical switches and receptacle outlets, and environmental controls shall comply with Section 309 of ICC A117.1.

1107.2.2.3 Knee and toe clearance. Clear floor space at fixtures shall be permitted to include knee and toe clearances complying with Section 306 of ICC A117.1.

1107.2.2.4 Overlap. Clear floor or ground spaces and clearances are permitted to overlap.

1107.2.2.5 Lavatory. Lavatories shall comply with Section 606 of ICC A117.1.

Exception: Cabinetry shall be permitted under the lavatory, provided:

- Such cabinetry can be removed without removal or replacement of the lavatory;

- The finish floor extends under such cabinetry; and

- The walls behind and surrounding cabinetry are finished.

1107.2.2.6 Mirrors and medicine cabinets. Mirrors above lavatories shall have the bottom edge of the reflecting surface 40 inches (1016 mm) maximum above the floor or ground. Medicine cabinets, if provided, must include a storage shelf no higher than 44 inches (1118 mm) above the floor.

1107.2.2.7 Water closet. Water closets shall comply with Sections 1107.2.2.7.1 through 1107.2.2.7.6.

1107.2.2.7.1 Location. The water closet shall be positioned with a wall to the rear and to one side. The centerline of the water closet shall be 18 inches (457 mm) from the side wall.

1107.2.2.7.2 Clearance. Clearance around the water closet shall comply with Sections 1107.2.2.7.2.1 through 1107.2.2.7.2.3.

1107.2.2.7.2.1 Parallel approach. Where only a parallel approach is provided to the water closet, the clearance shall be 56 inches (1422 mm) minimum, measured perpendicular from the rear wall, and 48 inches (1219 mm) minimum, measured perpendicular from the sidewall. A lavatory complying with Section 1107.2.2.5 shall be permitted on the rear wall, 18 inches (457 mm) minimum from the water closet centerline.

1107.2.2.7.2.2 Forward approach. Where only a forward approach is provided to the water closet, the clearance shall be 66 inches (1676 mm) minimum, measured perpendicular from the rear wall, and 48 inches (1219 mm) minimum, measured perpendicular from the side wall. A lavatory complying with Section 1107.2.2.5 shall be permitted on the rear wall, 18 inches (457 mm) minimum from the water closet centerline.

1107.2.2.7.2.3 Parallel and forward approach. Where both a parallel and a forward approach are provided to the water closet, the clearance shall be 56 inches (1422 mm) minimum, measured perpendicular from the rear wall, and 60 inches (1524 mm) minimum, measured perpendicular from the side wall. No fixtures or obstructions, other than the water closet, shall be within the clearance.

1107.2.2.7.3 Grab bars. Grab bars for water closets shall comply with Section 609 of ICC A117.1 and shall be provided in accordance with Sections 1107.2.2.7.3.1 through 1107.2.2.7.3.2 of this code. Mounting heights of grab bars shall comply with Section 609.4 of ICC A117.1.

Exception: Grab bars are not required to be installed where reinforcement for such grab bars is installed and located to permit future installation of grab bars complying with Section 1107.2.2.7.3.

1107.2.2.7.3.1 Fixed side wall grab bars. Fixed side wall grab bars shall be 42 inches (1067 mm) minimum in length, located 12 inches (305 mm) maximum from the rear wall and extending 54 inches (1372 mm) minimum from the rear wall. In addition, a vertical grab bar 18 inches (457 mm) minimum in length shall be mounted with the bottom of the bar located between 39 inches (991 mm) and 41 inches (1041 mm) above the floor, and with the center of the bar located at 30 inches (762 mm) from the rear wall.

Exception: Where a side wall is not available for a 42-inch (1067 mm) grab bar, the sidewall grab bar shall be permitted to be 24 inches (610 mm) minimum in length, located 12 inches (305 mm) maximum from the rear wall.

FIGURE 1107.2.2.7.3.1
SIDEWALL GRAB BAR LOCATION

1107.2.2.7.3.2 Rear wall grab bars. The rear wall grab bar shall be 36 inches (915 mm) minimum in length, and extend from the centerline of the water closet 12 inches (305 mm) minimum on the side closet to the wall, and 24 inches (610 mm) minimum on the transfer side.

Exception: Where wall space will not permit a grab bar 36 inches (915 mm) minimum in length, reinforcement for a rear wall grab bar 24 inches (610 mm) minimum in length centered on the water closet shall be provided.

1107.2.2.7.4 Height. The top of the toilet seat shall be 15 inches (381 mm) minimum and 19 inches (483 mm) maximum above the floor or ground.

1107.2.2.7.5 Flush controls. Flush controls shall comply with Section 309 of ICC A117.1. Flush controls shall be located in accordance with one of the following:

1.	on the open side of the water closet; or

2.	centrally located on the top of the tank or water closet; or

3.	centrally located on the water closet rear wall.

1107.2.2.7.6 Dispensers. Toilet paper dispensers shall comply with this section.  The outlet of the dispenser shall be located within an area 24 inches (610 mm) minimum and 42 inches (1067 mm) maximum from the rear wall.  The outlet of the dispenser shall be located 18 inches (457 mm) minimum above the floor.  Dispensers shall comply with Section 609.3 of ICC A117.1.

FIGURE 1107.2.2.7.6
DISPENSER OUTLET LOCATION

1107.2.2.8 Bathing facilities. Where provided, a bathtub shall comply with Section 1107.2.2.8.1, and a shower compartment shall comply with Section 1107.2.2.8.2.

1107.2.2.8.1 Bathtubs. Bathtubs shall comply with Section 607 of ICC A117.1. Lavatories complying with Section 1107.2.2.5 of this code shall be permitted in the clearance required by Section 607.2 of ICC A117.1. Bathtub seats shall not be required.

Exception: Where a hand shower in compliance with Section 607.6 of ICC A117.1 is not provided, the owner shall provide such a hand shower at the time an individual with disabilities takes occupancy of the unit, or within 10 days of the date the request is made by an individual with disabilities, whichever is later, at the owner’s expense.

1107.2.2.8.1.1 Grab bars. Grab bars for bathtubs shall comply with Section 609 of ICC A117.1 and shall be provided in accordance with Section 607.4 of ICC A117.1.

Exception: Grab bars are not required to be installed where reinforcement for such grab bars is installed and located to permit future installation of grab bars complying with Section 1107.2.2.8.1.1.

1107.2.2.8.2 Showers. Showers shall comply with Section 608 of ICC A117.1.

Exceptions:

1.	For showers other than transfer-type showers, counter tops and cabinetry shall be permitted at the control end of the clearance, provided such counter tops and cabinetry can be removed and the floor finish extends under such cabinetry.

2.	Where a hand shower in compliance with Section 608.5 of ICC A117.1 is not provided pursuant to the exception in such section, the owner shall provide such a hand shower at the time an individual with disabilities takes occupancy of the unit, or within 10 days of the date the request is made by an individual with disabilities, whichever is later, at the owner’s expense.

1107.2.2.8.2.1 Grab bars and seats. Grab bars and seats for showers shall comply with Sections 609 and 610 of ICC A117.1 and shall be provided in accordance with Sections 608.2.3.2 and 608.3 of ICC A117.1.

Exception: Grab bars and seats are not required to be installed where reinforcement for such grab bars and seats is installed and located to permit future installation of grab bars and seats complying with Section 1107.2.2.8.2.1.

1107.2.2.9 Additional fixtures. Additional fixtures provided within toilet and bathing rooms shall comply with Sections 1004.11.1 (Grab Bar and Shower Seat Reinforcement), 1004.11.3.1.1 (Lavatory), 1004.11.3.1.2 (Water Closet), and 1004.11.3.1.3 (Bathing Fixtures) of ICC A117.1.

1107.2.3 Type B+NYC unit kitchen and kitchenette. Where kitchens and kitchenettes are provided in [the] a Type B+NYC dwelling unit or sleeping unit, the primary kitchen or kitchenette shall be constructed in accordance with the kitchen requirements of Section 1003.12 (Kitchen) and 1003.3.2 (Turning Space) of ICC A117.1, [and] including any modifications made by Sections 1107.2.3.1 through 1107.2.3.5 of this code. Secondary kitchens and kitchenettes within the same dwelling unit or sleeping unit shall be required to comply only with Section 1004.12 (Kitchens) of ICC A117.1.

1107.2.3.1 Kitchen counters. A kitchen counter that is required to comply with Section 1003.12.3.2 or 1003.12.4.2 (Height) of ICC A117.1 shall be permitted to be adjustable or designed to be replaceable as a unit at variable heights between 29 inches and 36 inches (737 mm and 914 mm), measured from the floor to the top of the work surface. The owner shall adjust or replace such countertop at the time [a person] an individual with [physical] disabilities takes occupancy of the unit, or within 10 days of the date the request is made by [a person with physical disabilities] such individual, whichever is later, at the owner’s expense.

1107.2.3.2 Appliances in kitchen and kitchenette. Appliances in kitchens and kitchenettes shall comply with Section 1003.12.5 (Appliances) of ICC A117.1.

Exception: Where appliances’ controls are not in compliance with Section 309.3 (Height) of ICC A117.1, the owner shall replace such appliances with appliances in conformance with Section 309.3 of ICC A117.1 at the time [a person] an individual with [physical] disabilities takes occupancy of the unit, or within 10 days of the date the request is made by [a person with physical disabilities] such individual, whichever is later, at the owner’s expense. However, the owner shall not be responsible to provide a particular model or type of appliances provided such appliances and controls comply with Sections 1003.12.5 and 309.3 of ICC A117.1.

1107.2.3.3 Refrigerator/freezers. Combination refrigerators and freezers shall comply with Section 1003.12.5.6 (Refrigerator/Freezer) of ICC A117.1. In addition, where less than 100 percent of storage volume of the freezer is located within 54 inches (1372 mm) maximum above the floor, such freezer shall be a self-defrosting type.

Exception: Where refrigerators and freezers are not in compliance with this section, the owner shall replace such appliances with complying appliances at the time [a person] an individual with [physical] disabilities takes occupancy of the unit, or within 10 days of the date the request is made by [a person with physical disabilities] such individual, whichever is later, at the owner’s expense. However, the owner shall not be responsible to provide a particular model or type of appliances provided such appliances comply with this section.

1107.2.3.4 Cooktops and ovens. Cooktops and ovens shall comply with [Section] Sections 1003.12.5.4 and 1003.12.5.5 of ICC A117.1, respectively. However, oven controls shall not be required to be located on either side of the oven door, provided such controls comply with Section 1003.12.5.5.4 of ICC A117.1. Where double ovens are provided, at least one oven interior and its controls shall comply with Section 309.3 (Height) of ICC A117.1.

1107.2.3.5 Kitchen and kitchenette storage. Kitchen storage, kitchen cabinets, drawers, and shelf storage areas, within kitchen and kitchenettes [that are required to] shall comply with Section [1003.12] 905 (Storage Facilities) of ICC A117.1 pursuant to Section 1107.2.3 of this code, except overhead cabinets[, shall comply with Section 905 (Storage Facilities) of ICC A117.1]. In addition, at least one storage shelf or cabinet, mounted above the work [counters] surface at 48 inches (1219 mm) maximum above the floor, shall be provided.

Exception: Where the storage shelf or cabinet is not provided in accordance with this section, the owner shall install such storage shelf or cabinet in compliance with this section at the time [a person] an individual with [physical] disabilities takes occupancy of the unit, or within 10 days of the date the request is made by [a person with physical disabilities] such individual, whichever is later, at the owner’s expense.

1107.2.4 Type B+NYC unit operable windows. All operable windows required to provide natural ventilation and/or an emergency escape and rescue opening in rooms or spaces in [the] a Type B+NYC dwelling unit or sleeping unit shall comply with Section 1003.13 (Windows) of ICC A117.1.

Exceptions:

1.	Where windows that are required to provide natural ventilation are not in compliance with reach ranges specified in Section 309.3 (Height) for operable parts as required by Section 1003.13.1 of ICC A117.1, the operable parts of such windows shall be designed to be operable by the use of adaptive devices. The owner shall provide such adaptive devices at the time [a person] with an individual with [physical] disabilities takes occupancy of the unit, or within 10 days of the date the request is made by [a person with physical disabilities] such individual, whichever is later, at the owner’s expense.

2.	Compliance with Section 1107.2.4 of this code is not required in kitchenettes less than 80 square feet (7.4 m2) in area and equipped with an accessible mechanical means of ventilation complying with the New York City Mechanical Code, and in bathrooms equipped with an accessible mechanical means of ventilation complying with the New York City Mechanical Code.

1107.2.5 Type B+NYC multistory units. Multistory Type B+NYC dwelling units or sleeping units shall comply with the following:

1.	One of the stories with an accessible entrance shall be designated as the primary entry story to the unit;

2.	All rooms, spaces and doors on the primary entry story shall comply with Section 1107.2; and

3.	Rooms, spaces or doors located on other than the primary entry story, and interior routes thereto, need not comply with Section 1107.2 where the primary entry story contains equivalent functional facilities. Functional facilities shall include cooking facilities, bathing facilities, laundry equipment, sleeping areas, living areas, dining areas, and outdoor areas such as balconies or terraces.

Exception: Functional facilities in compliance with Section 1107.2 need not be located on the primary entry story, but may be located on any story within the dwelling unit or sleeping unit, provided that all rooms, spaces and doors located on such story containing such functional facilities comply with Section 1107.2. Notwithstanding the above, at least one toilet room complying with Section 1107.2.2 shall be provided on the primary entry story. In addition, one of the following conditions shall be met:

1.	An accessible external elevator is provided to connect all such stories of the multistory dwelling unit or sleeping unit; or

2.	[A stairway complying with Section 504 (Stairways) of ICCA117.1 with a minimum clear width of 36 inches (914 mm) is provided within the multistory dwelling unit or sleeping unit to connect all such stories of the unit; or]

[3.]	An accessible route complying with Section 402 (accessible routes) of ICC A117.1 is provided within the dwelling unit or sleeping unit to connect all such stories of the unit.

1107.2.6 Type B+NYC unit raised or sunken floor area. Where a raised or sunken floor area in a portion of a living, dining, or sleeping room within a Type B+NYC dwelling unit or sleeping unit that is permitted by Section 1004.3 (Accessible route, Exception 1 and 2) of ICC A117.1 is provided, steps complying with Section 504 (Stairways) of ICC A117.1 with a minimum clear width of 36 inches (914 mm) shall connect such portion of raised or sunken floor area to an accessible route. In addition, a minimum area of 80 square feet (7.4 m2), and 8 feet (2438 mm) in one dimension, of each of such living, dining, or sleeping room shall be connected by an accessible route that is in compliance with Section 1004.3.2 (Components) of ICC A117.1.

1107.2.7 Type B+NYC unit storage facilities. Where storage facilities are provided within [the] a Type B+NYC dwelling unit or sleeping unit, they shall comply with Section 905 (Storage Facilities) of ICC A117.1.

Exceptions:

- A turning space shall [not] be required in storage facilities greater than 48 inches (1219 mm) in depth in compliance with Section 1003.3.2 of ICC A117.1.

- Where accessible storage elements are not in compliance with Section 905.3 of ICC A117.1, the owner shall relocate such elements to be in compliance with the section at the time [a person] an individual with [physical] disabilities takes occupancy of the unit, or within 10 days of the date the request is made by [a person] an individual with [physical] disabilities, whichever is later, at the owner’s expense.

1107.2.8 Type B+NYC unit laundry equipment. Where washing machines or clothes dryers are provided within [the] a Type B+NYC dwelling unit or sleeping unit, such equipment shall comply with Section 611 (Washing Machines and Clothes Dryers) of ICC A117.1 and shall be front loading. Laundry equipment in accessible common-use areas as required in Section 1107.3 shall comply with Section E105.2.

Exception: At the option of the owner, laundry equipment conforming to this section within the dwelling unit or sleeping unit may be provided at the time [a person] an individual with [physical] disabilities takes occupancy of the unit, or within 10 days of the date the request is made by [a person with physical disabilities] such individual, whichever is later, at the owner’s expense. However, the owner shall not be responsible to provide a particular model or type of equipment provided such equipment complies with this section.

1107.3 Accessible spaces. Rooms and spaces available to the general public or available for common use by residents [of] and serving Accessible units, Type B+NYC units[,] or Type B units shall be accessible. Accessible spaces shall include, but not be limited to, spaces for residents’ use, such as laundry rooms, refuse disposal and storage locations, mailbox areas, recreational facilities, assembly and tenants’ meeting rooms, storage rooms, management offices, parking areas, toilet and bathing rooms, kitchen, living and dining areas[,] and any exterior spaces, including patios, terraces and balconies[, management offices, and stores].

Exception: [In Group I-2 facilities, doors to sleeping units shall be exempted from the requirements for maneuvering clearance at the room side provided the door is a minimum of 44 inches (1118 mm) in width.] Stories and mezzanines exempted by Section 1107.4.

1107.3.1 Mailboxes. Except as otherwise provided by rules of the department for the purposes of complying with rules and regulations established by the United States Postal Service and/or the United States Department of Housing and Urban Development, where mailboxes are provided for each dwelling unit or sleeping unit in an interior location, 100 percent of such mailboxes shall comply with ICC A117.1, and the operable parts of such mailboxes shall be no higher than 48 inches (1219 mm) above the finished floor.

1107.4 Accessible route. At least one accessible route shall connect accessible building or facility entrances with the required accessible entrance(s) of each Accessible unit, Type B+NYC unit, and Type B unit within the building or facility and with those exterior and interior spaces and facilities that serve the units.

[Exception] Exceptions:

1.	Exterior spaces, including but not limited to roof terraces, exterior decks, patios or balconies that are part of Type B+NYC units or Type B units, that are not for public use or common use, that have impervious surfaces, and that are not more than 4 inches (102 mm) below the finished floor level of the adjacent interior space of the unit. Such roof terraces, decks, patios or balconies shall be designed so that accessibility can be readily provided, without modifications to the guard rail heights and structural supports, by the installation of a noncombustible ramp in compliance with Section 405 (Ramps) of ICC A117.1, or a noncombustible level platform, with removable panel for access to floor drainage, that is permeable to weather and in compliance with Section 302 (Floor Surfaces) and Section 303 (Changes in Level) of ICC A117.1.

2.	In Group I-3 facilities, an accessible route is not required to connect other levels or mezzanines where Accessible units, all common use areas serving Accessible units and all public use areas are on levels served by an accessible route.

3.	In Group R-1 occupancies, an accessible route is not required to connect stories or mezzanines within individual units, provided the accessible level meets the provisions for Accessible units and sleeping accommodations for two persons minimum and a toilet facility are provided on that level.

4.	An accessible route between stories is not required where Type B units are exempted by Section 1107.7.

1107.5 Group I. Accessible units shall be provided in Group I occupancies in accordance with Sections 1107.5.1 through [1107.5.6] 1107.5.5.

1107.5.1 Group I-1 [Accesible] Accessible units. [Group I-1 occupancies shall be provided with accessible features in accordance with Section 1107.5.1.1.] In Group I-1 occupancies, at least ten percent, but not less than one, of the dwelling units and sleeping units shall be Accessible units. The remainder shall be Type B+NYC units with all grab bars installed where grab bar reinforcements are required.

Exceptions:

- In Group I-1 occupancies classified as “convalescent facilities,” one hundred percent of the dwelling units or sleeping units shall be Accessible units.

- In Group I-1 occupancies where the governmental agency that licenses, funds or approves such facilities documents that such facilities are not targeted for people with conditions that affect mobility, at least five percent, but not less than one, of the dwelling units and sleeping units shall be Accessible units, and the remainder shall be Type B+NYC units. Conditions that affect mobility include conditions requiring the use or assistance of a brace, cane, crutch, prosthetic device, wheelchair, or powered mobility aid; arthritic, neurological, or orthopedic conditions that severely limit one’s ability to walk: respiratory diseases and other conditions which may require the use of portable oxygen; and cardiac conditions that impose significant functional limitations.

1107.5.2 Group I-2 [Nursing] nursing homes [Accessible units]. In nursing homes of Group I-2 occupancies 100 percent of the dwelling units and sleeping units shall be Accessible units.

1107.5.3 Group I-2 [Hospitals] hospitals. In general purpose hospitals, psychiatric facilities, detoxification facilities and residential care/assisted living facilities of Group I-2 occupancies, 100 percent of the dwelling units and sleeping units shall be Accessible units.

1107.5.3.1 Accessible unit entry doors. Entry doors to accessible dwelling units or sleeping units shall not be required to provide the maneuvering clearance beyond the latch side of the door.

1107.5.4 Group I-2 [Rehabilitation] rehabilitation facilities. In hospitals and rehabilitation facilities of Group I-2 occupancies [which] that specialize in treating conditions that affect mobility, or units within either [which] that specialize in treating conditions that affect mobility, 100 percent of the dwelling units and sleeping units shall be Accessible units.

1107.5.4.1 Enriched assisted living residences [(EARL)] (EALR) and special needs assisted living residences [(SNARL)] (SNALR). In enriched assisted living residences [(EARL)] (EALR) and special needs assisted living residences [(SNARL)] (SNALR) licensed by the New York State Department of Health, at least ten percent, but not less than one, of the dwelling units and sleeping units shall be Accessible units. The remainder shall be Type B+NYC units with all grab bars installed where grab bar reinforcements are required.

1107.5.5 Group I-3. Accessible units shall be provided in Group I-3 occupancies in accordance with Sections 1107.5.5.1 through 1107.5.5.3.

1107.5.5.1 Group I-3 sleeping units. In Group I-3 occupancies, at least [two] 3 percent of the total number of sleeping units in the facility, but not less than one [, of the dwelling units and sleeping units] unit in each classification level, shall be Accessible units.

1107.5.5.2 Special holding cells and special housing cells or rooms. In addition to the Accessible units required by Section 1107.5.5.1, where special holding cells or special housing cells or rooms are provided, at least one serving each purpose shall be an Accessible unit. Cells or rooms subject to this requirement include, but are not limited to, those used for purposes of orientation, protective custody, administrative or disciplinary detention or segregation, detoxification and medical isolation.

Exception: Cells or rooms specially designed without protrusions and that are used solely for purposes of suicide prevention shall not be required to include grab bars.

1107.5.5.3 Medical care facilities. In addition to any medical isolation cells required by Section 1107.5.5.2 to be Accessible units, 100 percent of the patient sleeping units or cells in medical facilities of [group] Group I-3 occupancies shall be Accessible units.[.]

1107.6 Group R. Accessible units, Type B+NYC units and Type B units shall be provided in Group R occupancies in accordance with Sections 1107.6.1 through 1107.6.3.

1107.6.1 Group R-1. Accessible units, Type B+NYC units, and Type B units shall be provided in Group R-1 occupancies in accordance with Sections 1107.6.1.1 through 1107.6.1.3.

Exception: Boarding houses, dormitories, fraternity houses and sorority houses in Group R-1 occupancies shall comply with Section 1107.6.1.4.

1107.6.1.1 Accessible units. [In Group R-1 occupancies,] Accessible dwelling units and sleeping units shall be provided in accordance with Table 1107.6.1.1.[All] Where buildings contain more than 50 dwelling units or sleeping units, the number of Accessible units shall be determined per building. Where buildings contain 50 or fewer dwelling units or sleeping units, all dwelling units and sleeping units [in Group R-1 occupancies] on a site shall be considered to determine the total number of Accessible units. Accessible units shall be dispersed among the various classes of units. Roll-in showers provided in Accessible units shall include a permanently mounted folding shower seat.

TABLE 1107.6.1.1
ACCESSIBLE DWELLING UNITS AND SLEEPING UNITS

| TOTAL NUMBER OF UNITS PROVIDED | MINIMUM REQUIRED NUMBER OF ACCESSIBLE UNITS WITHOUT ROLL-IN SHOWERS | MINIMUM REQUIRED NUMBER OF ACCESSIBLE UNITS WITH ROLL-IN SHOWERS | TOTAL NUMBER OF REQUIRED ACCESSIBLE UNITS |
| --- | --- | --- | --- |
| 1 to 25 | 1 | 0 | 1 |
| 26 to 50 | 2 | 0 | 2 |
| 51 to 75 | 3 | 1 | 4 |
| 76 to 100 | 4 | 1 | 5 |
| 101 to 150 | 5 | 2 | 7 |
| 151 to 200 | 6 | 2 | 8 |
| 201 to 300 | 7 | 3 | 10 |
| 301 to 400 | 8 | 4 | 12 |
| 401 to 500 | 9 | 4 | 13 |
| 501 to 1,000 | 2% of total | 1% of total | 3% of total |
| Over 1,000 | 20, plus 1 for each 100, or fraction thereof, over 1,000 | 10 plus 1 for each 100, or fraction thereof, over 1,000 | 30 plus 2 for each 100, or fraction thereof, over 1,000 |

1107.6.1.2 Type B+NYC units. In structures with four or more dwelling units or sleeping units intended to be occupied as a residence, every dwelling unit and sleeping unit intended to be occupied as a residence and not required to be an Accessible unit shall be a Type B+NYC unit unless the number of Type B+NYC units is permitted to be reduced in accordance with Section 1107.7.4. Where no Type B+NYC units are required per Section 1107.7.4, all units not required to be Accessible units shall be Type B units.

Exception: The number of Type B units is permitted to be reduced in accordance with Section 1107.7.

1107.6.1.3 Doors and doorways. In all units, including those not required to be Accessible units, Type B+NYC units, or Type B units, entrances, [,] doors, and doorways providing user passage into and within units shall comply with Section 404.2.2 (Clear Width) of ICC A117.1.

1107.6.1.4 Boarding houses, dormitories, fraternity houses and sorority houses in Group R-1. Accessible units and Type B+NYC units shall be provided in boarding houses, dormitories, fraternity houses and sorority houses in Group R-1 occupancies in accordance with Sections 1107.6.1.4.1 and 1107.6.1.4.2. Where the building or part thereof contains sleeping units where residents share bathroom or kitchen facilities, or both, bedrooms shall be counted as sleeping units for the purpose of determining the number of units. Where the sleeping units are grouped in suites, only one sleeping unit in each suite shall be permitted to count towards the number of required Accessible units.

1107.6.1.4.1 Accessible units. Accessible dwelling units and sleeping units shall be provided in accordance with Table 1107.6.1.1.

1107.6.1.4.2 Type B+NYC units. Every dwelling unit and every sleeping unit not required to be an Accessible unit shall be a Type B+NYC unit unless the number of Type B+NYC units is permitted to be reduced in accordance with Section 1107.7.4. Where no Type B+NYC units are required in accordance with Section 1107.7.4, all units shall be Type B units.

Exception: The number of Type B units is permitted to be reduced in accordance with Section 1107.7.

1107.6.2 Group R-2. Type B+NYC units and Type B units shall be provided in [occupancies in] Group R-2 occupancies in accordance with Section 1107.6.2.1.

1107.6.2.1 [Type B and] Type B+NYC units. Every dwelling unit and sleeping unit shall be a Type B+NYC unit.

Exception: [unless the] The number of Type B+NYC units is permitted to be reduced in accordance with Section 1107.7.4.

1107.6.2.2 Type B units. Where no Type B+NYC units are required in accordance with Section 1107.7.4, all units intended to be occupied as a residence shall be Type B units.

[Exception] Exceptions:

1.	The number of Type B units is permitted to be reduced in accordance with Section 1107.7.

2.	Buildings containing fewer than four dwelling units or sleeping units need not provide Type B units.

1107.6.3 Group R-3. In Group R-3 occupancies where there are four or more dwelling units or sleeping units intended to be occupied as a residence in a single structure, every dwelling unit and sleeping unit intended to be occupied as a residence shall be a Type B unit.

Exception: The number of Type B units is permitted to be reduced in accordance with Section 1107.7.

1107.7 General exceptions for Type B units.  Where specifically permitted by Section 1107.6, the required number of Type B units is permitted to be reduced in accordance with Sections 1107.7.1 through 1107.7.3.

1107.7.1 Structures without elevator service where Type B units are required.  Where no elevator service is provided in a structure or required by other sections of this code,[,] only the dwelling units and sleeping units that are located on stories indicated in Sections 1107.7.1.1 and 1107.7.1.2 are required to be Type B units.

1107.7.1.1 One story with Type B units required. At least one story containing dwelling units or sleeping units intended to be occupied as a residence shall be provided with an accessible entrance and accessible route from the exterior of the structure and all units intended to be occupied as a residence on that story shall be Type B units.

1107.7.1.2 Other stories with Type B units required. If other stories containing dwelling units or sleeping units intended to be occupied as a residence are served by a building entrance that is in proximity to arrival points as indicated in Items 1 and 2, such building entrance shall be accessible and all dwelling units and sleeping units intended to be occupied as a residence served by that entrance on that story shall be Type B units.

1.	Where the slopes of the undisturbed site measured between the planned entrance and all vehicular or pedestrian arrival points within 50 feet (15 240 mm) of the planned entrance are 10 percent or less, and

2.	Where the slopes of the planned finished grade measured between the entrance and all vehicular or pedestrian arrival points within 50 feet (15 240 mm) of the planned entrance are 10 percent or less.

Where no such arrival points are within 50 feet (15 240 mm) of the entrance, the closest arrival point shall be used unless that arrival point serves the story required by Section 1107.7.1.1.

1107.7.2 Multistory units where Type B units are required. A multistory dwelling unit or sleeping unit [which] that is not provided with elevator service is not required to be a Type B unit. Where a multistory unit is provided with external elevator service to only one floor, the floor provided with elevator service shall be the primary entry to the unit, shall comply with the requirements for a Type B unit and, where provided within the unit, a living area, a kitchen and a toilet facility shall be provided on that floor.

1107.7.3 Elevator service to the lowest story with Type B units. Where elevator service in the building [is provided for the sole purpose of complying with the provisions of Section 1107.7.1.1 to serve as] provides an accessible route only to the lowest story containing dwelling units or sleeping units intended to be occupied as a residence, only the units on that story that are intended to be occupied as a residence on the lowest story served by the elevator are required to be Type B units.

1107.7.4 General exceptions for Type B+NYC units. Where specifically permitted by Sections 1107.5 and 1107.6, the required number of Type B+NYC units is permitted to be reduced in accordance with Section 1107.7.4.1.

1107.7.4.1 Buildings or structures without elevator service where Type B+NYC units are required. In buildings or structures where no elevator service is provided or required by other sections of this code, only the dwelling units and sleeping units that are located on stories indicated in Section 1107.7.4.1.1 are required to be Type B+NYC units.

1107.7.4.1.1 Units located in the cellar, basement, or first floor. In buildings or structures where the lowest story containing dwelling or sleeping units is the cellar, basement, or first floor, at least one such story containing dwelling or sleeping units, regardless of intent to occupy as a residence, shall be provided with an accessible entrance and accessible route from the exterior of the building or structure and all units on that story, regardless of intent to occupy as a residence, shall be Type B+NYC units. Where no dwelling units or sleeping units are located in the cellar, basement, or first floor, Type B units shall be provided where required by Section 1107.7.1 through 1107.7.3.

Exceptions:

1.	Buildings containing fewer than four dwelling units or sleeping units need not provide Type B units.

2.	Group R-2 occupancies in buildings with first occupancy on or before March 13, 1991 need not provide Type B units.

SECTION BC 1108
SPECIAL OCCUPANCIES

1108.1 General. In addition to the other requirements of this chapter and applicable provisions of Appendices E and N, the requirements of Sections 1108.2 through [1108.4] 1108.5 shall apply to specific occupancies.

1108.2 Assembly area seating. Assembly areas with seating shall comply with Sections 1108.2.1 through [1108.2.8] 1108.2.5. Lawn seating shall comply with Section 1108.2.6. Assistive listening systems shall comply with Section 1108.2.7. Performance areas viewed from assembly seating areas shall comply with Section 1108.2.8. Dining and drinking areas shall comply with Section 1108.2.9. [In addition, lawn seating shall comply with Section 1108.2.6.]

1108.2.1 Services. If a service or facility is provided in an area that is not required to be accessible in accordance with Section 1108.2.9, the same service or facility shall be provided on an accessible level and shall be accessible.

1108.2.2 Wheelchair spaces. In theaters, bleachers, grandstands, stadiums, arenas and other assembly areas, accessible wheelchair spaces, companion seats, and designated aisle seats complying with ICC A117.1, including Section 802 (Assembly Areas), shall be provided in accordance with Sections 1108.2.2.1 through [1108.2.2] 1108.2.2.4. Required accessible wheelchair spaces and their companion seats as required in Section 1108.2.5 shall be delineated on the approved seating plans. Such spaces and seats which are unsold 1 day (24 hours) before the event shall be permitted to be released for sale to the public, including [persons] individuals without [physical] disabilities.

1108.2.2.1 General seating. Wheelchair spaces shall be provided in accordance with Table 1108.2.2.1.

TABLE 1108.2.2.1
ACCESSIBLE WHEELCHAIR SPACES

| CAPACITY OF SEATING IN ASSEMBLY AREAS | MINIMUM REQUIRED NUMBEROF WHEELCHAIR SPACES |
| --- | --- |
| 4 to 25 | 1 |
| 26 to 50 | 2 |
| 51 to 100 | 4 |
| 101 to 300 | 5 |
| 301 to 500 | 6 |
| 501 to 5,000 | 6, plus 1 for each 150, or fraction thereof, between 501 through 5,000 |
| 5,001 and over | 36 plus 1 for each 200, or fraction thereof, over 5,000 |

1108.2.2.2 Luxury boxes, club boxes and suites. In each luxury box, club box[,] and suite within arenas, stadiums and grandstands, wheelchair spaces shall be provided in accordance with Table 1108.2.2.1.

1108.2.2.3 Other boxes. In boxes other than those required to comply with Section 1108.2.2.2, the total number of wheelchair spaces provided shall be determined in accordance with Table 1108.2.2.1. Wheelchair spaces shall be located in not less than 20 percent of all boxes provided.

[1108.2.2.4 Team or player seating. At least one wheelchair space shall be provided in team or player seating areas serving areas of sport activity.]

[Exception: Wheelchair spaces shall not be required in team or player seating areas serving bowling lanes that are not required to be located on an accessible route in accordance with Section 1109.14.4.1.]

1108.2.3 Companion seats. At least one companion seat complying with ICC A117.1, including Section 802.7 (Companion Seat), shall be provided for each wheelchair space required by Sections 1108.2.2.1 through 1108.2.2.3.

1108.2.4 Dispersion of wheelchair spaces in multilevel assembly seating areas. In multilevel assembly seating areas, wheelchair spaces shall be provided on the main floor level and on one of each two additional floor or mezzanine levels. Wheelchair spaces shall be provided in each luxury box, club box and suite within assembly facilities.

Exceptions:

1.	In multilevel assembly [spaces] seating areas utilized as place of religious worship where the second floor or mezzanine level contains 25 percent or less of the total seating capacity, wheelchair spaces shall be permitted to all be located on the main level.

2.	In multilevel assembly seating areas where the second floor or mezzanine level provides 25 percent or less of the total seating capacity and 300 or fewer seats, all wheelchair spaces shall be permitted to be located on the main level.

3.	Wheelchair spaces in team or player seating serving areas of sport activity are not required to be dispersed.

1108.2.5 Designated aisle seats. At least [five] 5 percent, but not less than one, of the total number of aisle seats provided shall be designated aisle seats[,] and shall be the aisle seats located closest to accessible routes, and shall comply with ICC A117.1, including Section 802.8 (Designated Aisle Seats).

Exception: Designated aisle seats are not required in team or player seating serving areas of sport activity.

1108.2.6 Lawn seating. Lawn seating areas and exterior overflow seating areas, where fixed seats are not provided, shall connect to an accessible route.

1108.2.7 Assistive listening systems. Each building, room or space used for assembly [area] purposes where audible communications are integral to the use of the space, regardless of the occupancy load of such space, shall have an assistive listening system in compliance with ICC A117.1, including Section 706 (Assistive Listening Systems) and Appendix N of this code.

Exception: Other than in courtrooms, an assistive listening system is not required where there is no audio amplification system.

1108.2.7.1 Receivers.[Receivers] The number and type of receivers shall be provided for assistive listening systems in accordance with Table 1108.2.7.1[All receivers shall be hearing-aid compatible].

Exceptions:

1.	Where a building contains more than one room or space used for assembly [area] purposes, the total number of required receivers shall be permitted to be calculated [according to] based on the total number of seats in the [assembly areas in the] building, provided that all receivers are usable with all systems[,] and if the rooms or spaces used for assembly [areas] purposes required to provide assistive listening are under one management.

2.	Where all seats in [an] a building, room or space used for assembly [area] purposes are served by an induction loop assistive listening system, the minimum number of receivers required by Table 1108.2.7.1 to be hearing-aid compatible shall not be required.

TABLE 1108.2.7.1
RECEIVERS FOR ASSISTIVE LISTENING SYSTEMS

| CAPACITY OF SEATING IN ASSEMBLY AREAS | MINIMUM REQUIRED NUMBER OF RECEIVERS | MINIMUM NUMBER OF RECEIVERS TO BE HEARING-AID COMPATIBLE |
| --- | --- | --- |
| 50 or less | 2 | 2 |
| 51 to 200 | 2, plus 1 per 25 seats over 50 seats* | 2 |
| 201 to 500 | 2, plus 1 per 25 seats over 50 seats* | 1 per 4 receivers* |
| 501 to 1,000 | 20, plus 1 per 33 seats over 500 seats* | 1 per 4 receivers* |
| 1,001 to 2,000 | 35, plus 1 per 50 seats over 1,000 seats* | 1 per 4 receivers* |
| Over 2,000 | 55, plus 1 per 100 seats over 2,000 seats* | 1 per 4 receivers* |

NOTE: * = or fraction thereof

1108.2.7.2 Ticket windows. Where ticket windows are provided, at least one window at each location shall have an assistive listening system.

1108.2.7.3 Public address systems. Where stadiums, arenas and grandstands provide audible public announcements, they shall also provide equivalent text information regarding events and facilities in compliance with Sections [1108.2.7.2.1] 1108.2.7.3.1 and [1108.2.7.2.2] 1108.2.7.3.2.

[1108.2.7.2.1] 1108.2.7.3.1 Prerecorded text messages. Where electronic signs are provided and have the capability to display prerecorded text messages containing information that is the same, or substantially equivalent, to information that is provided audibly, signs shall display text that is equivalent to audible announcements.

Exception: Announcements that cannot be prerecorded in advance of the event shall not be required to be displayed.

[1108.2.7.2.2] 1108.2.7.3.2 Real-time messages. Where electronic signs are provided and have the capability to display real-time messages containing information that is the same, or substantially equivalent, to information that is provided audibly, signs shall display text that is equivalent to audible announcements.

1108.2.8 Performance areas. An accessible route shall directly connect the performance area to the assembly seating area where a circulation path directly connects a performance area to an assembly seating area. An accessible route shall be provided from performance areas to ancillary areas or facilities used by performers.

1108.2.9 Dining and drinking areas. In dining and drinking areas, [the total] all interior and exterior floor [area allotted for seating and tables] areas shall be accessible and be on an accessible route.

Exceptions:

1.	[In buildings or facilities not required to provide an] An accessible route between accessible levels [as described in] and stories above or below is not required where permitted by Section 1104.4, Exception 1 [, an].

2.	An accessible route to dining and drinking areas in a mezzanine [seating area] is not required, provided that the mezzanine contains less than [33] 25 percent of the total [seating] combined area for dining and drinking and the same services, and decor are provided in the accessible area.

[2.] 3.	In sports facilities, tiered dining areas providing seating required to be accessible shall be required to have accessible routes serving at least 25 percent of the dining area, provided that accessible routes serve accessible seating and where each tier is provided with the same services and similar view.

4.	Employee-only work areas shall comply with Sections 1103.2.2 and 1104.3.1.

1108.2.9.1 Dining surfaces. Where dining surfaces for the consumption of food or drink are provided, at least [5] 10 percent of the total number of seating and standing spaces, but not less than one, of each type of [the] dining surfaces [for the seating and standing spaces] shall be accessible and be distributed throughout the facility and located on a level [connected] accessed by an accessible route.

[Exception: Where food or drink is served at counters exceeding 34 inches (864 mm) in height, such dining surfaces shall not be required to comply with Section 1108.2.9.1 provided equivalent service is available at accessible tables or counters that are in compliance with Section 902 (Dining Surfaces and Work Surfaces) of ICC A117.1 within the same dining area.]

1108.2.9.2 Dining and drinking counters. Where seating is provided at dining or drinking counters, at least one 60 inch (1524 mm) long portion of the counter shall be provided with two accessible seating spaces. Such accessible seating space shall comply with Section 902 (Dining Surfaces and Work Surfaces) of ICC A117.1, and shall not be located within 40 inches (1016 mm) of either end of the counter, so as to provide individuals with disabilities with the same level of service and experience as that provided to others.

Exceptions:

1.	Where the linear length of counter is 12 feet (3658 mm) or less, one accessible seating space shall be provided, at least 30 inches (762 mm) long, for each accessible seating space required by Section 1108.2.9.1. Such accessible seating space may be located anywhere along the counter.

2.	In Group R-2 occupancies, one accessible seating space shall be provided, at least 30 inches (762 mm) long, for each accessible seating space required by Section 1108.2.9.1.

1108.3 Self-service storage facilities. Self-service storage facilities shall provide accessible individual self-storage spaces in compliance with Section 1104 of this code and ICC A117.1, including Section 905 (Storage Facilities). The number of required self-storage spaces shall be in accordance with Table 1108.3.

TABLE 1108.3
ACCESSIBLE SELF-SERVICE STORAGE FACILITIES

| TOTAL SPACES IN FACILITY | MINIMUM NUMBER OF REQUIRED ACCESSIBLE SPACES |
| --- | --- |
| 1 to 200 | 5%, but not less than 1 |
| Over 200 | 10, plus 2% of total number of units over 200 |

1108.3.1 Dispersion. Accessible individual self-service storage spaces shall be dispersed throughout the various classes of spaces provided. Where more classes of spaces are provided than the number of required accessible spaces, the number of accessible spaces shall not be required to exceed that required by Table 1108.3. Accessible spaces are permitted to be dispersed in a single building of a multibuilding facility.

1108.4 Judicial facilities. Judicial facilities shall comply with Sections 1108.4.1 [through 1108.4.3] and 1108.4.2.

1108.4.1 Courtrooms. Each courtroom shall be accessible and comply with ICC A117.1, including Section 807 (Courtrooms), and Sections 1108.4.1.1 through 1108.4.1.5.

1108.4.1.1 Jury box. A wheelchair space complying with ICC A117.1 shall be provided within the jury box.

Exception: Adjacent companion seating is not required.

1108.4.1.2 Gallery seating. Wheelchair spaces complying with ICC A117.1 shall be provided in accordance with Table 1108.2.2.1. Designated aisle seats shall be provided in accordance with Section 1108.2.5.

1108.4.1.3 Assistive listening systems. An assistive listening system must be provided. Receivers shall be provided for the assistive listening system in accordance with Section 1108.2.7.1.

1108.4.1.4 Employee work stations. The judge’s bench, clerk’s station, bailiff’s station, deputy clerk’s station and court reporter’s station shall be located on an accessible route. The vertical access to elevated employee work stations within a courtroom is not required at the time of initial construction, provided a ramp, lift or elevator complying with ICC A117.1 can be installed without requiring reconfiguration or extension of the courtroom or extension of the electrical system.

1108.4.1.5 Other work stations. The litigant’s and counsel stations, including the lectern, shall be accessible in accordance with ICC A117.1.

1108.4.2 Holding cells. Central holding cells and court-floor holding cells shall comply with Sections 1108.4.2.1 and 1108.4.2.2.

1108.4.2.1 Central holding cells. Where separate central holding cells are provided for adult males, juvenile males, adult females or juvenile females, one of each type shall be accessible. Where central holding cells are provided and are not separated by age or [sex] gender, at least one accessible cell shall be provided.

1108.4.2.2 Court-floor holding cells. Where separate court-floor holding cells are provided for adult males, juvenile males, adult females or juvenile females, each courtroom shall be served by one accessible cell of each type. Where court-floor holding cells are provided and are not separated by age or [sex] gender, courtrooms shall be served by at least one accessible cell. Accessible cells shall be permitted to serve more than one courtroom.

[1108.4.3 Visiting areas. Visiting areas shall comply with Sections 1108.4.3.1 and 1108.4.3.2.]

[1108.4.3.1 Cubicles and counters. At least 5 percent, but not fewer than one, of the cubicles shall be accessible on both the visitor and detainee sides. Where counters are provided, at least one shall be accessible on both the visitor and detainee sides.]

[Exception: This requirement shall not apply to the detainee side of cubicles or counters at noncontact visiting areas not serving accessible holding cells.]

[1108.4.3.2 Partitions. Where solid partitions or security glazing separate visitors form detainees, at least one of each type of cubicle or counter partition shall be accessible.]

1108.5 Assembly areas without seating. Assembly areas without seating shall comply with Section 1108.2.7.

SECTION BC 1109
OTHER FEATURES AND FACILITIES

1109.1 General. Accessible building features and facilities shall be provided in accordance with Sections 1109.2 through [1109.16] 1109.15.

Exception: Type B+NYC and Type B units shall comply with Section 1107 and ICC A117.1.

1109.2 Toilet and bathing rooms. Each toilet room and bathing room shall be accessible. Where a floor level is not required to be connected by an accessible route, the only toilet rooms or bathing rooms provided within the facility shall not be located on the [in accessible] inaccessible floor. [At] Except as provided for in Sections 1109.2.2 and 1109.2.3, at least one of each type of fixture, element, control or dispenser in each accessible toilet room and bathing room shall be accessible.

Exceptions:

1.	In nonresidential occupancies, for toilet rooms or bathing rooms accessed only through a private office, not for common or public use, and intended for use by a single occupant of such private office, any of the following alternatives are allowed:

1.1.	Doors are permitted to swing into the clear floor space provided the door swing can be reversed to meet the requirements in Section 603.2.2 (Door Swing) of ICC A117.1; [and]

1.2.	The height requirements for the water closet in Section 604.4 (Height) of ICC A117.1 are not applicable; [and]

1.3.	Grab bars are not required to be installed in a toilet room, provided that the reinforcement has been installed in the walls and located so as to permit the installation of such grab bars; and

1.4.	The requirement for height, knee and toe clearance shall not apply to a lavatory.

2.	This section is not applicable to dwelling units, sleeping units and patient toilet and bathing rooms that are not required to be accessible by Section 1107.

3.	Where multiple single-user toilet rooms or bathing rooms are clustered to be within sight of, or adjacent to one another at a single location, at least 50 percent, but not less than one room for each use at each cluster, shall be accessible. In Group R-2 occupancies, where multiple single-user toilet rooms or bathing rooms are clustered, all such rooms must comply with the design and construction requirements of the Fair Housing Act.

4.	 [Where] In other than Group R-2 occupancies, where no more than one urinal is provided in a toilet room or bathing room, the urinal is not required to be accessible.

5.	Toilet rooms or bathing rooms that are part of [critical-care] critical care or intensive care patient sleeping rooms serving Accessible units are not required to be accessible.

6.	Toilet rooms or bathing rooms designed for bariatrics patients are not required to comply with the toilet room and bathing room requirements in ICC A117.1. The sleeping units served by bariatrics toilet or bathing rooms shall not count toward the required number of Accessible sleeping units.

7.	Where toilet facilities are primarily for children’s use, required accessible water closets, toilet compartments and lavatories shall be permitted to comply with children’s provision of ICC A117.1.

8.	Where multiple single user portable toilet or bathing units are clustered at a single location, [not less than 5] at least five percent, but not less than one of the toilet units and bathing units at each cluster shall be accessible. Accessible portable toilet units and bathing units shall be identified by the [International Symbol of Accessibility] dynamic accessibility symbol complying with Section [1110.1] 1111.1.

1109.2.1 Family or assisted-use toilet and bathing rooms. In assembly and mercantile occupancies, an accessible family or assisted-use toilet room shall be provided where an aggregate of six or more male and female water closets is required. In buildings of mixed occupancy, only those water closets required for the assembly or mercantile occupancy shall be used to determine the family or assisted-use toilet room requirement. In recreational facilities where separate-sex bathing rooms are provided, an accessible family or assisted-use bathing room shall be provided. Fixtures located within family or assisted-use toilet and bathing rooms required by this section are permitted to be included in the number of fixtures required by the New York City Plumbing Code for either the male or female occupants.

Exception: Where each separate-sex bathing room has only one shower or bathtub fixture, a family or assisted-use bathing room is not required.

1109.2.1.1 Standard. Family or assisted-use toilet and bathing rooms shall comply with Sections 1109.2.1.2 through 1109.2.1.7[and ICC A117.1].

1109.2.1.2 Family or assisted-use toilet rooms. Family or assisted-use toilet rooms shall include only one water closet and only one lavatory. A family or assisted-use bathing room in accordance with Section 1109.2.1.3 shall be considered a family or assisted-use toilet room.

Exception: A urinal is permitted to be provided in addition to the water closet in a family or assisted-use toilet room.

1109.2.1.3 Family or assisted-use bathing rooms. Family or assisted-use bathing rooms shall include only one shower or bathtub fixture. Family or assisted-use bathing rooms shall also include one water closet and one lavatory. Where storage facilities are provided for separate-sex bathing rooms, accessible storage facilities complying with Section [1109.8] 1109.9 shall be provided for family or assisted-use bathing rooms.

1109.2.1.4 Location. Family or assisted-use toilet and bathing rooms shall be located on an accessible route. Family or assisted-use toilet rooms shall be located not more than one story above or below separate-sex toilet rooms. The accessible route from any separate-sex toilet room to a family or assisted-use toilet room shall not exceed 500 feet (152 m).

1109.2.1.5 Prohibited location. In passenger transportation facilities and airports, the accessible route from separate-sex toilet rooms to a family or assisted-use toilet room shall not pass through security checkpoints.

1109.2.1.6 Clear floor space. Where doors swing into a family or assisted-use toilet or bathing room, a clear floor space not less than 30 inches by 48 inches (762 mm by 1219 mm) shall be provided, within the room, beyond the area of the door swing.

1109.2.1.7 Privacy. Doors to family or assisted-use toilet and bathing rooms shall be securable from within the room.

1109.2.2 Water closet compartment. Where water closet compartments are provided in a toilet room or bathing room, at least [one wheelchair-accessible compartment shall be provided 5 percent, but not less than one of the total number of compartments shall be wheelchair accessible. Where the combined total water closet compartments and urinals provided in a toilet room or bathing room is six or more, at least [one ambulatory-accessible water closet compartment shall be] 5 percent, but not less than one of the total number of compartments shall be ambulatory accessible, provided in addition to the wheelchair-accessible compartment. Wheelchair-accessible and ambulatory-accessible compartments shall comply with ICC A117.1 including Section 604.9 (Wheelchair Accessible Compartments) and 604.10 (Ambulatory Accessible Compartments).

1109.2.3 Lavatories. Where lavatories are provided, at least 5 percent, but not less than one, shall be accessible. Where an accessible lavatory is located within the accessible water closet compartment, at least one additional accessible lavatory shall be provided in the multicompartment toilet room outside the accessible water closet compartment. Where the total lavatories provided in a toilet room or bathing [room] facility is six or more, at least one lavatory with enhanced reach ranges [in accordance with ICC A117.1,] shall be provided.

1109.2.4 Diaper changing accommodations. In assembly [group A occupancies] and mercantile [group M] occupancies on each floor level containing a public toilet room, both male and female occupants shall have access to at least one safe, sanitary and convenient diaper changing station, deck, table or similar amenity, which shall comply with Section 603.5 (Diaper Changing Tables) of ICC A117.1.

1109.3 Sinks. Where sinks are provided, at least [five] 5 percent[,] but not less than one[,] provided in accessible spaces shall comply with ICC A117.1, including Section 606 (Lavatories and Sinks).

Exception: Mop or service sinks are not required to be accessible.

1109.4 Kitchens, kitchenettes and wet bars.  Where kitchen, kitchenettes and wet bars not located within dwelling or sleeping units, are provided in accessible spaces or rooms, they shall be accessible in accordance with ICC A117.1 including Section 804 (Kitchens and Kitchenettes), and Section 1109.9 of this code for storage.

1109.5 Drinking fountains. Where drinking fountains are provided on an exterior site, on a floor or within a secured area, the drinking fountains shall be provided in accordance with Sections 1109.5.1 and 1109.5.2.[.]

1109.5.1 Minimum number. No fewer than two drinking fountains shall be provided. One drinking fountain shall comply with the requirements for people who use a wheelchair and one drinking fountain shall comply with the requirements for standing persons.

[Exception] Exceptions:

1.	A single drinking fountain with two separate spouts that complies with the requirements for people who use a wheelchair and standing persons shall be permitted to be substituted for two separate drinking fountains.

2.	Where drinking fountains are primarily for children’s use, drinking fountains for people using wheelchairs shall be permitted to comply with the children’s provisions in ICC A117.1 and drinking fountains for standing children shall be permitted to provide the spout at 30 inches (762 mm) minimum above the floor.

1109.5.2 More than the minimum number. Where more than the minimum number of drinking fountains specified in Section 1109.5.1 [are] is provided,[50 percent of the total number of drinking fountains provided shall comply with the requirements for persons who use a wheelchair and] 50 percent of the total number of drinking fountains provided shall comply with the requirements for [standing persons] people who use a wheelchair and 50 percent of the total number of drinking fountains provided shall comply with the requirements for standing persons.

[Exception] Exceptions:

1.	Where 50 percent of the drinking fountains yields a fraction, 50 percent shall be permitted to be rounded up or down, provided that the total number of drinking fountains complying with this section equals 100 percent of the drinking fountains.

2.	Where drinking fountains are primarily for children’s use, drinking fountains for people using wheelchairs shall be permitted to comply with the children’s provisions in ICC A117.1 and drinking fountains for standing children shall be permitted to provide the spout at 30 inches (762 mm) minimum above the floor.

1109.5.3 Container faucets. Where a separate faucet designed for filling a container is provided at the drinking fountain pursuant to Section 410.1 of the New York City Plumbing Code, such container faucet shall comply with Section 606.4 of ICC A117.1.

1109.6 Saunas and steam rooms. Where provided, saunas and steam rooms shall be accessible. Such saunas and steam rooms shall comply with Section 612 of ICC A117.1.

Exception: Where saunas or steam rooms are clustered at a single location, at least 5 percent of the saunas and steam rooms, but not less than one, of each type in each cluster shall be accessible.

1109.7 Elevators. All passenger elevators on an accessible route shall be accessible and comply with [3001.3] ICC A117.1 and Chapter 30 of this code.

Exception: Section 407.4.6.2.2 (Arrangement) of ICC A117.1 shall not apply.

[1109.6.1] 1109.7.1 Limited-Use/Limited-Application (LULA) elevators. LULA elevators shall comply with Section 408 (Limited-Use/Limited-Application Elevators) of ICC A117.1 and with Part [XXV] 5.2 of ASME A17.1 as modified by Appendix K of this code, and shall be limited to a maximum rise of not more than 25 feet (7620 mm)[) and serving not more than three contiguous levels]. In new construction, such LULA elevators shall be permitted:

1.	To be a part of the required accessible route where either a wheelchair lift complying with Section 1109.7 is permitted or a private residence elevator complying with Section 409 (Private Residence Elevators) of ICC A117.1 is permitted;

2.	To be part of the required accessible route in places of religious services; or

3.	In multilevel buildings and facilities not required to have an accessible route pursuant to the exceptions in Section 1104.4.

[1109.6.1.1] 1109.7.1.1 Prior code buildings. In prior code buildings, LULA elevators shall comply with Section 408 (Limited-use/Limited-Application Elevators) of ICC A117.1 and with Part 5.2 of ASME A17.1 as modified by Appendix K of this code. LULA elevators shall be limited to a maximum rise of not more than 25 feet (7620 mm) and shall be permitted to be a part of the required accessible route [where the total floor area of the entire building is less than 10,000 square feet (929 m2) provided such LULA elevator is limited to a maximum rise of not more than 25 feet, serves not more than three contiguous levels, and elevators are not otherwise required by Chapter 30.] as follows:

1.	In spaces complying with Section 1109.7.1 where a LULA is permitted in new construction;

2.	Where the total floor area of the entire building is less than 10,000 square feet (929 m²); or

3.	Where it serves an individual occupancy of less than 10,000 square feet (929 m²) in buildings of 10,000 square feet (929 m²) or more.

1109.7.2 Destination–oriented elevators. Where destination-oriented elevators are provided, hall call consoles shall comply with Sections 1109.7.2.1 through 1109.7.2.3.  Responding elevator cars shall comply with Section 1109.7.2.5.

1109.7.2.1 Hall call console number and location. Hall call consoles shall be located and provided in a number complying with Section 1109.7.2.1.1 or 1109.7.2.1.2, as applicable.  Where provided, hall call consoles shall be located on accessible routes connecting to the elevator landings they serve.

Exception: Where hall call consoles are an integral part of security barriers, at least one console for each type of use at each distinct location shall be located on an accessible route connecting to the elevator landings served by all such consoles.

1109.7.2.1.1 Transfer floors, sky lobbies and floors containing building entrances. Elevator landings on transfer floors, sky lobbies and floors containing building entrances shall provide at least one wall-mounted hall call console adjacent to each elevator hoistway entrance. When the accessibility function button is activated, the system shall assign an elevator car located to one side (left or right) of the hall call console to be the responding elevator.

1109.7.2.1.2 Other floors. Floors other than those subject to Section 1109.7.2.1.1 shall provide one hall call console for every five elevators, or fraction thereof, on each side of the elevator landing. The hall call console shall be located immediately adjacent to one or more elevator hoistway entrances. When the accessibility function button is activated, the system shall assign the elevator car located closest to one side (left or right) of the hall call console to be the responding elevator.

1109.7.2.2 Required features. Hall call consoles shall include the features specified in this section. Consoles shall not be flush with the surrounding surfaces and shall protrude or be recessed a minimum of ¾ inch (19mm) and a maximum 4 inches (102 mm).

1109.7.2.2.1 Accessibility function button.  Hall call consoles shall provide accessibility function buttons complying with Section 1109.7.2.2.1.

1109.7.2.2.1.1 Upon Activation.  The accessibility function button shall be programed to activate the audio output required by Section 1109.7.2.2.2.

1109.7.2.2.1.2 Identification.  Accessibility function buttons shall be visibly and tactilely identified.  The visible identification shall consist of the International Symbol of Accessibility or the dynamic accessibility symbol and shall be a minimum height of 5/8 inch (16 mm). The visible symbol shall contrast with its background, light-on-dark or dark-on-light. The tactile identification shall consist of three raised dots. All dots shall be the same size and shall have a base diameter of 0.059 inch (1.5 mm) minimum and 0.063 inch (1.6 mm) maximum.  Dot height shall be 0.025 inch (0.6 mm) minimum and 0.037 inch (0.9 mm) maximum. The dots shall be spaced ¼ inch (6.4 mm) at base diameter,  measured center to center, and shall be arranged in the form of an equilateral triangle with the vertex pointing up.

1109.7.2.2.2 Audio output.  Audio output shall be provided for floor selection and responding elevator identification.  Audio output shall be initiated upon activation of the accessibility function button and shall comply with Sections 1109.7.2.2.2.1 and 1109.7.2.2.2.

1109.7.2.2.2.1 Content.  Audio output shall include all the information necessary to successfully call and locate the responding elevator without the use of a visual display including, but not limited to operating instructions, floor selection options, confirmation of floor selection, responding elevator car designation, directions to the responding elevator car and error messages.

1109.7.2.2.2.2 Delivery method and volume.  Audio output shall be provided through a mechanism that does not require the use of private listening devices, and that is located at the hall call console.  Audio output shall commence within one second of the activation of the accessibility function button.  Audio output shall be synthesized speech or, recorded or digitized human speech.  Volume shall be a minimum of 10 dBA above ambient sound level, measured during peak occupancy, but shall not exceed 80 dB, measured horizontally 36 inches (914 mm) from the source.  Audio output for floor selection shall commence at the hall call console used within one second of activation of the accessibility function button.  Audio output for responding car identification shall commence when the elevator arrives and shall be repeated until the elevator doors begin to close.

1109.7.2.2.3 Visible display screen. Visible display screens, including touchscreens, shall be provided in accordance with this section.

1109.7.2.2.3.1 Contrast. Characters, numbers and symbols shall contrast with the background on which they are displayed at a ratio of 4.5:1 (relative illuminance). The background shall be solid and static.

Exception:  Information unrelated to floor levels and their selection shall not be required to comply with Section 1109.7.2.2.3.1.

1109.7.2.2.3.2 Size. Characters, numbers and symbols shall be a minimum height of 5/8 inch (16 mm).

1109.7.2.2.3.3 Duration. Elevator assignment characters and numbers shall be displayed for a minimum of five seconds.

1109.7.2.2.4 Floor selection controls. Hall call consoles shall provide a method of floor selection that does not require user vision.  Input methods shall comply with Section 1109.7.2.2.4.1 or 1109.7.2.2.4.2.

1109.7.2.2.4.1 Numeric keypad.  Numeric keypads shall be a minimum of 2¾ inches (70 mm) wide by 5 inches (127 mm) high and shall be arranged in a 12-key ascending telephone keypad layout.  Individual keys shall be tactilely discernible, and the number five key shall be tactilely distinct from the other keys.  Where the keypad provides an alphabetic overlay on numeric keys, the relationships between letters and digits shall conform to ITU-T Recommendation E.161.

1109.7.2.2.4.2 Step scanner.  Step scanners shall consist of three horizontally arranged buttons.  The center button shall serve as the “select” button and may also serve as the accessibility function button.  The button to the right of the center button shall be the “up” button and the button to the left of the center button shall be the “down” button.  When the “up” and “down” buttons are pressed and released, the scanner shall announce the next floor above and below, respectively.  When the user releases the “up” or “down” button, the system shall pause to allow the user to press the “select” button.  If the “select” button is not chosen, the system shall resume at the next floor in the sequence when the button is again depressed.  In buildings with more than ten floor levels, when the “up” or “down” buttons are depressed and held for more than three seconds, the scanner shall present options for floor selection in groups of ten beginning with the next group of ten above or below the floor last announced.  An interval of silence, one second  minimum and two seconds maximum, shall be provided between such announcements.

Exception:  Step scanners may consist of one button, where the application for construction document approval is submitted within six months after the date of enactment of this section. The button shall serve as the “select” button and may also serve as the accessibility function button.

1109.7.2.2.5 Tactile discernibility.  Accessibility function buttons and floor selection controls shall be tactilely discernible and shall be raised above surrounding surfaces.  When pressed, buttons shall provide mechanical motion to indicate activation.  Where a step scanner complying with Section 1109.7.2.2.4.2 is provided, the “up” and “down” arrows shall include tactilely discernible “up” and “down” arrows.  The “up” and “down” arrows shall be tactilely distinct from the tactile marking on the accessibility function button.

1109.7.2.3 Hall call console arrangement.  Features of hall call consoles shall be arranged in accordance with Section 1109.7.2.3. Where an accessibility function button complying with Sections 1109.7.2.2.1 and 1109.7.2.3.1 also serves as the “select” button, the provisions of Section 1109.7.2.3.2 shall not apply.

1109.7.2.3.1 Accessibility function button.  The accessibility function button shall be located at a height of 36 inches (914 mm) minimum and a maximum of 42 inches (1067 mm)  above the finish floor and shall be nominally centered on the hall call console.

1109.7.2.3.2 Floor selection controls.  Floor selection controls shall be located above the accessibility function button and shall be no higher than 48 inches (1219 mm) above the finish floor and shall be nominally centered on the console.

1109.7.2.3.3 Display screens.  Where provided, display only screens shall be located above the floor selection controls.

1109.7.2.4 Instructions. Where hall call consoles are provided, written instructions on the proper use shall be posted in a conspicuous location, adjacent to such devices. The instructions shall include, but are not limited to, operating instructions, and console features.

1109.7.2.5 Responding car. When an elevator car responds to a call following activation of the accessibility function button, it shall provide audio output complying with Section 1109.7.2.2.2.  In addition, during travel, the responding car shall provide an in-car announcement of all floors on which it stops.

[1109.7] 1109.8 Lifts. Platform (wheelchair) lifts shall not be a part of a required accessible route in new construction except as indicated in Items 1 through [9] 10. Platform (wheelchair) lifts shall be installed in accordance with [Chapter 30 of this code,] Section 410 (Platform Lifts) of ICC A117.1, [and] ASME A18.1, and Chapter 30 of this code. Platform (wheelchair) lifts are permitted to be part of a required accessible route in new construction as follows:

1.	An accessible route to a performing area and speaker platforms [in Group A occupancies].

2.	An accessible route to wheelchair spaces required to comply with the wheelchair space dispersion requirements of Sections 1108.2.2 through 1108.2.6.

3.	An accessible route to spaces that are not open to the general public with an occupant load of not more than five.

4.	An accessible route [as permitted in Section 1107.2.5] within [a] an individual dwelling unit or sleeping unit required to be an Accessible unit, Type A unit or Type B unit.

5.	An interior accessible route to jury boxes and witness stands; raised courtroom stations including judges’ benches, clerks’ stations, bailiffs’ stations, deputy clerks’ stations and court reporters’ stations; and to depressed areas such as the well of the court.

6.	[An accessible route where existing exterior site constraints make use of a ramp or elevator infeasible as determined by the commissioner pursuant to the rules of the department.]

[7.	]	An accessible route to load and unload areas serving amusement rides.

[8.] 7.	An accessible route to play components or soft contained play structures.

[9.] 8.	An accessible route to team or player seating areas serving areas of sport activity.

9.	An accessible route instead of gangways serving recreational boating facilities and fishing piers and platforms.

10.	An accessible route where existing exterior site constraints make the use of a ramp or elevator infeasible as determined by the commissioner pursuant to the rules of the department.

1109.8.1 Prior code buildings. In prior code buildings, platform (wheelchair) lifts installed in accordance with Section 410 (Platform Lifts) of ICC A117.1, ASME A18.1, and Chapter 30 of this code, shall be permitted to be a part of the required accessible route.

[1109.8] 1109.9 Storage. Where fixed or built-in storage elements [such as] including but not limited to cabinets, coat hooks, shelves, medicine cabinets, lockers, closets[,] and drawers are provided in required accessible spaces, at least [one of each type shall contain storage space complying with ICC A117.1] 5 percent, but not less than one of each type shall be accessible.

[1109.8.1 Lockers. Where lockers are provided in accessible spaces, at least five percent, but not less than one, of each type shall be accessible.]

1109.9.1 Equity. Accessible facilities and spaces shall be provided with the same storage elements as provided in the similar nonaccessible facilities and spaces.

[1109.8.2] 1109.9.2 Shelving and display units. Self-service shelves and display units shall be located on an accessible route. Such shelving and display units shall not be required to comply with reach-range provisions.

[1109.8.3 Coat hooks and shelves. Where coat hooks and shelves are provided in toilet rooms or toilet compartments, or in dressing, fitting or locker rooms, at least one of each type shall be provided in accessible toilet rooms without toilet compartment, accessible toilet compartments, and accessible dressing, fitting and locker rooms.]

1109.9.3 Cycle storage. Cycle storage shall comply with Section 905 (Storage Facilities) of ICC A117.1 and Sections 1109.9.3.1 through 1109.9.3.4 of this code.

1109.9.3.1 Accessible cycle storage. Where cycle storage is provided, 10 percent of the total number, but not less than one, shall be a minimum of 86 inches (2184 mm) long and 42 inches (1067 mm) wide to accommodate the storage of an accessible cycle.

1109.9.3.2 Accessible route. At least one accessible route shall connect to the accessible cycle storage area.

1109.9.3.3 Turning space. A turning space shall be provided and comply with Section 304 (Turning Space) of ICC A117.1.

1109.9.3.4 Loading area. A clear floor space shall be located on the long side of the accessible cycle storage and shall comply with Section 305 (Clear Floor Space) of ICC A117.1.

[1109.9] 1109.10 Detectable warnings. Detectable warnings shall be provided where required in Sections [1109.9.1] 1109.10.1 through [1109.9.5] 1109.10.3.

[1109.9.1] 1109.10.1 Detectable warnings at passenger transit platforms. Passenger transit platform edges bordering a drop-off and not protected by platform screens or guards shall have a detectable warning.

Exception: Detectable warnings are not required at bus stops.

[1109.9.2 Detectable warnings at hazardous vehicular areas. If a walk crosses or adjoins a vehicular way, and the walking surfaces are not separated by curbs, railings, or other elements between the pedestrian areas and vehicular areas, the boundary between the areas shall be defined by a continuous detectable warning which is 36 inches (914 mm) wide.]

[1109.9.3] 1109.10.2 Detectable warnings at pools. The edges of reflecting pools and similar decorative pools without physical barriers, and in which occupants are not expected or permitted to engage in swimming, bathing, therapeutic or other physical activities, shall be provided with detectable warnings.

[1109.9.4] 1109.10.3 Detectable warnings at curb ramps. A curb ramp shall have a detectable warning. The detectable warning shall extend the full width and a depth of 24 inches (610 mm) along the curb ramp. The curb ramp shall comply with Section 406 of ICC A117.1.

[1109.9.5 Detectable warnings at other locations. Detectable warnings shall be located at hazardous locations on floors, doors, and stairs. Doors that lead to areas that might prove hazardous to a person who is blind, including, but not limited to, doors to leading platforms, boiler rooms, and stages, shall be made identifiable to the touch by a textured surface on the door handle, knob, pull or other operating hardware. This textured surface may be made by knurling or roughening or by material applied to the contact surface. Such textured surfaces shall not be provided for emergency exit doors or any doors other than those to hazardous areas.]

[1109.10] 1109.11 Seating at tables, counters and work surfaces. Where seating or standing space at fixed or built-in tables, counters or work surfaces is provided in accessible spaces, at least [5] 10 percent of the total number of seating and standing spaces, but not less than one of each type, shall be accessible. [In Group I-3 occupancy visiting areas at least 5 percent, but not less than one, cubicle or counter shall be accessible on both the visitor and detainee sides.]

[Exceptions] Exception:

[1.	]  Check-writing surfaces at check-out aisles not required to comply with Section [1109.11.2] 1109.12.2 are not required to be accessible.

[2.	In Group I-3 occupancies, the counter or cubicle on the detainee side is not required to be accessible at noncontact visiting areas or in areas not serving accessible holding cells or sleeping units.]

[1109.10.1] 1109.11.1 Dispersion. Accessible fixed or built-in seating at tables, counters or work surfaces shall be distributed throughout the space or facility containing such elements and located on a level accessed by an accessible route.

1109.11.2 Visiting areas. Visiting areas in judicial facilities and Group I-3 shall comply with Sections 1109.11.2.1 and 1109.11.2.2.

1109.11.2.1 Cubicles and counters. At least 5 percent, but not less than one of the cubicles, shall be accessible on both the visitor and detainee sides. Where counters are provided, at least one shall be accessible on both the visitor and detainee sides.

Exception: This requirement shall not apply to the detainee side of cubicles or counters at noncontact visiting areas not serving Accessible unit holding cells.

1109.11.2.2 Partitions. Where solid partitions or security glazing separate visitors from detainees, at least one of each type of cubicle or counter partition shall be accessible.

[1109.11] 1109.12 Service facilities.[Customer service] Service facilities shall provide for accessible features in accordance with Sections [1109.11.1] 1109.12.1 through [1109.11.5] 1109.12.5.

[1109.11.1] 1109.12.1 Dressing, fitting and locker rooms. Where dressing rooms, fitting rooms[,] or locker rooms are provided, at least [five] 5 percent, but not less than one, of each type of use in each cluster provided shall be accessible.

[1109.11.2] 1109.12.2 Check-out aisles. Where check-out aisles are provided, accessible check-out aisles shall be provided in accordance with Table [1109.11.2] 1109.12.2. [Where check-out aisles serve different functions, at least one accessible check-out aisle shall be provided for each function.] Where check-out aisles serve different functions, accessible check-out aisles shall be provided in accordance with Table [1109.11.2] 1109.12.2 for each function. Where check-out aisles are dispersed throughout the building or facility, accessible check-out aisles shall also be dispersed. Traffic control devices, security devices and turnstiles located in accessible check-out aisles or lanes shall be accessible.

Exception: Where the public use area is under 5,000 square feet (465 m2), not more than one accessible check-out aisle shall be required.

TABLE [1109.11.2] 1109.12.2
ACCESSIBLE CHECK-OUT AISLES

| TOTAL CHECK-OUT AISLES OF EACH FUNCTION | MINIMUM NUMBER OF ACCESSIBLE CHECK-OUT AISLES OF EACH FUNCTION |
| --- | --- |
| 1 to 4 | 1 |
| 5 to 8 | 2 |
| 9 to 15 | 3 |
| Over 15 | 3, plus 20% of additional aisles |

[1109.11.3] 1109.12.3 Point of [sales] sale and service counters. Where counters are provided for sales or distribution of goods or services, at least one of each type provided shall be accessible. Where such counters are dispersed throughout the building or facility, [the] accessible counters shall also be dispersed.

[1109.11.4] 1109.12.4 Food service lines. Food service lines shall be accessible. Where self-service shelves are provided, at least 50 percent, but not less than one, of each type provided shall be accessible.

[1109.11.5] 1109.12.5 Queue and waiting lines. Queue and waiting lines servicing accessible counters or check-out aisles shall be accessible.

[1109.12] 1109.13 Controls, operating mechanisms and hardware. Controls, operating mechanisms and hardware intended for operation by the occupant, including switches that control lighting and ventilation[,] and electrical convenience outlets, in accessible spaces, along accessible routes or as parts of accessible elements shall be accessible.

Exceptions:

1.	Operable parts that are intended for use only by [use only by] service or maintenance personnel shall not be required to be accessible.

2.	Electrical or communication receptacles serving a dedicated use shall not be required to be accessible.

3.	Where two or more outlets are provided in a kitchen above a length of countertop that is uninterrupted by a sink or appliance, one outlet shall not be required to be accessible.

4.	Floor electrical receptacles shall not be required to be accessible.

5.	HVAC diffusers shall not be required to be accessible.

6.	Except for light switches, where redundant controls are provided for a single element, one control in each space shall not be required to be accessible.

7.	Access doors or gates in barrier walls and fences protecting pools, spas and hot tubs shall be permitted to [have operable parts of the release of latch on self-latching devices at 54 inches (1370 mm) maximum and 48 inches (1219 mm) minimum above the finished floor or ground, provided the self-latching devices are not also self-locking devices, operated by means of a key, electronic opener, or integral combination lock] comply with Sections 3109.4 and 3109.5.

8.	Electrical panelboards in Type B+NYC units and Type B units shall not be required to be accessible.

9.	Within kitchens and bathrooms, lighting controls, electrical switches and receptacle outlets are permitted to be located over cabinets with counter tops 36 inches (914 mm) maximum in height and 25½ inches (648 mm) maximum in depth.

[1109.12.1] 1109.13.1 Operable windows. Where operable windows are provided in rooms or spaces that are required to be accessible in accordance with Sections 1107.5.1, 1107.5.2, 1107.5.3, 1107.5.4, 1107.6.1.1, [and] or 1107.6.1.4.1, at least one window in each room shall be accessible and each required operable window shall be accessible. Where operable windows are provided in Type B+NYC units in accordance with Section 1107.6.2, such windows shall comply with Section 1107.2.4.

Exception: Accessible windows are not required in bathrooms or kitchens unless otherwise required in Section 1107.2.4.

[1109.13] 1109.14 Fuel-dispensing systems. Fuel-dispensing systems shall [comply with ICC A117.1] be accessible.

[1109.14 Recreational and sports facilities. Recreational and sports facilities shall be accessible.]

[1109.14.1 Recreational and sports facilities exceptions. Recreational and sports facilities required to be accessible shall be exempt from this chapter to the extent specified in this section.]

[1109.14.1.1 Bowling lanes. An accessible route shall be provided to at least 5 percent, but no less than one, of each type of bowling lane.]

[1109.14.1.2 Court sports. In court sports, at least one accessible route shall directly connect both sides of the court.]

[1109.14.1.3 Raised boxing or wrestling rings. Raised boxing or wrestling rings are not required to be accessible.]

[1109.14.1.4 Raised refereeing, judging and scoring areas. Raised structures used solely for refereeing, judging or scoring a sport are not required to be accessible.]

[1109.14.1.5 Raised diving boards and diving platforms. Raised diving boards and diving platforms are not required to be accessible.]

1109.15 Gaming machines and gaming tables. Five percent, but not less than one, of each type of gaming table provided shall be accessible and provided with a front approach. Five percent of gaming machines provided shall be accessible and provided with a front approach. Accessible gaming machines shall be distributed throughout the different types of gaming machines provided.

[1109.15] 1109.16 Stairways. Stairways located alongside accessible routes connecting floor levels that are not connected by an elevator shall be designed and constructed to comply with ICC A117.1 and Chapter 10 of this code.

1109.17 Refuse disposal, refuse recyclable and refuse storage rooms. Refuse disposal, refuse recyclable and refuse storage rooms intended for common-use shall comply with this section. Each room must comply with Section 304 (Turning Space), Section 305 (Clear Floor Space), Section 309 (Operable Parts) and Section 404 (Doors and Doorways) of ICC A117.1. The room door is permitted to swing into the room provided that a clear floor space not less than 30 inches by 48 inches (762 mm by 1219 mm) is provided within the room and beyond the arc of the door swing.

Exceptions:

1.	An alternative design is permitted provided that all of the following conditions are met:

1.1.	The room shall be designed so that the wheelchair user can enter the room head on, and back out without turning or changing direction.

1.2.	An automatic door complying with Section 404.3 (Automatic Doors) of ICC A117.1 must be provided.

1.3.	The minimum doorway clear opening required by Section 404.3.1 must be increased to a minimum 36 inches (914 mm) in power-on and power-off mode.

1.4.	All controls, trash chutes, recycling bins and operating mechanisms intended for operation shall comply with Section 305 (Clear Floor Space) and Section 309 (Operable Parts) of ICC A117.1.

1.5.	An occupancy sensor shall be provided in the refuse room to detect the presence and the absence of occupants. Upon the detection of an occupant in the room, the door shall be maintained in the open position during the entire period of occupancy of the room. Upon the absence of an occupant in the room, the door shall automatically return to the closed position.

1.6.	The automatic door shall return to the closed position in the case of a power failure, upon the activation of the fire alarm systems or upon the activation of smoke detectors.

2.	Controls for maintenance and service are not required to comply with this section.

SECTION BC 1110
RECREATIONAL FACILITIES

1110.1 General. Recreational facilities shall be provided with accessible features in accordance with Sections 1110.2 through 1110.4.

1110.2 Facilities serving Group R-2 and R-3 occupancies. Recreational facilities that serve Group R-2 and R-3 occupancies shall comply with Sections 1110.2.1 through 1110.2.3, as applicable.

1110.2.1 Facilities serving Accessible units. In Group R-2 occupancies where recreational facilities serve Accessible units, every recreational facility of each type serving Accessible units shall be accessible.

1110.2.2 Facilities serving Type A, Type B+NYC and Type B units in a single building. In Group R-2 and R-3 occupancies and where there are four or more dwelling units, where common recreational facilities serve a single building containing Type A, Type B+NYC units or Type B units, 25 percent, but not less than one, of each type of recreational facility shall be accessible. Every recreational facility of each type on a site shall be considered to determine the total number of each type that is required to be accessible.

1110.2.3 Facilities serving Type A, Type B+NYC and Type B units in multiple buildings. In Group R-2 and R-3 occupancies, where there are four or more dwelling units within a single structure, on a single site where multiple buildings containing Type A, Type B+NYC units or Type B units are served by common recreational facilities, 25 percent, but not less than one, of each type of recreational facility serving each building shall be accessible. The total number of each type of recreational facility that is required to be accessible shall be determined by considering every recreational facility of each type serving each building on the site.

1110.3 Other occupancies. Recreational facilities not falling within the purview of Section 1110.2 shall be accessible.

1110.4 Recreational facilities. Recreational facilities shall be accessible and shall be on an accessible route to the extent specified in this section.

1110.4.1 Area of sport activity. Each area of sport activity shall be on an accessible route and shall not be required to be accessible except as provided for in Sections 1110.4.2 through 1110.4.14.

1110.4.2 Team or player seating. At least one wheelchair space shall be provided in team or player seating areas serving areas of sport activity.

Exception: Wheelchair spaces shall not be required in team or player seating areas serving bowling lanes that are not required to be accessible in accordance with Section 1110.4.3.

1110.4.3 Bowling lanes. An accessible route shall be provided to at least 5 percent, but not less than one, of each type of bowling lane.

1110.4.4 Court sports. In court sports, at least one accessible route shall directly connect both sides of the court.

1110.4.5 Raised boxing or wrestling rings. Raised boxing or wrestling rings are not required to be accessible or to be on an accessible route.

1110.4.6 Raised refereeing, judging and scoring areas. Raised structures used solely for refereeing, judging or scoring a sport are not required to be accessible or to be on an accessible route.

1110.4.7 Animal containment areas. Animal containment areas that are not within public use areas are not required to be accessible or to be on an accessible route.

1110.4.8 Amusement rides. Amusement rides that move persons through a fixed course within a defined area shall comply with Sections 1110.4.8.1 through 1110.4.8.3.

Exception: Mobile or portable amusement rides shall not be required to be accessible.

1110.4.8.1 Load and unload areas. Load and unload areas serving amusement rides shall be accessible and be on an accessible route. Where load and unload areas have more than one loading or unloading position, at least one loading and unloading position shall be on an accessible route.

1110.4.8.2 Wheelchair spaces, ride seats designed for transfer and transfer devices. Where amusement rides are in the load and unload position, the following shall be on an accessible route.

1.	The position serving a wheelchair space.

2.	Amusement ride seats designed for transfer.

3.	Transfer devices.

1110.4.8.3 Minimum number. Amusement rides shall provide at least one wheelchair space, amusement ride seat designed for transfer or transfer device.

Exceptions:

1.	Amusement rides that are controlled or operated by the rider are not required to comply with this section.

2.	Amusement rides designed primarily for children, where children are assisted on and off the ride by an adult, are not required to comply with this section.

3.	Amusement rides that do not provide seats that are built-in or mechanically fastened shall not be required to comply with this section.

1110.4.9 Recreational boating facilities. Boat slips required to be accessible by Sections 1110.4.9.1 and 1110.4.9.2 and boarding piers at boat launch ramps required to be accessible by Section 1110.4.9.3 shall be on an accessible route.

1110.4.9.1 Boat slips. Accessible boat slips shall be provided in accordance with Table 1110.4.9.1. All units on the site shall be combined to determine the number of accessible boat slips required. Where the number of boat slips is not identified, each 40 feet (12 m) of boat slip edge provided along the perimeter of the pier shall be counted as one boat slip for the purpose of this section.

Exception: Boat slips not designed for embarking or disembarking are not required to be accessible or be on an accessible route.

TABLE 1110.4.9.1
BOAT SLIPS

| TOTAL NUMBER OF BOAT SLIPS PROVIDED | MINIMUM NUMBER OF REQUIRED ACCESSIBLE BOAT SLIPS |
| --- | --- |
| 1 to 25 | 1 |
| 26 to 50 | 2 |
| 51 to 100 | 3 |
| 101 to 150 | 4 |
| 151 to 300 | 5 |
| 301 to 400 | 6 |
| 401 to 500 | 7 |
| 501 to 600 | 8 |
| 601 to 700 | 9 |
| 701 to 800 | 10 |
| 801 to 900 | 11 |
| 901 to 1000 | 12 |
| 1001 and over | 12, plus 1 for every 100, or fraction thereof, over 1,000 |

1110.4.9.2 Dispersion. Accessible boat slips shall be dispersed throughout the various types of boat slips provided. Where the minimum number of accessible boat slips has been met, no further dispersion shall be required.

1110.4.9.3 Boarding piers at boat launch ramps. Where boarding piers are provided at boat launch ramps, at least 5 percent, but not less than one, of the boarding piers shall be accessible.

1110.4.10 Exercise machines and equipment. At least one of each type of exercise machine and equipment shall be on an accessible route and shall be in compliance with Section 1104 (Exercise Machines and Equipment) of ICC A117.1.

1110.4.11 Fishing piers and platforms. Fishing piers and platforms shall be accessible and be located on an accessible route and shall be in compliance with Section 1105 (Fishing Piers and Platforms) of ICC A117.1.

1110.4.12 Miniature golf facilities. Miniature golf facilities shall be accessible and shall comply with Section 1107 (Miniature Golf Facilities) of ICC A117.1.

1110.4.13 Swimming pools, wading pools, hot tubs and spas. Swimming pools, wading pools, hot tubs and spas shall be accessible and be on an accessible route.

Exceptions:

1.	Catch pools or a designated section of a pool used as a terminus for a water slide flume shall not be required to provide an accessible means of entry, provided that a portion of the catch pool edge is on an accessible route.

2.	Where spas or hot tubs are provided in a cluster, at least 5 percent, but not less than one spa or hot tub in each cluster, shall be accessible and be on an accessible route.

3.	Swimming pools, wading pools, spas and hot tubs that are required to be accessible by Sections 1110.2.2 and 1110.2.3 are not required to provide accessible means of entry into the water.

1110.4.13.1 Raised diving boards and diving platforms. Raised diving boards and diving platforms are not required to be accessible or to be on an accessible route.

1110.4.13.2 Water slides. Water slides are not required to be accessible or to be on an accessible route.

1110.4.14 Shooting facilities with firing positions. Where shooting facilities with firing positions are designed and constructed at a site, at least 10 percent, but not less than one, of each type of firing position shall be accessible and be on an accessible route.

SECTION BC [1110] 1111
SIGNAGE

[1110.1] 1111.1 Signs. Required accessible elements shall be identified by the [International Symbol of Accessibility] dynamic accessibility symbol, in accordance with Figure 1111.1, at the following locations[:].

1.	Accessible parking spaces required by Section 1106.1 [except where].

Exception: Where the total number of parking spaces provided is [no more than] one, identification of the accessible parking space is not required.

2.	Accessible parking spaces required by Section 1106.2.

Exception: In Group I-1, R-2 and R-3 occupancies, where parking spaces are assigned to specific dwelling units or sleeping units, identification of accessible parking spaces is not required.

3.	Accessible passenger loading zones.

[3.	Accessible areas of rescue assistance required by Section 1007.6.]

4.	[Exterior areas of assisted rescue required by Section 1007.6.]

[5.	] Accessible rooms where multiple [single-user] single-occupant toilet rooms or bathing rooms are clustered at a single location pursuant to Section 1109.2, Exception 3.

[6.	Accessible rooms where] Where multiple single user portable toilet or bathing units are clustered at a single location pursuant to Section 1109.2, Exception [6] 8.

[7.] 5.	Accessible entrances where not all entrances are accessible. The sign, where provided, shall include a contact telephone number or instructions to gain access if an otherwise accessible building entrance is locked at all times or locked when the building is otherwise open.

[8.] 6.	Accessible check-out aisles where not all aisles are accessible. The sign, where provided, shall be above the check-out aisle in the same location as the check-out aisle number or type of check-out identification.

[9.] 7.	Family or assisted-use toilet and bathing rooms.

[10.] 8.	Accessible dressing, fitting and locker rooms where not all such rooms are accessible.

9.	Accessible areas of rescue assistance in accordance with Section 1009.9.

10.	Exterior areas for assisted rescue in accordance with Section 1009.9.

11.	In recreational facilities, lockers that are required to be accessible in accordance with Section 1109.9.

12.	Accessible seating.

[12.] 13.	Accessible portable toilets.

[13.] 14.	Public telephones.

15.	Refuse Disposal and Refuse Storage Rooms.

FIGURE 1111.1
DYNAMIC ACCESSIBILITY SYMBOL

[1110.2] 1111.2 Directional signage. Directional signage indicating the route to the nearest like accessible element shall be provided at or in close proximity to the following locations, such that [a person] an individual with disabilities will not be required to retrace the approach route from the inaccessible element.

1.	Inaccessible building entrances.

2.	Inaccessible public toilets and bathing facilities.

3.	Elevators not serving an accessible route.

4.	At each separate-sex toilet and bathing room indicating the location of the nearest accessible family or assisted-use toilet [or] and bathing room where provided in accordance with Section 1109.2.1.

5.	At exits and exit stairways serving an accessible space, but not providing an approved accessible means of egress, signage shall be provided in accordance with Section [1007.10] 1009.10.

6.	Where drinking fountains for people using wheelchairs and drinking fountains for standing persons are not located adjacent to each other, directional signage shall be provided indicating the location of the other drinking fountains.

These directional signs shall include the [International Symbol of Accessibility] dynamic accessibility symbol. Such signs shall comply with either [section] Section 703.2, or Sections 703.3 and 703.4 of ICC A117.1 [:].

[1110.3] 1111.3 Other signs. Signage indicating special accessibility provisions shall be provided as follows:

1.	Each assembly area required to comply with Section 1108.2.7 shall provide a sign notifying patrons of the availability of assistive listening systems. The sign shall comply with ICC A117.1 requirements for visual characters and shall include the International Symbol of Access for Hearing Loss.

Exception: Where ticket offices or windows are provided, signs are not required at each assembly area provided that signs are displayed at each ticket office or window informing patrons of the availability of assistive listening systems.

2.	At each door to an area of rescue assistance, an exterior area for assisted rescue, an egress stairway, exit passageway and exit discharge, signage shall be provided in accordance with Section [1011.3] 1013.4.

3.	At areas of rescue assistance, signage shall be provided in accordance with Section [1007.11] 1009.11.

4.	At exterior areas for assisted rescue, signage shall be provided in accordance with Section [1007.11] 1009.11.

5.	At two-way communication systems, signage shall be provided in accordance with Section [1007.8.2] 1009.8.2.

6.	[Within] In interior exit [enclosures,] stairways and ramps, floor level signage shall be provided in accordance with Section [1022.8] 1023.9.

7.	At prior code buildings with one or more inaccessible entrances, signage stating that a portable ramp is available, if provided by the building, shall be provided at each inaccessible building entrance and shall contain the phone number to request such ramp. The use of a portable ramp by any building must comply with all applicable laws and any such ramp shall comply with Section 405 (Ramps) of ICC A117.1, except to the extent the commissioner has waived a requirement pursuant to section 28-313.3.1. All signage posted pursuant to this section shall comply with Section 1110 and be maintained in good condition. Nothing in this section shall be construed to authorize the provision of a portable ramp where such provision would not otherwise be lawful.

8.	Signs identifying the type of access provided on amusement rides required to be accessible by Section 1110.4.8 shall be provided at entries to queues and waiting lines. In addition, where accessible unload areas also serve as accessible load areas, signs indicating the location of the accessible load and unload areas shall be provided at entries to queues and waiting lines. These directional sign characters shall meet the visual character requirements in accordance with Section 703.2 (Visual Characters) of ICC A117.1.

[1110.4] 1111.4 Variable message signs. Where provided in the locations in Sections [1110.4.1] 1111.4.1 and [1110.4.2] 1111.4.2, variable message signs [(VMS)] shall comply with the [VMS] variable message sign requirements of ICC A117.1.

[1110.4.1] 1111.4.1 Transportation facilities. Where provided in transportation facilities, variable message signs conveying transportation-related information shall comply with Section [1110.4] 1111.4.

[1110.4.2] 1111.4.2 Emergency shelters. Where provided in buildings that are designated as emergency shelters, variable message signs conveying emergency-related information shall comply with Section [1110.4] 1111.4.

Exception: Where equivalent information is provided in an audible manner, [VMS] variable message signs are not required to comply with ICC A117.1.

§ 13. Chapter 12 of the New York city building code, as added by local law number 33 for the year 2007, section 1213.2 as amended by local law number 8 for the year 2008, section 1213.1 as amended by local law number 60 for the year 2012, and sections 1202, 1203, 1205, 1206.4, 1207, 1210.1, 1210.2 and 1213.3 as amended by local law number 141 for the year 2013, is amended to read as follows:

CHAPTER 12
INTERIOR ENVIRONMENT

SECTION BC 1201
GENERAL

1201.1 Scope. The provisions of this chapter shall govern ventilation, temperature control, lighting, yards and courts, sound transmission, room dimensions, surrounding materials and rodent proofing associated with the interior spaces of buildings.

SECTION BC 1202
DEFINITIONS

1202.1 [General] Definitions. The following [words and] terms [shall, for the purposes of this chapter and as used elsewhere] are defined in [this code, have the meanings shown herein.] Chapter 2:

HABITABLE SPACE. [All rooms and spaces within a dwelling unit in Group R or I-1, including bedrooms, living rooms, studies, recreation rooms, kitchens, dining rooms and other similar spaces.]

[Exception: The following spaces within a dwelling unit shall not be considered habitable spaces:]

[1.	A dining space 55 square feet (5.1 m2) or less located off a living room, foyer or kitchen;]

[2.	A kitchenette;]

[3.	A bathroom or toilet room;]

[4.	A laundry room; and]

[5.	A corridor, passageway, or private hall; and a foyer used as an entrance hall in a dwelling unit: not exceeding 10 percent of the total floor area of the dwelling unit; or not exceeding 20 percent of the floor area of the dwelling unit where every habitable room is at least 20 percent larger than the required minimum room sizes established by the New York City Housing Maintenance Code.]

KITCHEN.[A room with 80 square feet (7.4 m2) or more of floor area which is intended, arranged, designed or used for cooking or warming of food.]

KITCHENETTE.[A space with less than 80 square feet (7.4 m2) of floor area which is intended, arranged, designed or used for cooking or warming of food.]

OCCUPIABLE SPACE.[A room or enclosed space, other than a habitable space, designed for human occupancy or use in which individuals may remain for a period of time for rest, amusement, treatment, education, dining, shopping, employment, labor or other similar purposes.]

SUNROOM.[A one-story structure attached to a building with a glazing area in excess of 40 percent of the gross area of the structure’s exterior walls and roof.]

THERMAL ISOLATION.[Physical and space conditioning separation from conditioned space(s). The conditioned space(s) shall be controlled as separate zones for heating and cooling or conditioned by separate equipment.]

SECTION BC 1203
VENTILATION

1203.1 General. Buildings shall be provided with [natural] ventilation in accordance with Section [1203.4,] 1203.5 of this code and [/or mechanical ventilation in accordance with] the New York City Mechanical Code [and this chapter. All habitable spaces shall be provided with natural ventilation in accordance with Section 1203.4].

1203.2 [Attic spaces] Ventilation required. Enclosed attics and enclosed rafter spaces formed where ceilings are applied directly to the underside of roof framing members shall have cross ventilation for each separate space by [ventilating] ventilation openings protected against the entrance of rain and snow. Blocking and bridging shall be arranged so as not to interfere with the movement of air. [A minimum] An airspace of not less than 1 inch (25 mm) [of airspace] shall be provided between the insulation and the roof sheathing. The net free ventilating area shall be not [be] less than 1/150 of the area of the space ventilated. [, with 50 percent of the required ventilating area provided by ventilators located in the upper portion of the space to be ventilated at least 3 feet (914 mm) above eave or cornice vents with the balance of the required ventilation provided by eave or cornice vents.] Ventilators shall be installed in accordance with the manufacturer’s instructions.

1203.2.1 Openings into attic.  Exterior openings into the attic space of any building intended for human occupancy shall be protected to prevent the entry of birds, squirrels, rodents, snakes and other similar creatures. Openings for ventilation having a least dimension of not less than 1/16 inch (1.6 mm) [minimum] and not more than ¼ inch (6.4 mm) [maximum] shall be permitted.[.] Openings for ventilation having a least dimension larger than ¼ inch (6.4 mm) shall be provided with corrosion-resistant wire cloth screening, hardware cloth, perforated vinyl or similar material with openings having a least dimension of not less than 1/16 inch (1.6 mm) [minimum] and not more than ¼ inch (6.4 mm) [maximum]. Where combustion air is obtained from an attic area, it shall be in accordance with Chapter 7 of the New York City Mechanical Code.

1203.3 Unvented attic and unvented enclosed rafter assemblies. Unvented attics and unvented enclosed roof framing assemblies created by ceilings applied directly to the underside of the roof framing members/rafters and the structural roof sheathing at the top of the roof framing members shall be permitted where all the following conditions are met:

1.	The unvented attic space is completely within the building thermal envelope.

2.	No interior Class I vapor retarders are installed on the ceiling side (attic floor) of the unvented attic assembly or on the ceiling side of the unvented enclosed roof framing assembly.

3.	Where wood shingles or shakes are used, a minimum ¼-inch (6.4 mm) vented airspace separates the shingles or shakes and the roofing underlayment above the structural sheathing.

4.	Insulation shall be located in accordance with the following:

4.1.	Item 4.1.1, 4.1.2, 4.1.3 or 4.1.4 shall be met, depending on the air permeability of the insulation directly under the structural roof sheathing.

4.1.1.	Where only air-impermeable insulation is provided, it shall be applied in direct contact with the underside of the structural roof sheathing.

4.1.2.	Where air-permeable insulation is provided inside the building thermal envelope, it shall be installed in accordance with Item 4.1. In addition to the air-permeable insulation installed directly below the structural sheathing, rigid board or sheet insulation shall be installed directly above the structural roof sheathing in accordance with the R values in Table 1203.3 for condensation control.

4.1.3.	Where both air-impermeable and air-permeable insulation are provided, the air-impermeable insulation shall be applied in direct contact with the underside of the structural roof sheathing in accordance with Item 4.1.1 and shall be in accordance with the R values in Table 1203.3 for condensation control. The air-permeable insulation shall be installed directly under the air-impermeable insulation.

4.1.4.	Alternatively, sufficient rigid board or sheet insulation shall be installed directly above the structural roof sheathing to maintain the monthly average temperature of the underside of the structural roof sheathing above 45°F (7°C). For calculation purposes, an interior air temperature of 68°F (20°C) is assumed and the exterior air temperature is assumed to be the monthly average outside air temperature of the three coldest months.

4.2.	Where preformed insulation board is used as the air-permeable insulation layer, it shall be sealed at the perimeter of each individual sheet interior surface to form a continuous layer.

Exception: Section 1203.3 does not apply to special use structures or enclosures such as swimming pool enclosures, data processing centers, hospitals or art galleries.

#### TABLE 1203.3
INSULATION FOR CONDENSATION CONTROL

| CLIMATE ZONE | MINIMUM R-VALUE OF AIR-IMPERMEABLE INSULATIONa |
| --- | --- |
| 2B and 3B tile roof only | 0 (none required) |
| 1, 2A, 2B, 3A, 3B, 3C | R-5 |
| 4C | R-10 |
| 4A, 4B | R-15 |
| 5 | R-20 |
| 6 | R-25 |
| 7 | R-30 |
| 8 | R-35 |

a.	Contributes to, but does not supersede, thermal resistance requirements for attic and roof assemblies in the New York City Energy Conservation Code.

1203.4 Under-floor ventilation.  The space between the bottom of the floor joists and the surface under any building except spaces occupied by basements or cellars shall be provided with ventilation openings through foundation walls or exterior walls. Such openings shall be placed so as to provide cross ventilation of the under-floor space.

[1203.3.1] 1203.4.1 Openings for under-floor ventilation. The [minimum] net area of ventilation openings shall be not [be] less than 1 square foot for each 150 square feet ([0.09] 0.67 m2 for each [13.9] 100 m2) of [crawl-space] crawl space area. Ventilation openings shall be covered for their height and width with any of the following materials, provided that the least dimension of the covering shall [not exceed] be not greater than ¼ inch (6.4 mm):

1.	Perforated sheet metal plates not less than 0.070 inch (1.8 mm) thick.

2.	Expanded sheet metal plates not less than 0.047 inch (1.2 mm) thick.

3.	Cast-iron grilles or gratings.

4.	Extruded load-bearing vents.

5.	Hardware cloth of 0.035 inch (0.89 mm) wire or heavier.

6.	Corrosion-resistant wire mesh, with the least dimension not [exceeding] greater than ⅛ inch (3.2 mm).

[1203.3.2] 1203.4.2 Exceptions.  The following are exceptions to Sections [1203.3] 1203.4 and [1203.3.1] 1203.4.1:

1.	Where warranted by climatic conditions, ventilation openings to the outdoors are not required if ventilation openings to the interior are provided.

2.	The total area of ventilation openings is permitted to be reduced to 1/1,500 of the under-floor area where the ground surface is covered with a Class I vapor retarder material and the required openings are placed so as to provide cross ventilation of the space. The installation of operable louvers, in accordance with Section [1203.3.1] 1203.4.1, shall not be prohibited.

3.	Ventilation openings are not required where continuously operated mechanical ventilation is provided at a rate of 1.0 cubic foot per minute (cfm) for each 50 square feet (1.02 L/s for each 10 m2) of crawl space floor area and the ground surface is covered with a Class I vapor retarder.

4.	Ventilation openings are not required [when] where the ground surface is covered with a Class I vapor retarder, the perimeter walls are insulated and the space is conditioned in accordance with the New York City Energy Conservation Code.

5.	[For buildings in areas of special flood hazard, the openings] Openings for under-floor ventilation for buildings in flood hazard areas shall also comply with the additional requirements of Appendix G.

[1203.4] 1203.5 Natural ventilation.  Natural ventilation of occupiable and habitable space shall be through openings to the outdoors. The openings shall be of a type permitted under Sections [1203.4.1.1] 1203.5.1.1, [1203.4.1.2] 1203.5.1.2, [1203.4.1.3] 1203.5.1.3 and [1203.4.1.4] 1203.5.1.4. The operating mechanism for such openings shall be provided with ready access so that the openings are readily controllable by the building occupants.

Exception: An opening providing the required dimensional operable area shall be permitted to be reduced by limiting devices in accordance with the New York City Health Code, provided that the owner shall remove such limiting devices where requested by the occupant. In such cases, where required by the New York City Health Code, alternative means of compliance shall be provided in accordance with the New York City Health Code.

[1203.4.1] 1203.5.1 Ventilation area required. Ventilation areas shall be as set forth in Sections [1203.4.1.1] 1203.5.1.1 through [1203.4.1.4] 1203.5.1.4.

[1203.4.1.1] 1203.5.1.1 Occupiable spaces. Where occupiable spaces are not required to be provided with mechanical ventilation in accordance with the New York City Mechanical Code, natural ventilation shall be provided in accordance with Section [1203.4.1.1] 1203.5.1.1. Openings providing required natural ventilation to occupiable spaces shall be windows, doors, louvers, skylights or other similar ventilating openings.

Exceptions:

1.	Bathrooms and toilet rooms in Group R or I-1 occupancies shall comply with Section [1203.4.1.3] 1203.5.1.3.

2.	Kitchenettes in Group R or I-1 occupancies shall comply with Section [1203.4.1.4] 1203.5.1.4.

[1203.4.1.1.1] 1203.5.1.1.1 Minimum opening. The minimum openable area to the outdoors shall be 4 percent of the floor area of the occupiable space being ventilated.

[1203.4.1.1.2] 1203.5.1.1.2 Adjoining spaces. Where occupiable rooms and spaces without openings to the outdoors are ventilated through an adjoining room, the opening to the adjoining room shall be unobstructed and shall have an area of not less than 8 percent of the floor area of the interior room or space, but not less than 25 square feet (2.3 m2). The [minimum] openable area of the openings to the outdoors shall be based on the total floor area being ventilated.

Exception: Exterior openings required for ventilation shall be permitted to open into a sunroom or covered patio provided that the openable area between such sunroom addition or covered patio and the interior room shall have an area of not less than 8 percent of the floor area of the interior room or space, but not less than 20 square feet (1.9 m2). The [minimum] openable area of the openings to the outdoors shall be based on the total floor area being ventilated.

[1203.4.1.1.3] 1203.5.1.1.3 Openings below grade.  Where openings below grade provide required natural ventilation, the outside horizontal clear space measured perpendicular to the opening shall be one and one-half times the depth of the opening. The depth of the opening shall be measured from the average adjoining ground level to the bottom of the opening.

[1203.4.1.1.4] 1203.5.1.1.4 Mezzanines. Where an interior balcony or mezzanine opens to form part of another room or space, its area shall be added to the area of the room or space in which it is located to compute the ventilation required for both spaces.

[1203.4.1.2] 1203.5.1.2 Habitable spaces. All habitable spaces shall be provided with natural ventilation in accordance with [Section 1203.4.1.2] this section. Openings providing required natural ventilation to habitable spaces shall be windows and/or glazed doors to the outdoors.

Exception: Group R-3 occupancies. Openable skylights opening directly to the outer air, transparent or translucent panels, or other natural light-transmitting media may be substituted for window openings in Group R-3 occupancies provided that they meet the minimum dimensional requirements of Section [1203.4.1.2.1] 1203.5.1.2.1.

[1203.4.1.2.1] 1203.5.1.2.1 Minimum opening. The minimum openable area to the outdoors shall be 5 percent of the floor area of the habitable space being ventilated.  Every opening providing required natural ventilation shall be at least 12 square feet (1.1 m2) of glazed area, providing a minimum of 6 square feet (0.56 m2) of openable area.

Exceptions:

1.	Where fresh air is furnished in any habitable room or space by mechanical means supplying a minimum of 40 cubic feet per minute (0.02 m3/s), the free openable area of the openings may be reduced to 2½ percent of the floor area but each such opening shall provide not less than 5½ square feet (0.51 m2) of openable area.

2.	The minimum free openable area of a mullioned casement window shall be 5½ square feet (0.51 m2), provided that the minimum ratio of floor area to openable area is met.

[1203.4.1.2.2] 1203.5.1.2.2 Adjoining spaces. An alcove or room opening off another room or space shall be considered as a separate room in determining its requirements for ventilation.

Exceptions:

1.	Alcoves within Group R-3 dwelling units. In Group R-3 occupancies, where an opening between the alcove and the room or space is at least 80 percent of the area of the common wall and the floor area of the alcove does not exceed twice the area of the opening, the alcove and the room opening into the alcove may be considered as a single space.

2.	Balconies, partially enclosed. Exterior openings required for ventilation shall be permitted to open upon a partially enclosed balcony or space above a setback when:

2.1.	Such balcony or space faces upon a public street, space, alley, park, highway, or right of way; or upon a yard, court, plaza, or space above a setback where such yard, court, plaza, or space above a setback complies with Section 1206;

2.2.	The maximum depth of any habitable room is 30 feet (9144 mm) measured from the outer face of the exterior wall forming the partial or full enclosure of the balcony or space;

2.3.	The enclosure of the balcony or space is not more than one story in height; and

2.4.	The front of a partially enclosed balcony or space above a setback shall be open to the outer air with an open area equal to at least 75 percent of the floor surface area of such balcony or space.

3.	Balconies, fully enclosed. Exterior openings required for ventilation shall be permitted to open upon a fully enclosed balcony or space above a setback, including sunroom and patio covers, when:

3.1.	Such balcony or space faces upon a public street, space, alley, park, highway, or right of way; or upon a yard, court, plaza, or space above a setback where such yard, court, plaza, or space above a setback complies with Section 1206;

3.2.	The maximum depth of any habitable room is 30 feet (9144 mm) measured from the outer face of the exterior wall forming the partial or full enclosure of the balcony or space;

3.3.	The enclosure of the balcony or space is not more than one story in height;

3.4.	The building is of Type I or II construction;

3.5.	The outer enclosing walls of the balcony or space are glazed with an area at least 50 percent of the area of the interior enclosing walls of such balcony or space; the glazing may be clear plate glass or slow burning plastic;

3.6.	At least 50 percent of the glazed area required by Exception 3.5 of this section is openable; and

3.7.	No window from any bathroom, toilet room, kitchen or kitchenette shall open on such balcony or space.

4.	Mezzanines and split-level rooms. Where a habitable mezzanine or portion of a split-level room or space is not directly served by an opening providing natural ventilation in accordance with Section [1203.4.1.2] 1203.5.1.2, such mezzanine or space shall open for its full width with no obstruction, except for railings, to an adjoining habitable room which is provided with natural ventilation. The floor area of such mezzanine or portion of the split-level room or space shall be added to the floor area of the adjoining room to compute the required ventilation in accordance with Section [1203.4.1.2.1] 1203.5.1.2.1. The combined space shall also comply with Section [1203.4.1.2.4] 1203.5.1.2.4. When required natural ventilation is not provided, mechanical ventilation shall be provided to the mezzanine and split-level rooms in accordance with the New York City Mechanical Code capable of providing 2 cubic feet per minute (0.00094 m3/s) of fresh air per square foot (0.09 m2) of floor area of mezzanine.

[1203.4.1.2.3] 1203.5.1.2.3 Basements and cellars. Where openings provide natural ventilation to habitable spaces located in basements or cellars, such opening shall also comply with the applicable provisions of Sections 27-2081 through 27-2087 of the New York City Housing Maintenance Code and Sections 26(8) and 34 of the New York State Multiple Dwelling Law.

[1203.4.1.2.4] 1203.5.1.2.4 Maximum depth of room. No part of any room shall be more than 30 feet (9144 mm) from a window opening onto a street or yard unless such room also opens onto a court complying with Section 1206.

Exception: In dwelling units containing more than three habitable rooms in Group R-1 or R-2 occupancies in buildings of Type I or II construction, rooms may be greater than 30 feet (9144 mm) in depth provided that all other requirements of Section [1203.4.1.2] 1203.5.1.2 are met and that the required windows are so located as to properly light all portions of the room in accordance with Section 1205.

[1203.4.1.3] 1203.5.1.3 Bathrooms and toilet rooms in Group R and I-1 occupancies. Bathrooms [or] and toilet rooms in Group R or I-1 occupancies shall be provided with natural ventilation in accordance with Section [1203.4.1.3] 1203.5.1.3, unless provided with [exhaust] ventilation in accordance with the New York City Mechanical Code. Openings providing required natural ventilation shall be windows.

Exception: Openable skylights may be substituted for windows provided that the bathroom or toilet room is on the top story.

[1203.4.1.3.1] 1203.5.1.3.1 Minimum opening. The minimum openable area to the outdoors shall be 5 percent of the floor area of the space being ventilated. Every window or skylight providing required natural ventilation shall be at least 3 square feet (0.28 m2) providing a minimum of 1½ square feet (0.14 m2) of openable area.

[1203.4.1.3.2] 1203.5.1.3.2 Adjoining spaces. Natural ventilation for bathrooms and toilet rooms may not be through openings from another room or space.

Exception: A bathroom or toilet room may open onto a partially enclosed balcony or space above a setback conforming with Exception 2 of Section [1203.4.1.2.2] 1203.5.1.2.2.

[1203.4.1.3.3] 1203.5.1.3.3 Basements and cellars. Where openings provide natural ventilation to bathrooms or toilet rooms located in basements or cellars, such opening shall also comply with the applicable provisions of Sections 27-2081 through 27-2087 of the New York City Housing Maintenance Code and Sections 26(8) and 34 of the New York State Multiple Dwelling Law.

[1203.4.1.4] 1203.5.1.4 Kitchenettes in Group R and I-1 occupancies. Kitchenettes in Group R or I-1 occupancies shall be provided with natural ventilation in accordance with Section [1203.4.1.4] 1203.5.1.4, unless provided with [exhaust] ventilation in accordance with the New York City Mechanical Code. Openings providing required natural ventilation shall be windows.

Exception: Openable skylights may be substituted for windows provided that:

1.	The kitchenette is on the top story;

2.	The skylight is 12 inches (305 mm) in its least dimensions;

3.	The skylight is at least 4 square feet (0.37 m2) or one-eighth of the area of the kitchenette, whichever is greater; and

4.	The skylight provides ventilating openings for at least one-half of its area.

[1203.4.1.4.1] 1203.5.1.4.1 Minimum opening. The minimum openable area to the outdoors shall be 5 percent of the floor area of the space being ventilated. Every window or other opening providing required natural ventilation shall be at least 1 foot (305 mm) wide and at least 3 square feet (0.28 m2) in total area, providing a minimum of 1½ square feet (0.14 m2) of openable area.

Exception: Skylights shall comply with the exception of Section [1203.4.1.4] 1203.5.1.4.

[1203.4.1.4.2] 1203.5.1.4.2 Adjoining spaces. Natural ventilation for kitchenettes shall not be through openings off another room or space.

Exception: A kitchenette may open onto a partially enclosed balcony or space above a setback conforming with Exception 2 of Section [1203.4.1.2.2] 1203.5.1.2.2.

[1203.4.1.4.3] 1203.5.1.4.3 Basements and cellars. Where openings provide natural ventilation to kitchenettes less than 80 square feet (7.4 m2) located in basements or cellars, such opening shall also comply with the applicable provisions of Sections 27-2081 through 27-2087 of the New York City Housing Maintenance Code and Sections 26(8) and 34 of the New York State Multiple Dwelling Law.

[1203.4.2] 1203.5.2 Contaminants exhausted. Contaminant sources in naturally ventilated spaces, including kitchens, kitchenettes, toilet rooms and bathing rooms, shall be [removed] exhausted in accordance with the New York City Mechanical Code.

[1203.4.2.1] 1203.5.2.1 Bathrooms. Rooms containing bathtubs, showers, spas and similar bathing fixtures in other than Group R and I-1 occupancies shall be mechanically ventilated in accordance with the New York City Mechanical Code, whether or not they are also provided with natural ventilation.

[1203.4.3] 1203.5.3 Openings on yards or courts. Natural ventilation shall be provided by openings to a public street, space, alley, park, highway, or right-of-way; or upon a yard, court, plaza, or space above a setback where such yard, court, plaza, or space above a setback complies with Section 1206. No such opening shall be on a recess of less than 6 feet (1829 mm) in width.

Exceptions:

1.	Openings providing natural ventilation to habitable spaces located in basements or cellars shall also comply with the applicable provisions of Sections 27-2081 through 27-2087 of the New York City Housing Maintenance Code and Sections 26(8) and 34 of the New York State Multiple Dwelling Law.

2.	A kitchenette, a bathroom, or a water closet compartment may be located on a recess of less than 6 feet (1829 mm) in width.

[1203.4.4] 1203.5.4 Measurement of openings. Dimensions of windows and other openings shall always be taken between stop beads or, if there are no stop beads, between the sides, head, and sill of the sash opening.

[1203.5.] 1203.6 Other ventilation and exhaust systems.  Ventilation and exhaust systems for occupancies and operations involving flammable or combustible hazards or other contaminant sources as covered in the New York City Mechanical Code or the New York City Fire Code shall be provided as required by both codes.

SECTION BC 1204
TEMPERATURE AND HUMIDITY CONTROL

1204.1 Equipment and systems.  Interior spaces intended for human occupancy shall be provided with active or passive [space-heating] space heating systems capable of maintaining [a minimum] an indoor temperature as indicated in Table 1204.1 at a point 3 feet (914 mm) above the finished floor. The heating capacity of heat-producing devices and equipment which are contained in the room and in constant use during occupancy may be deducted from the capacity of the heating system. Portable heating systems shall not be considered as contributing to the capacity of the heating system.

Exception: Where specific rooms or spaces are not listed, the temperature shall be determined by the requirements of the listed space to which they most nearly conform or as determined by the registered design professional.

TABLE 1204.1
MINIMUM SPACE TEMPERATURE REQUIREMENTSa

| ROOMS OR SPACES |  | MINIMUM TEMPERATURE [(F)] (°F) |
| --- | --- | --- |
| Habitable rooms in all buildings |  | 68 |
| Building equipment and machinery rooms |  | 50 |
| Patients’ rooms, bathrooms and toilet rooms, stairs and corridors in hospitals and nursing homes | As per the New York State Health Code |
| Bathrooms and toilet rooms except patients’ bathrooms and toilet rooms in hospitals and nursing homes |  | 68 |
| Offices, waiting rooms, art galleries, museums, libraries, meeting rooms, houses of worship, classrooms, auditoriums, lecture halls, nightclubs, restaurants, theatres, locker rooms, dressing rooms, and spaces where persons are engaged in sedentary activities |  | 68 |
| Laboratories, light machine work, product inspections, loft buildings, shops, stores, display rooms, show rooms, sales rooms, and spaces where persons are engaged in moderate physical activities |  | 65 |
| Gymnasia, dance halls, skating rinks, bowling alleys, heavy assembly workrooms or shops, and spaces where persons are engaged in vigorous physical activities |  | 60 |
| Automotive repair shops |  | 50 |
| Storage areas, garages, space where work or process requires a low temperature |  | None |
| Hospital operating rooms, and recovery, labor, delivery, and nursery rooms | As per the New York State Health Code |
| Swimming pools, bath houses, and shower rooms |  | 75 |

a.	Temperatures listed here are the minimum requirements of the department. However, other jurisdictional authorities may have more stringent requirements.

Exceptions:

1.	Heating systems are not required when occupancy is seasonal and the rooms or buildings are not occupied between November 1st and May 1st of the following year.

2.	Heating systems are not required when the processes or activities normally conducted in the space will generate sufficient heat to maintain the prescribed temperatures during the time of occupancy.

3.	Spaces where strict process requirements mandate temperatures other than those cited above shall be exempt from the minimum requirements listed in Table 1204.1.

1204.2 Air conditioning. Interior spaces intended for human occupancy that are provided with air conditioning shall be provided with active or passive systems that are capable of maintaining 78°F (26°C) at 50-percent relative humidity when the outdoor air temperature is 89°F (32°C) and the coincident wet bulb temperature is 73°F (23°C). Interior spaces without air conditioning shall be provided with mechanical or natural ventilation in compliance with other subsections of this code.

1204.3 Freeze protection. All interior spaces shall be provided with active or passive systems or with methods of construction capable of preventing wet piping systems and vessels from freezing at all times, including permanently installed pipe heat tracing systems.

1204.4 System design. The heating system and air-conditioning system, as applicable, shall be designed to provide sufficient capacity to meet the temperature and humidity requirements of Section 1204 when considering the outdoor air ventilation requirements and all losses in the system and ancillary uses, such as domestic hot water, for which the system is used. The system shall be designed and installed to meet all other applicable provisions of this code.

SECTION BC 1205
LIGHTING

1205.1 General.  Every room and space in every building shall be provided with artificial light in accordance with Section 1205.3. Every habitable room and space shall also be provided with natural light by means of exterior glazed openings in accordance with Section 1205.2.

Exceptions: Artificial light need not be provided in rooms or spaces:

1.	Occupied exclusively during the daylight hours between 1 hour after sunrise and 1 hour before sunset, and which are provided with natural light meeting the requirements of Section 1205.2; or

2.	With less than 40 square feet (3.7 m2) of floor area if they are used exclusively for storage purposes or for mechanical facilities containing no rotating or moving parts, no combustion equipment, or no other hazardous equipment.

1205.2 Natural light.  Every opening providing required natural light shall be so located so as to properly light all portions of the room. Openings providing required natural light shall be windows [and/] or glazed doors.

Exception: Group R-3 occupancies. Skylights, opening directly to the outer air, transparent or translucent panels, or other light-transmitting media, may be substituted for window openings in Group R-3 occupancies provided that they meet the minimum dimensional requirements of Section [1205.2.2] 1205.2.1.

1205.2.1 Minimum opening. The minimum net glazed area shall [not] be not less than 10 percent of the floor area of the room served. Every opening providing required natural light shall be at least 12 square feet (1.1 m2) of glazed area.

Exception: For Group R-3 occupancies, the net glazed area shall be not less than 10 percent of the floor area of the room served, or 12 square feet (1.1 m2), whichever is greater.

1205.2.2 Adjoining spaces. An alcove or room opening off another room or space shall be considered as a separate room in determining its requirements for natural lighting.

Exceptions:

1.	Alcoves within Group R-3 dwelling units. In Group R-3 occupancies, where an opening between the alcove and the room or space is at least 80 percent of the area of the common wall and the floor area of the alcove does not exceed twice the area of the opening, the alcove and the room opening into the alcove may be considered as a single space.

2.	Balconies, partially enclosed. Exterior openings required for natural light shall be permitted to open upon a partially enclosed balcony or space above a setback when:

2.1.	Such balcony or space faces upon a public street, space, alley, park, highway, or right of way; or upon a yard, court, plaza, or space above a setback where such yard, court, plaza, or space above a setback complies with Section 1206;

2.2.	The maximum depth of any habitable room is 30 feet (9144 mm) measured from the outer face of the exterior wall forming the partial or full enclosure of the balcony or space;

2.3.	The enclosure of the balcony or space is not more than one story in height; and

2.4.	The front of a partially enclosed balcony or space above a setback shall be open to the outer air with an open area equal to at least 75 percent of the floor surface area of such balcony or space.

3.	Balconies, fully enclosed. Exterior openings required for natural lighting shall be permitted to open upon a fully enclosed balcony or space above a setback, including thermally isolated sunroom additions and covered patios, when:

3.1.	Such balcony or space faces upon a public street, space, alley, park, highway, or right of way; or upon a yard, court, plaza, or space above a setback where such yard, court, plaza, or space above a setback complies with Section 1206;

3.2.	The maximum depth of any habitable room is 30 feet (9144 mm) measured from the outer face of the wall forming the partial or full enclosure of the balcony or space;

3.3.	The enclosure of the balcony or space is not more than one story in height;

3.4.	The building is of Type I or II construction;

3.5.	The outer enclosing walls of the balcony or space are glazed with an area at least 50 percent of the area of the interior enclosing walls of such balcony or space; the glazing may be clear plate glass or slow burning plastic;

3.6.	At least 50 percent of the glazed area required by Exception 3.5 of this section is openable; and

3.7.	No window from any bathroom, toilet room, kitchen or kitchenette shall open on such balcony or space.

4.	Mezzanines and split-level rooms. Where a habitable mezzanine or portion of a split-level room or space is not directly served by an opening providing natural lighting in accordance with Section 1205.2, such space shall be open for its full width with no obstruction, except for railings, to an adjoining habitable room which is provided with such window or other opening. The floor area of the mezzanine or portion of the split level room or space shall be added to the floor area of the adjoining room to compute the required lighting in accordance with Section 1205.2.1. The combined space shall also comply with Sections 1205.2.4 and 1205.2.7.

1205.2.3 Basements and cellars. Where openings provide natural light to habitable spaces located in basements or cellars, such openings shall comply with Sections 1205.2.3.1 through 1205.2.3.2.

1205.2.3.1 Adequate adjacent space for multiple dwellings. Where rooms within a dwelling unit in a multiple dwelling are located in a cellar or a basement, such rooms shall have at least one-half of their height and all of their required window surfaces above every part of an “adequate adjacent space.” Such “adequate adjacent space” shall be open to the sky and shall be a continuous surface area not less than 30 feet (9144 mm) in its least dimension abutting at same level or directly below the exterior walls of every part of the basement and cellar portions of such dwelling unit. Such “adequate adjacent space” shall be spaces that are located on the same tax lot or plot in compliance with Section 1206.1 as the building or a public street, space, alley, park, highway or right of way and the level of such areas which abut or adjoin the habitable room shall be at least 6 inches (152 mm) below the window sills of any windows.

1205.2.3.2 Other applicable laws. Where openings provide natural lighting to habitable spaces located in basements or cellars, such opening shall comply with the applicable provisions of Sections 27-2081 through 27-2087 of the New York City Housing Maintenance Code and Sections 26(8) and 34 of the New York State Multiple Dwelling Law.

1205.2.4 Maximum depth of room. No part of any room shall be more than 30 feet (9144 mm) from a window opening on a street or yard unless such room also opens onto a legal court in compliance with Section 1206.1.

Exception: In dwelling units containing more than three habitable rooms in Group R- 1 or R-2 occupancies in buildings of Type I or II construction, rooms may be greater than 30 feet (9144 mm) in depth provided that all other requirements of Section 1205.2 are met and that the required windows are located so as to properly light all portions of the room.

1205.2.5 Openings on yards or courts. Exterior glazed openings shall open directly onto a public street, space, alley, park, highway, or right-of-way; or upon a yard, court, plaza, or space above a setback where such yard, court, plaza, or space above a setback complies with Section 1206. No such opening shall be on a recess of less than 6 feet (1829 mm) in width.

Exception: Spaces located in basements or cellars shall also comply with Section 1205.2.3.

1205.2.6 Measurement of glazed areas. Dimensions of windows and other glazed areas shall always be taken between stop beads or, if there are no stop beads, between the sides, head, and sill.

1205.2.7 Height of glazed areas. Height of glazed areas on openings providing natural light shall comply with Sections 1205.2.7.1 and 1205.2.7.2.

1205.2.7.1 Only that portion of glazed areas higher than 30 inches (9144 mm) above the floor shall be considered as providing the required natural lighting.

1205.2.7.2 The top of at least one window or other opening providing required natural lighting to a habitable room shall be a minimum of 7 feet (2134 mm) above the floor of the room or space served by the window or opening.

Exception: Mezzanines. Where the required natural lighting for a habitable mezzanine level is provided by a window(s) on the lower level in accordance with Section 1205.2.2, Exception 4, and where compliance with Section 1205.2.7.2 is not feasible on the mezzanine floor, Section 1205.2.7.2 shall not apply to such mezzanine floor provided that such window(s) is on the opposite wall from the mezzanine, and the top of such window is at least 12 inches (305 mm) above the floor of the mezzanine.

1205.3 Artificial light. Artificial light shall be provided in accordance with Sections 1205.3.1 through 1205.3.5.

1205.3.1 General. Artificial light shall meet the minimum illumination standards set forth in Section 1205.3. Artificial light shall not exceed maximum energy consumption requirements, if applicable, as required by the New York City Energy Conservation Code.

1205.3.2 Rooms and spaces. Artificial light shall be adequate to provide an average illumination of 10 [foot-candles] footcandles (107 lux) over the area of the room at a height of 30 inches (762 mm) above the floor level.

1205.3.3 Stairways. Stairways within dwelling units and exterior stairways serving a dwelling unit shall have an illumination level on tread runs of not less than 1 [foot-candle] footcandle (11 lux). Stairs in other occupancies shall be governed by Chapter 10.

1205.3.4 Means of egress. The means of egress shall be illuminated in accordance with Section [1006.1] 1008. Exterior lights near entranceways to multiple dwellings shall also comply with Section 27-2040 of the New York City Housing Maintenance Code.

1205.3.5 Places of assembly. Places of assembly shall be illuminated in accordance with Chapter 10.

1205.4 Reserved.

1205.5 Reserved.

SECTION BC 1206
YARDS AND COURTS

1206.1 General.  This section shall apply to yards and courts adjacent to exterior openings that provide required natural light or required natural ventilation. Such yards and courts shall be on the same zoning lot as the building. Where such yard or court is wholly or partially on a different tax lot from the exterior opening which the yard or court serves, a light and air easement or restrictive declaration acceptable to the commissioner shall be recorded against the tax lot or lots where such yard or court is located.

1206.2 Yards. Yards shall [not] be not less than the dimensions prescribed by the New York City Zoning Resolution and other applicable laws, rules, and regulations.

1206.2.1 Rear yard access for multiple dwellings. For multiple dwellings, there shall be direct access from the street to every rear yard through a noncombustible 2-hour fire-resistance-rated passage either in a direct line or through a court, except that the passage may be 1-hour fire-resistance-rated for dwellings not exceeding three stories in height and occupied by not more than two families on any story. Such passage shall be at least 36 inches (914 mm) in clear width and 7 feet (2134 mm) in height.

Exceptions: No such passage shall be required for:

1.	Buildings of Type IA or IB construction.

2.	Buildings not exceeding three stories in height, and occupied by not more than one family on any story nor more than three families in all.

3.	Buildings not exceeding two stories in height, and occupied by not more than two families on any story nor more than four families in all.

1206.3 Courts. Courts shall not be less than the dimensions prescribed by the New York City Zoning Resolution and other applicable laws, rules and regulations.

1206.3.1 Court access. Access shall be provided to the bottom of courts for cleaning purposes.

1206.3.2 Air intake. Courts more than two stories in height shall be provided with a horizontal air intake at the bottom not less than 10 square feet (0.93 m2) in area and leading to the exterior of the building unless abutting a yard or public way.

Exception: For multiple dwellings more than two stories in height, an air intake with a vertical cross-sectional area of 21 square feet (1.95 m2) and a least minimum dimension of 3 feet (914 mm) shall be provided at or near the lowest level of any court, in accordance with Section 26(7)(a) of the New York State Multiple Dwelling Law.

1206.3.3 Court drainage. The bottom of every court shall be properly graded and drained to a public sewer or other approved disposal system complying with the New York City Plumbing Code. For Group R and I-1 occupancies, such grading and drainage shall also comply with Section 27-2027 of the New York City Housing Maintenance Code. For Group R-1, R-2 and I-1 occupancies, such grading and drainage shall also comply with Section 77 of the New York State Multiple Dwelling Law.

1206.3.4 Court walls for multiple dwellings. All walls enclosing courts of multiple dwellings shall be of light colored materials or shall be painted a light color.

Exceptions:

1.	Outer courts that open to a street.

2.	Courts that exceed the minimum dimension set forth in the New York City Zoning Resolution by at least 50 percent.

1206.4 Lighting in courts and yards. In Group I-1, R-1 or R-2 occupancies, all yards and courts shall be artificially illuminated with a minimum intensity of not less than 1 [foot-candle] footcandle (11 lux) measured 30 inches (762 mm) above the floor of the lowest level of such yards or courts.

Exception: Such lighting is not required in an inner court that is accessible only from the interior of the building and to which access is restricted for clean-out purposes.

SECTION BC 1207
SOUND TRANSMISSION

1207.1 Scope. This section shall apply to common interior walls, partitions and floor/ceiling assemblies between adjacent dwelling units, between dwelling units and adjacent mechanical equipment spaces, or between dwelling units and adjacent occupancies, and public areas such as halls, corridors, stairs or service areas.

1207.2 Air-borne sound. Walls, partitions and floor/ceiling assemblies separating dwelling units from each other, from adjacent occupancies, from public or service areas, from stairs or from mechanical equipment spaces, including boiler rooms, or elevator or other shafts shall have a sound transmission class (STC) for air-borne noise of not less than 50 based upon laboratory measurements made in accordance with ASTM E 90, or not less than 45 if field tested in accordance with ASTM E 336. Dwelling unit entrance doors shall be installed of assemblies having an STC of not less than 30 based upon laboratory measurements made in accordance with ASTM E 90. Penetrations or openings in construction assemblies for piping; electrical devices; recessed cabinets; bathtubs; soffits; or heating, ventilating or exhaust ducts shall be sealed, lined, insulated or otherwise treated to maintain the required ratings.

1207.2.1 Masonry. The sound transmission class of concrete masonry and clay masonry assemblies shall be calculated in accordance with TMS [0302] 302 or determined through testing in accordance with ASTM E 90.

1207.2.2 Machine and equipment rooms. Elevator machine rooms and machinery spaces containing equipment totaling more than 75 rated h.p. shall not be located vertically or horizontally adjacent to dwelling units unless the total sound pressure level output of all the equipment in the machine room or space is certified not to exceed the maximum sound pressure levels of Table 1207.2.1 in any octave band.

TABLE 1207.2.1
MAXIMUM SOUND PRESSURE LEVELS FOR MACHINE ROOMS ADJACENT TO DWELLING UNITS, MEASURED IN THE DWELLING UNIT

| OCTAVE BANDS, HZ MID-FREQUENCY | MAXIMUM SOUND PRESSURE LEVEL dba |
| --- | --- |
|  | db re 0.0002 microbars |
| 63 | 61 |
| 125 | 53 |
| 250 | 46 |
| 500 | 40 |
| 1000 | 36 |
| 2000 | 34 |
| 4000 | 33 |
| 8000 | 32 |

- The maximum sound pressure levels shall be reduced five db in any octave band where the equipment data indicate pure tone generation. The presence of pure tones may be determined by means of one-third octave band analysis. The criterion for a significant pure tone component shall be an audible pure-tone sound together with an increase of the sound pressure level in the corresponding one-third octave band above the mean of the two adjacent one-third of at least:

| Center frequency of one-third octave band: | 40/125 | 160/250 | 215/500 | 630/1,000 | 1,000/10,000 |
| --- | --- | --- | --- | --- | --- |
| Increase in sound pressure level (db): | 6 | 4 | 3 | 2 | 1½ |

1207.3 Structure-borne sound. Floor/ceiling assemblies between dwelling units and sleeping units or between a dwelling unit or sleeping unit and a public or service area stair, exterior mechanical equipment, or other mechanical equipment space, including boiler rooms, shall be constructed of assemblies having an impact insulation class (IIC) rating of not less than 50 based upon laboratory measurements made in accordance with ASTM E 492, or not less than 45 if field tested in accordance with ASTM E 1007 in completed construction. See Chapter 30 for additional sound control requirements for elevator machinery.

1207.3.1 Refuse chutes. Metal refuse chutes, metal chute supports, and [/or] metal chute bracing shall be free of direct contact with the shaft enclosure and the openings provided in the floor construction. Metal chutes shall be resiliently supported at each structural support location. Isolators shall provide a minimum static deflection of 0.3 inches (7.62 mm). All chutes shall be plumb.

1207.4 Field testing. Where conditions indicate that the installed construction or equipment does not meet the noise control prescribed in Section 1207, measurements shall be taken to determine conformance or nonconformance.

SECTION BC 1208
INTERIOR SPACE DIMENSIONS

1208.1 Minimum room widths.  Habitable spaces, other than a kitchen, shall [not] be not less than 8 feet (2438 mm) in any plan dimension. Kitchens and kitchenettes shall have a clear passageway of not less than 3 feet (914 mm) between counter fronts and appliances or counter fronts and walls.

Exceptions:

1.	A room that complies with the requirements for natural light and natural ventilation and in addition has an unobstructed opening of not less than 60 square feet (5.6 m2) into an immediately adjoining room shall [not] be not less than 7 feet (2134 mm) in any plan dimension.

2.	A habitable dining space that complies with the requirements for natural light and natural ventilation may be less than 8 feet (2438 mm) in any plan dimension.

3.	One-half the number of bedrooms in a dwelling unit containing three or more bedrooms shall [not] be not less than 7 feet (2134 mm) in any plan dimension.

4.	A room in a Group R-1 dwelling or sleeping unit shall [not] be not less than 6 feet (1829 mm) in any plan dimension.

1208.2 Minimum ceiling heights. Habitable rooms and spaces shall have a ceiling height of not less than 8 feet (2438 mm).  Occupiable spaces and corridors shall have a ceiling height of not less than 7 feet 6 inches (2286 mm). Bathrooms, toilet rooms, kitchens in other than Group I-1 and R occupancies, kitchenettes in Group I-1 or R occupancies, storage rooms and laundry rooms shall [be permitted to] have a ceiling height of not less than 7 feet (2134 mm). All measurements shall be taken from the finished floor to the finished underside of the ceiling or ceiling beams.

Exceptions:

1.	In one- and two-family dwellings, beams or girders spaced not less than 4 feet (1219 mm) on center may project not more than 6 inches (152 mm) below the required ceiling height, provided that a clear height of 7 feet (2134 mm) is maintained.

2.	Habitable rooms in basements of one- or two-family dwellings, including any projecting beams, shall have a ceiling height of not less than 7 feet (2134 mm).

3.	Habitable rooms in basements of multiple dwellings may have as many as four beams crossing the ceiling if none of the beams exceeds 12 inches (305 mm) in width or extends below the ceiling more than 6 inches (152 mm).

4.	Spaces above and below a mezzanine, other than habitable spaces, shall have a ceiling height of not less than 7 feet (2134 mm).

1208.2.1 Furred ceiling. Any room with a furred ceiling shall be required to have the minimum ceiling height in two-thirds of the area thereof, but in no case shall the height of the furred ceiling be less than 7 feet (2134 mm).

Exception: Minimum ceiling heights of habitable rooms and spaces shall [not] be not less than established in Section 1208.2.

1208.3 Room area. Minimum net floor areas of rooms shall be in accordance with Sections 1208.3.1 and 1208.3.2.

1208.3.1 Habitable rooms and spaces. Every habitable room or space shall have not less than 80 square feet (7.4 m2) in net floor area.

Exceptions:

1.	A room that complies with the requirements for natural light and natural ventilation and in addition has an unobstructed opening of not less than 60 square feet (5.6 m2) into an immediately adjoining room shall have not less than 70 square feet (6.5 m2) of net floor area.

2.	A habitable dining space, as defined by the New York City Housing Maintenance Code, that complies with the requirements for natural light and natural ventilation may have less than 80 square feet (7.4 m2) of net floor area.

3.	A room in a Group R-1 dwelling unit shall have not less than 60 square feet (5.6 m2) of net floor area.

1208.3.2 Dwelling units. In a dwelling unit, at least one habitable room shall have not less than 150 square feet (13.9 m) of net floor area.

Exception: Group R-1 dwelling or sleeping units.

1208.3.2.1. Single room occupancy of a single room. Where a single room within a dwelling unit is used for single room occupancy, as such term is used in Section 27-2074(e) of the New York City Housing Maintenance Code, such room shall have not less than 150 square feet (13.9 m2) of net floor area.

1208.3.2.2 Single room occupancy of a suite of rooms. Where two or more rooms, joined together and separated from all other rooms within a dwelling unit, are used for single room occupancy, as such term is used in Section 27-2074(e) of the New York City Housing Maintenance Code, at least one of such separated rooms shall have not less than 150 square feet (13.9 m2) of net floor area.

1208.4 Reserved.

SECTION BC 1209
ACCESS TO UNOCCUPIED SPACES

1209.1 Crawl spaces.  Crawl spaces shall be provided with [a minimum of] not fewer than one access opening that shall be not less than 18 inches by 24 inches (457 mm by 610 mm). All crawl spaces shall have a minimum clear height of 18 inches (457 mm).

1209.2 Attic spaces.  An opening not less than 20 inches by 30 inches (508 mm by 762 mm) shall be provided to any attic area having a clear height of over 30 inches (762 mm). [A] Clear headroom of not less than 30[-inch] inches (762 mm) [minimum clear headroom] shall be provided in the attic space [shall be provided] at or above the access opening.

1209.3 Mechanical appliances. Access to mechanical appliances installed in under-floor areas, in attic spaces and on roofs or elevated structures shall be in accordance with the New York City Mechanical Code.

SECTION BC 1210
[SURROUNDING MATERIALS] TOILET AND BATHROOM REQUIREMENTS

1210.1 Required fixtures. The number and type of plumbing fixtures provided in any occupancy shall comply with the New York City Plumbing Code.

1210.2 Finish materials. Walls, floors and partitions in toilet and bathrooms shall comply with Sections 1210.2.1 through 1210.2.4.

1210.2.1 Floors and wall [base finish materials] bases. [Toilet,] In other than dwelling units, toilet, bathing[,] and shower room floor finish materials shall have a smooth, hard, nonabsorbent surface. The intersections of such floors with walls shall have a smooth, hard, nonabsorbent vertical base that extends upward onto the walls [at least] not less than 4 inches (101.6 mm).

Exception: [Occupancy Classes] Group I-1, R-1 and R-2 occupancies shall have a vertical base that extends upward onto walls at least 6 inches (152 mm).

[1210.2] 1210.2.2 Walls and partitions. Walls and partitions within 2 feet (610 mm) of service sinks, urinals and water closets shall have a smooth, hard, nonabsorbent surface, to a height of not less than 4 feet (1219 mm) above the floor, and except for structural elements, the materials used in such walls shall be of a type that is not adversely affected by moisture.

Exceptions:

1.	Dwelling units.

2.	Toilet rooms that are not accessible to the public and [which] that have not more than one water closet.

Accessories such as grab bars, towel bars, paper dispensers and soap dishes, provided on or within walls, shall be installed and sealed to protect structural elements from moisture.

[1210.3] 1210.2.3 Showers.  Shower compartments and walls above bathtubs with installed shower heads shall be finished with a smooth, nonabsorbent surface to a height not less than [70] 72 inches ([1778] 1829 mm) above the drain inlet.

[1210.4] 1210.2.4 Waterproof joints.  Built-in tubs with showers shall have waterproof joints between the tub and adjacent wall.

1210.3 Privacy.  Privacy at water closets and urinals shall be provided in accordance with Sections 1210.3.1 and 1210.3.2.

1210.3.1 Water closet compartment. Each water closet utilized by the public or employees shall occupy a separate compartment with walls or partitions and a door enclosing the fixtures for privacy.

Exceptions:

1.	Water closet compartments shall not be required in a single-occupant toilet room with a lockable door.

2.	Toilet rooms located in child day care facilities and containing two or more water closets shall be permitted to have one water closet without an enclosing compartment.

3.	This provision is not applicable to toilet areas located within Group I-3 occupancy housing areas.

1210.3.2 Urinal partitions. Each urinal utilized by the public or employees shall occupy a separate area with walls or partitions to provide privacy. The walls or partitions shall begin at a height not more than 12 inches (305 mm) from and extend not less than 60 inches (1524 mm) above the finished floor surface. The walls or partitions shall extend from the wall surface at each side of the urinal not less than 18 inches (457 mm) or to a point not less than 6 inches (152 mm) beyond the outermost front lip of the urinal measured from the finished backwall surface, whichever is greater.

Exceptions:

1.	Urinal partitions shall not be required in a single-occupant or family or assisted-use toilet room with a lockable door.

2.	Toilet rooms located in child day care facilities and containing two or more urinals shall be permitted to have one urinal without partitions.

[1210.5] 1210.4 Toilet rooms. Toilet rooms shall not open directly into a room used for the preparation of food for service to the public. In multiple dwellings no toilet room or bathroom shall open onto any kitchen or kitchenette.

SECTION BC 1211
KITCHENS AND KITCHENETTES

1211.1 Sleeping. No kitchen or kitchenette shall be occupied for sleeping purposes.

1211.2 Kitchenettes in multiple dwellings. Except at entrances thereto, every kitchenette in a multiple dwelling shall be surrounded by partitions extending from floor to ceiling, and/or by a soffit dropped 1 foot (305 mm) from the ceiling.

SECTION BC 1212
[RODENT-PROOFING] RODENTPROOFING

1212.1 General. [Rodent-proofing] Rodentproofing shall be in accordance with Appendix F.

SECTION BC 1213
REFUSE AND RECYCLABLE STORAGE

1213.1 General. Multiple dwellings shall comply with Section 81 of the New York State Multiple Dwelling Law and Section 27-2021 of the New York City Housing Maintenance Code. In Group R-2 occupancies, space shall be provided for the storage of refuse and recyclables as a common accessory space. The location of such refuse and recyclables storage space shall be clearly identified on the construction documents and configured to permit separate unobstructed access by building personnel to stored refuse and recyclables. Such refuse and recyclables storage space shall be a minimum of 1.5 square feet (0.140 m2) per dwelling unit, or a minimum of 350 square feet (32.516 m2), whichever is less, for the storage of collected refuse and recyclables.

Exceptions:

1.	In multiple dwellings required to have a compactor in accordance with Section 1213.2, such refuse and recyclables storage space shall be, in addition to space required for equipment or circulation, a minimum of 1.0 square foot (0.094 m2) per dwelling unit, or a minimum of 350 square feet (32.516 m2), whichever is less, for the storage of collected refuse and recyclables.

2.	Refuse and recyclables storage space shall not be required in multiple dwellings equipped with a chute system that provides for source separation of refuse and recyclable materials without cross contamination and an integrated mechanical system to transport such materials off-site that has been approved by the commissioner.

1213.1.1 Interior space. Where an interior room is provided for the storage of refuse and recyclables, such room shall be completely enclosed by construction that has a fire-resistance rating of not less than 2 hours, with self-closing opening protective having a fire protection rating of not less than 1½ hours.

1213.1.2 Exterior space. Where space is provided on the exterior of a building for the storage of refuse and recyclables, such refuse and recyclables storage space shall include a minimum of 4 square feet (0.372 m2) in addition to the space per dwelling unit required by Section 1213.1, shall be clearly identified on the construction documents, and shall not be located in the public right-of-way.

1213.2 Compactor. A refuse compacting system shall be provided in multiple dwellings in a [Groups] Group I-1 or R-2 occupancy that are four or more stories in height and contain 12 or more dwelling units, and in buildings of any size occupied as a Group R-1 multiple dwelling. Such system shall be located within a refuse storage room constructed in accordance with Section 1213.1 or in a refuse chute termination room constructed in accordance with Section [707.13.4] 713.13.4. The floor within such room shall be constructed of concrete and shall be sloped to a floor drain connected to the building sewer. A hose connection shall be provided within such room.

1213.3 Refuse chute. A multiple dwelling that is five or more stories in height and that contains 9 or more dwelling units shall be provided with a refuse chute, refuse chute access rooms, and refuse chute termination room constructed in accordance with Section [707.13] 713.13. A minimum of 5 square feet (0.470 m2) of floor area within each refuse chute access room shall be provided for the temporary holding of recyclables. Such floor area shall be clearly identified on the construction documents. In Group I-1 and R-1 occupancies, access to the chute access room shall be permitted to be restricted to employees provided that separate refuse storage rooms are located on each story for general occupant use.

Exceptions:

1.	In buildings without an elevator, floor area within refuse chute access rooms for the temporary holding of recyclables is not required.

2.	In buildings equipped with separate chutes designated for refuse, for paper and cardboard, and for metal, glass and plastic, and in buildings equipped with a chute system that provides for source separation of recyclable materials without cross contamination, floor area within refuse chute access rooms for the temporary holding of recyclables is not required. Chutes for designated recyclable materials shall be constructed in accordance with Section [707.13] 713.13 of this code.

3.	The refuse chute and the occupant use storage rooms shall not be required in transient hotels meeting the following requirements:

3.1.	the refuse is removed from rooms by a daily cleaning service, with the staff using a service elevator that is not accessed by hotel guests;

3.2.	the building is of [Group] Type I or [Group] Type II construction; or

3.3.	a compactor and refuse storage room is provided in accordance with Section 1213.2.

1213.3.1 Refuse chute access room floor and wall base finish materials. Refuse chute access rooms shall have a smooth, hard and nonabsorbent surface. The intersection of such floors with walls shall have a smooth, hard and nonabsorbent vertical base that extends upward onto the walls at least 4 inches (101.6 mm).

§ 15.  Chapter 14 of the New York city building code, as amended by local law number 141 for the year 2013, is amended to read as follows:

CHAPTER 14
EXTERIOR WALLS

SECTION BC 1401
GENERAL

1401.1 Scope.  The provisions of this chapter shall establish the minimum requirements for exterior: walls; wall coverings; wall openings; windows and doors; architectural trim; balconies; projections; and other appendages.

1401.2 Construction documents. Construction documents for exterior wall coverings required to be tested in accordance with NFPA 285 pursuant to this code shall include the following data and information:

1.	Design documentation of the NFPA 285 tested assembly from the manufacturer shall be included in the construction documents. This shall include section and elevation drawings that identify materials and components of the tested assembly, including panel sizes and joint locations. All components used in the tested assembly shall be clearly identified. Material thicknesses, relative locations of components and offsets shall be fully dimensioned.

2.	Information shall be provided for verification in accordance with Sections.16 and 1705.20 special inspections.

3.	A certification by the applicant that “Any deviation which occur during the course of installation will be evaluated and approved by the applicant of record or registered design professional. No deviation shall be approved that would result in an assembly that would otherwise fail to pass the acceptance criteria of NFPA 285.”

SECTION BC 1402
DEFINITIONS

1402.1 [General] Definitions.  The following [words and terms shall, for the purposes of this chapter and as used elsewhere in this code, have the meanings shown herein.] terms are defined in Chapter 2:

ADHERED MASONRY VENEER.[Veneer secured and supported through the adhesion of an approved bonding material applied to an approved backing.]

ANCHORED MASONRY VENEER.[Veneer secured with approved mechanical fasteners to an approved backing.]

BACKING.[The wall or surface to which the veneer is secured.]

BIRD FRIENDLY MATERIAL. [A material or assembly that has, or has been treated to have a maximum threat factor of 25 in accordance with the American Bird Conservancy Bird Collision Deterrence Material Threat Factor Reference Standard, or with the American Bird Conservancy Bird-friendly Materials Evaluation Program at Carnegie Museum’s Avian Research Center test protocol, or with a relevant ASTM standard.]

BIRD HAZARD INSTALLATIONS. [Monolithic glazing installations that provide a clear line of sight on the exterior of buildings, including, but not limited to, glass awnings, glass handrails and guards, glass wind break panels, or glass acoustic barriers.]

CURTAIN WALL.[A curtain wall or panel wall system is a nonload-bearing building wall, in skeleton frame construction attached and supported to the structure at every floor or other periodic locations. Assemblies may include glass, metal, precast concrete or masonry elements arranged so as not to exert common action under load and to move independently of each other and the supporting structure.]

EXTERIOR INSULATION AND FINISH SYSTEMS (EIFS).[EIFS are nonstructural, nonload-bearing, exterior wall cladding systems that consist of an insulation board attached either adhesively or mechanically, or both, to the substrate, an integrally reinforced base coat and a textured protective finish coat.]

EXTERIOR INSULATION AND FINISH SYSTEMS (EIFS) WITH DRAINAGE.[An EIFS that incorporates a means of drainage applied over a water-resistive barrier.]

EXTERIOR WALL.[A wall, bearing or nonbearing, that is used as an enclosing wall for a building, other than a fire wall, and that has a slope of 60 degrees (1.05 rad) or greater with the horizontal plane.]

EXTERIOR WALL COVERING.[A material or assembly of materials applied on the exterior side of exterior walls for the purpose of providing a weather-resisting barrier, insulation or for aesthetics, including but not limited to, veneers, siding, exterior insulation and finish systems, architectural trim and embellishments such as cornices, soffits, facias, gutters and leaders.]

EXTERIOR WALL ENVELOPE.[A system or assembly of exterior wall components, including exterior wall finish materials, that provides protection of the building structural members, including framing and sheathing materials, and conditioned interior space, from the detrimental effects of the exterior environment.]

FENESTRATION.

[FIBER CEMENT SIDING. A manufactured, fiber-reinforcing product made with an inorganic hydraulic or calcium silicate binder formed by chemical reaction and reinforced with discrete organic or inorganic nonasbestos fibers, or both. Additives that enhance manufacturing or product performance are permitted. Fiber cement siding products have either smooth or textured faces and are intended for exterior wall and related applications.] FIBER-CEMENT SIDING.

FLY-THROUGH CONDITIONS. [One or more panels of glass that provide a clear line of sight through such elements creating the illusion of a void leading to the other side, including parallel glass elements, at a distance of 17 feet (5182 mm) or less, or a convergence of glass sides creating a perpendicular, acute or obtuse corner.]

HIGH-PRESSURE DECORATIVE EXTERIOR-GRADE COMPACT LAMINATE (HPL).

METAL COMPOSITE MATERIAL (MCM).[A factory-manufactured panel consisting of metal skins bonded to both faces of a plastic core.]

METAL COMPOSITE MATERIAL (MCM) SYSTEM.[An exterior wall covering fabricated using MCM in a specific assembly including joints, seams, attachments, substrate, framing and other details as appropriate to a particular design.]

POLYPROPYLENE SIDING.

PORCELAIN TILE.

VENEER.[A facing attached to a wall for the purpose of providing ornamentation, protection or insulation, but not counted as adding strength to the wall. Veneers are nonstructural in that they do not carry any load other than their own weight.]

VINYL SIDING.[A shaped material, made principally from rigid polyvinyl chloride (PVC) that is used as an exterior wall covering.]

WATER-RESISTIVE BARRIER.[A material behind an exterior wall covering that is intended to resist liquid water that has penetrated behind the exterior wall covering from further intruding into the exterior wall assembly.]

SECTION BC 1403
PERFORMANCE REQUIREMENTS

1403.1 General.  The provisions of this section shall apply to exterior walls, exterior wall coverings and components thereof.

1403.2 Weather protection.  Exterior walls shall provide the building with a weather-resistant exterior wall envelope. The exterior wall envelope shall include flashing, as described in Section 1405.4. The exterior wall envelope shall be designed and constructed in such a manner as to prevent the accumulation of water within the wall assembly by providing a water-resistive barrier behind the exterior veneer, as described in Section 1404.2, and a means for draining water that enters the assembly to the exterior. Protection against condensation shall be provided as required.

Exceptions:

1.	A weather-resistant exterior wall envelope shall not be required over concrete and masonry walls[,] designed to resist water penetration and detrimental effects from freeze/thaw cycling and in accordance with Chapters 19 and 21, as applicable.

2.	Compliance with the requirements for a means of drainage, and the requirements of Sections 1404.2 and 1405.4, shall not be required for an exterior wall envelope that has been demonstrated through testing to resist wind-driven rain, including joints, penetrations and intersections with dissimilar materials, in accordance with ASTM E 331 under the following conditions:

2.1.	Exterior wall envelope test assemblies shall include at least one opening, one control joint, and where required, one wall/eave interface and one wall sill. [All tested] Tested openings and penetrations shall be representative of the intended end-use configuration.

2.2.	Exterior wall envelope test assemblies shall be at least 4 feet by 8 feet (1219 mm by 2438 mm) in size.

2.3.	Exterior wall envelope assemblies shall be tested at a minimum differential pressure of 6.24 pounds per square foot (psf) (0.297 kN/m2) for a duration of 2 hours. The exterior wall envelope assemblies shall also be tested at a minimum differential pressure not less than 20 percent of the positive design wind load as calculated per Chapter 16, or 15 pounds per square foot (psf) (0.718 kN/m2) for a duration of 15 minutes.

2.4.	The exterior wall envelope design shall be considered to resist wind-driven rain where the results of testing indicate that water did not penetrate the test assembly including control joints in the exterior wall envelope, joints at the perimeter of openings[,] or intersections of terminations with dissimilar materials.

3.	Exterior insulation and finish systems (EIFS) complying with Section 1408.4.1.

1403.3 Structural.  Exterior wall envelope, and the associated openings, shall be designed and constructed to resist safely the superimposed loads required by Chapter 16.

1403.4 Fire resistance.  Exterior wall envelope shall be fire-resistance rated as required by other sections of this code with opening protection as required by Chapter 7.

1403.5 Vertical and lateral flame propagation. Exterior walls that contain foam plastic insulation including exterior insulation and finish systems (EIFS), metal composite material (MCM) systems, high-pressure decorative exterior-grade compact laminates (HPL), and fiber-reinforced polymer (FRP) shall be tested in accordance with and comply with the acceptance criteria of NFPA 285. Foam plastic insulation assemblies and FRP shall be tested in accordance with Section 2603.5.5. MCM systems shall be tested in accordance with Section 1407.11. HPL systems shall be tested in accordance with Section 1409.11.  Approved NFPA 285 tested assembly design documentation shall be included on the submitted construction documents complying with Section 1401.2. Deviation from the NFPA 285 tested design shall be approved by the registered design professional and additional documentation shall be provided if requested by the department. Combustible exterior wall coverings shall comply with Section 1406.

Exception: Fiber-reinforced polymer (FRP) where permitted by Section 2613.5 not to be tested.

1403.5.1 Exterior walls with water-resistive barriers. Exterior walls on buildings of Type I, II, III, or IV construction that are greater than 40 feet (12 192 mm) in height above grade plane and contain a combustible water-resistive barrier shall be tested in accordance with and comply with the acceptance criteria of NFPA 285. For the purposes of this section, fenestration products and flashing of fenestration products shall not be considered part of the water-resistive barrier.

Exceptions:

1.	Walls in which the water-resistive barrier is the only combustible component of the wall covering and the exterior wall has a wall covering of brick, concrete, stone, terra cotta, stucco or steel with minimum thicknesses in accordance with Table 1405.2.

2.	Walls in which the water-resistive barrier is the only combustible component and the water-resistive barrier has a peak heat release rate of less than 150 kW/m2, a total heat release of less than 20 MJ/m2 and an effective heat of combustion of less than 18 MJ/kg as determined in accordance with ASTM E 1354 and has a flame spread index of 25 or less and a smoke-developed index of 450 or less as determined in accordance with ASTM E 84 or UL 723. The ASTM E 1354 test shall be conducted on specimens at the thickness intended for use, in the horizontal orientation and at an incident radiant heat flux of 50 kW/m2.

1403.6 Flood resistance.  For buildings in [areas of special] flood hazard areas, the exterior wall envelope extending below the design flood elevation shall be resistant to water damage and shall comply with Appendix G.

1403.7 Thermal and condensation resistance. The exterior wall envelope shall be designed and constructed [required] for thermal and condensation resistance as necessary to meet the requirements of the New York City Energy Conservation Code.

1403.8 Bird friendly materials. Bird friendly materials shall be required in accordance with [sections] Sections 1403.8.1 through 1403.8.4.

1403.8.1 Exterior wall envelope. The exterior wall envelope, and any associated openings, shall be constructed with bird friendly materials up to 75 feet (22 860 mm) above grade. Materials other than bird friendly materials shall not exceed an aggregate of 10 square feet (0.93 m²) within any 10 feet (3048 mm) by 10 feet (3048 mm) square area of exterior wall below 75 feet (22 860 mm) above grade.

Exceptions:

1.  Where ground floor transparency is required by the New York City Zoning Resolution, transparent bird friendly material with a UV-reflective pattern and a maximum threat factor of 27 shall be provided.

2.  In areas of special flood hazard and shaded X-Zones where flood resistant glazing is proposed and ground floor transparency is required by the New York City Zoning Resolution, transparent bird friendly material with a UV-reflective pattern and a maximum threat factor of 36 shall be provided.

1403.8.2 Bird hazard installations. Bird hazard installations shall be constructed of bird friendly materials regardless of their height above grade.

1403.8.3 Fly-through conditions. Fly-through conditions located 75 feet (22 860 mm) or less above grade shall be constructed with bird friendly materials.

1403.8.4 Adjacency to green roofs. The exterior wall envelope, and any associated openings, installed adjacent to a green roof system on the same building shall be constructed with bird friendly materials up to 12 feet (3658 mm) above the walking surface.

1403.9 Air barrier.  The exterior wall envelope shall be designed and constructed with an air barrier as necessary to meet the requirements of the New York City Energy Conservation Code and this code.

SECTION BC 1404
MATERIALS

1404.1 General.  Materials used for the construction of exterior walls shall comply with the provisions of this section. Materials not prescribed herein shall be permitted, provided that any such alternative has been approved.

1404.2 Water-resistive barrier. [A minimum of] Not fewer than one layer of No. 15 asphalt felt[,] complying with ASTM D 226 for Type 1 felt[,] or other approved materials, shall be attached to the studs or sheathing, with flashing as described in Section 1405.4, in such a manner as to provide a continuous water-resistive barrier behind the exterior wall veneer. Combustible water-resistive barriers shall comply with special inspection requirements of Chapter 17.

1404.3 Wood.  Exterior walls of wood construction shall be designed and constructed in accordance with Chapter 23.

1404.3.1 Basic hardboard.  Basic hardboard shall conform to the requirements of [AHA] ANSI A135.4.

1404.3.2 Hardboard siding.  Hardboard siding shall conform to the requirements of [AHA] ANSI A135.6 and, where used structurally, shall be so identified by the label of an approved agency.

1404.4 Masonry.  Exterior walls of masonry construction shall be designed and constructed in accordance with this chapter and Chapter 21. Masonry units, mortar and metal accessories used in anchored and adhered veneer shall meet the physical requirements of Chapter 21. The backing of anchored and adhered veneer shall be of concrete, masonry, steel framing or wood framing. Continuous insulation meeting the applicable requirements of this code shall be permitted between the backing and the masonry veneer.

1404.5 Metal.  Exterior walls [of formed steel construction, structural steel or lightweight metal alloys] constructed of cold-formed steel, structural steel or aluminum shall be designed in accordance with Chapters [22 and 20] 20 and 22, as applicable.

1404.5.1 Aluminum siding.  Aluminum siding shall conform to the requirements of AAMA 1402.

1404.5.2 Cold-rolled copper.  Copper shall conform to the requirements of ASTM B 370.

1404.5.3 Lead-coated copper.  Lead-coated copper shall conform to the requirements of ASTM B 101.

1404.6 Concrete.  Exterior walls of concrete construction shall be designed and constructed in accordance with Chapter 19.

1404.7 Glass-unit masonry.  Exterior walls of glass-unit masonry shall be designed and constructed in accordance with Chapter 21.

1404.8 Plastics. Plastic panel, apron or spandrel walls as defined in this code shall not be limited in thickness, provided that such plastics and their assemblies conform to the requirements of Chapter 26 and other applicable requirements of this chapter, and are constructed of approved weather-resistant materials of adequate strength to resist the wind loads for cladding specified in Chapter 16.

1404.9 Vinyl siding.  Vinyl siding shall be certified and labeled as conforming to the requirements of ASTM D 3679 by an approved agency.

1404.10 [Fiber cement] Fiber-cement siding. [Fiber cement] Fiber-cement siding shall conform to the requirements of ASTM C 1186, Type A[,] or ISO 8336, Category A, and shall be so identified on labeling listing an approved agency.

1404.11 Exterior insulation finish system (EIFS). EIFS shall be designed and constructed in accordance with Section 1408.

1404.12 Polypropylene siding. Polypropylene siding shall be certified and labeled as conforming to the requirements of ASTM D 7254 and those of Section 1404.12.1 or 1404.12.2 by an approved agency. Polypropylene siding shall be installed in accordance with manufacturer’s instructions and the requirements of Section 1405.18 of this code. Polypropylene siding shall be secured to the building so as to provide weather protection for the exterior walls of the building.

1404.12.1 Flame spread index.  The certification of the flame spread index shall be accompanied by a test report stating that all portions of the test specimen ahead of the flame front remained in position during the test in accordance with ASTM E 84 or UL 723.

1404.12.2 Distance between adjacent buildings.  The distance between a building with polypropylene siding and the adjacent building shall be not less than 10 feet (3048 mm).

1404.13 Foam plastic insulation. Foam plastic insulation used in exterior wall covering assemblies shall comply with Chapter 26 and be fireblocked in accordance with Section 718.2.6.1.

SECTION BC 1405
INSTALLATION OF WALL COVERINGS

1405.1 General.  Exterior wall coverings shall be designed and constructed in accordance with the applicable provisions of this section. Installations not prescribed herein shall be permitted, provided that such alternative has been approved. Installations shall be in accordance with approved construction documents where a permit is required. Installations of exterior wall coverings shall comply with the special inspection requirements of Chapter 17.

1405.2 Weather protection.  [Exterior] The exterior wall envelope shall provide weather protection for the building. The materials of the minimum nominal thickness specified in Table 1405.2 shall be acceptable as approved weather coverings.

Exception: Weather coverings not meeting the minimum nominal thicknesses specified in Table 1405.2 shall be permitted provided such alternative has been approved.

| TABLE 1405.2 MINIMUM THICKNESS OF WEATHER COVERINGS |
| --- |
| COVERING TYPE | MINIMUM THICKNESS (inches) |
| Adhered masonry veneer* | 0.25 |
| Aluminum siding | 0.019 |
| Anchored masonry veneer | 2.625 |
| Asbestos-cement boards | 0.125 |
| Asbestos shingles | 0.156 |
| Cold-rolled copperd | 0.0216 nominal |
| Copper shinglesd | 0.0162 nominal |
| Exterior plywood (with sheathing) | 0.313 |
| Exterior plywood (without sheathing) | See Section 2304.6 |
| Fiber cement lap siding | 0.25c |
| Fiber cement panel siding | 0.25c |
| Fiberboard siding | 0.5 |
| Glass-fiber reinforced concrete panels | 0.375 |
| Hardboard sidingc | 0.25 |
| High-yield copperd | 0.0162 nominal |
| Lead-coated copperd | 0.0216 nominal |
| Lead-coated high-yield copper | 0.0162 nominal |
| Marble slabs | 1 |
| Particleboard (with sheathing) | See Section 2304.6 |
| Particleboard (without sheathing) | See Section 2304.6 |
| [Precast stone facing] Porcelain tile | [0.625] 0.25 |
| Steel (approved corrosion resistant) | 0.0149 |
| Stone [(cast artificial)] (cast artificial, anchored) | 1.5 |
| Stone (natural) | 2 |
| Structural glass | 0.344 |
| Stucco or exterior cement plaster |  |
| Three-coat work over: |  |
| Metal plaster base | 0.875b |
| Unit masonry | 0.625b |
| Cast-in-place or precast concrete | 0.625b |
| Two-coat work over: |  |
| Unit masonry | 0.5b |
| Cast-in-place or precast concrete | 0.375b |
| Terra cotta (anchored) | 1 |
| Terra cotta (adhered) | 0.25 |
| Vinyl siding | 0.035 |
| Wood shingles | 0.375 |
| Wood siding (without sheathing)a | 0.5 |

For SI: 1 inch = 25.4 mm, 1 ounce = 28.35 g, 1 square foot = 0.093 m2.

a.	Wood siding of thicknesses less than 0.5 inch shall be placed over sheathing that conforms to Section 2304.6.

b.	Exclusive of texture.

c.	As measured at the bottom of decorative grooves.

d.	16 ounces per square foot for cold-rolled copper and lead-coated copper, 12 ounces per square foot for copper shingles, high-yield copper and lead-coated high-yield copper.

*Veneer units in this group shall be of an approved type and not be greater than 2 inches in thickness.

1405.3 Vapor retarders. [Class I or II vapor retarders shall be provided on the interior side of frame walls in Zones 5, 6, 7, 8 and Marine 4.] Vapor retarders as described in Section 1405.3.3 shall be provided based on an approved design using accepted engineering practice for hygrothermal analysis.

[Exceptions:]

[1.	Basement walls.]

[2.	Below-grade portion of any wall.]

[3.	Construction where moisture or its freezing will not damage materials.]

1405.3.1 [Class III vapor retarders.  Class III vapor retarders shall be permitted where any one of the conditions in Table 1405.3.1 is met.] Reserved.

| [TABLE 1405.3.1 CLASS III VAPOR RETARDERS |
| --- |
| ZONE | CLASS III VAPOR RETARDERS PERMITTED FOR:a |
| Marine 4 | Vented cladding over OSB Vented cladding over plywood Vented cladding over fiberboard Vented cladding over gypsum Insulated sheathing with R-value ~ R2.5 over 2×4 wall Insulated sheathing with R-value ~ R3.75 over 2×6 wall |
| 5 | Vented cladding over OSB Vented cladding over plywood Vented cladding over fiberboard Vented cladding over gypsum Insulated sheathing with R-value ~ R5 over 2×4 wall Insulated sheathing with R-value ~ R7.5 over 2×6 wall |
| 6 | Vented cladding over fiberboard Vented cladding over gypsum Insulated sheathing with R-value ~ R7.5 over 2×4 wall Insulated sheathing with R-value ~ R11.25 over 2×6 wall |
| 7 and 8 | Insulated sheathing with R-value ~ R10 over 2×4 wall Insulated sheathing with R-value ~ R15 over 2×6 wall |

##### For SI: 1 pound per cubic foot = 16 kg/m3.

- Spray foam with a minimum density of 2 lbs/ft3 applied to the interior cavity side of OSB, plywood, fiberboard, insulating sheathing or gypsum is deemed to meet the insulating sheathing requirement where the spray foam R-value meets or exceeds the specified insulating sheathing R-value.]

1405.3.2 Reserved.

1405.3.3 Material vapor retarder class.  The vapor retarder class shall be based on the manufacturer’s certified testing or a tested assembly.

The following shall be deemed to meet the class specified:

[1.]  Class I:	Sheet polyethylene, non-perforated aluminum foil with a perm rating of less than or equal to 0.1.

[2.]  Class II:	Kraft-faced fiberglass batts or paint with a perm rating greater than 0.1 and less than or equal to 1.0.

[3.]  Class III:	Latex or enamel paint with a perm rating of greater than 1.0 and less than or equal to 10.0.

1405.3.4 Minimum clear airspaces and vented openings for vented cladding.  For the purposes of this section, vented cladding shall include the following minimum clear airspaces[.]:

1.	Vinyl lap or horizontal aluminum siding applied over a weather-resistive barrier as specified in this chapter.

2.	Brick veneer with a clear airspace as specified in this code.

3.	Other approved vented claddings.

1405.4 Flashing.  Flashing shall be installed in such a manner so as to prevent moisture from entering the wall or to redirect [it] moisture to the exterior. Flashing shall be installed where required at the perimeters of exterior door and window assemblies, penetrations and terminations of exterior wall assemblies, exterior wall intersections with roofs, chimneys, porches, decks, balconies and similar projections and at built-in gutters and similar locations where moisture could enter the wall. Flashing with projecting flanges shall be installed on both sides and the ends of copings, under sills and continuously above projecting trim.

1405.4.1 Exterior wall pockets.  In exterior walls of buildings or structures, wall pockets or crevices in which moisture can accumulate shall be avoided or protected with caps or drips, or other approved means shall be provided to prevent water damage.

1405.4.2 Masonry.  Flashing and [weepholes] weep holes in anchored veneer shall be located in the first course of masonry above finished ground level above the foundation wall or slab, and other points of support, including structural floors, shelf angles and lintels where anchored veneers are designed in accordance with Section 1405.6.

1405.5 Wood veneers.  Wood veneers on exterior walls of buildings of Type I, II, III and IV construction shall be not less than 1-inch (25 mm) nominal thickness, 0.438-inch (11.1 mm) exterior hardboard siding or 0.375-inch (9.5 mm) exterior-type wood structural panels or particleboard and shall conform to the following:

1.	The veneer shall not exceed 40 feet (12 190 mm) in height above grade. Where fire-retardant-treated wood is used, the height shall not exceed 60 feet (18 290 mm) in height above grade.

2.	The veneer is attached to or furred from a noncombustible backing that is fire-resistance rated as required by other provisions of this code.

3.	Where open or spaced wood veneers (without concealed spaces) are used, they shall not project more than 24 inches (610 mm) from the building wall.

1405.6 Anchored masonry veneer.  Anchored masonry veneer shall comply with the provisions of Sections 1405.6, 1405.7, 1405.8[,] and 1405.9 and Sections [6.1] 12.1 and [6.2] 12.2 of TMS 402[/ACI 530/ASCE 5], as modified by Chapter 21 of this code.

1405.6.1 Tolerances.  Anchored masonry veneers in accordance with Chapter 14 are not required to meet the tolerances in Article 3.3 [G1] F1 of TMS 602 [/ACI 530.1/ASCE 6].

1405.6.2 Seismic requirements.  Anchored masonry veneer located in Seismic Design Category C or D shall conform to the requirements of Section [6.2.2.10] 12.2.2.10 of TMS 402[/ACI 530/ASCE 5], as modified by Chapter 21 of this code.[Anchored masonry veneer located in Seismic Design Category D shall also conform to the requirements of Section 6.2.2.10.3.3 of TMS 402/ACI 530/ASCE 5.]

1405.7 Stone veneer. [Stone] Anchored stone veneer units not exceeding 10 inches (254 mm) in thickness shall be anchored directly to masonry, concrete or to stud construction by one of the following methods:

1.	With concrete or masonry backing, anchor ties shall be not less than 0.1055-inch (2.68 mm) corrosion-resistant wire, or approved equal, formed beyond the base of the backing. The legs of the loops shall be not less than 6 inches (152 mm) in length bent at right angles and laid in the mortar joint, and spaced so that the eyes or loops are 12 inches (305 mm) maximum on center [(o.c.)] in both directions. There shall be provided not less than a 0.1055-inch (2.68 mm) corrosion-resistant wire tie, or approved equal, threaded through the exposed loops for every 2 square feet (0.2 m2) of stone veneer. This tie shall be a loop having legs not less than 15 inches (381 mm) in length, so bent [so] that [it] the tie will lie in the stone veneer mortar joint. The last 2 inches (51 mm) of each wire leg shall have a right-angle bend. One-inch (25 mm) minimum thickness of cement grout shall be placed between the backing and the stone veneer.

2.	With wood stud backing, a 2-inch by 2-inch (51 by 51 mm) 0.0625-inch (1.59 mm) [corrosion-resistant] zinc-coated or nonmetallic coated wire mesh with two layers of [water resistive] water-resistive barrier in accordance with Section 1404.2 shall be applied directly to wood studs spaced [a maximum of] not more than 16 inches (406 mm) [o.c.] on center. On studs, the mesh shall be attached with 2-inch-long (51 mm) corrosion-resistant steel wire furring nails at 4 inches (102 mm) [o.c.] on center providing a minimum 1.125-inch (29 mm) penetration into each stud and with 8d [common] annular threaded nails at 8 inches (203 mm) [o.c.] on center into top and bottom plates or with equivalent wire ties. There shall be not less than a 0.1055-inch (2.68 mm) [corrosion-resistant] zinc-coated or nonmetallic coated wire, or approved equal, [looped through the mesh] attached to the stud with not smaller than an 8d (0.120 in. diameter) annular threaded nail for every 2 square feet (0.2 m2) of stone veneer. This tie shall be a loop having legs not less than 15 inches (381 mm) in length, so bent that [it] the tie will lie in the stone veneer mortar joint. The last 2 inches (51 mm) of each wire leg shall have a right-angle bend. One-inch (25 mm) minimum thickness of cement grout shall be placed between the backing and the stone veneer.

3.	With cold-formed steel stud backing, a 2-inch by 2-inch (51 by 51 mm) 0.0625-inch (1.59 mm) zinc-coated or nonmetallic coated wire mesh with two layers of water-resistive barrier in accordance with Section 1404.2 shall be applied directly to steel studs spaced at not more than 16 inches (406 mm) on center. The mesh shall be attached with corrosion-resistant #8 self-drilling, tapping screws at 4 inches (102 mm) on center, and at 8 inches (203 mm) on center into top and bottom tracks or with equivalent wire ties. Screws shall extend through the steel connection not fewer than three exposed threads. There shall be not less than a 0.1055-inch (2.68 mm) corrosion-resistant wire, or approved equal, attached to the stud with not smaller than a #8 self-drilling, tapping screw extending through the steel framing not fewer than three exposed threads for every 2 square feet (0.2 m2) of stone veneer. This tie shall be a loop having legs not less than 15 inches (381 mm) in length, so bent that the tie will lie in the stone veneer mortar joint. The last 2 inches (51 mm) of each wire leg shall have a right-angle bend. One-inch (25 mm) minimum thickness of cement grout shall be placed between the backing and the stone veneer. The cold-formed steel framing members shall have a minimum bare steel thickness of 0.0428 inches (1.087 mm).

1405.8 Slab-type veneer. [Slab-type] Anchored slab-type veneer units not exceeding 2 inches (51 mm) in thickness shall be anchored directly to masonry, concrete or [stud] light-frame construction. For veneer units of marble, travertine, granite or other stone units of slab form, ties of corrosion-resistant dowels in drilled holes shall be located in the middle third of the edge of the units, spaced [a maximum of] not more than 24 inches (610 mm) apart around the periphery of each unit with not less than four ties per veneer unit. Units shall not exceed 20 square feet (1.9 m2) in area. If the dowels are not tight fitting, the holes shall be drilled not more than 0.063 inch (1.6 mm) larger in diameter than the dowel, with the hole countersunk to a diameter and depth equal to twice the diameter of the dowel in order to provide a tight-fitting key of cement mortar at the dowel locations [when] where the mortar in the joint has set. Veneer ties shall be corrosion-resistant metal capable of resisting, in tension or compression, a force equal to two times the weight of the attached veneer. If made of sheet metal, veneer ties shall be not smaller in area than 0.0336 by 1 inch (0.853 by 25 mm) or, if made of wire, not smaller in diameter than 0.1483-inch (3.76 mm) wire.

1405.9 Terra cotta. [Anchored terra cotta or ceramic units not less than 1⅝ inches (41 mm) thick shall be anchored directly to masonry, concrete or stud construction. Tied terra cotta or ceramic veneer units shall be not less than 1⅝ inches (41 mm) thick with projecting dovetail webs on the back surface spaced approximately 8 inches (203 mm) o.c. The facing shall be tied to the backing wall with corrosion-resistant metal anchors of not less than No. 8 gage wire installed at the top of each piece in horizontal bed joints not less than 12 inches (305 mm) nor more than 18 inches (457 mm) o.c.; these anchors shall be secured to ¼-inch (6.4 mm) corrosion-resistant pencil rods that pass through the vertical aligned loop anchors in the backing wall. The veneer ties shall have sufficient strength to support the full weight of the veneer in tension. The facing shall be set with not less than a 2-inch (51 mm) space from the backing wall and the space shall be filled solidly with Portland cement grout and pea gravel. Immediately prior to setting, the backing wall and the facing shall be drenched with clean water and shall be distinctly damp when the grout is poured.] Anchored terra cotta or ceramic units not less than 1 inch (25.4 mm) thick shall be anchored directly to masonry, concrete or stud construction. Terra cotta or ceramic unit anchorage shall be engineered to transfer loads to stable backup walls utilizing not less than two non-corrosive anchors per unit.

1405.10 Adhered masonry veneer.  Adhered masonry veneer shall comply with the applicable requirements in [Section 1405.10.1] this section and Sections [6.1] 12.1 and [6.3] 12.3 of TMS 402[/ACI 530/ASCE 5], as modified by Chapter 21 of this code.

1405.10.1 Exterior adhered masonry veneer.  Exterior adhered masonry veneer shall be installed in accordance with the manufacturer’s instructions and Section 1405.10 of this code.

1405.10.1.1 Water-resistive barriers.  Water-resistive barriers shall be installed as required in Section 2510.6.

1405.10.1.2 Flashing.  Flashing shall comply with this section and the applicable requirements of Section 1405.4.

1405.10.1.2.1 Flashing at foundation.  A corrosion-resistant screed or flashing of a minimum 0.019-inch (0.48 mm) or 26 gage galvanized or plastic with a minimum vertical attachment flange of 3½ inches (89 mm) shall be installed to extend not less than 1 inch (25 mm) below the foundation plate line on exterior stud walls in accordance with Section 1405.4. The water-resistive barrier shall lap over the exterior of the attachment flange of the screed or flashing.

1405.10.1.3 Clearances.  On exterior stud walls, adhered masonry veneer shall be installed not less than 4 inches (102 mm) above the earth, or not less than 2 inches (51 mm) above paved areas, or not less than ½ inch (12.7 mm) above exterior walking surfaces that are supported by the same foundation that supports the exterior wall.

1405.10.1.4 Adhered masonry veneer installed with lath and mortar.  Exterior adhered masonry veneer installed with lath and mortar shall comply with the following.

1405.10.1.4.1 Lathing.  Lathing shall comply with the requirements of Section 2510.

1405.10.1.4.2 Scratch coat.  A nominal ½-inch-thick (12.7 mm) layer of mortar complying with the material requirements of Sections 2103 and 2512.2 shall be applied, encapsulating the lathing. The surface of this mortar shall be scored horizontally, resulting in a scratch coat.

1405.10.1.4.3 Adhering veneer.  The masonry veneer units shall be adhered to the mortar scratch coat with a nominal ½-inch-thick (12.7 mm) setting bed of mortar complying with Sections 2103 and 2512.2 applied to create a full setting bed for the back of the masonry veneer units. The masonry veneer units shall be worked into the setting bed resulting in a nominal ⅜-inch (9.5 mm) setting bed after the masonry veneer units are applied.

1405.10.1.5 Adhered masonry veneer applied directly to masonry and concrete.  Adhered masonry veneer applied directly to masonry or concrete shall comply with the applicable requirements of Section 1405.10, and with the requirements of Section 1405.10.1.4 or 2510.7.

1405.10.1.6 Cold weather construction.  Cold weather construction of adhered masonry veneer shall comply with the requirements of Sections 2104 and 2512.4.

1405.10.1.7 Hot weather construction.  Hot weather construction of adhered masonry veneer shall comply with the requirements of Section 2104.

1405.10.2 Exterior adhered masonry veneers—porcelain tile.  Adhered units shall not exceed ⅝ inch (15.8 mm) thickness and 24 inches (610 mm) in any face dimension nor more than 3 square feet (0.28 m2) in total face area and shall not weigh more than 9 pounds psf (0.43 kN/m2). Porcelain tile shall be adhered to an approved backing system.

1405.10.3 Interior adhered masonry veneers.  Interior adhered masonry veneers shall have a maximum weight of 20 psf (0.958 kg/m2) and shall be installed in accordance with Section 1405.10. [Where the interior adhered masonry veneer is supported by wood construction, the] The supporting members shall be designed to limit deflection to 1/600 of the span of the supporting members.

1405.11 Metal veneers.  Veneers of metal shall be fabricated from approved corrosion-resistant materials or shall be protected front and back with porcelain enamel, or otherwise be treated to render the metal resistant to corrosion. Such veneers shall be not [be] less than 0.0149-inch (0.378 mm) nominal thickness sheet steel mounted on wood or metal furring strips or approved sheathing on [the wood] light-frame construction.

1405.11.1 Attachment.  Exterior metal veneer shall be securely attached to the supporting masonry or framing members with corrosion-resistant fastenings, metal ties or by other approved devices or methods. The spacing of the fastenings or ties shall not exceed 24 inches (610 mm) either vertically or horizontally, but where units exceed 4 square feet (0.4 m2) in area there shall be not less than four attachments per unit. The metal attachments shall have a cross-sectional area not less than provided by W 1.7 wire. Such attachments and their supports shall be [capable of resisting a horizontal force in accordance with  the wind loads specified in Section 1609, but in no case less than 20 psf (0.958 kg/m2)] designed and constructed to resist the wind loads as specified in Section 1609 for components and cladding.

1405.11.2 Weather protection.  Metal supports for exterior metal veneer shall be protected by painting, galvanizing or by other approved coating or treatment. Wood studs, furring strips or other wood supports for exterior metal veneer shall be approved pressure-treated wood or protected as required in Section 1403.2. Joints and edges exposed to the weather shall be caulked with approved durable waterproofing material or by other approved means to prevent penetration of moisture.

1405.11.3 Backup.  Masonry backup shall not be required for metal veneer [except as is necessary to meet] unless required by the fire-resistance requirements of this code.

1405.11.4 Grounding.  Grounding of metal veneers on buildings shall comply with the requirements of [Chapter 27 and the New York City Electrical Code] the New York City Electrical Code and Chapter 27 of this code.

1405.12 Thin exterior structural glass veneer.  The area of a single section of thin exterior structural glass veneer shall not exceed 10 square feet (0.93 m2) where [it] that section is not more than 15 feet (4572 mm) above the level of the sidewalk or grade level directly below, and shall not exceed 6 square feet (0.56 m2) where it is more than 15 feet (4572 mm) above that level. In no event shall thin exterior structural glass veneer be installed more than 35 feet (10 668 mm) above the level of the sidewalk or grade level directly below.

1405.12.1 Length and height.  The length or height of any section of thin exterior structural glass veneer shall not exceed 48 inches (1219 mm).

1405.12.2 Thickness.  The thickness of thin exterior structural glass veneer shall be not less than 0.344 inch (8.7 mm).

1405.12.3 Application.  Thin exterior structural glass veneer shall be set only after backing is thoroughly dry and after application of an approved bond coat uniformly over the entire surface of the backing so as to effectively seal the surface. Glass shall be set in place with an approved mastic cement in sufficient quantity so that at least 50 percent of the area of each glass unit is directly bonded to the backing by mastic not less than ¼ inch (6.4 mm) thick and not more than ⅝ inch (15.9 mm) thick. The bond coat and mastic shall be evaluated for compatibility and shall bond firmly together.

1405.12.4 Installation at sidewalk level.  Where thin exterior structural glass veneer extends to a sidewalk surface, each section shall rest in an approved metal molding, and be set at least ¼ inch (6.4 mm) above the highest point of the sidewalk. The space between the molding and the sidewalk shall be thoroughly caulked and made water tight.

1405.12.4.1 Installation above sidewalk level.  Where thin exterior structural glass veneer is installed above the level of the top of a bulkhead facing, or at a level more than 36 inches (914 mm) above the sidewalk level, the mastic cement binding shall be supplemented with approved nonferrous metal shelf angles located in the horizontal joints in every course. Such shelf angles shall be not less than 0.0478-inch ([1.21] 1.2 mm) thick and not less than 2 inches (51 mm) long and shall be spaced at approved intervals, with not less than two angles for each glass unit. Shelf angles shall be secured to the wall or backing with expansion bolts, toggle bolts or by other approved methods.

1405.12.5 Joints.  Unless otherwise specifically approved by the commissioner, abutting edges of thin exterior structural glass veneer shall be ground square. Mitered joints shall not be used except where specifically approved for wide angles. Joints shall be uniformly buttered with an approved jointing compound and horizontal joints shall be held to not less than 0.063 inch (1.6 mm) by an approved nonrigid substance or device. Where thin exterior structural glass veneer abuts nonresilient material at sides or top, expansion joints not less than ¼ inch (6.4 mm) wide shall be provided.

1405.12.6 Mechanical fastenings.  Thin exterior structural glass veneer installed above the level of the heads of show windows and veneer installed more than 12 feet (3658 mm) above sidewalk level shall, in addition to the mastic cement and shelf angles, be held in place by the use of fastenings at each vertical or horizontal edge, or at the four corners of each glass unit. Fastenings shall be secured to the wall or backing with expansion bolts, toggle bolts or by other methods. Fastenings shall be so designed as to hold the glass veneer in a vertical plane independent of the mastic cement. Shelf angles providing both support and fastenings shall be permitted.

1405.12.7 Flashing.  Exposed edges of thin exterior structural glass veneer shall be flashed with overlapping corrosion-resistant metal flashing or equivalent and caulked with a waterproof compound in a manner to effectively prevent the entrance of moisture between the glass veneer and the backing.

1405.13 Exterior windows and doors.  Windows and doors installed in exterior walls shall conform to the testing and performance requirements of Section [1715.5] 1709.5.

1405.13.1 Installation.  Windows and doors shall be installed in accordance with [approved] the manufacturer’s instructions. Fastener size and spacing shall be provided in such instructions and shall be calculated based on maximum loads and spacing used in the tests.

1405.13.2 Windows in Group R-2 and R-3 occupancies. Windows in Group R-2 and R-3 occupancies shall comply with Sections 1015.9 and 1015.8, respectively.

[1405.13.2 Window sills in R-3 occupancy. In Occupancy Group R-3, one- and two-family dwellings, where the opening of the sill portion of an operable window is located more than 72 inches (1829 mm) above the finished grade or other surface below, the lowest part of the clear opening of the window shall be at a height not less than 24 inches (610 mm) above the finished floor surface of the room in which the window is located. Glazing between the floor and a height of 24 inches (610 mm) shall be fixed or have openings through which a 4-inch (102 mm) diameter sphere cannot pass.]

[Exception: Openings that are provided with window guards that comply with ASTM F 2090.]

[1405.13.3 Windows in R-2 occupancy. Windows in R-2 occupancy shall be subject to any applicable requirements of the New York City Department of Health and Mental Hygiene with regard to window guards.]

1405.14 Vinyl siding.  Vinyl siding conforming to the requirements of this section and complying with ASTM D 3679 shall be permitted on exterior walls of buildings located in areas where the [basic wind speed specified in Chapter 16] allowable stress design speed Vasd, as determined in accordance with Section 1609.3.1, does not exceed 100 miles per hour (45 m/s) and the building height is less than or equal to 40 feet (12 192 mm) in Exposure C. Where construction is located in areas where the [basic wind speed] allowable stress design speed Vasd, as determined in accordance with Section 1609.3.1, exceeds 100 miles per hour [45 m/s] (45 m/s), or building heights are in excess of 40 feet (12 192 mm), tests or calculations [indicating] showing compliance with Chapter 16 shall be submitted. Vinyl siding shall be secured to the building so as to provide weather protection for the exterior walls of the building.

1405.14.1 Application.  The siding shall be applied over sheathing or materials listed in Section 2304.6. Siding shall be applied to conform [with] to the water-resistive barrier requirements in Section 1403. Siding and accessories shall be installed in accordance with [approved] the manufacturer’s instructions. Unless otherwise specified in the [approved] manufacturer’s instructions, nails used to fasten the siding and accessories shall have a minimum 0.313-inch (7.9 mm) head diameter and ⅛-inch (3.18 mm) shank diameter. The nails shall be corrosion resistant and shall be long enough to penetrate the studs or nailing strip at least ¾ inch (19 mm). For cold-formed steel light-frame construction, corrosion-resistant fasteners shall be used. Screw fasteners shall penetrate the cold-formed steel framing at least three exposed threads. Other fasteners shall be installed in accordance with the manufacturer’s instructions. Where the siding is installed horizontally, the fastener spacing shall not exceed 16 inches (406 mm) horizontally and 12 inches (305 mm) vertically. Where the siding is installed vertically, the fastener spacing shall not exceed 12 inches (305 mm) horizontally and 12 inches (305 mm) vertically.

1405.15 Cement plaster.  Cement plaster applied to exterior walls shall conform to the requirements specified in Chapter 25.

1405.16 [Fiber cement] Fiber-cement siding.  [Fiber cement] Fiber-cement siding complying with Section 1404.10 shall be permitted on exterior walls of Type I, II, III, IV and V construction for wind pressure resistance or wind speed exposures as indicated by the manufacturer’s listing and label, and [approved] the installation instructions. Where specified, the siding shall be installed over sheathing or materials listed in Section 2304.6 and shall be installed to conform to the water-resistive barrier requirements in Section 1403. Siding and accessories shall be installed in accordance with [approved] the manufacturer’s instructions. Unless otherwise specified in the [approved] manufacturer’s instructions, nails used to fasten the siding to wood studs shall be corrosion-resistant round head smooth shank and shall be long enough to penetrate the studs at least 1 inch (25 mm). [For metal framing, all-weather screws shall be used and shall penetrate the metal] For cold-formed steel light-frame construction, corrosion-resistant fasteners shall be used. Screw fasteners shall penetrate the cold-formed steel framing at least three exposed full threads. Other fasteners shall be installed in accordance with the manufacturer’s instructions.

1405.16.1 Panel siding.  Fiber-cement panels shall comply with the requirements of ASTM C 1186, Type A, minimum Grade II or ISO 8336, Category A, minimum Class 2. Panels shall be installed with the long dimension either parallel or perpendicular to framing. Vertical and horizontal joints shall occur over framing members and shall be [sealed] protected with [caulking] sealant, [covered with] battens or [shall be] flashing. Alternatively, vertical or horizontal joints shall be shiplap or otherwise designed to comply with Section 1403.2. Panel siding shall be installed with fasteners in accordance with the [approved] manufacturer’s instructions.

1405.16.2 Lap siding.  Fiber-cement lap siding having a maximum width of 12 inches (305 mm) shall comply with the requirements of ASTM C 1186, Type A, minimum Grade II or ISO 8336, Category A, minimum Class 2. Lap siding shall be lapped a minimum of 1¼ inches (32 mm) and lap siding not having tongue-and-groove end joints shall have the ends [sealed] protected with caulking, covered with an H-section joint cover, located over a strip of flashing or shall be otherwise designed to comply with Section 1403.2. Lap siding courses shall be installed with the fastener heads exposed or concealed in accordance with the [approved] manufacturer’s instructions.

1405.17 Fastening.  Weather boarding and wall coverings shall be securely fastened with aluminum, copper, zinc, zinc-coated or other approved corrosion-resistant fasteners in accordance with the nailing schedule in Table [2304.9.1] 2304.10.1 or the [approved] manufacturer’s [installation] instructions. Shingles and other weather coverings shall be attached with appropriate [standard shingle] standard-shingle nails to furring strips securely nailed to studs, or with approved mechanically bonding nails, except where sheathing is of wood not less than 1-inch (25 mm) nominal thickness or of wood structural panels as specified in Table [2308.9.3(3)] 2308.6.3(3).

1405.18 Polypropylene siding.  Polypropylene siding conforming to the requirements of this section and complying with Section 1404.12 shall be limited to exterior walls of Type VB construction located in areas where the wind speed specified in Chapter 16 does not exceed 100 miles per hour (45 m/s) and the building height is less than or equal to 40 feet (12 192 mm) in Exposure C. Where construction is located in areas where the basic wind speed exceeds 100 miles per hour (45 m/s), or building heights are in excess of 40 feet (12 192 mm), tests or calculations showing compliance with Chapter 16 shall be submitted. Polypropylene siding shall be installed in accordance with the manufacturer’s instructions. Polypropylene siding shall be secured to the building so as to provide weather protection for the exterior walls of the building.

SECTION BC 1406
COMBUSTIBLE MATERIALS ON THE EXTERIOR
SIDE OF EXTERIOR WALLS

1406.1 General. Section 1406 shall apply to exterior wall coverings, exterior balconies and similar projections, bay and oriel windows, decks, porches, porticos, entranceways, and storm enclosures constructed of combustible materials. Combustible water-resistive barriers complying with Section 1403.5.1 shall be permitted in exterior wall coverings. Fireblocking shall be installed in accordance with Section 1406.2.3. Existing building retrofits utilizing combustible exterior wall coverings shall also comply with Section 1406.5. Combustible exterior wall coverings shall be subject to the special inspection requirements of Section 1705.16.

1406.2 Combustible exterior wall coverings. Combustible exterior wall coverings, including architectural trim, shall comply with this section.

[Exception:] Exceptions:

1.	Plastics complying with Chapter 26.

2.	Metal composite materials (MCM) complying with Section 1407.

3.	High-pressure decorative exterior-grade compact laminates (HPL) complying with Section 1409.

1406.2.1 Type I, II, III and IV construction. In buildings of Type I, II, III and IV construction, exterior wall coverings shall be permitted to be constructed of combustible materials in accordance with Section 1406.2.1.1, subject to the following limitations:

1.	Combustible exterior wall coverings shall not exceed 10 percent of an exterior wall surface area on any given story. Such combustible exterior wall covering shall not be permitted on exterior walls where the fire separation distance is 5 feet (1524 mm) or less.

2.	Combustible exterior wall coverings shall be limited to 40 feet (12 192 mm) in height above grade plane.

3.	Combustible exterior wall coverings constructed of fire‐retardant‐treated wood complying with Section 2303.2 for exterior installation shall not be limited in wall surface area where the fire separation distance is 5 feet (1524 mm) or less and shall be permitted up to 60 feet (18 288 mm) in height above grade plane, regardless of the fire separation distance.

4.	Wood veneers shall comply with Section 1405.5.

5.	Combustible exterior wall coverings shall not be permitted on buildings of Type IV construction utilizing cross-laminated timber (CLT) or structural composite lumber (SCL) complying with Section 602.4.

6.	Combustible exterior wall coverings shall not be permitted at exterior balconies in accordance with Section 1406.3.

[1406.2.1] 1406.2.1.1 Ignition resistance. [Combustible] Where permitted by Section 1406.2.1, combustible exterior wall coverings shall be tested in accordance with NFPA 268.

Exceptions: The following materials are not required to be tested in accordance with NFPA 268. However, such materials shall comply with all other provisions of Section 1406.

1.	Wood or wood-based products.

2.	Other combustible materials covered with an exterior weather covering other than vinyl sidings [listed in,] included in and complying with the thickness requirements of Table 1405.2.

3.	Aluminum having a minimum thickness of 0.019 inch (0.48 mm).

[4.	Exterior wall coverings on exterior walls of Type V construction.]

[1406.2.1.1] 1406.2.1.1.1 Fire separation 5 feet or less. Where installed on exterior walls having a fire separation distance of 5 feet (1524 mm) or less, combustible exterior wall coverings shall not exhibit sustained flaming as defined in NFPA 268.

[1406.2.1.2] 1406.2.1.1.2 Fire separation greater than 5 feet. For fire separation distances greater than 5 feet (1524 mm), [an assembly] any exterior wall covering shall be permitted that has been exposed to a reduced level of incident radiant heat flux in accordance with the NFPA 268 test method without exhibiting sustained flaming. The minimum fire separation distance required for the [assembly] exterior wall covering shall be determined from Table [1406.2.1.2] 1406.2.1.1.2 based on the maximum tolerable level of incident radiant heat flux that does not cause sustained flaming of the [assembly] exterior wall covering.

| TABLE [1406.2.1.2] 1406.2.1.1.2 MINIMUM FIRE SEPARATION FOR COMBUSTIBLE [VENEERS] EXTERIOR WALL COVERINGS |
| --- |
| FIRE SEPARATION DISTANCE (feet) | TOLERABLE LEVEL INCIDENT RADIANT HEAT ENERGY (kW/m2) | FIRE SEPARATION DISTANCE (feet) | TOLERABLE LEVEL INCIDENT RADIANT HEAT ENERGY (kW/m2) |
| 5 | 12.5 | 16 | 5.9 |
| 6 | 11.8 | 17 | 5.5 |
| 7 | 11.0 | 18 | 5.2 |
| 8 | 10.3 | 9 | 4.9 |
| 9 | 9.6 | 20 | 4.6 |
| 10 | 8.9 | 21 | 4.4 |
| 11 | 8.3 | 22 | 4.1 |
| 12 | 7.7 | 23 | 3.9 |
| 13 | 7.2 | 24 | 3.7 |
| 14 | 6.7 | 25 | 3.5 |
| 15 | 6.3 |  |  |

For SI: 1 foot = 304.8 mm, 1 Btu/H2 ×°F = [.0057] 0.0057 kW/m2 × K.

[1406.2.2 Type I, II, III and IV construction. In buildings of Type I, II, III and IV construction, exterior wall coverings shall be permitted to be constructed of combustible materials in accordance with Section 1406.2.1 and with the following limitations.]

[1.	Combustible exterior wall coverings shall not exceed 10 percent of the exterior wall surface area on any given story. Such combustible exterior wall coverings shall not be permitted on exterior walls where the fire separation distance is 5 feet (1524 mm) or less.]

[2.	Combustible wall coverings shall be limited to 40 feet (12 192 mm) in height above grade plane.]

[3.	Combustible exterior wall coverings constructed of fire-retardant-treated wood complying with Section 2303.2 for exterior installation shall not be limited in wall surface area where the fire separation distance is 5 feet (1524 mm) or less and shall be permitted up to 60 feet (18 288 mm) in height above grade plane regardless of the fire separation distance.]

[1406.2.3] 1406.2.2 Location. [Where combustible] Combustible exterior wall [covering is] coverings located along the top of exterior walls[, such trim] shall be completely backed up by the exterior wall and shall not extend over or above the top of the exterior walls.

[1406.2.4] 1406.2.3 Fireblocking. [Where the combustible exterior wall covering is furred from the wall and forms a solid surface, the distance between the back of the covering and the wall shall not exceed 15/8 inches (41 mm). Where required by Section 717, the space thereby created shall be fireblocked.] Exterior wall coverings shall be fireblocked in accordance with Section 718.2.6.

1406.3 Exterior balconies and similar projections. [Exterior balconies and similar projections shall be permitted to be constructed of combustible materials provided that the exterior balcony or similar projection affords the fire-resistance rating required by Table 601 for floor construction.] Exterior wall covering on walls abutting balconies, and cladding on the sides and underside of balconies, shall be constructed of noncombustible materials. Exterior walls abutting balconies shall be noncombustible up to 12 feet (3658 mm) above the walking surface or to the underside of the balcony above, whichever is less. On cantilevered balconies, the exterior wall abutting the balcony, plus 3 feet (914 mm) on each side, shall be constructed of noncombustible materials. On recessed and semi-recessed balconies, the exterior walls abutting the balconies shall be constructed of noncombustible materials.

[Exceptions:]

[1.	Balconies or similar projections serving as a required exit shall not be constructed of combustible materials.]

[2.	Balconies or similar projections on the exterior of buildings of Type I or II construction shall not be constructed of combustible materials.]

Exception: Combustible exterior wall coverings shall be allowed on balconies in Type V construction with a fire separation distance greater than or equal to 5 feet (1524 mm).

1406.4 Bay and oriel windows, decks, porches, porticos, entranceways, and storm enclosures. Bay and oriel windows, decks, porches, porticos, entranceways and storm enclosures shall conform to the type of construction required for the building to which they are attached, including required fire rating, unless otherwise modified by the requirements of this section. For the purposes of this section, such structures shall be referred to as, “appendages.”

Exception: Plastic complying with Chapter 26.

1406.4.1 Appendages on Type I and II construction. Appendages on buildings of Type I or II construction shall be constructed of noncombustible materials. However, on buildings not more than three stories or 40 feet (12 192 mm) in height, whichever is less, fire-retardant-treated wood shall be permitted.

1406.4.2 Appendages on Type III, IV and VA construction. Appendages on buildings of Type III, IV and VA construction may be constructed of combustible materials, provided that all the following conditions are met:

- Such building does not exceed 3 stories or 40 feet (12 192 mm) in height, whichever is less.

- The main use or dominant occupancy of such building is classified in Occupancy Group R-2 or R-3.

- The appendage has an exterior separation on all exposed sides of at least 15 feet (4572 mm), measured from the outermost surface of the appendage, except that appendages with exposed sides protected by minimum 1-hour fire-rated construction extending at least 36 inches (914 mm) above the highest combustible horizontal surface may be located up to a minimum distance of 36 inches (914 mm) from any property line.

- The appendage is so constructed that its removal or destruction will not reduce the structural stability or fire-resistive integrity of the building.

- The appendage has a superficial area not exceeding 150 square feet (13.9 m2) when viewed from directly above and is included in the area limitations of Table 503 for the entire building.

- The appendage is not higher than the sills of the second-story windows.

- The vertical surface area of the combustible portions of the appendage does not exceed 10 percent of the total wall area (windows excluded) of the building.

- For enclosed appendages, the roof of the appendage has a class A roof covering, and the soffit or ceiling covering the combustible roof framing shall have a minimum 1-hour fire-resistance rating.

Exception: Appendages constructed of fire-retardant-treated wood, on buildings not exceeding 3 stories or 40 feet (12 192 mm) in height, whichever is less, need not comply with Items 2 through 8.

1406.4.3 Appendages on Type VB construction. Appendages may be constructed of combustible materials on buildings of construction Type VB.

1406.5 Retrofit of existing buildings. Combustible materials shall not be permitted for use at the outermost surface of the exterior wall covering for exterior envelope retrofits of existing nonsprinklered buildings over 75 feet (22 860 mm), unless the following conditions are satisfied:

1.	The outermost surface of the combustible exterior wall covering shall be interrupted by a noncombustible material at least 3 feet (914 mm) high between the top of one opening and the bottom of the opening immediately above to form a continuous band across building elevations.

2.	On walls without openings, a 3 feet (914 mm) high noncombustible band shall interrupt the outermost surface of the combustible exterior wall covering at least every 15 feet (4572 mm) vertically.

SECTION BC 1407
METAL COMPOSITE MATERIALS (MCM)

1407.1 General. The provisions of this section shall govern the materials, construction and quality of metal composite materials (MCM) for use as exterior wall coverings in addition to other applicable requirements of Chapters 14 and 16.

1407.1.1 Plastic core. The plastic core of the MCM shall not contain foam plastic insulation as defined in Section [2602.1] 202.

1407.1.2 Prohibited locations. The use of MCM in exterior wall coverings is subject to the following limitations:

1.	MCM is prohibited in exterior wall coverings in Type IV construction utilizing cross-laminated timer (CLT) or structural composite lumber (SCL) complying with Section 602.4.

2.	MCM is prohibited in exterior wall coverings at exterior balconies and shall comply with Section 1406.3.

1407.2 Exterior wall finish. MCM used as exterior wall finish or as elements of [balconies and similar appendages and] bay and oriel windows to provide cladding or weather resistance shall comply with Sections 1407.4 through [1407.14] 1407.16.

1407.3 Architectural trim and embellishments. MCM used as architectural trim or embellishments shall comply with Sections 1407.7 through 1407.14.

1407.4 Structural design. MCM systems shall be designed and constructed to resist wind loads as required by Chapter 16 for components and cladding.

1407.5 Approval. Results of approved tests or an engineering analysis shall be submitted to the commissioner to verify compliance with the requirements of Chapter 16 for wind loads.

1407.6 Weather resistance. MCM systems shall comply with Section 1403 and shall be designed and constructed to resist wind and rain in accordance with this section and the manufacturer’s installation instructions.

1407.7 Durability. MCM systems shall be constructed of approved materials that maintain the performance characteristics required in Section 1407 for the duration of use.

1407.8 Fire-resistance rating. Where MCM systems are used on exterior walls required to have a fire-resistance rating in accordance with Section 705, evidence shall be submitted to the commissioner that the required fire-resistance rating is maintained.

Exception: MCM systems not containing foam plastic insulation, which are installed on the outer surface of a fire-resistance-rated exterior wall in a manner such that the attachments do not penetrate through the entire exterior wall assembly, shall not be required to comply with this section.

1407.9 [Surface-burning characteristics. Unless otherwise specified, MCM shall have a flame spread index of 75 or less and a smoke-developed index of 450 or less when tested in the maximum thickness intended for use in accordance with ASTM E 84 or UL 723.]

[1407.10 Type I, II, III and IV construction. Where installed on buildings of Type I, II, III and IV construction, MCM systems shall comply with Sections 1407.10.1 through 1407.10.3, or Section 1407.11.]

[1407.10.1] Surface-burning characteristics. MCM shall have a flame spread index of not more than 25 and a smoke-developed index of not more than 450 when tested as an assembly in the maximum thickness intended for use in accordance with ASTM E 84 or UL 723.

[1407.10.2] 1407.10 Thermal barriers. MCM shall be separated from the interior of a building by an approved thermal barrier consisting of [1/2-inch (12.7 mm)] 5/8-inch (15.9 mm) Type X gypsum wallboard or equivalent thermal barrier material that will limit the average temperature rise of the unexposed surface to not more than 250°F (121°C) after [15] 20 minutes of fire exposure in accordance with the standard time-temperature curve of ASTM E 119 or UL 263. The thermal barrier shall be installed in [such a manner that it will remain in place for not less than 15 minutes based on a test conducted] accordance with criteria established by testing in accordance with UL 1715, where the thermal barrier shall remain in place for 20 minutes.

[Exceptions:]

[1.	The thermal barrier is not required where the MCM system is specifically approved based on tests conducted in accordance with UL 1040 or UL 1715. Such testing shall be performed with the MCM in the maximum thickness intended for use. The MCM system shall include seams, joints and other typical details used in the installation and shall be tested in the manner intended for use.]

[2.	The thermal barrier is not required where the MCM is used as elements of balconies and similar appendages, architectural trim or embellishments.]

[1407.10.3] 1407.11 Full-scale tests. [The] All MCM [system] systems shall be tested in accordance with, and comply with, the acceptance criteria of NFPA 285. Such testing shall be performed on the MCM system with the MCM in the maximum thickness intended for use, including any required fireblocking. Approved NFPA 285 tested assembly design documentation of the MCM system shall be included on the submitted construction documents complying with Section 1401.2. Deviation from the NFPA 285 tested design shall be approved by the registered design professional and additional documentation shall be provided if requested by the department.

[1407.11 Alternate conditions. MCM and MCM systems shall not be required to comply with Sections 1407.10.1 through 1407.10.3 provided such systems comply with Section 1407.11.1 or 1407.11.2.]

[1407.11.1 Installations up to 40 feet in height. MCM shall be permitted to be installed no more than 40 feet (12 190 mm) in height above grade provided the MCM is installed in accordance with Sections 1407.11.1.1 and 1407.11.1.2.]

[1407.11.1.1 Fire separation distance of 5 feet or less. Where the fire separation distance is 5 feet (1524 mm) or less, the area of MCM shall not exceed 10 percent of the exterior wall surface.]

[1407.11.1.2 Fire separation distance greater than 5 feet. Where the fire separation distance is greater than 5 feet (1524 mm), there shall be no limit on the area of exterior wall surface coverage using MCM.]

[1407.11.2 Installations up to 50 feet in height. MCM shall be permitted to be installed no more than 50 feet (15 240 mm) in height above grade provided the MCM meets the requirements of Sections 1407.11.2.1 and 1407.11.2.2.]

[1407.11.2.1 Self ignition temperature. MCM shall have a self-ignition temperature of 650°F (343°C) or greater when tested in accordance with ASTM D 1929.]

[1407.11.2.2 Limitations. Sections of MCM shall not exceed 300 square feet (27.9 m2) in area and shall be separated by a minimum of 4 feet (1219 mm) vertically.]

1407.12 [Type V construction. MCM shall be permitted to be installed on buildings of Type V construction.] Reserved.

1407.13 Foam plastic insulation. MCM systems containing foam plastic insulation shall also comply with the requirements of Section 2603.

1407.14 Labeling. MCM shall be labeled in accordance with [Chapter 17] this code and Section 28-113 of the Administrative Code.

1407.15 Special inspection. MCM shall be subject to special inspection in accordance with Chapter 17.

1407.16 Fireblocking. MCM installations shall be fireblocked in accordance with Section 718.2.6.1.

SECTION BC 1408
EXTERIOR INSULATION AND FINISH SYSTEMS (EIFS)

1408.1 General. The provisions of this section shall govern the materials, construction and quality of exterior insulation and finish systems (EIFS) for use as exterior wall coverings in addition to other applicable requirements of Chapters 7, 14, 16, 17 and 26.

1408.1.1 Prohibited locations. The use of EIFS containing foam plastic insulation in exterior wall coverings is subject to the following limitations:

1.	EIFS containing foam plastic insulation is prohibited in exterior wall coverings in Type IV construction utilizing cross-laminated timer (CLT) or structural composite lumber (SCL) complying with Section 602.4.

2.	EIFS containing foam plastic insulation is prohibited in exterior wall coverings at exterior balconies and shall comply with Section 1406.3.

1408.2 Performance characteristics. EIFS shall be constructed such that it meets the performance characteristics required in ASTM E 2568.

1408.3 Structural design. The underlying structural framing and substrate shall be designed and constructed to resist loads as required by Chapter 16.

1408.4 Weather resistance. EIFS shall comply with Section 1403 and shall be designed and constructed to resist [wind and rain in accordance with this section and the manufacturer’s application instructions] environmental conditions in accordance with this section, the approved construction documents and manufacturer’s installation instructions.

1408.4.1 EIFS with drainage. EIFS with drainage shall have an average minimum drainage efficiency of 90 percent when tested in accordance with requirements of ASTM E 2273 and is required on framed walls of Type V construction, residential Group R occupancies.

1408.4.1.1 Water-resistive barrier. For EIFS with drainage, the water-resistive barrier shall comply with Section 1404.2 or ASTM E 2570.

1408.5 Installation. Installation of the EIFS and EIFS with drainage shall be in accordance with the EIFS manufacturer’s instructions and this section.

1408.6 Special inspections. EIFS installations shall comply with the provisions of Chapter 17.

1408.7 Fireblocking. EIFS installations containing foam plastic insulation shall be fireblocked in accordance with Section 718.2.6.1.

1408.8 Foam plastic insulation.  EIFS installations containing foam plastic insulation shall be tested and comply with the requirements of Section 2603.

1408.9 Thermal barrier. EIFS installations containing foam plastic insulation shall be separated from the interior of a building in accordance with Section 2603.5.2.

SECTION BC 1409
HIGH-PRESSURE DECORATIVE
EXTERIOR-GRADE COMPACT LAMINATES (HPL)

1409.1 General.  The provisions of this section shall govern the materials, construction and quality of High-Pressure Decorative Exterior-Grade Compact Laminates (HPL) for use as exterior wall coverings in addition to other applicable requirements of Chapters 14 and 16.

1409.1.1 Prohibited locations. The use of HPL in exterior wall coverings is subject to the following limitations:

1.	HPL is prohibited in exterior wall coverings in Type IV construction utilizing cross-laminated timer (CLT) or structural composite lumber (SCL) complying with Section 602.4.

2.	HPL is prohibited in exterior wall coverings at exterior balconies and shall comply with Section 1406.3.

1409.2 Exterior wall finish.  HPL used as exterior wall covering or as elements of bay and oriel windows to provide cladding or weather resistance shall comply with Sections 1409.4 through 1409.16.

1409.3 Architectural trim and embellishments. HPL used as architectural trim or embellishments shall comply with Sections 1409.7 through 1409.14.

1409.4 Structural design.  HPL systems shall be designed and constructed to resist wind loads as required by Chapter 16 for components and cladding.

1409.5 Approval.  Results of approved tests or an engineering analysis shall be submitted to the commissioner to verify compliance with the requirements of Chapter 16 for wind loads.

1409.6 Weather resistance.  HPL systems shall comply with Section 1403 and shall be designed and constructed to resist wind and rain in accordance with this section and the manufacturer’s instructions.

1409.7 Durability.  HPL systems shall be constructed of approved materials that maintain the performance characteristics required in Section 1409 for the duration of use.

1409.8 Fire-resistance rating.  Where HPL systems are used on exterior walls required to have a fire-resistance rating in accordance with Section 705, evidence shall be submitted to the commissioner that the required fire-resistance rating is maintained.

Exception: HPL systems not containing foam plastic insulation that are installed on the outer surface of a fire-resistance-rated exterior wall in a manner such that the attachments do not penetrate through the entire exterior wall assembly, shall not be required to comply with this section.

1409.9 Surface-burning characteristics. HPL shall have a flame spread index of not more than 25 and a smoke-developed index of not more than 450 when tested in the minimum and maximum thicknesses intended for use in accordance with ASTM E 84 or UL 723.

1409.10 Thermal barriers.  HPL shall be separated from the interior of a building by an approved thermal barrier consisting of 5/8-inch (15.9 mm) Type X gypsum wallboard or equivalent thermal barrier material that will limit the average temperature rise of the unexposed surface to not more than 250°F (121°C) after 20 minutes of fire exposure in accordance with the standard time temperature curve of ASTM E 119 or UL 263. The thermal barrier shall be installed in accordance with criteria established by testing performed in accordance with UL 1715, where the thermal barrier shall remain in place for 20 minutes.

1409.11 Full-scale tests.  All HPL systems shall be tested in accordance with, and comply with, the acceptance criteria of NFPA 285. Such testing shall be performed on the HPL system with the HPL in the minimum and maximum thicknesses intended for use, including any required fireblocking. Approved NFPA 285 tested assembly design documentation of the HPL system shall be included on the submitted construction documents complying with Section 1401.2. Deviation from the NFPA 285 tested design shall be approved by the registered design professional and additional documentation shall be provided if requested by the department.

1409.12 Reserved.

1409.13 Foam plastic insulation.  HPL systems containing foam plastic insulation shall also comply with the requirements of Section 2603.

1409.14 Labeling.  HPL shall be labeled in accordance with this code and Section 28-113 of the Administrative Code.

1409.15 Special inspection.  HPL shall be subject to the special inspection requirements of Chapter 17.

1407.16 Fireblocking. HPL installations shall be fireblocked in accordance with Section 718.2.6.1.

SECTION BC 1410
PLASTIC COMPOSITE DECKING

1410.1 Plastic composite decking.  Exterior deck boards, stair treads, handrails and guardrail systems constructed of plastic composites, including plastic lumber, shall comply with Section 2612.

§ 16. Chapter 15 of the New York city building code, as amended by local law number 141 for the year 2013, sections 1507.3.9, 1507.5.7, 1507.8.8 and 1507.9.9 as amended by local law number 51 for the year 2014, and sections 1504.9 and 1511 as amended by local law number 94 for the year 2019, is amended to read as follows:

CHAPTER 15
ROOF ASSEMBLIES AND ROOFTOP STRUCTURES

SECTION BC 1501
GENERAL

1501.1 Scope. The provisions of this chapter shall govern the design, materials, construction and quality of roof assemblies, and rooftop structures.

SECTION BC 1502
DEFINITIONS

1502.1 [General] Definitions. The following terms [shall, for the purposes of this chapter and as used elsewhere in this code, have the meanings shown herein.] are defined in Chapter 2:

AGGREGATE. [In roofing, crushed stone, crushed slag or water-worn gravel used for surfacing for roof coverings.]

BALLAST.[In roofing, ballast comes in the form of large stones or paver systems or light-weight interlocking paver systems and is used to provide uplift resistance to components of the roof assembly systems that are not adhered or mechanically attached to the roof deck.]

BUILDING-INTEGRATED PHOTOVOLTAIC (BIPV) PRODUCT.

BUILT-UP ROOF COVERING.[Two or more layers of felt cemented together and surfaced with a cap sheet, mineral aggregate, smooth coating or similar surfacing material.]

BULKHEAD.[An enclosed rooftop structure enclosing a shaft, stairway, tank or service equipment, or other space not designed or used for human occupancy.]

CONTAINER GARDEN.[A plant or plants maintained in a pot or planters that is at least 6 inches (152 mm) high and located on a roof, terrace, or other horizontal exterior area.]

GREEN ROOF SYSTEM.[A system constructed in-situ consisting of either a roof assembly and additional landscape material components, including growing media, engineered soils, filter fabric, integral drainage systems and roof surface to facilitate the growth of vegetation or a pre-vegetated tray or trays no more than 6 inches (152 mm) high and assembled on top of a roof covering.] “See definition for VEGETATIVE ROOF.”

INTERLAYMENT.[A layer of felt or nonbituminous saturated felt not less than 18 inches (457 mm) wide, shingled between each course of a wood-shake roof covering.]

MECHANICAL EQUIPMENT SCREEN.[A partially enclosed rooftop structure used to aesthetically conceal heating, ventilating and air conditioning (HVAC) electrical or mechanical equipment from view.]

METAL ROOF PANEL.[An interlocking metal sheet having a minimum installed weather exposure of 3 square feet (.279 m2) per sheet.]

METAL ROOF SHINGLE.[An interlocking metal sheet having an installed weather exposure less than 3 square feet (.279 m2) per sheet.]

MODIFIED BITUMEN ROOF COVERING.[One or more layers of polymer-modified asphalt sheets. The sheet materials shall be fully adhered or mechanically attached to the substrate or held in place with an approved ballast layer.]

PENTHOUSE.[An enclosed rooftop structure which is designed or used for human occupancy.]

PHOTOVOLTAIC MODULE.

PHOTOVOLTAIC PANEL.

PHOTOVOLTAIC PANEL SYSTEM.

PHOTOVOLTAIC SHINGLES.

POSITIVE ROOF DRAINAGE.[The drainage condition in which consideration has been made for all loading deflections of the roof deck, including ponding instability, and additional slope has been provided to ensure drainage of the roof within 48 hours of precipitation.]

RADIANT BARRIER.

REROOFING.[The process of recovering or replacing an existing roof covering. See “Roof recover” and “Roof replacement.”]

ROOF ASSEMBLY.[A system designed to provide weather protection and resistance to design loads. The system consists of a roof covering and roof deck or a single component serving as both the roof covering and the roof deck. A roof assembly includes the roof deck, substrate or thermal barrier, insulation, vapor retarder and roof covering. This definition of “Roof assembly” is limited in application to the provisions of Chapter 15.]

ROOF COVERING.[The covering applied to the roof deck for weather resistance, fire classification or appearance.]

ROOF COVERING SYSTEM.[See “Roof assembly.”]

ROOF DECK.[The flat or sloped surface not including its supporting members or vertical supports.]

ROOF RECOVER.[The process of installing an additional roof covering over a prepared existing roof covering without removing the existing roof covering.]

ROOF REPAIR.

ROOF REPLACEMENT.[The process of removing the existing roof covering, repairing any damaged substrate and installing a new roof covering.]

ROOF VENTILATION.[The natural or mechanical process of supplying conditioned or unconditioned air to, or removing such air from, attics, cathedral ceilings or other enclosed spaces over which a roof assembly is installed.]

ROOFTOP STRUCTURE.[An enclosed or unenclosed structure on or above the roof of any part of a building.]

SCUPPER.

SINGLE-PLY MEMBRANE.[A roofing membrane that is field applied using one layer of membrane material (either homogeneous or composite) rather than multiple layers.]

SUSTAINABLE ROOFING ZONE.  [Areas of a roof assembly where a solar photovoltaic electricity generating system, a green roof system, or a combination thereof, is installed.]

UNDERLAYMENT. [One or more layers of felt, sheathing paper, nonbituminous saturated felt or other approved material over which a steep-slope roof covering is applied.]

VEGETATIVE ROOF.

SECTION BC 1503
WEATHER PROTECTION

1503.1 General. Roof decks shall be covered with approved roof coverings secured to the building or structure in accordance with the provisions of this chapter. Roof coverings shall be designed and installed in accordance with this code and the [approved] manufacturer’s instructions such that the roof covering shall serve to protect the building or structure.

1503.2 Flashing. Flashing shall be installed in such a manner so as to prevent moisture entering the wall and roof through joints in copings, through moisture-permeable materials and at intersections with parapet walls and other penetrations through the roof plane.

1503.2.1 Locations. Flashing shall be installed at wall and roof intersections, at gutters, wherever there is a change in roof slope or direction and around roof openings. Where flashing is of metal, the metal shall be corrosion resistant with a thickness of not less than 0.019 inch ([.483] 0.483 mm) (No. 26 galvanized sheet).

1503.3 Coping. Parapet walls shall be properly coped with noncombustible, weatherproof materials of a width no less than the thickness of the parapet wall.

1503.4 Roof drainage. Design and installation of roof drainage systems shall comply with [this section and] Chapter 11 of the New York City Plumbing Code and this section.

1503.4.1 Secondary [drainage required] (emergency overflow) drains or scuppers. [Secondary] Where roof drains are required, secondary (emergency overflow) roof drains or scuppers shall be provided where the roof perimeter construction extends above the roof in such a manner that water will be entrapped if the primary drains allow buildup for any reason. The installation and sizing of secondary (emergency overflow) drains, leaders and conductors shall comply with Chapter 11 of the New York City Plumbing Code, as applicable.

1503.4.2 Scuppers. When scuppers are used for secondary (emergency overflow) roof drainage, the quantity, size, location and inlet elevation of the scuppers shall be sized to prevent the depth of ponding water from exceeding that for which the roof was designed as determined by Section [1503.4.1] 1611.1. Scuppers shall not have an opening dimension of less than 4 inches (102 mm). The flow through the primary system shall not be considered when locating and sizing scuppers.

1503.4.3 Gutters. Gutters [and leaders] placed on the outside of buildings shall be of noncombustible, corrosion-resistant material[, or a minimum of Schedule 40 plastic pipe] in accordance with Chapter 11 of the New York City Plumbing Code.  Gutters and vertical sections of exterior leaders shall be adequately anchored. Gutters and leaders installed more than 15 feet (4572 mm) above grade shall be designed to resist loads in accordance with Chapter 16.

1503.4.3 Gutters. Gutters [and leaders] placed on the outside of buildings shall be of noncombustible, corrosion-resistant [material, or a minimum of Schedule 40 plastic pipe] materials. Leaders placed on the outside of buildings shall be of noncombustible, corrosion-resistant materials in accordance with Chapter 11 of the New York City Plumbing Code.

[1503.4.3.1 Height limitations. Vertical sections of exterior leaders made from galvanized steel, galvanized wrought iron, cast iron, brass, or similar heavy material shall be permitted only for the first 15 feet (4572 mm) of leader extending up from grade, provided that the leader is securely anchored with offset clamps to the face of the building at no fewer than two points along the vertical section of the leader. Horizontal sections of exterior gutter made from such heavy materials shall not be permitted higher than 15 feet (4572 mm) above grade.]

1503.5 [Roof ventilation.] Attic and rafter ventilation. Intake and exhaust vents shall be provided in accordance with Section 1203.2 and the vent product’s manufacturer’s [installation] instructions.

1503.6 Crickets and saddles. A cricket or saddle shall be installed on the ridge side of any chimney or penetration greater than 30 inches (762 mm) wide as measured perpendicular to the slope. Cricket or saddle coverings shall be sheet metal or of the same material as the roof covering.

Exception: Unit skylights installed in accordance with Section 2405.5 and flashed in accordance with the manufacturer’s instructions shall be permitted to be installed without a cricket or saddle.

SECTION BC 1504
PERFORMANCE REQUIREMENTS

1504.1 Wind resistance of roofs. Roof decks and roof coverings shall be designed for wind loads in accordance with Chapter 16 and Sections 1504.2, 1504.3 and 1504.4.

1504.1.1 Wind resistance of asphalt shingles. Asphalt shingles shall [comply with Section 1507.2.] be tested in accordance with ASTM D 7158. Asphalt shingles shall meet the classification requirements of Table 1504.1.1 for the appropriate maximum wind speed. Asphalt shingle packaging shall bear a label to indicate compliance with ASTM D 7158 and the required classification in Table 1504.1.1 of this code.

Exception: Asphalt shingles that are not included in the scope of ASTM D 7158 shall be tested and labeled to indicate compliance with ASTM D 3161 and the required classification in Table 1504.1.1 of this code.

| TABLE 1504.1.1 CLASSIFICATION OF ASPHALT SHINGLES |
| --- |
| MAXIMUM ALLOWABLE STRESS DESIGN WIND SPEED, Vasd | MAXIMUM BASIC DESIGN WIND SPEED, V, FROM TABLE 1609.3 | ASTM D 7158a CLASSIFICATION | ASTM D 3161 CLASSIFICATION |
| 88 | 110 | D, G or H | A, D or F |
| 94 | 117 | G or H | A, D or F |
| 102 | 127 | G or H | F |
| 106 | 132 | G or H | F |

1504.2 Wind resistance of clay and concrete tile. Wind loads on clay and concrete tile roof coverings shall be in accordance with Section 1609.

1504.2.1 Testing. Testing of concrete and clay roof tiles shall be in accordance with Sections 1504.2.1.1 and 1504.2.1.2.

1504.2.1.1 Overturning resistance. Concrete and clay roof tiles shall be tested to determine their resistance to overturning due to wind in accordance with SBCCI SSTD 11 and this chapter.

1504.2.1.2 Wind tunnel testing. Where concrete and clay roof tiles do not satisfy the limitations in Chapter 16 of this code for rigid tile, a wind tunnel test shall be used to determine the wind characteristics of the concrete or clay tile roof covering in accordance with SBCCI SSTD 11 and this chapter.

1504.3 Wind resistance of nonballasted roofs. Roof coverings installed on roofs in accordance with Section 1507 that are mechanically attached or adhered to the roof deck shall be designed to resist the design wind load pressures for components and cladding in accordance with Section 1609.

1504.3.1 Other roof systems. [Roof systems with built-up] Built-up, modified bitumen, fully adhered or mechanically attached single-ply [through fastened] roof systems, metal panel roof systems[,] applied to a solid or closely fitted deck and other types of membrane roof coverings shall [also] be tested in accordance with FM 4474, UL 580 or UL 1897.

1504.3.2 [Metal panel roof systems.] Structural metal panel roof systems. [Metal panel roof systems through fastened or standing seam] Where the metal roof panel functions as the roof deck and roof covering and it provides both weather protection and support for loads, the structural metal panel roof system shall comply with this section. Structural standing-seam metal panel roof systems shall be tested in accordance with ASTM E 1592 or FM 4474. Structural through-fastened metal panel roof systems shall be tested in accordance with FM 4474, UL 580 or ASTM E 1592.

[Exception: Metal roofs constructed of cold-formed steel, where the roof deck acts as the roof covering and provides both weather protection and support for structural loads, shall be permitted to be designed and tested in accordance with the applicable referenced structural design standard in Section 2209.1.]

Exceptions:

1.	Metal roofs constructed of cold-formed steel shall be permitted to be designed and tested in accordance with the applicable referenced structural design standard in Section 2210.1.

2.	Metal roofs constructed of aluminum shall be permitted to be designed and tested in accordance with the applicable referenced structural design standard in Section 2002.1.

1504.4 Ballasted low-slope roof systems. Ballasted low-slope (roof slope < 2:12) single-ply roof system coverings installed in accordance with Sections 1507.12 and 1507.13 shall be designed in accordance with ANSI/SPRI RP-4 and Section 1504.8 [and ANSI/SPRI RP-4] of this code.

1504.5 Edge securement for low-slope roofs. Low-slope membrane roof systems metal edge securement, except gutters, shall be designed and installed for wind loads in accordance with Chapter 16 and tested for resistance in accordance with [ANSI/SPRI ES-1,] Test Methods RE-1, RE-2 and RE-3 of ANSI/SPRI/FM 4435 ES-1, except the basic design wind speed V shall be determined in accordance with Chapter 16 of this code.

1504.6 Physical properties. Roof coverings installed on low-slope roofs (roof slope < 2:12) in accordance with Section 1507 shall demonstrate physical integrity over the working life of the roof based upon 2,000 hours of exposure to accelerated weathering tests conducted in accordance with ASTM G 152, ASTM G 155 or ASTM G 154. Those roof coverings that are subject to cyclical flexural response due to wind loads shall not demonstrate any significant loss of tensile strength for unreinforced membranes or breaking strength for reinforced membranes when tested as herein required.

1504.7 Impact resistance. Roof coverings installed on low-slope roofs (roof slope < 2:12) in accordance with Section 1507 shall resist impact damage based on the results of tests conducted in accordance with ASTM D 3746, ASTM D 4272, CGSB 37-GP-52M or the “Resistance to Foot Traffic Test” in Section 5.5 of FM 4470.

1504.8 [Aggregate.] Surfacing and ballast materials. Aggregate, gravel or crushed stone shall not be used as surfacing for roof coverings.[and aggregate, gravel or stone used as ballast shall not be used on the roof of a building located in a hurricane-prone region as defined in Section 1609.2, or on any other building with a mean roof height exceeding that permitted by Table 1504.8 based on the exposure category and basic wind speed at the site.]

| [TABLE 1504.8 MAXIMUM ALLOWABLE MEAN ROOF HEIGHT PERMITTED FOR BUILDINGS WITH AGGREGATE ON THE ROOF IN AREAS OUTSIDE A HURRICANE-PRONE REGIONd |
| --- |
| BASIC WIND SPEED FROM SECTION 1609.3 (mph)b | MAXIMUM MEAN ROOF HEIGHT (ft)a,c |
|  | Exposure category |
|  | B | C | D |
| 85 | 170 | 60 | 30 |
| 90 | 110 | 35 | 15 |
| 95 | 75 | 20 | NP |
| 100 | 55 | 15 | NP |
| 105 | 40 | NP | NP |
| 110 | 30 | NP | NP |
| 115 | 20 | NP | NP |
| 120 | 15 | NP | NP |
| Greater than 120 | NP | NP | NP |

For SI: 1 foot = 304.8 mm; 1 mile per hour = 0.447 m/s.

a.	Mean roof height as defined in ASCE 7.

b.	For intermediate values of basic wind speed, the height associated with the next higher value of wind speed shall be used, or direct interpolation is permitted.

c.	NP = gravel and stone not permitted for any roof height.

d.	New York City is in a Hurricane-Prone Region pursuant to Section 1609.2.]

1504.9 Reflectance. Roof coverings on roofs or setbacks with slope equal to or less than two units vertical in 12 units horizontal (17 percent) shall have:

1.	A minimum initial solar reflectance of 0.7 in accordance with ASTM C 1549 or ASTM E 1918, and a minimum thermal emittance of 0.75 as determined in accordance with ASTM C 1371 or ASTM E 408; or

2.	A minimum SRI of 82 as determined in accordance with ASTM E 1980.

Roof coverings on roofs or setbacks with slope greater than two units vertical in 12 units horizontal (17 percent) shall have:

1.	A minimum initial solar reflectance of 0.25 in accordance with ASTM C 1549 or ASTM E 1918, and a minimum thermal emittance of 0.75 as determined in accordance with ASTM C 1371 or ASTM E 408; or

2.	A minimum SRI of 39 as determined in accordance with ASTM E 1980.

Exceptions:

1.	Terraces on setbacks comprising less than 25 percent of the area of the largest floor plate in the building.

2.	Any portion of a roof covered by a green roof system, including such a system with agricultural plantings, in compliance with Section 1507.16.

3.	Any portion of a roof used as outdoor recreation space by the occupants of the building that is landscaped, covered by wood decking or covered with a walking surface or other protective surface, provided that such walking surface or protective surface has a minimum initial solar reflectance of 0.3 as determined in accordance with ASTM C 1549 or ASTM E 1918.

4.	Ballasted roofs, provided that the ballast has a minimum initial solar reflectance of 0.2 as determined in accordance with ASTM C 1549 or ASTM E 1918.

5.	Any portion of a roof that is under mechanical equipment, duckboarding, decking, platform, roof tank, cooling tower or any other rooftop structure or equipment exempted by rule by the commissioner.

6.	Any roof or portion of a roof composed of glass, metal, clay or concrete tile or plastic/rubber intended to simulate clay or concrete tile, wood, or slate.

7.	Any portion of a roof used by a school or daycare center as a playground for children.

8.	Any roof, if the amount of rooftop space not subject to exceptions 1 through 7 is in the aggregate less than 100 square feet (9.3 m2).

SECTION BC 1505
FIRE CLASSIFICATION

1505.1 General. Roof assemblies shall be divided into the classes defined below. Class A, B and C roof assemblies and roof coverings required to be listed by this section shall be tested in accordance with ASTM E 108 or UL 790. In addition, fire-retardant-treated wood roof coverings shall be tested in accordance with ASTM D 2898. The minimum roof coverings installed on buildings shall comply with Table 1505.1 based on the type of construction of the building.

Exception: Skylights and sloped glazing that comply with Chapter 24 or Section 2610.

| TABLE 1505.1a,b MINIMUM ROOF COVERING CLASSIFICATION FOR TYPES OF CONSTRUCTION |
| --- |
| IA | IB | IIA | IIB | IIIA | IIIB | IV | VA | VB |
| B | B | B | B | B | B | B | B | Cb |

For SI: 1 foot = 304.8 mm, 1 square foot = 0.0929 m2.

a.	Unless otherwise required due to the location of the building within a fire district in accordance with Section D102.2.3 in Appendix D.

b.	Buildings that are not more than two stories above grade plane and having not more than 6,000 square feet of projected roof area and where there is a minimum 10-foot fire-separation distance from the leading edge of the roof to a lot line on all sides of the building, except for street fronts or public ways, shall be permitted to have roofs of No. 1 cedar or redwood shakes and No. 1 shingles in accordance with Section 1505.6.

1505.2 Class A roof assemblies. Class A roof assemblies are those that are effective against severe fire test exposure. Class A roof assemblies and roof coverings shall be listed and identified as Class A by an approved testing agency. Class A roof assemblies shall be permitted for use in buildings or structures of all types of construction.

Exceptions:

1.	Class A roof assemblies include those with coverings of brick, masonry, or an exposed concrete roof deck.

2.	Class A roof assemblies also include ferrous or copper shingles or sheets, metal sheets and shingles, clay or concrete roof tile or slate installed on noncombustible decks or ferrous, copper or metal sheets installed without a roof deck on noncombustible framing.

3.	Class A roof assemblies include minimum 16 ounce per square foot (0.0416 kg/m2) copper sheets installed over combustible decks.

4.	Class A roof assemblies include slate installed over ASTM D 226, Type II underlayment over combustible decks.

1505.3 Class B roof assemblies. Class B roof assemblies are those that are effective against moderate fire-test exposure. Class B roof assemblies and roof coverings shall be listed and identified as Class B by an approved testing agency.

1505.4 Class C roof assemblies. Class C roof assemblies are those that are effective against light fire-test exposure. Class C roof assemblies and roof coverings shall be listed and identified as Class C by an approved testing agency.

1505.5 Construction of sloping roofs. Roofs having a slope of more than 60 degrees (1.05 rad) to the horizontal shall be constructed of material having the same fire-resistance rating as required for an exterior nonbearing wall of the building of which it is a part. When the slope is 60 degrees (1.05 rad) or less to the horizontal, the sloping roof shall be constructed as required for the roof of the building. Where the back of a false mansard is exposed to the outdoors, the back shall be covered with noncombustible material or with roof covering as required for the roof of the building.

1505.6 Fire-retardant-treated wood shingles and shakes. Fire-retardant-treated wood shakes and shingles shall be treated by impregnation with chemicals by the full-cell vacuum-pressure process, in accordance with AWPA C1. Each bundle shall be marked to identify the manufactured unit and the manufacturer, and shall also be labeled to identify the classification of the material in accordance with the testing required in Section 1505.1, the treating company and the quality control agency.

1505.7 Special purpose roofs. Special purpose wood shingle or wood shake roofing shall conform [with] to the grading and application requirements of Section 1507.8 or Section 1507.9. In addition, an underlayment of ⅝-inch (15.9 mm) Type X water-resistant gypsum backing board or gypsum sheathing shall be placed under minimum nominal ½-inch-thick (12.7 mm) wood structural panel solid sheathing or 1-inch (25 mm) nominal spaced sheathing.

1505.8 [Photovoltaic systems. Rooftop installed photovoltaic systems that are adhered or attached to the roof covering or photovoltaic modules/shingles installed as roof coveringsshall be labeled to identify their fire classification in accordance with the testing required in Section 1505.1.] Building-integrated photovoltaic products. Building-integrated photovoltaic products installed as the roof covering shall be tested, listed and labeled for fire classification in accordance with Section 1505.1.

1505.9 Photovoltaic panels and modules. Rooftop-mounted photovoltaic panel systems shall be tested, listed and identified with a fire classification in accordance with UL 1703. The fire classification shall comply with Table 1505.1 based on the type of construction of the building.

1505.10 Roof gardens and landscaped roofs. Roof gardens and landscaped roofs shall comply with Section 1507.16.

SECTION BC 1506
MATERIALS

1506.1 Scope. The requirements set forth in this section shall apply to the application of roof-covering materials specified herein. Roof coverings shall be applied in accordance with this chapter and the manufacturer’s [installation] instructions. Installation of roof coverings shall comply with the applicable provisions of Section 1507.

1506.2 [Compatibility of materials. Roofs and roof coverings shall be of materials that are compatible with each other and with the building or structure to which the materials are applied.]

[1506.3] Material specifications and physical characteristics. Roof-covering materials shall conform to the applicable standards listed in this chapter. In the absence of applicable standards or where materials are of questionable suitability, testing by an approved agency shall be required by the commissioner to determine the character, quality and limitations of application of the materials.

[1506.4] 1506.3 Product identification. Roof-covering materials shall be delivered in packages bearing the manufacturer’s identifying marks and approved testing agency labels required in accordance with Section 1505. Bulk shipments of materials shall be accompanied with the same information issued in the form of a certificate or on a bill of lading by the manufacturer.

SECTION BC 1507
REQUIREMENTS FOR ROOF COVERINGS

1507.1 Scope. Roof coverings shall be applied in accordance with the applicable provisions of this section and the manufacturer’s [installation] instructions.

1507.2 Asphalt shingles. The installation of asphalt shingles shall comply with the provisions of this section.

1507.2.1 Deck requirements. Asphalt shingles shall be fastened to solidly sheathed decks.

1507.2.2 Slope. Asphalt shingles shall only be used on roof slopes of two units vertical in 12 units horizontal (17-percent slope) or greater. For roof slopes from two units vertical in 12 units horizontal (17-percent slope) up to four units vertical in 12 units horizontal (33-percent slope), double underlayment application is required in accordance with Section 1507.2.8.

1507.2.3 Underlayment. Unless otherwise noted, required underlayment shall conform to ASTM D 226, Type I, ASTM D 4869, Type I, or ASTM D 6757.

1507.2.4 Self-adhering polymer modified bitumen sheet. Self-adhering polymer modified bitumen sheet shall comply with ASTM D 1970.

1507.2.5 Asphalt shingles. Asphalt shingles shall comply with ASTM D 225 or ASTM D 3462.

1507.2.6 Fasteners. Fasteners for asphalt shingles shall be galvanized, stainless steel, aluminum or copper roofing nails, minimum [12 gage] 12-gage (0.105 [inches] inch (2.67 mm)) shank with a minimum ⅜ inch-diameter (9.5 mm) head, of a length to penetrate through the roofing materials and a minimum of ¾ inch (19.1 mm) into the roof sheathing. Where the roof sheathing is less than ¾ inch (19.1 mm) thick, the nails shall penetrate through the sheathing. Fasteners shall comply with ASTM F 1667.

1507.2.7 Attachment. Asphalt shingles shall have the minimum number of fasteners required by the manufacturer, but not less than four fasteners per strip shingle or two fasteners per individual shingle. Where the roof slope exceeds 21 units vertical in 12 units horizontal (21:12), shingles shall be installed as required by the manufacturer.

[1507.2.7.1 Wind resistance. Asphalt shingles shall be tested in accordance with ASTM D 7158. Asphalt shingles shall meet the classification requirements of Table 1507.2.7.1(1) for the maximum basic wind speed per Section 1609. Asphalt shingle packaging shall bear a label to indicate compliance with ASTM D 7158 and the required classification in Table 1507.2.7.1(1).]

[Exception: Asphalt shingles not included in the scope of ASTM D 7158 shall be tested and labeled to indicate compliance with ASTM D 3161 and the required classification in Table 1507.2.7.1(2).]

| [TABLE 1507.2.7.1(1) CLASSIFICATION OF ASPHALT ROOF PER ASTM D 7158a |
| --- |
| MAXIMUM BASIC WIND SPEED FROM SECTION 1609 | CLASSIFICATION REQUIREMENT |
| 85 | D, G, or H |
| 90 | D, G, or H |
| 100 | G or H |
| 110 | G or H |
| 120 | G or H |
| 130 | H |
| 140 | H |
| 150 | H |

a.	The standard calculations contained in ASTM D 7158 assume exposure category B or C and building height of 60 feet (18 288 mm) or less. Additional calculations are required for conditions outside of these assumptions.]

| [TABLE 1507.2.7.1(2) CLASSIFICATION OF ASPHALT SHINGLES PER ASTM D 3161 |
| --- |
| MAXIMUM BASIC WIND SPEED FROM SECTION 1609 | CLASSIFICATION REQUIREMENT |
| 85 | A, D or F |
| 90 | A, D or F |
| 100 | A, D or F |
| 110 | F |
| 120 | F |
| 130 | F |
| 140 | F |
| 150 | F |

1507.2.8 Underlayment application. For roof slopes from two units vertical in 12 units horizontal (17-percent slope) up to four units vertical in 12 units horizontal (33-percent slope), underlayment shall be two layers applied in the following manner. Apply a minimum 19-inch-wide (483 mm) strip of underlayment felt parallel with and starting at the eaves, fastened sufficiently to hold in place. Starting at the eave, apply 36-inch-wide (914 mm) sheets of underlayment overlapping successive sheets 19 inches (483 mm) and fastened sufficiently to hold in place. Distortions in the underlayment shall not interfere with the ability of the shingles to seal. For roof slopes of four units vertical in 12 units horizontal (33-percent slope) or greater, underlayment shall be one layer applied in the following manner. Underlayment shall be applied shingle fashion, parallel to and starting from the eave and lapped 2 inches (51 mm), fastened only as necessary to hold in place. Distortions in the underlayment shall not interfere with the ability of the shingles to seal.

1507.2.8.1 Ice barrier. An ice barrier that consists of at least two layers of underlayment cemented together or of a self-adhering polymer modified bitumen sheet shall be used in lieu of normal underlayment and extend from the lowest edges of all roof surfaces to a point at least 24 inches (610 mm) inside the exterior wall line of the building.

Exception: Detached accessory structures that contain no conditioned floor area.

1507.2.9 Flashings. Flashing for asphalt shingles shall comply with this section. Flashing shall be applied in accordance with this section and the asphalt shingle manufacturer’s [printed] instructions.

1507.2.9.1 Base and cap flashing. Base and cap flashing shall be installed in accordance with the manufacturer’s instructions. Base flashing shall be of either corrosion-resistant metal of minimum nominal 0.019-inch (0.483 mm) thickness or mineral-surfaced roll roofing weighing a minimum of 77 pounds per 100 square feet (3.76 kg/m2). Cap flashing shall be corrosion-resistant metal of minimum nominal 0.019-inch (0.483 mm) thickness.

1507.2.9.2 Valleys. Valley linings shall be installed in accordance with the manufacturer’s instructions before applying shingles. Valley linings of the following types shall be permitted:

1.	For open valleys (valley lining exposed) lined with metal, the valley lining shall be at least 24 inches (610 mm) wide and of any of the corrosion-resistant metals in Table 1507.2.9.2.

2.	For open valleys, valley lining of two plies of mineral-surfaced roll roofing complying with ASTM D 3909 or ASTM D 6380 shall be permitted. The bottom layer shall be 18 inches (457 mm) and the top layer a minimum of 36 inches (914 mm) wide.

3.	For closed valleys (valleys covered with shingles), valley lining of one ply of smooth roll roofing complying with ASTM D 6380, and at least 36 inches (914 mm) wide or types as described in Item 1 or 2 above shall be permitted. Self-adhering polymer modified bitumen underlayment complying with ASTM D 1970 shall be permitted in lieu of the lining material.

| TABLE 1507.2.9.2 VALLEY LINING MATERIAL |
| --- |
| MATERIAL | MINIMUM THICKNESS | GAGE | WEIGHT |
| Aluminum | 0.024 in. | — | — |
| Cold-rolled copper | 0.0216 in. | — | ASTM B 370, 16 oz. per [sq.] square ft. |
| Copper | — | — | 16 oz. |
| Galvanized steel | 0.0179 in. | 26 (zinc-coated G90) | — |
| High-yield copper | 0.0162 in. | — | ASTM B 370, 12 oz. per [sq.] square ft. |
| Lead | — | — | 2.5 pounds |
| Lead-coated copper | 0.0216 in. | — | ASTM B 101, 16 oz. per square [foot] ft. |
| Lead-coated high-yield copper | 0.0162 in. | — | ASTM B 101, 12 oz. per [sq.] square ft. |
| Painted terne | — | — | 20 pounds |
| Stainless steel | — | 28 | — |
| Zinc alloy | 0.027 in. | — | — |

For SI: 1 inch = 25.4 mm, 1 pound = 0.454 kg, 1 ounce = 28.35 g, 1 square foot = 0.0929 m2.

1507.2.9.3 Drip edge. [Provide drip edge at eaves and gables of shingle roofs. Overlap to be a minimum of 2 inches (51 mm). Eave drip edges shall extend ¼ inch (6.4 mm) below sheathing and extend back on the roof a minimum of 2 inches (51 mm). Drip edge shall be mechanically fastened a maximum of 12 inches (305 mm) o.c.] A drip edge shall be provided at eaves and rake edges of shingle roofs. Adjacent segments of the drip edge shall be lapped a minimum of 2 inches (51 mm). The vertical leg of drip edges shall be a minimum of 1½ inches (38 mm) in width and shall extend a minimum of ¼ inch (6.4 mm) below sheathing. The drip edge shall extend back on the roof a minimum of 2 inches (51 mm). Underlayment shall be installed over drip edges along eaves. Drip edges shall be installed over underlayment along rake edges. Drip edges shall be mechanically fastened a maximum of 12 inches (305 mm) on center.

1507.3 Clay and concrete tile. The installation of clay and concrete tile shall comply with the provisions of this section.

1507.3.1 Deck requirements. Concrete and clay tile shall be installed only over solid sheathing or spaced structural sheathing boards.

1507.3.2 Deck slope. Clay and concrete roof tile shall be installed on roof slopes of 2½ units vertical in 12 units horizontal (21-percent slope) or greater. For roof slopes from 2½ units vertical in 12 units horizontal (21-percent slope) to four units vertical in 12 units horizontal (33-percent slope), double underlayment application is required in accordance with Section 1507.3.3.

1507.3.3 Underlayment. Unless otherwise noted, required underlayment shall conform to: ASTM D 226, Type II; ASTM D 2626 or ASTM D 6380, Class M mineral-surfaced roll roofing.

1507.3.3.1 Low-slope roofs. For roof slopes from 2½ units vertical in 12 units horizontal (21-percent slope), up to four units vertical in 12 units horizontal (33-percent slope), underlayment shall be a minimum of two layers applied as follows:

1.	Starting at the eave, a 19-inch (483 mm) strip of underlayment shall be applied parallel with the eave and fastened sufficiently in place.

2.	Starting at the eave, 36-inch-wide (914 mm) strips of underlayment felt shall be applied overlapping successive sheets 19 inches (483 mm) and fastened sufficiently in place.

1507.3.3.2 High-slope roofs. For roof slopes of four units vertical in 12 units horizontal (33-percent slope) or greater, underlayment shall be a minimum of one layer of underlayment felt applied shingle fashion, parallel to, and starting from the eaves and lapped 2 inches (51 mm), fastened only as necessary to hold in place.

1507.3.4 Clay tile. Clay roof tile shall comply with ASTM C 1167.

1507.3.5 Concrete tile. Concrete roof tile shall comply with ASTM C 1492.

1507.3.6 Fasteners. Tile fasteners shall be corrosion resistant and not less than 11 gage, 5/16-inch (8.0 mm) head, and of sufficient length to penetrate the deck a minimum of ¾ inch (19.1 mm) or through the thickness of the deck, whichever is less. Attaching wire for clay or concrete tile shall be not [be] [smaller] less than 0.083 inch (2.1 mm). Perimeter fastening areas include three tile courses but not less than 36 inches (914 mm) from either side of hips or ridges and edges of eaves and gable rakes.

1507.3.7 Attachment. Clay and concrete roof tiles shall be fastened in accordance with Table 1507.3.7.

| TABLE 1507.3.7 CLAY AND CONCRETE TILE ATTACHMENTa,b,c |
| --- |
| GENERAL - CLAY OR CONCRETE ROOF TILE |
| Maximum [basic wind speed] Nominal Design Wind Speed, Vasdf (mph) | Mean roof height (feet) | Roof slope [up to]< 3:12 | Roof slope 3:12 and over |
| 85 | 0-60 | One fastener per tile. Flat tile without vertical laps, two fasteners per tile. | Two fasteners per tile. Only one fastener on slopes of 7:12 and less for tiles with installed weight exceeding 7.5 lbs./sq. ft. having a width not more than 16 inches. |
| 100 | 0-40 |  |  |
| 100 | >40-60 | The head of all tiles shall be nailed. The nose of all eave tiles shall be fastened with approved clips. All rake tiles shall be nailed with two nails. The nose of all ridge, hip and rake tiles shall be set in a bead of roofer’s mastic. |
| 110 | 0-60 | The fastening system shall resist the wind forces in Section [1609.7.3] 1609.5.3. |
| 120 | 0-60 | The fastening system shall resist the wind forces in Section [1609.7.3] 1609.5.3. |
| 130 | 0-60 | The fastening system shall resist the wind forces in Section [1609.7.3] 1609.5.3. |
| All | >60 | The fastening system shall resist the wind forces in Section [1609.7.3] 1609.5.3. |
| INTERLOCKING CLAY OR CONCRETE ROOF TILE WITH PROJECTING ANCHOR LUGSd,e (Installations on spaced/solid sheathing with battens or spaced sheathing) |
| Maximum [basic wind speed] Nominal Design Wind Speed, Vasdf (mph) | Mean roof height (feet) | Roof slope [up to] < 5:12 | Roof slope 5:12 < 12:12 | Roof slope 12:12 and over |
| 85 | 0-60 | Fasteners are not required. Tiles with installed weight less than 9 lbs./sq. ft. require a minimum of one fastener per tile. | One fastener per tile every other row. All perimeter tiles require one fastener. Tiles with installed weight less than 9 lbs./sq. ft. require a minimum of one fastener per tile. | One fastener required for every tile. Tiles with installed weight less than 9 lbs./sq. ft. require a minimum of one fastener per tile. |
| 100 | 0-40 |  |  |  |
| 100 | >40-60 | The head of all tiles shall be nailed. The nose of all eave tiles shall be fastened with approved clips. All rake tiles shall be nailed with two nails. The nose of all ridge, hip and rake tiles shall be set in a bead of roofer’s mastic. |
| 110 | 0-60 | The fastening system shall resist the wind forces in Section [1609.7.3] 1609.5.3. |
| 120 | 0-60 | The fastening system shall resist the wind forces in Section [1609.7.3] 1609.5.3. |
| 130 | 0-60 | The fastening system shall resist the wind forces in Section [1609.7.3] 1609.5.3. |
| All | >60 | The fastening system shall resist the wind forces in Section [1609.7.3] 1609.5.3. |
| INTERLOCKING CLAY OR CONCRETE ROOF TILE WITH PROJECTING ANCHOR LUGS (Installations on solid sheathing without battens) |
| Maximum [basic wind speed] Nominal Design Wind Speed, Vasdf (mph) | Mean roof height (feet) | All roof slopes |
| 85 | 0-60 | One fastener per tile. |
| 100 | 0-40 | One fastener per tile. |
| 100 | >40-60 | The head of all tiles shall be nailed. The nose of all eave tiles shall be fastened with approved clips. All rake tiles shall be nailed with two nails. The nose of all ridge, hip and rake tiles shall be set in a bead of roofer’s mastic. |
| 110 | 0-60 | The fastening system shall resist the wind forces in Section [1609.7.3] 1609.5.3. |
| 120 | 0-60 | The fastening system shall resist the wind forces in Section [1609.7.3] 1609.5.3. |
| 130 | 0-60 | The fastening system shall resist the wind forces in Section [1609.7.3] 1609.5.3. |
| All | >60 | The fastening system shall resist the wind forces in Section [1609.7.3] 1609.5.3. |

For SI: 1 inch = 25.4 mm, 1 foot = 304.8 mm, 1 mile per hour = 0.447 m/s, 1 pound per square foot = 4.882 kg/m2.

a.	Minimum fastener size. Corrosion-resistant nails not less than No. 11 gage with 5/16-inch head. Fasteners shall be long enough to penetrate into the sheathing 3/4-inch or through the thickness of the sheathing, whichever is less. Attaching wire for clay and concrete tile shall not be smaller than 0.083 inch.

b.	Snow areas. A minimum of two fasteners per tile are required or battens and one fastener.

c.	Roof slopes greater than 24:12. The nose of all tiles shall be securely fastened.

d.	Horizontal battens. Battens shall be not less than 1 inch by 2 inch nominal. Provisions shall be made for drainage by a minimum of 1/8-inch riser at each nail or by 4-foot-long battens with at least a 1/2-inch separation between battens. Horizontal battens are required for slopes over 7:12.

e.	Perimeter fastening areas include three tile courses but not less than 36 inches from either side of hips or ridges and edges of eaves and gable rakes.

f.	Vasd shall be determined in accordance with Section 1609.3.1.

1507.3.8 Application. Tile shall be applied according to the manufacturer’s [installation] instructions, based on the following:

1.	Climatic conditions.

2.	Roof slope.

3.	Underlayment system.

4.	Type of tile being installed.

1507.3.9 Flashing. At the juncture of the roof vertical surfaces, flashing and counterflashing shall be provided in accordance with the manufacturer’s [installation] instructions, and where of metal, shall not be less than 0.019-inch (0.483 mm) (No. 26 galvanized sheet gage) corrosion-resistant metal. The valley flashing shall extend at least 11 inches (279 mm) from the centerline each way and have a splash diverter rib not less than 1 inch (25 mm) high at the flow line formed as part of the flashing. Sections of flashing shall have an end lap of not less than 4 inches (102 mm). For roof slopes of three units vertical in 12 units horizontal (25-percent slope) and over, the valley flashing shall have a 36-inch-wide (914 mm) underlayment of either one layer of Type I underlayment running the full length of the valley, or a self-adhering polymer-modified bitumen sheet complying with ASTM D 1970, in addition to other required underlayment. For slopes under seven units vertical in 12 units horizontal (58-percent slope), the metal valley flashing underlayment shall be solid cemented to the roofing underlayment or a self-adhering polymer modified bitumen sheet shall be installed.

1507.4 Metal roof panels. The installation of metal roof panels shall comply with the provisions of this section.

1507.4.1 Deck requirements. Metal roof panel roof coverings shall be applied to a solid or closely fitted deck, except where the roof covering is specifically designed to be applied to spaced supports.

1507.4.2 Deck slope. The minimum slope for metal roof panels shall comply with the following:

1.	The minimum slope for lapped, nonsoldered seam metal [roofs] roof panels without applied lap sealant shall be three units vertical in 12 units horizontal (25-percent slope).

2.	The minimum slope for lapped, nonsoldered seam metal [roofs] roof panels with applied lap sealant shall be one-half unit vertical in 12 units horizontal (4-percent slope). Lap sealants shall be applied in accordance with the [approved] manufacturer’s [installation] instructions.

3.	The minimum slope for standing-seam [of] metal roof panel systems shall be one-quarter unit vertical in 12 units horizontal (2-percent slope).

1507.4.3 Material standards. Metal-sheet roof covering systems that incorporate supporting structural members shall be designed in accordance with Chapter 22. Metal-sheet roof coverings installed over structural decking shall comply with Table 1507.4.3(1). The materials used for metal-sheet roof coverings shall be naturally corrosion resistant or provided with corrosion resistance in accordance with the standards and minimum thicknesses shown in Table 1507.4.3(2).

| TABLE 1507.4.3(1) METAL ROOF COVERINGS |
| --- |
| ROOF COVERING TYPE | STANDARD APPLICATION RATE/THICKNESS |
| Aluminum | ASTM B 209, 0.024 inch minimum thickness for roll-formed panels and 0.019 inch minimum thickness for press-formed shingles. |
| Aluminum-zinc alloy coated steel | ASTM A 792 AZ 50 |
| Cold-rolled copper | ASTM B 370 minimum 16 oz./sq. ft. and 12 oz./sq. ft. high yield copper for metal-sheet roof covering systems: 12 oz./sq. ft. for [pre formed] pre-formed metal shingle systems. |
| Copper | 16 oz./sq. ft. for metal-sheet roof-covering systems; 12 oz./sq. ft. for preformed metal shingle systems. |
| Galvanized steel | ASTM A 653 G-90 zinc-coateda [,] |
| Hard [Lead] lead | 2 lbs./sq. ft. |
| Lead-coated copper | ASTM B 101 |
| Prepainted steel | ASTM A 755 |
| Soft [Lead] lead | 3 lbs./sq. ft. |
| Stainless steel | ASTM A 240, 300 Series Alloys |
| Steel | ASTM A 924 |
| Terne and terne-coated stainless | Terne coating of 40 lbs. per double base box, field painted where applicable in accordance with manufacturer’s [installation] instructions. |
| Zinc | 0.027 inch minimum thickness; 99.995% electrolytic high grade zinc with alloy additives of copper (0.08% - 0.20%), titanium (0.07% - 0.12%) and aluminum (0.015%). |

For SI: 1 ounce per square foot = [0.0026] 0.305 kg/m2, 1 pound per square foot = 4.882 kg/m2, 1 inch = 25.4 mm, 1 pound = 0.454 kg.

a.	For Group U buildings, the minimum coating thickness for ASTM A 653 galvanized steel roofing shall be G-60.

| TABLE 1507.4.3(2) MINIMUM CORROSION RESISTANCE |
| --- |
| MATERIAL | STANDARD |
| 55% Aluminum-zinc alloy coated steel | ASTM A 792 AZ 50 |
| 5% Aluminum alloy-coated steel | ASTM A 875 GF60 |
| Aluminum-coated steel | ASTM A 463 T2 65 |
| Galvanized steel | ASTM A 653 G-90 |
| Prepainted steel | ASTM A 755a |

a.	Paint systems in accordance with ASTM A 755 shall be applied over steel products with corrosion-resistant coatings complying with ASTM A 792, ASTM A 875, ASTM A 463 or ASTM A 653.

1507.4.4 Attachment. Metal roof panels shall be secured to the supports in accordance with the approved manufacturer’s fasteners. In the absence of manufacturer recommendations, the following fasteners shall be used:

1.	Galvanized fasteners shall be used for steel roofs.

2.	Copper, brass, bronze, copper alloy or 300 series stainless-steel fasteners shall be used for copper roofs.

3.	Stainless-steel fasteners are acceptable for all types of metal roofs.

4.	Aluminum fasteners are acceptable for aluminum roofs attached to aluminum supports.

1507.5 Metal roof shingles. The installation of metal roof shingles shall comply with the provisions of this section.

1507.5.1 Deck requirements. Metal roof shingles shall be applied to a solid or closely fitted deck, except where the roof covering is specifically designed to be applied to spaced sheathing.

1507.5.2 Deck slope. Metal roof shingles shall not be installed on roof slopes below three units vertical in 12 units horizontal (25-percent slope).

1507.5.3 Underlayment. Underlayment shall comply with ASTM D 226, Type I or ASTM D 4869.

1507.5.4 Ice barrier. An ice barrier that consists of at least two layers of underlayment cemented together or of a self-adhering polymer-modified bitumen sheet, shall be used in lieu of normal underlayment and extend from the lowest edges of all roof surfaces to a point at least 24 inches (610 mm) inside the exterior wall line of the building.

Exception: Detached accessory structures that contain no conditioned floor area.

1507.5.5 Material standards. Metal roof shingle roof coverings shall comply with Table 1507.4.3(1). The materials used for metal-roof shingle roof coverings shall be naturally corrosion resistant or provided with corrosion resistance in accordance with the standards and minimum thicknesses specified in the standards listed in Table 1507.4.3(2).

1507.5.6 Attachment. Metal roof shingles shall be secured to the roof in accordance with the [approved] manufacturer’s [installation] instructions.

1507.5.7 Flashing. Roof valley flashing shall be of corrosion-resistant metal of the same material as the roof covering or shall comply with the standards in Table 1507.4.3(1). The valley flashing shall extend at least 8 inches (203 mm) from the centerline each way and shall have a splash diverter rib not less than ¾ inch (19.1 mm) high at the flow line formed as part of the flashing. Sections of flashing shall have an end lap of not less than 4 inches (102 mm). The metal valley flashing shall have a 36-inch-wide (914 mm) underlayment directly under it consisting of either one layer of underlayment running the full length of the valley or a self-adhering polymer-modified bitumen sheet complying with ASTM D 1970, in addition to underlayment required for metal roof shingles. For slopes under seven units vertical in 12 units horizontal (58-percent slope), the metal valley flashing underlayment shall be solid cemented to the roofing underlayment) or a self-adhering polymer modified bitumen sheet shall be installed.

1507.6 Mineral-surfaced roll roofing. The installation of mineral-surfaced roll roofing shall comply with this section.

1507.6.1 Deck requirements. Mineral-surfaced roll roofing shall be fastened to solidly sheathed roofs.

1507.6.2 Deck slope. Mineral-surfaced roll roofing shall not be applied on roof slopes below one unit vertical in 12 units horizontal (8-percent slope).

1507.6.3 Underlayment. Underlayment shall comply with ASTM D 226, Type I or ASTM D 4869.

1507.6.4 Ice barrier. An ice barrier that consists of at least two layers of underlayment cemented together or of a self-adhering polymer-modified bitumen sheet, shall be used in lieu of normal underlayment and extend from the lowest edges of all roof surfaces to a point at least 24 inches (610 mm) inside the exterior wall line of the building.

Exception: Detached accessory structures that contain no conditioned floor area.

1507.6.5 Material standards. Mineral-surfaced roll roofing shall conform to ASTM D 3909 or ASTM D 6380.

1507.7 Slate shingles. The installation of slate shingles shall comply with the provisions of this section.

1507.7.1 Deck requirements. Slate shingles shall be fastened to solidly sheathed roofs.

1507.7.2 Deck slope. Slate shingles shall only be used on slopes of four units vertical in 12 units horizontal (4:12) or greater.

1507.7.3 Underlayment. Underlayment shall comply with ASTM D 226, Type [I] II or ASTM D 4869, Type III or IV.

1507.7.4 Ice barrier. An ice barrier that consists of at least two layers of underlayment cemented together or of a self-adhering polymer-modified bitumen sheet, shall extend from the lowest edges of all roof surfaces to a point at least 24 inches (610 mm) inside the exterior wall line of the building.

Exception: Detached accessory structures that contain no conditioned floor area.

1507.7.5 Material standards. Slate shingles shall comply with ASTM C 406.

1507.7.6 Application. Minimum headlap for slate shingles shall be in accordance with Table 1507.7.6. Slate shingles shall be secured to the roof with two fasteners per slate.

| TABLE 1507.7.6 SLATE SHINGLE HEADLAP |
| --- |
| SLOPE | HEADLAP (inches) |
| 4:12 < slope < 8:12 | 4 |
| 8:12 < slope < 20:12 | 3 |
| slope ≥ 20:12 | 2 |

For SI: 1 inch = 25.4 mm.

1507.7.7 Flashing. Flashing and counterflashing shall be made with sheet metal. Valley flashing shall be a minimum of 15 inches (381 mm) wide. Valley and flashing metal shall be a minimum uncoated thickness of 0.0179-inch (0.455 mm) zinc-coated G90. Chimneys, stucco or brick walls shall have a minimum of two plies of felt for a cap flashing consisting of a 4-inch-wide (102 mm) strip of felt set in plastic cement and extending 1 inch (25 mm) above the first felt and a top coating of plastic cement. The felt shall extend over the base flashing 2 inches (51 mm).

1507.8 Wood shingles. The installation of wood shingles shall comply with the provisions of this section and Table 1507.8.

| TABLE 1507.8 WOOD SHINGLE AND SHAKE INSTALLATION |
| --- |
| ROOF ITEM | WOOD SHINGLES | WOOD SHAKES |
| 1. Roof slope | Wood shingles shall be installed on slopes of not less than three units vertical in 12 units horizontal [(3:12) or greater] (3:12). | Wood shakes shall be installed on slopes of not less than four units vertical in 12 units horizontal [(4:12) or greater] (4:12). |
| 2. Deck requirement | [—] | [—] |
| Temperate climate | Shingles shall be applied to roofs with solid or spaced sheathing. Where spaced sheathing is used, sheathing boards shall be not [be] less than 1″ × 4″ nominal dimensions and shall be spaced on [center] centers equal to the weather exposure to coincide with the placement of fasteners. | Shakes shall be applied to roofs with solid or spaced sheathing. Where spaced sheathing is used, sheathing boards shall be not [be] less than 1″ × 4″ nominal dimensions and shall be spaced on [center] centers equal to the weather exposure to coincide with the placement of fasteners. When 1″ × 4″ spaced sheathing is installed at 10 inches, boards must be installed between the sheathing boards. |
| Ice forming along the eaves causing a backup of water. | Solid sheathing required. | Solid sheathing is required. |
| 3. Interlayment | No requirements. | Interlayment shall comply with ASTM D 226, Type 1. |
| 4. Underlayment | [—] | [—] |
| Temperate climate | Underlayment shall comply with ASTM D 226, Type 1. | Underlayment shall comply with ASTM D 226, Type 1. |
| Ice forming along the eaves causing a backup of water. | An ice barrier that consists of at least two layers of underlayment cemented together or of a self-adhering polymer-modified bitumen sheet shall extend from the eave’s edge to a point at least 24 inches inside the exterior wall line of the building. | An ice barrier that consists of at least two layers of underlayment cemented together or of a self-adhering polymer-modified bitumen sheet shall extend from the lowest eave’s edge of all roof surfaces to a point at least 24 inches inside the exterior wall line of the building. |
| 5. Application | [—] | [—] |
| Attachment | Fasteners for wood shingles shall be hot-dipped galvanized or Type 304 (Type 316 for coastal areas) stainless steel with a minimum penetration of 0.75 inch into the sheathing. For sheathing less than 0.5 inch thick, the fasteners shall extend through the sheathing. | Fasteners for wood shakes shall be hot-dipped galvanized or Type 304 (Type 316 for coastal areas) with a minimum penetration of 0.75 inch into the sheathing. For sheathing less than 0.5 inch thick, the fasteners shall extend through the sheathing. |
| No. of fasteners | Two per shingle. | Two per shake. |
| Exposure | Weather exposures shall not exceed those set forth in Table 1507.8.7. | Weather exposures shall not exceed those set forth in Table 1507.9.8. |
| Method | Shingles shall be laid with a side lap of not less than 1.5 inches between joints in courses, and no two joints in any three adjacent courses shall be in direct alignment. Spacing between shingles shall be 0.25 to 0.375 inch. | Shakes shall be laid with a side lap of not less than 1.5 inches between joints in adjacent courses. Spacing between shakes shall not be less than 0.375 inch or more than 0.625 inch for shakes and [tapersawn] taper sawn shakes of naturally durable wood and shall be 0.25 to 0.375 inch for [preservative] preservative-treated taper sawn shakes. |
| Flashing | In accordance with Section 1507.8.8. | In accordance with Section 1507.9.9. |

For SI: 1 inch = 25.4 mm, °C = ((°F) – 32)/1.8.

1507.8.1 Deck requirements. Wood shingles shall be installed on solid or spaced sheathing. Where spaced sheathing is used, sheathing boards shall be not [be] less than 1-inch by 4-inch (25 mm by 102 mm) nominal dimensions and shall be spaced on centers equal to the weather exposure to coincide with the placement of fasteners.

1507.8.1.1 Solid sheathing required. Solid sheathing is required.

1507.8.2 Deck slope. Wood shingles shall be installed on slopes of not less than three units vertical in 12 units horizontal [(25-percent slope) or greater.] (25-percent slope).

1507.8.3 Underlayment. Underlayment shall comply with ASTM D 226, Type I or ASTM D 4869.

1507.8.4 Ice barrier. An ice barrier that consists of at least two layers of underlayment cemented together or of a self-adhering polymer-modified bitumen sheet shall be used in lieu of normal underlayment and extend from the lowest edges of all roof surfaces to a point at least 24 inches (610 mm) inside the exterior wall line of the building.

Exception: Detached accessory structures that contain no conditioned floor area.

1507.8.5 Material standards. Wood shingles shall be of naturally durable wood and comply with the requirements of Table 1507.8.5.

| TABLE 1507.8.5 WOOD SHINGLE MATERIAL REQUIREMENTS |
| --- |
| MATERIAL | APPLICABLE MINIMUM GRADES | GRADING RULES |
| Wood shingles of naturally durable wood | 1, 2 or 3 | CSSB |

CSSB = Cedar Shake and Shingle Bureau

1507.8.6 Attachment. Fasteners for wood shingles shall be corrosion resistant with a minimum penetration of ¾ inch (19.1 mm) into the sheathing. For sheathing less than ½ inch (12.7 mm) in thickness, the fasteners shall extend through the sheathing. Each shingle shall be attached with a minimum of two fasteners.

1507.8.7 Application. Wood shingles shall be laid with a side lap not less than 1½ inches (38 mm) between joints in adjacent courses, and not be in direct alignment in alternate courses. Spacing between shingles shall be ¼ to ⅜ inches (6.4 to 9.5 mm). Weather exposure for wood shingles shall not exceed that set in Table 1507.8.7.

| TABLE 1507.8.7 WOOD SHINGLE WEATHER EXPOSURE AND ROOF SLOPE |
| --- |
| ROOFING MATERIAL | LENGTH (inches) | GRADE | EXPOSURE (inches) |
|  |  |  | 3:12 pitch to < 4:12 | 4:12 pitch or steeper |
| Shingles of naturally durable wood | 16 | No. 1 No. 2 No. 3 | 3.75 3.5 3 | 5 4 3.5 |
|  | 18 | No. 1 No. 2 No. 3 | 4.25 4 3.5 | 5.5 4.5 4 |
|  | 24 | No. 1 No. 2 No. 3 | 5.75 5.5 5 | 7.5 6.5 5.5 |

For SI: 1 inch = 25.4 mm.

1507.8.8 Flashing. At the juncture of the roof and vertical surfaces, flashing and counterflashing shall be provided in accordance with the manufacturer’s [installation] instructions, and where of metal, shall be not [be] less than 0.019-inch (0.48 mm) (No. 26 galvanized sheet gage) corrosion-resistant metal. The valley flashing shall extend at least 11 inches (279 mm) from the centerline each way and have a splash diverter rib not less than 1 inch (25 mm) high at the flow line formed as part of the flashing. Sections of flashing shall have an end lap of not less than 4 inches (102 mm). For roof slopes of three units vertical in 12 units horizontal (25-percent slope) and over, the valley flashing shall have a 36-inch-wide (914 mm) underlayment of either one layer of Type I underlayment running the full length of the valley [valley] or a self-adhering polymer-modified bitumen sheet complying with ASTM D 1970, in addition to other required underlayment. For slopes under seven units vertical in 12 units horizontal (58-percent slope), the metal valley flashing underlayment shall be solid cemented to the roofing underlayment or a self-adhering polymer modified bitumen sheet shall be installed.

1507.9 Wood shakes. The installation of wood shakes shall comply with the provisions of this section and Table 1507.8.

1507.9.1 Deck requirements. Wood shakes shall only be used on solid or spaced sheathing. Where spaced sheathing is used, sheathing boards shall be not [be] less than 1-inch by 4-inch (25 mm by 102 mm) nominal dimensions and shall be spaced on centers equal to the weather exposure to coincide with the placement of fasteners. Where 1-inch by 4-inch (25 mm by 102 mm) spaced sheathing is installed at 10 inches (254 mm) [o.c.] on center, additional 1-inch by 4-inch (25 mm by 102 mm) boards shall be installed between the sheathing boards.

1507.9.1.1 Solid sheathing required. Solid sheathing is required in areas where the average daily temperature in January is 25°F (-4°C) or less or where there is a possibility of ice forming along the eaves causing a backup of water.

1507.9.2 Deck slope. Wood shakes shall only be used on slopes of not less than four units vertical in 12 units horizontal (33-percent slope)[or greater].

1507.9.3 Underlayment. Underlayment shall comply with ASTM D 226, Type I or ASTM D 4869.

1507.9.4 Ice barrier. An ice barrier that consists of at least two layers of underlayment cemented together or of a self-adhering polymer-modified bitumen sheet shall be used in lieu of normal underlayment and extend from the lowest edges of all roof surfaces to a point at least 24 inches (610 mm) inside the exterior wall line of the building.

Exception: Detached accessory structures that contain no conditioned floor area.

1507.9.5 Interlayment. Interlayment shall comply with ASTM D 226, Type I.

1507.9.6 Material standards. Wood shakes shall comply with the requirements of Table 1507.9.6.

| TABLE 1507.9.6 WOOD SHAKE MATERIAL REQUIREMENTS |
| --- |
| MATERIAL | MINIMUM GRADES | APPLICABLE GRADING RULES |
| Wood shakes of naturally durable wood | 1 | CSSB |
| Taper sawn shakes of naturally durable wood | 1 or 2 | CSSB |
| Preservative-treated shakes and shingles of naturally durable wood | 1 | CSSB |
| Fire-retardant-treated shakes and shingles of naturally durable wood | 1 | CSSB |
| Preservative-treated taper sawn shakes of Southern pine treated in accordance with AWPA U1 (Commodity Specification A, Use Category 3B and Section 5.6) | 1 or 2 | TFS |

CSSB = Cedar Shake and Shingle Bureau.

TFS = Forest Products Laboratory of the Texas Forest Services.

1507.9.7 Attachment. Fasteners for wood shakes shall be corrosion resistant with a minimum penetration of ¾ inch (19.1 mm) into the sheathing. For sheathing less than ½ inch (12.7 mm) in thickness, the fasteners shall extend through the sheathing. Each shake shall be attached with a minimum of two fasteners.

1507.9.8 Application. Wood shakes shall be laid with a side lap not less than 1½ inches (38 mm) between joints in adjacent courses. Spacing between shakes in the same course shall be ⅜ to ⅝ inches (9.5 to 15.9 mm) for shakes and taper sawn shakes of naturally durable wood and shall be ¼ to ⅜ inch (6.4 to 9.5 mm) for preservative taper sawn shakes. Weather exposure for wood shakes shall not exceed those set in Table 1507.9.8.

| TABLE 1507.9.8 WOOD SHAKE WEATHER EXPOSURE AND ROOF SLOPE |
| --- |
| ROOFING MATERIAL | LENGTH (inches) | GRADE | EXPOSURE (inches) 4:12 PITCH OR STEEPER |
| Shakes of naturally durable wood | 18 24 | No. 1 No. 1 | 7.5 10a |
| Preservative-treated taper sawn shakes of Southern yellow pine | 18 24 | No. 1 No. 1 | 7.5 10 |
|  | 18 24 | No. 2 No. 2 | 5.5 7.5 |
| Taper sawn shakes of naturally durable wood | 18 24 | No. 1 No. 1 | 7.5 10 |
|  | 18 24 | No. 2 No. 2 | 5.5 7.5 |

For SI: 1 inch = 25.4 mm.

a.	For 24-inch by 0.375-inch handsplit shakes, the maximum exposure is 7.5 inches.

1507.9.9 Flashing. At the juncture of the roof and vertical surfaces, flashing and counterflashing shall be provided in accordance with the manufacturer’s [installation] instructions, and where of metal, shall be not [be] less than 0.019-inch (0.48 mm) (No. 26 galvanized sheet gage) corrosion-resistant metal. The valley flashing shall extend at least 11 inches (279 mm) from the centerline each way and have a splash diverter rib not less than 1 inch (25 mm) high at the flow line formed as part of the flashing. Sections of flashing shall have an end lap of not less than 4 inches (102 mm). For roof slopes of three units vertical in 12 units horizontal (25-percent slope) and over, the valley flashing shall have a 36-inch-wide (914 mm) underlayment of either one layer of Type I underlayment running the full length of the valley or a self-adhering polymer-modified bitumen sheet complying with ASTM D 1970, in addition to other required underlayment. For slopes under seven units vertical in 12 units horizontal (58-percent slope) the metal valley flashing underlayment shall be solidly cemented to the roofing underlayment or a self-adhering polymer-modified bitumen sheet shall be installed.

1507.10 Built-up roofs. The installation of built-up roofs shall comply with the provisions of this section.

1507.10.1 Slope. Built-up roofs shall have a slope designed and built to provide positive roof drainage.

1507.10.2 Material standards. Built-up roof covering materials shall comply with UL 55A or the standards in Table 1507.10.2 of this code.

| TABLE 1507.10.2 BUILT-UP ROOFING MATERIAL STANDARDS |
| --- |
| MATERIAL STANDARD | STANDARD |
| Acrylic coatings used in roofing | ASTM D 6083 |
| Aggregate surfacing | ASTM D 1863 |
| Asphalt adhesive used in roofing | ASTM D 3747 |
| Asphalt cements used in roofing | ASTM D 3019; D 2822; D 4586 |
| Asphalt-coated glass fiber base sheet | ASTM D 4601 |
| Asphalt coatings used in roofing | ASTM D 1227; D 2823; D 2824; D 4479 |
| Asphalt glass felt | ASTM D 2178 |
| Asphalt primer used in roofing | ASTM D 41 |
| Asphalt-saturated and asphalt-coated organic felt base sheet | ASTM D 2626 |
| Asphalt-saturated organic felt (perforated) | ASTM D 226 |
| Asphalt used in roofing | ASTM D 312 |
| Coal-tar cements used in roofing | ASTM D 4022; D 5643 |
| Coal-tar saturated organic felt | ASTM D 227 |
| Coal-tar pitch used in roofing | ASTM D 450; Type I or II |
| Coal-tar primer used in roofing, dampproofing and waterproofing | ASTM D 43 |
| Glass mat, coal tar | ASTM D 4990 |
| Glass mat, venting type | ASTM D 4897 |
| Mineral-surfaced inorganic cap sheet | ASTM D 3909 |
| Thermoplastic fabrics used in roofing | ASTM D 5665, D 5726 |

1507.11 Modified bitumen roofing. The installation of modified bitumen roofing shall comply with the provisions of this section.

1507.11.1 Slope. Modified bitumen membrane roofs shall have a slope designed and built to provide positive roof drainage.

1507.11.2 Material standards. Modified bitumen roof coverings shall comply with CGSB 37-GP-56M, ASTM D 6162, ASTM D 6163, ASTM D 6164, ASTM D 6222, ASTM D 6223, ASTM D 6298 [and] or ASTM D 6509.

1507.12 Thermoset single-ply roofing. The installation of thermoset single-ply roofing shall comply with the provisions of this section.

1507.12.1 Slope. Thermoset single-ply membrane roofs shall have a slope designed and built to provide positive roof drainage.

1507.12.2 Material standards. Thermoset single-ply roof coverings shall comply with ASTM D 4637, ASTM D 5019 or CGSB 37-GP-52M.

1507.12.3 Ballasted thermoset low-slope roofs. Ballasted thermoset low-slope roofs (roof slope < 2:12) shall be installed in accordance with this section and Section 1504.4, and subject to the limitations of Section 1504.8. [Stone used as ballast shall comply with ASTM D 448.]

1507.13 Thermoplastic single-ply roofing. The installation of thermoplastic single-ply roofing shall comply with the provisions of this section.

1507.13.1 Slope. Thermoplastic single-ply membrane roofs shall have a slope designed and built to provide positive roof drainage.

1507.13.2 Material standards. Thermoplastic single-ply roof coverings shall comply with ASTM D 4434, ASTM D 6754, ASTM D 6878 or CAN/CGSB 37-54.

1507.13.3 Ballasted thermoplastic low-slope roofs. Ballasted thermoplastic low-slope roofs (roof slope < 2:12) shall be installed in accordance with this section and Section 1504.4, and subject to the limitations of Section 1504.8. [Stone used as ballast shall comply with ASTM D 448.]

1507.14 Sprayed polyurethane foam roofing. The installation of sprayed polyurethane foam roofing shall comply with the provisions of this section.

1507.14.1 Slope. Sprayed polyurethane foam roofs shall have a slope designed and built to provide positive roof drainage.

1507.14.2 Material standards. Spray-applied polyurethane foam insulation shall comply with Type III or IV as defined in ASTM C 1029.

1507.14.3 Application. Foamed-in-place roof insulation shall be installed in accordance with the manufacturer’s instructions. A liquid-applied protective coating that complies with [Section 1507.15] Table 1507.14.3 shall be applied no less than 2 hours nor more than 72 hours following the application of the foam.

| TABLE 1507.14.3 PROTECTIVE COATING MATERIAL STANDARDS |
| --- |
| MATERIAL | STANDARD |
| Acrylic coating | ASTM D 6083 |
| Silicone coating | ASTM D 6694 |
| Moisture-cured polyurethane coating | ASTM D 6947 |

1507.14.4 Foam plastics. Foam plastic materials and installation shall comply with Chapter 26.

1507.15 Liquid-applied roofing. The installation of liquid-applied roofing shall comply with the provisions of this section.

1507.15.1 Slope. Liquid-applied roofing shall have a slope designed and built to provide positive roof drainage.

1507.15.2 Material standards. Liquid-applied roofing shall comply with ASTM C 836, ASTM C 957, ASTM D 1227[,] or ASTM D 3468, ASTM D 6083, ASTM D 6694 or ASTM D 6947.

1507.16 [Green roof systems] Vegetative roofs, roof gardens and landscaped roofs. [The green roof system] Vegetative roofs, roof gardens and landscaped roofs shall comply with the provisions of this section and New York City Fire Code.

1507.16.1 Design standards. [Green roof systems] Vegetative roofs, roof gardens and landscaped roofs shall comply with ANSI/SPRI RP-14 and ANSI/SPRI VF-1, or with FM DS 1-35.

Exceptions:

1.	The aggregate area of landscaping materials or growth media or both on any single roof level of a building or structure is 250 square feet (23.2 m2) or less.

2.	The roof area is 22 feet (6706 mm) or less from grade.

3.	The [green] vegetative roof system is a container garden.

1507.16.2 Roof structure. The roof structure shall comply with Chapter 16 for the design of the [green roofs system] vegetative roofs, roof gardens and landscaped roofs.

1507.16.3 Roof covering. Roof covering shall comply with Section 1507.10, 1507.11, 1507.12, 1507.13, or 1507.15.

1507.16.4 Slope. The roofing membrane shall have a design slope in accordance with the roof covering utilized. Overburden shall be installed to prevent slippage tested as an assembly.

1507.16.5 Structural fire resistance. The structural frame and roof construction supporting the load imposed upon the roof by the vegetative roof, roof gardens or landscaped roofs shall comply with the requirements of Table 601.

1507.17 Photovoltaic shingles. The installation of photovoltaic shingles shall comply with the provisions of this section.

1507.17.1 Deck requirements. Photovoltaic shingles shall be applied to a solid or closely fitted deck, except where the shingles are specifically designed to be applied over spaced sheathing.

1507.17.2 Deck slope. Photovoltaic shingles shall not be installed on roof slopes less than three units vertical in 12 units horizontal (25-percent slope).

1507.17.3 Underlayment. Unless otherwise noted, required underlayment shall conform to ASTM D 226, ASTM D 4869 or ASTM D 6757.

1507.17.4 Underlayment application. Underlayment shall be applied shingle fashion, parallel to and starting from the eave, lapped 2 inches (51 mm) and fastened sufficiently to hold in place.

1507.17.4.1 High wind attachment. Underlayment applied in areas subject to high winds (Vasd greater than 110 mph (49 m/s) as determined in accordance with Section 1609.3.1) shall be applied with corrosion-resistant fasteners in accordance with the manufacturer’s instructions. Fasteners shall be applied along the overlap at not more than 36 inches (914 mm) on center. Underlayment installed where Vasd is not less than 120 mph (54 m/s) shall comply with ASTM D 226, Type II, ASTM D 4869, Type IV or ASTM D 6757. The underlayment shall be attached in a grid pattern of 12 inches (305 mm) between side laps with a 6-inch (152 mm) spacing at the side laps. Underlayment shall be applied in accordance with Section 1507.2.8 except all laps shall be a minimum of 4 inches (102 mm). Underlayment shall be attached using metal or plastic cap nails with a head diameter of not less than 1 inch (25 mm) with a thickness of not less than 32-gage (0.0134 inch (0.34 mm)) sheet metal. The cap nail shank shall be a minimum of 12 gage (0.105 inch (2.67 mm)) with a length to penetrate through the roof sheathing or a minimum of 3/4 inch (19.1 mm) into the roof sheathing.

Exception: As an alternative, adhered underlayment complying with ASTM D 1970 shall be permitted.

1507.17.4.2 Ice barrier. An ice barrier that consists of at least two layers of underlayment cemented together or of a self-adhering polymer modified bitumen sheet shall be used instead of normal underlayment and extend from the lowest edges of all roof surfaces to a point not less than 24 inches (610 mm) inside the exterior wall line of the building.

Exception: Detached accessory structures that contain no conditioned floor area.

1507.17.5 Fasteners. Fasteners for photovoltaic shingles shall be galvanized, stainless steel, aluminum or copper roofing nails, minimum 12-gage (0.105 inch (2.67 mm)) shank with a minimum ⅜-inch-diameter (9.5 mm) head, of a length to penetrate through the roofing materials and a minimum of ¾ inch (19.1 mm) into the roof sheathing. Where the roof sheathing is less than ¾ inch (19.1 mm) thick, the nails shall penetrate through the sheathing. Fasteners shall comply with ASTM F 1667.

1507.17.6 Material standards. Photovoltaic shingles shall be listed and labeled in accordance with UL 1703.

1507.17.7 Attachment. Photovoltaic shingles shall be attached in accordance with the manufacturer’s instructions.

1507.17.8 Wind resistance. Photovoltaic shingles shall be tested in accordance with procedures and acceptance criteria in ASTM D 3161. Photovoltaic shingles shall comply with the classification requirements of Table 1504.1.1 for the appropriate maximum nominal design wind speed. Photovoltaic shingle packaging shall bear a label to indicate compliance with the procedures in ASTM D 3161 and the required classification from Table 1504.1.1.

SECTION BC 1508
ROOF INSULATION

1508.1 General. The use of above-deck thermal insulation shall be permitted provided such insulation is covered with an approved roof covering and passes the tests of [FM 4450] NFPA 276 or UL 1256 when tested as an assembly.

Exceptions:

1.	Foam plastic roof insulation shall conform to the material and installation requirements of Chapter 26.

2.	Where a concrete roof deck is used and the above-deck thermal insulation is covered with an approved roof covering.

1508.1.1 Cellulosic fiberboard. Cellulosic fiberboard roof insulation shall conform to the material and installation requirements of Chapter 23.

1508.2 Material standards.  Above-deck thermal insulation board shall comply with the standards in Table 1508.2.

| TABLE 1508.2 MATERIAL STANDARDS FOR ROOF INSULATION |
| --- |
| Material | Standard |
| Cellular glass board | ASTM C 552 |
| Composite boards | ASTM C 1289, Type III, IV, V or VI |
| Expanded polystyrene | ASTM C 578 |
| Extruded polystyrene [board] | ASTM C 578 |
| Fiber-reinforced gypsum board | ASTM C 1278 |
| Glass-faced gypsum board | ASTM C 1177 |
| Mineral fiber insulation board | ASTM C 726 |
| Perlite board | ASTM C 728 |
| Polyisocyanurate board | ASTM C 1289, Type I or [Type] II |
| Wood fiberboard | ASTM C 208 |

SECTION BC 1509
RADIANT BARRIERS INSTALLED ABOVE DECK

1509.1 General. A radiant barrier installed above a deck shall comply with Sections 1509.2 through 1509.4.

1509.2 Fire testing. Radiant barriers shall be permitted for use above decks where the radiant barrier is covered with an approved roof covering and the system consisting of the radiant barrier and the roof covering complies with the requirements of either FM 4550 or UL 1256.

1509.3 Installation. The low emittance surface of the radiant barrier shall face the continuous airspace between the radiant barrier and the roof covering.

1509.4 Material standards. A radiant barrier installed above a deck shall comply with ASTM C 1313/1313M.

SECTION BC 1510
ROOFTOP STRUCTURES

[1509.1] 1510.1 General. The provisions of this section shall govern the construction of rooftop structures.  All rooftop structures shall be subject to the roof area coverage limitations and building height requirements of Chapter 5. Rooftop structures shall be constructed with materials as required for the building, except as provided for in this section.

[1509.2] 1510.2 Bulkheads and penthouses. Bulkheads and penthouses shall comply with the construction requirements of this Section 1509.2.

[1509.2.1] 1510.2.1 Type of construction. Bulkheads and penthouses shall be constructed with walls, floors and roof as required for the building.

Exceptions: Where the total aggregate area of all rooftop structures does not exceed 33 percent of the area of the roof of the building upon which they are erected[;], the following shall apply:

1.	Bulkheads on buildings of Type I and II construction. The exterior walls and roofs of such bulkheads with a fire separation distance of more than 5 feet (1524 mm) and less than 30 feet (9144 mm) shall be of at least 1-hour fire-resistance-rated noncombustible construction. Walls and roofs with a fire separation distance of 30 feet (9144 mm) or greater shall be of noncombustible construction. Interior framing and walls shall be of noncombustible construction.

2.	Bulkheads on buildings of Type III, IV and V construction. The exterior walls of such bulkheads with a fire separation distance of more than 5 feet (1524 mm) and less than 30 feet (9144 mm) shall be at least 1-hour fire-resistance-rated construction. Walls with a fire separation distance of 30 feet (9144 mm) or greater from a common property line shall be of Type IV construction, or noncombustible construction. Roofs shall be constructed of materials and fire-resistance rated as required in Table 601 [and Section 603, Item 25.3]. Interior framing and walls shall be Type IV or noncombustible or fire-retardant-treated wood construction

[3. On one-story buildings, combustible unroofed mechanical equipment screens, fences or similar enclosures are permitted where located with a fire separation distance of at least 20 feet (6096 mm) from adjacent property lines and where not exceeding 4 feet (1219 mm) in height above the roof surface.]

[1509.2.2] 1510.2.2 Penthouses. Enclosed walls of penthouses shall comply with the requirements for exterior walls as per Tables 601 and 602 for the construction class of the building on which they are erected. Roofs of penthouses shall comply with the requirements for roof construction of Table 601 and Chapter 15 of this code.

[1509.2.3] 1510.2.3 Bulkheads. An enclosed rooftop structure not intended for human occupancy shall not be used for purposes other than shelter of mechanical equipment or shelter of vertical shaft openings in the roof. Provisions, such as louvers, louver blades or flashing, shall be made to protect the mechanical equipment and the building interior from the elements.

[1509.3 Tank Supports] 1510.3 Tanks. Tanks having a capacity of more than 500 gallons [(2 m3) placed in or on] (1893 L) located on the roof deck of a building shall be supported on masonry, reinforced concrete, steel or Type IV construction provided that, where such supports are located in the building above the lowest story, the support shall be fire-resistance rated as required for Type IA construction.

[1509.3.1] 1510.3.1 Valve and drain. [Such tanks shall have in] In the bottom or on the side near the bottom of the tank, a pipe or outlet, fitted with a suitable [quick opening] quick-opening valve for discharging the contents into a drain in an emergency [through an adequate drain] shall be provided.

[1509.3.2] 1510.3.2 Location. [Such tanks] Tanks shall not be placed over or near a [line of stairs] stairway or an elevator shaft, unless there is a solid roof or floor underneath the tank.

[1509.3.3] 1510.3.3 Tank cover. Unenclosed roof tanks shall have covers sloping toward the [outer edges] perimeter of the tanks.

[1509.4] 1510.4 Cooling towers. [Cooling towers in excess of 250 square feet (23.2 m2) in base area or in excess of 15 feet (4572 mm) high where located on building roofs more than 50 feet (15 240 mm) high shall be of noncombustible construction.] Cooling towers shall be of noncombustible construction.

Exceptions:

1.	[Drip boards and the enclosing construction of wood not less than 1 inch (25 mm) nominal thickness, provided the wood is covered on the exterior of the tower with noncombustible material.] Fill and drift eliminators of limited combustible materials may be considered noncombustible if the cooling towers are provided with automatic sprinkler protection complying with Section 903 of this code.

[2.	Fill and drift eliminators may be of combustible material if the towers are provided with automatic sprinkler protection complying with Section 903 of this code.]

[3] 2.	Fill and drift eliminators that comply with Section 908 of the New York City Mechanical Code.

[1509.5] 1510.5 Steeples, minarets, spires, domes and cupolas. [Any steeple, minaret, spire, dome or cupola shall be of a type of construction not less in fire-resistance rating than required for the building to which it is attached except that any such steeple, minaret, spire, dome or cupola that exceeds 85 feet (25 908 mm) in height above grade plane, exceeds 200 square feet (18.6 m2) in horizontal area or is used for any purpose other than a belfry or an architectural embellishment shall be constructed of and supported on Type I or II construction.] Steeples, minarets, spires, domes, cupolas and other similar architectural elements not used for occupancy or storage, shall be constructed of materials consistent with the required type of construction of the building and shall be of a type of construction having fire-resistance ratings not less than required for the building on top of which such steeple, minaret, spire, dome or cupola is built.

[1509.5.1] 1510.5.1 Noncombustible construction required.  [Any steeple, minaret, spire, dome or cupola that exceeds 60 feet (18 288 mm) in height above the highest point at which it comes in contact with the roof, or that exceeds 200 square feet (18.6 m2) in area at any horizontal section, or which is intended to be used for any purpose other than a belfry or architectural embellishment, shall be entirely constructed of and supported by noncombustible materials. Such structures shall be separated from the building below by construction having a fire-resistance rating of not less than 1.5 hours with openings protected with a minimum 1.5-hour fire-protection rating. Such structures placed above the roof of any building more than 50 feet (15 240 mm) in height, shall be of noncombustible material and shall be supported by construction of noncombustible material.] Steeples, minarets, spires, domes and cupolas greater than 60 feet (18 288 mm) in height above the highest point at which such structure contacts the roof as measured to the highest point on such structure, or that exceeds 200 square feet (18.6 m2) in area at any horizontal section, or which is intended to be used for any purpose other than a belfry or architectural embellishment, or is located on the top of a building greater than 50 feet (1524 mm) in building height shall be constructed of and supported by noncombustible materials and shall be separated from the building below by construction having a fire-resistance rating of not less than 1.5 hours with openings protected in accordance with Section 712. Such structures located on the top of a building greater than 50 feet (15 240 mm) in building height, shall be supported by noncombustible construction.

[1509.5.2 Steeples, minarets and spires] 1510.5.2 Steeples, minarets and spires. Steeples, minarets, and spires [where enclosed] shall have exterior walls constructed as required for the building [to] on top of which [they] such steeples, minarets and spires are [attached] built. The roof covering of spires shall be [of a] not less than the same class of roof covering [as required for the main roof of the rest of the structure.] required for the building on top of which the spire is located.

[1509.6] 1510.6 Dormers. Dormers shall have exterior walls as required for the building to which they are attached. The roof covering of dormers shall be of a class of roof covering as required for the main roof of the rest of the structure.

[1509.7] 1510.7 Greenhouses. Greenhouses used for the cultivation of plants, on the roofs of buildings other than buildings of Type V construction, shall be constructed of noncombustible framework and shall be glazed with plain or wire glass, or light transmitting plastic glazing complying with the requirements of Section 2606. The floors of greenhouses shall be constructed to be at least equal to the requirements for roof construction on Table 601 for the construction class of the building on which it is located.

[1509.8] 1510.8 Protective guards. Buildings greater than 22 feet (6706 mm) in height with roof slopes less than 2.4 units vertical in 12 units horizontal (20-percent slope) shall be provided with a parapet, [railing] guards, fence, or combination thereof, not less than 42 inches (1067 mm) in height. [Railings] Guards or fences may be located inward from the face of the exterior wall a distance not exceeding 6 feet (1829 mm). [Railings] Guards or fences shall be of noncombustible material, except on buildings of Type V construction. [Railings] Guards shall be constructed to comply with the requirements of Sections [1012] 1015 and 1607.7.

[1509.8.1] 1510.8.1 Fences on roofs used for recreational purposes. Rooftops used for recreational purposes shall be provided with wire fencing at least 10 feet (3048 mm) in height. Openings in the fence shall not permit the passage of a 4-inch diameter (102 mm) sphere. Where ball games are played on rooftops the wire fencing shall be extended to provide an overhead closure.

[1509.9] 1510.9 Miscellaneous combustible roof structures. The following roof structures may be constructed of combustible material if less than 12 feet (1658 mm) high above the roof: antenna supports; flagpoles; clothes drying frames; duckboarding, decking or platforms that do not cover more than 20 percent of the contiguous roof area at that level.

1510.10 Mechanical equipment screens. Mechanical equipment screens shall be constructed of the materials specified for the exterior walls in accordance with the type of construction of the building.

1510.10.1 Type V construction. The height of mechanical equipment screens located on the roof decks of buildings of Type V construction, as measured from grade plane to the highest point on the mechanical equipment screen, shall be permitted to exceed the maximum building height allowed for the building by other provisions of this code where complying with any one of the following limitations, provided the fire separation distance is greater than 5 feet (1524 mm):

1.	Where the fire separation distance is not less than 20 feet (6096 mm), the height above grade plane of the mechanical equipment screen shall not exceed 4 feet (1219 mm) more than the maximum building height allowed;

2.	The mechanical equipment screen shall be constructed of noncombustible materials;

3.	The mechanical equipment screen shall be constructed of fire-retardant-treated wood complying with Section 2303.2 for exterior installation; or

4.	Where the fire separation distance is not less than 20 feet (6096 mm), the mechanical equipment screen shall be constructed of materials having a flame spread index of 25 or less when tested in the minimum and maximum thicknesses intended for use with each face tested independently in accordance with ASTM E 84 or UL 723.

[1509.10] 1510.11 Photovoltaic systems. Rooftop mounted photovoltaic systems shall be designed in accordance with this section.

[1509.10.1] 1510.11.1 Wind resistance. Rooftop mounted photovoltaic systems shall be designed for wind loads for component and cladding in accordance with Chapter 16 using an effective wind area based on the dimensions of a single unit frame.

[1509.10.2] 1510.11.2 Fire classification. Rooftop mounted photovoltaic [systems] panels and modules shall have the [same] fire classification [as the roof assembly required by] in accordance with Section [1505] 1505.9.

[1509.10.3] 1510.11.3 Installation. Rooftop mounted photovoltaic [systems] panels and modules shall be installed in accordance with the manufacturer’s [installation] instructions.

[1509.10.4] 1510.11.4 Photovoltaic panels and modules. Photovoltaic panels and modules Rooftop mounted on top of a roof shall be listed and labeled in accordance with UL 1703 and shall be installed in accordance with the manufacturer’s [installation] instructions.

SECTION BC [1510] 1511
REROOFING

[1510.1] 1511.1 General. Materials and methods of application used for recovering or replacing an existing roof covering shall comply with the requirements of Chapter 15.

[Exception] Exceptions:

1.	Section 1504.9 shall not apply if the area to be recovered or replaced is less than 50 percent of the roof area and less than 500 square feet (46 m2).

2.	Recovering or replacing an existing roof covering shall not be required to meet the requirement for secondary (emergency overflow) drains or scuppers in Section 1503.4 for roofs that provide for positive roof drainage. For the purposes of this exception, existing secondary drainage or scupper systems required in accordance with this code shall not be removed unless they are replaced by secondary drains or scuppers designed and installed in accordance with Section 1503.4.

[1510.1.1] 1511.1.1 Slope. Reroofs shall provide positive drainage.

[1510.2] 1511.2 Structural and construction loads. Structural roof components shall be capable of supporting the roof-covering system and the material and equipment loads that will be encountered during installation of the system.

[1510.3 Recovering versus replacement. New roof coverings shall not be installed without first removing all existing layers of roof coverings down to the roof deck where any of the following conditions occur:]

[1.	Where the existing roof or roof covering is water soaked or has deteriorated to the point that the existing roof or roof covering is not adequate as a base for additional roofing.]

[2.	Where the  existing roof covering is wood shake, slate, clay, cement or asbestos-cement tile.]

[3.	Where the existing roof has two or more applications of any type of roof covering.]

1511.3 Roof replacement.  Roof replacement shall include the removal of all existing layers of roof coverings down to the roof deck.

Exception: Where the existing roof assembly includes an ice barrier membrane that is adhered to the roof deck, the existing ice barrier membrane shall be permitted to remain in place and covered with an additional layer of ice barrier membrane in accordance with Section 1507.

1511.3.1 Roof recover. The installation of a new roof covering over an existing roof covering shall be permitted where any of the following conditions occur:

[Exceptions:]

1.	Where the new roof covering is installed in accordance with the roof covering manufacturer’s instructions.

[1.] 2.	Complete and separate roofing systems, such as standing-seam metal roof panel systems, that are designed to transmit the roof loads directly to the building’s structural system and that do not rely on existing roofs and roof coverings for support, shall not require the removal of existing roof coverings.

[2.] 3.	Metal panel, metal shingle [,] and concrete and clay tile roof coverings shall be permitted to be installed over existing wood shake roofs when applied in accordance with Section [1510.4] 1511.4.

[3.] 4.	The application of a new protective coating over an existing spray polyurethane foam roofing system shall be permitted without tear-off of existing roof coverings.

1511.3.1.1 Exceptions. A roof recover shall not be permitted where any of the following conditions occur:

1.	Where the existing roof or roof covering is water soaked or has deteriorated to the point that the existing roof or roof covering is not adequate as a base for additional roofing.

2.	Where the existing roof covering is slate, clay, cement or asbestos-cement tile.

3.	Where the existing roof has two or more applications of any type of roof covering.

[1510.4] 1511.4 Roof recovering. Where the application of a new roof covering over wood shingle or shake roofs creates a combustible concealed space, the entire existing surface shall be covered with gypsum board, mineral fiber, glass fiber or other approved materials securely fastened in place.

[1510.5] 1511.5 Reinstallation of materials. Existing slate, clay or cement tile shall be permitted for reinstallation, except that damaged, cracked or broken slate or tile shall not be reinstalled. Existing vent flashing, metal edgings, drain outlets, collars and metal counterflashings shall not be reinstalled where rusted, damaged or deteriorated. Aggregate surfacing materials shall not be reinstalled.

[1510.6] 1511.6 Flashings. Flashings shall be reconstructed in accordance with [approved] manufacturer’s [installation] instructions. Metal flashing to which bituminous materials are to be adhered shall be primed prior to installation.

1511.7 Roof assembly.  Roof assembly shall be designed and constructed to meet the requirements of the New York City Energy Conservation Code.

SECTION BC [1511] 1512
SOLAR PHOTOVOLTAIC PANELS/MODULES AND 
REQUIRED SUSTAINABLE ROOFING ZONES

[1511.1] 1512.1 Solar photovoltaic panels/modules. Solar photovoltaic panels/modules installed upon a roof or as an integral part of a roof assembly shall comply with the requirements of this code and the New York City Fire Code.

[1511.1.1] 1512.1.1 Structural fire resistance. The structural frame and roof construction supporting the load imposed upon the roof by the photovoltaic panels/modules shall comply with the requirements of Table 601.

[1511.2] 1512.2 Sustainable roofing zone. A sustainable roofing zone shall be required on 100 percent of the roof. For such sustainable roofing zone:

1.	A contiguous area of a sustainable roofing zone measuring less than 200 square feet (18.5 m2), or in the case of a building five stories or less in height where the main use or dominant occupancy is classified as Group R, such an area measuring less than 100 square feet (9.20 m2), shall be equipped with at least a solar photovoltaic electricity generating system if such system would accommodate at least 4kW of solar photovoltaic electricity generating capacity, as determined by the department; and

2.	A sustainable roofing zone with a slope less than or equal to two units vertical in 12 units horizontal (17 percent) that would accommodate less than 4kW of solar photovoltaic electricity generating capacity, as determined by the department, shall be equipped with at least a green roof system.

Exceptions:

1.	Areas required to be set aside for setbacks or access pursuant to the New York City Fire Code, the New York City Construction Codes, or the Zoning Resolution of the City of New York.

2.	Areas occupied by rooftop structures, mechanical equipment, towers, parapets, guardrails, solar thermal systems, and appurtenances.

[2.] 3.	Areas occupied by obstructions related to stormwater management practices including, but not limited to, cisterns, or reuse systems that are installed to comply with site connection or stormwater construction permits issued by the department of environmental protection.

[3.] 4.	Terraces on setbacks comprising less than 25 percent of the area of the largest floor plate in the building.

[4.] 5.	Recreational spaces that are principal to the use of the building on which the rooftop is located.

[5.] 6.	A roof assembly with a slope greater than two units vertical in 12 units horizontal (17 percent) that would accommodate less than 4kW of solar photovoltaic electricity generating capacity.

[6.] 7.	Areas where site conditions are determined by the department to be unfavorable to either a solar photovoltaic electricity generating system or a green roof system.

§ 17. Chapter 16 of the New York city building code, as amended by local law number 141 for the year 2013, is amended to read as follows:

CHAPTER 16
STRUCTURAL DESIGN

SECTION BC 1601
GENERAL

1601.1 Scope. The provisions of this chapter shall govern the structural design of buildings, structures and portions thereof regulated by this code. [(Note: Where the text in this Code refers to ASCE 7, the 2005 edition shall be used; and where the text in this Code refers to ASCE 7-10, the 2010 edition shall be used.)]

1601.1.1 Referenced standards. Where this code makes reference to the nationally recognized standard ASCE 7, such standard shall be as modified for New York City in accordance with this chapter.

1601.2 Special provisions for prior code buildings. The provisions of Sections 1601.2.1 through 1601.2.4 shall apply to structural work on prior code buildings.

1601.2.1 Use of this code. Notwithstanding the applicant’s election to use the 1968 Building Code or prior code, the structural calculations shall be permitted to be performed in accordance with this code provided that the structural safety of the prior code building is not reduced. Notwithstanding the provisions of Section 28-101.4.4 of the Administrative Code, the use of Load and Resistance Factor Design (LRFD) engineering calculations shall not be deemed to reduce structural safety provided the properties of the existing materials are determined using accepted engineering principles.

1601.2.2 Live loads. Loads indicated in the applicable prior code shall be permitted for structural calculations using engineering formulas from this code provided that the structural safety of the prior code building is not reduced.

1601.2.3 Seismic loads. The determination as to whether seismic requirements apply to an alteration shall be made in accordance with the 1968 Building Code and interpretations by the department relating to such determinations. Any applicable seismic loads and requirements, including for the bracing of architectural, mechanical, plumbing, fuel gas, fire suppression and electrical systems and equipment, shall be permitted to be determined in accordance with this chapter or the 1968 Building Code and reference standard RS 9-6 of such code.

1601.2.4 Wind loads. All alterations, minor alterations, and ordinary repairs, to the extent of such work, shall be permitted to be performed in accordance with the wind load requirements set forth in the 1968 Building Code, or where the 1968 Building Code so authorizes, the code in effect prior to December 6, 1968.

Exceptions:

1.	Equipment, appliances and supports that are exposed to wind shall be designed and installed to resist the wind pressures determined in accordance with Section 1609.

2.	Wind loads on glass shall not be permitted to be calculated in accordance with the code in effect prior to December 6, 1968.

3.	When the wind surface area of a prior code building or structure is increased by more than 5 percent in any direction or there is a permanent decrease of the lateral force capacity by more than 20 percent in any direction, the entire building or structure shall be designed to resist the design wind load as calculated pursuant to the applicable code, but not less than 5 psf (0.24k N/m2).

SECTION BC 1602
DEFINITIONS AND NOTATIONS

1602.1 Definitions. The following [words and terms shall, for the purposes of this code, have the meanings shown herein.] terms are defined in Chapter 2:

ALLOWABLE STRESS DESIGN.[A method of proportioning structural members, such that elastically computed stresses produced in the members by nominal loads do not exceed specified allowable stresses (also called “working stress design”).]

BALCONY, EXTERIOR.[See ASCE 7.]

DEAD [LOADS] LOAD.[The weight of materials of construction incorporated into the building, including but not limited to walls, floors, roofs, ceilings, stairways, built-in partitions, finishes, cladding and other similarly incorporated architectural and structural items, and the weight of fixed service equipment, such as cranes, plumbing stacks and risers, electrical feeders, heating, ventilating and air-conditioning systems and automatic sprinkler systems.]

DECK.[See ASCE 7.]

DESIGN STRENGTH.[The product of the nominal strength and a resistance factor (or strength reduction factor).]

DIAPHRAGM.[A horizontal or sloped system acting to transmit lateral forces to the vertical-resisting elements. When the term “diaphragm” is used, it shall include horizontal bracing systems.]

Diaphragm, blocked.[In light-frame construction, a diaphragm in which all sheathing edges not occurring on a framing member are supported on and fastened to blocking.]

Diaphragm boundary.[In light-frame construction, a location where shear is transferred into or out of the diaphragm sheathing. Transfer is either to a boundary element or to another force-resisting element.]

Diaphragm chord.[A diaphragm boundary element perpendicular to the applied load that is assumed to take axial stresses due to the diaphragm moment.]

[Diaphragm, flexible. A diaphragm is flexible for the purpose of distribution of story shear and torsional moment where so indicated in- Section 12.3.1 of ASCE 7-10.]

[Diaphragm, rigid. A diaphragm is rigid for the purpose of distribution of story shear and torsional moment when the lateral deformation of the diaphragm is less than or equal to two times the average story drift.]

[DURATION OF LOAD. The period of continuous application of a given load, or the aggregate of periods of intermittent applications of the same load.]

ESSENTIAL FACILITIES.[Buildings and other structures that are intended to remain operational in the event of extreme environmental loading from flood, wind, snow or earthquakes.]

FABRIC PARTITION.[A partition consisting of a finished surface made of fabric, without a continuous rigid backing, that is directly attached to a framing system in which the vertical framing members are spaced greater than 4 feet (1219 mm) on center.]

FACTORED LOAD.[The product of a nominal load and a load factor.]

[GUARD. See Section 1002.1.]

HELIPAD.

ICE-SENSITIVE STRUCTURE.

IMPACT LOAD.[The load resulting from moving machinery, elevators, craneways, vehicles and other similar forces and kinetic loads, pressure and possible surcharge from fixed or moving loads.]

LIMIT STATE.[A condition beyond which a structure or member becomes unfit for service and is judged to be no longer useful for its intended function (serviceability limit state) or to be unsafe (strength limit state).]

LIVE [LOADS] LOAD.[Those loads produced by the use and occupancy of the building or other structure and do not include construction or environmental loads such as wind load, snow load, rain load, earthquake load, flood load or dead load.]

LIVE [LOADS] LOAD (ROOF).[Those loads produced (1) during maintenance by workers, equipment and materials; and (2) during the life of the structure by movable objects such as planters and by people.]

LOAD AND RESISTANCE FACTOR DESIGN (LRFD). [A method of proportioning structural members and their connections using load and resistance factors such that no applicable limit state is reached when the structure is subjected to appropriate load combinations. The term “LRFD” is used in the design of steel and wood structures.]

LOAD EFFECTS.[Forces and deformations produced in structural members by the applied loads.]

LOAD FACTOR.[A factor that accounts for deviations of the actual load from the nominal load, for uncertainties in the analysis that transforms the load into a load effect, and for the probability that more than one extreme load will occur simultaneously.]

LOADS.[Forces or other actions that result from the weight of building materials, occupants and their possessions, environmental effects, differential movement and restrained dimensional changes. Permanent loads are those loads in which variations over time are rare or of small magnitude, such as dead loads. All other loads are variable loads (see also “Nominal loads”).]

NOMINAL LOADS.[The magnitudes of the loads specified in this chapter (dead, live, soil, wind, snow, rain, flood and earthquake).]

[NOTATIONS.]

[D = Dead load.]

[E = Combined effect of horizontal and vertical earthquake-induced forces as defined in Section 12.4.2 of ASCE 7-10.]

[F = Load due to fluids with well-defined pressures and maximum heights.]

[Fa = Flood load in accordance with Chapter 5 of ASCE 7.]

[H = Load due to lateral earth pressures, ground water pressure or pressure of bulk materials.]

[L = Live load, except roof live load, including any permitted live load reduction.]

[Lr = Roof live load including any permitted live load reduction.]

[plf = pounds per linear foot.]

[psig = pounds per square inch gauge.]

[R = Rain load.]

[S = Snow load.]

[T = Self-straining force arising from contraction or expansion resulting from temperature change, shrinkage, moisture change, creep in component materials, movement due to differential settlement or combinations thereof.]

[W = Load due to wind pressure.]

OTHER STRUCTURES.[Structures, other than buildings, for which loads are specified in this chapter.]

PANEL (PART OF A STRUCTURE).[The section of a floor, wall or roof comprised between the supporting frame of two adjacent rows of columns and girders or column bands of floor or roof construction.]

RESISTANCE FACTOR.[A factor that accounts for deviations of the actual strength from the nominal strength and the manner and consequences of failure (also called “strength reduction factor”).]

RISK CATEGORY.[See definition for “Structural Occupancy Category.”]

STRENGTH, NOMINAL.[The capacity of a structure or member to resist the effects of loads, as determined by computations using specified material strengths and dimensions and equations derived from accepted principles of structural mechanics or by field tests or laboratory tests of scaled models, allowing for modeling effects and differences between laboratory and field conditions.]

STRENGTH, REQUIRED.[Strength of a member, cross section or connection required to resist factored loads or related internal moments and forces in such combinations as stipulated by these provisions.]

STRENGTH DESIGN.[A method of proportioning structural members such that the computed forces produced in the members by factored loads do not exceed the member design strength. The term “strength design” is used in the design of concrete and masonry structural elements.]

[STRUCTURAL OCCUPANCY CATEGORY. A category used to determine structural requirements based on occupancy.]

SUSCEPTIBLE BAY.

VEHICLE BARRIER. [SYSTEM. A system of building components near open sides of a garage floor or ramp or building walls that act as restraints for vehicles.]

NOTATIONS.

| D | = | Dead load. |
| --- | --- | --- |
| Di | = | Weight of ice in accordance with Chapter 10 of ASCE 7. |
| E | = | Combined effect of horizontal and vertical earthquake induced forces as defined in Section 12.4.2 of ASCE 7. |
| F | = | Load due to fluids with well-defined pressures and maximum heights. |
| Fa | = | Flood load in accordance with Chapter 5 of ASCE 7. |
| H | = | Load due to lateral earth pressures, ground water pressure or pressure of bulk materials. |
| L | = | Roof live load greater than 20 psf (0.96 kN/m2) and floor live load. |
| Lr | = | Roof live load of 20 psf (0.96 kN/m2) or less. |
| R | = | Rain load. |
| S | = | Snow load. |
| T | = | Cumulative effects of self-straining load forces and effects. |
| Vasd | = | Allowable stress design wind speed, miles per hour (mph) (km/hr) where applicable. |
| V | = | Basic design wind speeds, miles per hour (mph) (km/hr) determined from Table 1609.3. |
| W | = | Load due to wind pressure. |
| Wi | = | Wind-on-ice in accordance with Chapter 10 of ASCE 7. |

SECTION BC 1603
CONSTRUCTION DOCUMENTS

1603.1 General. Construction documents shall include drawings that show the sizes, sections and relative locations of structural members with floor levels, column centers and offsets fully dimensioned. The design loads and other information pertinent to the structural design required by Sections 1603.1.1 through [1603.1.9] 1603.1.10 shall be clearly indicated on [the] such drawings of parts of the building or structure.

Exception: In lieu of the requirements of Sections 1603.1.1 through 1603.1.10, construction documents for buildings constructed in accordance with the conventional light-frame construction provisions of Section 2308 shall include drawings that indicate the following structural design information:

1.	Floor and roof dead and live loads.

2.	Ground snow load, Pg.

3.	Basic design wind speed [(3-second gust)], V, miles per hour (mph) (km/hr) and allowable stress design wind speed, Vasd, as determined in accordance with Section 1609.3.1 and wind exposure.

4.	Seismic design category and site class.

5.	Flood design data, if located in flood hazard areas [established in Section G102.2 of Appendix G].

6.	Design load-bearing values of soils or rock under shallow foundations and/or the design load capacity of deep foundations.

1603.1.1 Floor live load. The uniformly distributed, concentrated and impact floor live load used in the design shall be indicated for floor areas. [Live] Use of live load reduction [of the uniformly distributed floor live loads, if used] in [the design,] accordance with Section 1607.11 shall be indicated for each type of live load used in the design.

1603.1.2 Partition loads. The equivalent uniform partition loads or, in lieu of these, a statement to the effect that the design was predicated on actual partition loads.

1603.1.3 Roof live load. The roof live load used in the design shall be indicated for roof areas [(Section 1607.11)] (Section 1607.13).

1603.1.4 Roof snow load data. The ground snow load, Pg, shall be indicated. The following additional information shall also be provided, regardless of whether snow loads govern the design of the roof:

1.	Flat-roof snow load, Pf.

2.	Snow exposure factor, Ce.

3.	Snow load importance factor, Is.

4.	Thermal factor, Ct.

5.	Slope factor(s), Cs.

6.	Drift surcharge load(s), Pd, where the sum of Pd and Pf exceeds 20 psf (0.96 kN/m2).

7.	Width of snow drift(s), w.

1603.1.5 Wind design data. The following information related to wind loads shall be shown, regardless of whether wind loads govern the design of the [lateral-force-resisting] lateral force-resisting system of the [building] structure:

1.	Basic design wind speed [(3-second gust)], V, miles per hour (km/hr) and/or allowable stress design wind speed, Vasd, as determined in accordance with Section 1609.3 and 1609.3.1.

2.	[Wind importance factor, I, and structural occupancy] Risk category.

3.	Wind exposure. [Where] Applicable wind direction if more than one wind exposure is utilized [, the wind exposure and applicable wind direction shall be indicated].

4.	[The applicable] Applicable internal pressure coefficient.

5.	[Components and cladding. The design] Design wind pressures [in terms of psf (kN/m2)] to be used for [the design of] exterior component and cladding materials not specifically designed by the registered design professional responsible for the design of the structure, psf (kN/m2).

6.	Design base shear.

1603.1.6 Earthquake design data. The following information related to seismic loads shall be shown, regardless of whether seismic loads govern the design of the [lateral-force-resisting] lateral force-resisting system of the [building] structure:

1.	Risk category.

[1.] 2.	Seismic importance factor,[I, and structural occupancy category] Ie.

[2.] 3.	Mapped spectral response [accelerations] acceleration parameters, SS and S1.

[3.] 4.	Site class.

[4.] 5.	[Spectral] Design spectral response [coefficients] acceleration parameters, SDS and SD1.

[5.] 6.	Seismic design category.

[6.] 7.	Basic [seismic-force-resisting] seismic force-resisting system(s).

[7.] 8.	Design base shear(s).

[8.] 9.	Seismic response coefficient(s), CS.

[9.] 10.	Response modification [factor] coefficient(s), R.

[10.] 11. Analysis procedure used.

1603.1.7 Geotechnical information. The design load-bearing values of soils or rock under shallow foundations and/or the design load capacity of deep foundations shall be shown on the construction [drawings] documents.

1603.1.8 Flood [load. Buildings] hazard areas. Construction documents for buildings and other structures located in [areas of special] flood hazard areas shall [meet the design requirements of Section 5.3 of ASCE 7. The structural design shall be based on the design loads stated in Section 5.4 of ASCE 7.] comply with provisions of Section G104.2.1.

1603.1.9 Special loads. Special loads that are applicable to the design of the building, structure or portions thereof [shall be indicated along with the specified section of this code that addresses the special loading condition], including but not limited to the loads of machinery or equipment, and that are greater than the specified floor and roof loads shall be specified by their descriptions and locations.

1603.1.9.1 Photovoltaic panel systems. The dead load of rooftop-mounted photovoltaic panel systems, including rack support systems, shall be indicated on the construction documents.

1603.1.10 Superimposed dead loads. The uniformly distributed superimposed dead loads used in the design shall be indicated for floor and roof areas.

[1603.1.11 Other loads. Other loads used in the design, including but not limited to the loads of machinery or equipment, which are of greater magnitude than the loads defined in the specified floor and roof loads shall be indicated by their descriptions and locations.]

SECTION BC 1604
GENERAL DESIGN REQUIREMENTS

1604.1 General. Building, structures and parts thereof shall be designed and constructed in accordance with strength design, load and resistance factor design, allowable stress design, empirical design or conventional construction methods, as permitted by the applicable material chapters and referenced standards.

1604.2 Strength. Buildings and other structures, and parts thereof, shall be designed and constructed to support safely the factored loads in load combinations defined in this code without exceeding the appropriate strength limit states for the materials of construction. Alternatively, buildings and other structures, and parts thereof, shall be designed and constructed to support safely the nominal loads in load combinations defined in this code without exceeding the appropriate specified allowable stresses for the materials of construction. Loads and forces for occupancies or uses not covered in this chapter shall be subject to the approval of the commissioner.

1604.3 Serviceability. Structural systems and members thereof shall be designed to have adequate stiffness to limit deflections [and lateral drift. See Section 12.12.1 of ASCE 7-10 for drift limits applicable to earthquake loading.] as indicated in Table 1604.3. Drift limits applicable to earthquake loading shall be in accordance with ASCE 7 Chapter 12, 13, 15 or 16, as applicable.

| TABLE 1604.3 DEFLECTION LIMITSa,b,c,h,i |
| --- |
| CONSTRUCTION | L or Lr | S or Wf | D + Ld,g |
| Roof members:e |
| Supporting plaster or stucco ceiling | l/360 | l/360 | l/240 |
| Supporting nonplaster ceiling | l/240 | l/240 | l/180 |
| Not supporting ceiling | l/180 | l/180 | l/120 |
| Floor members | l/360 | — | l/240 |
| Exterior walls [and interior partitions]: |
| With plaster or stucco finishes | — | l/360 | — |
| With other brittle finishes | — | [l/120] l/240 | — |
| With flexible finishes | — | l/120 | — |
| Interior partitions:b |  |  |  |
| With plaster or stucco finishes | l/360 | — | — |
| With other brittle finishes | l/240 | — | — |
| With flexible finishes | l/120 | — | — |
| Farm buildings | — | — | l/180 |
| Greenhouses | — | — | l/120 |

For SI: 1 foot = 304.8 mm.

a.	For structural roofing and siding made of formed metal sheets, the total load deflection shall not exceed l/60. For secondary roof structural members supporting formed metal roofing, the live load deflection shall not exceed l/150. For secondary wall members supporting formed metal siding, the design wind load deflection shall not exceed l/90. For roofs, this exception only applies when the metal sheets have no roof covering.

- [Interior partitions not exceeding 6 feet in height and flexible] Flexible, folding and portable partitions are not governed by the provisions of this section. The deflection criterion for interior partitions is based on the horizontal load defined in Section [1607.13] 1607.15.

- See Section 2403 for glass supports.

- [For wood structural members having a moisture content of less than 16 percent at time of installation and used under dry conditions, the deflection resulting from L + 0.5D is permitted to be substituted for the deflection resulting from L + D.] The deflection limit for the D+(L+Lr) load combination only applies to the deflection due to the creep component of long-term dead load deflection plus the short-term live load deflection. For lumber, structural glued laminated timber, prefabricated wood I-joists and structural composite lumber members that are dry at time of installation and used under dry conditions in accordance with the ANSI/AWC NDS, the creep component of the long-term deflection shall be permitted to be estimated as the immediate dead load deflection resulting from 0.5D. For lumber and glued laminated timber members installed or used at all other moisture conditions or cross laminated timber and wood structural panels that are dry at time of installation and used under dry conditions in accordance with ANSI/AWC NDS, the creep component of the long-term deflection is permitted to be estimated as the immediate dead load deflection resulting from D. The value of 0.5D shall not be used in combination with ANSI/AWC NDS provisions for long-term loading.

- The [above] preceding deflections do not ensure against ponding. Roofs that do not have sufficient slope or camber to [assure] ensure adequate drainage shall be investigated for ponding. See [Section 1611 for rain and ponding requirements and Section 1503.4 for roof drainage requirements] Chapter 8 of ASCE 7.

- The wind load [is] shall be permitted to be taken as [0.7] 0.42 times the "component and cladding" loads or directly calculated using the 10-year mean return interval wind speed for the purpose of determining deflection limits [herein] in Table 1604.3. Where framing members support glass, the deflection limit therein shall not exceed that specified in Section 1604.3.7.

- For steel structural members, the deflection due to creep component of long-term dead load shall be permitted to be taken as zero.

- For aluminum structural members or aluminum panels used in skylights and sloped glazing framing, roofs or walls of sunroom additions or patio covers[,] not supporting edge of glass or aluminum sandwich panels, the total load deflection shall not exceed l/60. For continuous aluminum structural members supporting edge of glass, the total load deflection shall not exceed l/175 for each glass lite or l/60 for the entire length of the member, whichever is more stringent. For aluminum sandwich panels used in roofs or walls of sunroom additions or patio covers, the total load deflection shall not exceed l/120.

- I = Length of the member between supports. For cantilever members, l shall be taken as twice the length of the cantilever.

1604.3.1 Deflections. The deflections of structural members shall not exceed the more restrictive of the limitations of Sections 1604.3.2 through 1604.3.5 or that permitted by Table 1604.3.

1604.3.2 Reinforced concrete. The deflection of reinforced concrete structural members shall not exceed that permitted by ACI 318.

1604.3.3 Steel. The deflection of steel structural members shall not exceed that permitted by AISC 360, AISI [HSS S 100, ASCE 3] S100, ASCE 8, and SJI CJ-1.0 SJI JG-1.1, SJI K-1.1 or SJI LH/DLH-1.1] SJI 100 or SJI 200, as applicable.

1604.3.4 Masonry. The deflection of masonry structural members shall not exceed that permitted by TMS 402 [/ACI 530/ASCE 5], as modified by Chapter 21 of this code.

1604.3.5 Aluminum. The deflection of aluminum structural members shall not exceed that permitted by AA ADM1.

1604.3.6 Limits. [For limits on the deflection of structural members, refer to the relevant material design standards. Should a design standard not provide for deflection limits, deflection of structural members over span, l, shall not exceed that permitted by Table 1604.3.] The deflection limits of Section 1604.3.1 shall be used unless more restrictive deflection limits are required by a referenced standard for the element or finish material.

1604.3.7 Framing supporting glass. The deflection of framing members supporting glass subjected to 0.6 times the “component and cladding” wind loads shall not exceed either of the following:

1.	1/175 of the length of span of the framing member, for framing members having a length not more than 13 feet 6 inches (4115 mm).

2.	1/240 of the length of span of the framing member + ¼ inch (6.4 mm), for framing members having a length greater than 13 feet 6 inches (4115 mm).

1604.4 Analysis. Load effects on structural members and their connections shall be determined by methods of structural analysis that take into account equilibrium, general stability, geometric compatibility and both short- and long-term material properties.

Members that tend to accumulate residual deformations under repeated service loads shall have included in their analysis the [added eccentricities] effects of added deformations expected to occur during their service life. Secondary stresses in trusses shall be considered and, where of significant magnitude, their effects shall be provided for in the design.

Any system or method of construction to be used shall be based on a rational analysis in accordance with well-established principles of mechanics. Such analysis shall result in a system that provides a complete load path capable of transferring loads from their point of origin to the load-resisting elements.

The total lateral force shall be distributed to the various vertical elements of the [lateral-force-resisting] lateral force-resisting system in proportion to their rigidities, considering the rigidity of the horizontal bracing system or diaphragm. Rigid elements [that are] assumed not to be a part of the [lateral-force-resisting] lateral force-resisting system [shall be] are permitted to be incorporated into buildings provided that their effect on the action of the system is considered and provided for in the design. [Except where diaphragms are flexible, or are permitted to be analyzed as flexible] A diaphragm is rigid for the purpose of distribution of story shear and torsional moment when the lateral deformation of the diaphragm is less than or equal to two times the average story drift. Where required by ASCE 7, provisions shall be made for the increased forces induced on resisting elements of the structural system resulting from torsion due to eccentricity between the center of application of the lateral forces and the center of rigidity of the [lateral-force-resisting] lateral force-resisting system.

Every structure shall be designed to resist the effects caused by the forces specified in this chapter including overturning [effects caused by the lateral forces specified in this chapter], uplift and sliding. [See Section 1609 for wind loads, Section 1610 for lateral soil loads and Section 1613 for earthquake loads.] Where sliding is used to isolate the elements, the effects of friction between sliding elements shall be included as a force.

1604.5 [Structural occupancy] Risk category. Each building and structure shall be assigned a [structural occupancy] risk category in accordance with Table 1604.5. Where a referenced standard specifies an occupancy category, the risk category shall not be taken as lower than the occupancy category specified therein. Where a referenced standard specifies that the assignment of a risk category be in accordance with ASCE 7, Table 1.5-1, Table 1604.5 shall be used in lieu of ASCE 7, Table 1.5-1.

| TABLE 1604.5 [STRUCTURAL OCCUPANCY/] RISK CATEGORY OF BUILDINGS AND [IMPORTANCE FACTORS] OTHER STRUCTURES |
| --- |
| [STRUCTURAL STRUCTURAL OCCUPANCY/] RISK CATEGORY[a] | NATURE OF OCCUPANCY[/RISK] |
| I | Buildings and other structures that represent a low hazard to human life in the event of failure, including [,] but not limited to: 1. Agricultural facilities. 2. Certain temporary facilities. 3. Minor storage facilities. |
| II | Buildings and other structures except those listed in [Structural Structural Occupancy/] Risk Categories I, III and IV. |
| III | Buildings and other structures that represent a substantial hazard to human life in the event of failure, including[,] but not limited to: 1. Buildings and other structures whose primary occupancy is [public assembly] Places of Assembly with an occupant load greater than 300. 2. Buildings and other structures containing [elementary school, secondary school or day-care facilities] a Group E occupancy with an occupant load greater than 250. 3. Buildings and other structures containing [adult education facilities, such as colleges and universities] educational occupancies for students above the 12th grade with an occupant load greater than 500. 4. Group I-2 occupancies with an occupant load of 50 or more resident [patients] care recipients but not having surgery or emergency treatment facilities. 5. Group I-3 occupancies. 6. Any other occupancy with an occupant load greater than 5,000a. 7. Power-generating stations, water treatment facilities for potable water, waste[-] water treatment facilities and other public utility facilities not included in [Structural Structural Occupancy/] Risk Category IV. 8. Buildings and other structures not included in [Structural Structural Occupancy/] Risk Category IV containing [sufficient] quantities of toxic or explosive [substances to be dangerous to the public if released.] materials that: Exceed maximum allowable quantities per control area as given in Table 307.1(1) or 307.1(2), or per outdoor control area in accordance with the New York City Fire Code; and Are sufficient to pose a threat to the public if released.b |
| IV | Buildings and other structures designed as essential facilities, including[,] but not limited to: 1. Group I-2 occupancies having surgery or emergency treatment facilities. 2. Fire, rescue, ambulance and police stations and emergency vehicle garages. 3. Designated earthquake, hurricane or other emergency shelters. 4. Designated emergency preparedness, [communication,] communications and [operation] operations centers and other facilities required for emergency response. 5. Power-generating stations and other public utility facilities required as emergency backup facilities for [Structural Occupancy/] Risk Category IV structures. 6. [Structures] Buildings and other structures containing quantities of highly toxic materials [as defined by Section 307 where the quantity of the material exceeds the maximum allowable quantities of Table 307.7(2).] that: Exceed maximum allowable quantities per control area as given in Table 307.1(2) or per outdoor control area in accordance with the New York City Fire Code; and Are sufficient to pose a threat to the public if releasedb 7. Aviation control towers, air traffic control centers and emergency aircraft hangars. 8. Buildings and other structures having critical national defense functions. 9. Water storage facilities and pump structures required to maintain water pressure for fire suppression. |

a.	[For the purpose of Section 1616.2, Structural Occupancy Categories I and II are considered Seismic Use Group I, Structural Occupancy Category III is considered Seismic Use Group II and Structural Occupancy Category IV is equivalent to Seismic Use Group III.] For purposes of occupant load calculation, occupancies required by Table 1004.1.3 to use gross floor area calculations shall be permitted to use net floor areas to determine the total occupant load.

b.	Where approved by the commissioner, the classification of buildings and other structures as Risk Category III or IV based on their quantities of toxic, highly toxic or explosive materials is permitted to be reduced to Risk Category II, provided it can be demonstrated by a hazard assessment in accordance with Section 1.5.3 of ASCE 7 that a release of the toxic, highly toxic or explosive materials is not sufficient to pose a threat to the public.

1604.5.1 Multiple occupancies. Where a building or structure is occupied by two or more occupancies not included in the same [structural occupancy] risk category, it shall be assigned the classification of the highest [structural occupancy] risk category corresponding to the various occupancies. Where buildings or structures have two or more portions that are structurally separated, each portion shall be separately classified. Where a separated portion of a building or structure provides required access to, required egress from or shares life safety components with another portion having a higher [structural occupancy] risk category, both portions shall be assigned to the higher [structural occupancy] risk category.

Exception: Where a storm shelter designed and constructed in accordance with ICC 500 is provided in a building, structure or portion thereof normally occupied for other purposes, the risk category for the normal occupancy of the building shall apply unless the storm shelter is a designated emergency shelter in accordance with Table 1604.5.

1604.5.2 Importance factors. Importance factors for snow, ice, wind and seismic loads shall be determined in accordance with ASCE 7, Table [1604.5.2] 1.5-2 based on the [Structural Occupancy Category or] Risk Category assigned in accordance with Table 1604.5.

[TABLE 1604.5.2
IMPORTANCE FACTORS]

| [Structural Occupancy/Risk Category] | [Snow Importance Factor, I] | [Wind Importance Factor, I] | [Seismic Importance Factor, I] |
| --- | --- | --- | --- |
| [I] | [0.80] | [0.87] | [1.00] |
| [II] | [1.00] | [1.00] | [1.00] |
| [III] | [1.10] | [1.15] | [1.25] |
| [IV] | [1.20] | [1.15] | [1.50] |

1604.6 In-situ load tests. The commissioner is authorized to require an engineering analysis or a load test, or both, of any construction whenever there is reason to question the safety of the construction for the intended occupancy. Engineering analysis and load tests shall be conducted in accordance with Section [1714] 1708.

1604.7 Preconstruction load tests. Materials and methods of construction that are not capable of being designed by [recognized] approved engineering analysis or that do not comply with the applicable [material design] referenced standards [listed in Chapter 35], or alternative test procedures in accordance with Section [1712] 1709, shall be load tested in accordance with Section [1715] 1710.

1604.8 Anchorage. Buildings and other structures, and portions thereof, shall be provided with anchorage in accordance with Sections 1604.8.1 through 1604.8.4, as applicable.

1604.8.1 General. Anchorage of the roof to walls and columns, and of walls and columns to foundations, shall be provided to resist the uplift and sliding forces that result from the application of the prescribed loads and load combinations.

[1604.8.2 Walls. Walls shall be anchored to floors, roofs and other structural elements that provide lateral support for the wall. Such anchorage shall provide a positive direct connection capable of resisting the horizontal forces specified in this chapter but not less than the minimum strength design horizontal force specified in Section 11.7.3 of ASCE 7, substituted for “E” in the load combinations of Section 1605.2 or 1605.3. Concrete and masonry walls shall be designed to resist bending between anchors where the anchor spacing exceeds 4 feet (1219 mm). Required anchors in masonry walls of hollow units or cavity walls shall be embedded in a reinforced grouted structural element of the wall. See Section 1609 for wind design requirements and Section 1613 for and earthquake design requirements.]

1604.8.2 Structural walls. Walls that provide vertical load-bearing resistance or lateral shear resistance for a portion of the structure shall be anchored to the roof and to all floors and members that provide lateral support for the wall or that are supported by the wall. The connections shall be capable of resisting the horizontal forces specified in Section 1.4.4 of ASCE 7 for walls of structures assigned to Seismic Design Category A and to Section 12.11 of ASCE 7 for walls of structures assigned to all other seismic design categories. Required anchors in masonry walls of hollow units or cavity walls shall be embedded in a reinforced grouted structural element of the wall. See Sections 1609 for wind design requirements and Section 1613 for earthquake design requirements.

1604.8.3 Decks. Where supported by attachment to an exterior wall, decks shall be positively anchored to the primary structure and designed for both vertical and lateral loads as applicable. Such attachment shall not be accomplished by the use of toenails or nails subject to withdrawal. Where positive connection to the primary building structure cannot be verified during inspection, decks shall be self-supporting. Connections of decks with cantilevered framing members to exterior walls or other framing members shall be designed for both of the following:[.]

- The reactions resulting from the dead load and live load specified in Table 1607.1, or the snow load specified in Section 1608, in accordance with Section 1605, acting on all portions of the deck.

- The reactions resulting from the dead load and live load specified in Table 1607.1, or the snow load specified in Section 1608, in accordance with Section 1605, acting on the cantilevered portion of the deck, and no live load or snow load on the remaining portion of the deck.

1604.8.4 Non-structural walls and partitions. Walls not meeting the requirements of Section 1604.8.2 and partitions shall be laterally supported with sufficient mechanical anchorage to resist the loads imposed per this code, including but not limited to live loads, wind loads, and earthquake loads.

[1604.9 Counteracting structural actions. Structural members, systems, components and cladding shall be designed to resist forces due to earthquake and wind, with consideration of overturning, sliding and uplift. Continuous load paths shall be provided for transmitting these forces to the foundation. Where sliding is used to isolate the elements, the effects of friction between sliding elements shall be included as a force.]

[1604.10] 1604.9 Wind and seismic detailing. [Lateral-force-resisting] Lateral force-resisting systems shall meet seismic detailing requirements and limitations prescribed in this code and ASCE 7[-10, excluding ASCE 7-10  Chapter 14 and ASCE 7-10 Appendix 11A,] Chapters 11, 12, 13, 15, 17, and 18 as applicable, even when wind load effects are greater than seismic load effects. Where ASCE 7 references Chapter 14 of ASCE 7 those references shall not apply, except as specifically required in this code.

1604.10 Loads on storm shelters. Loads and load combinations on storm shelters shall be determined in accordance with ICC 500.

SECTION BC 1605
LOAD COMBINATIONS

1605.1 General. Buildings and other structures and portions thereof shall be designed to resist: [.]

1.	The load combinations specified in Section 1605.2 or 1605.3;

2.	The load combinations specified in Chapters 18 through 23; and

3.	The seismic load [combinations with] effects including overstrength [factors specified] factor in accordance with [Section 12.4.3.2] Sections 2.3.6 and 2.4.5 of ASCE 7[-10,] where required by [Section 12.2.5.2, 12.3.3.3 or 12.10.2.1 of ASCE 7-10] Chapters 12, 13, and 15 of ASCE 7. With the simplified procedure of [ASCE 7-10] Section 12.14 of ASCE 7, the seismic load [combinations with] effects including overstrength [factors specified] factor in accordance with Section 12.14.3.2 and Chapter 2 of ASCE 7[-10] shall be used.

Applicable loads shall be considered, including both earthquake and wind, in accordance with the specified load combinations. Each load combination shall also be investigated with one or more of the variable loads set to zero.

Where the load combinations with overstrength factor in [Section 12.4.3.2] Sections 2.3.6 and 2.4.5 of ASCE 7[-10] apply, they shall be used as follows:

- The basic combinations for strength design with overstrength factor in lieu of Equations 16-5 and 16-7 in Section 1605.2.1.

- The basic combinations for allowable stress design with overstrength factor in lieu of Equations 16-12, [16-13] 16-14 and [16-15] 16-16 in Section 1605.3.1.

1605.1.1 Stability. Regardless of which load combinations are used to design for strength, where overall structure stability (such as stability against overturning, sliding, or buoyancy) is being verified, use of the load combinations specified in Section 1605.2 or 1605.3 shall be permitted. Where the load combinations specified in Section 1605.2 are used, strength reduction factors applicable to soil resistance shall be provided by a registered design professional. The stability of retaining walls shall be verified in accordance with Section [1806.2] 1807.2.

1605.2 Load combinations using strength design or load and resistance factor design.

[1605.2.1Basic load combinations.] Where strength design or load and resistance factor design is used, buildings and other structures, and portions thereof, shall be designed to resist the most critical effects resulting from the following combinations of factored loads:

(D + F)	(Equation 16-1)

(Equation 16-2)

(Equation 16-3)

(Equation 16-4)

(Equation 16-5)

(Equation 16-6)

[

(Equation 16-7)

where:

[1.0] 1 for [floors in] places of public assembly [, for] live loads in excess of 100 pounds per square foot (4.79 kN/m2), and [for] parking [garage live load,] garages; and

[	] 0.5 for other live loads.

0.7 for roof configurations (such as saw tooth) that do not shed snow off the structure, and

[	] 0.2 for other roof configurations.

[Exception:] Exceptions:

1.	Where other factored load combinations are specifically required by [the] other provisions of this code, such combinations shall take precedence.

2.	Where the effect of H resists the primary variable load effect, a load factor of 0.9 shall be included with H where H is permanent and H shall be set to zero for all other conditions.

[1605.2.2] 1605.2.1 Other loads. Where a structure is located in a V zone or Coastal A zone and Fa is to be considered in design, in addition to the load combinations of Equations 16-1 through 16-7, the structure and portions thereof shall resist the most critical effects of the load combinations of Equations 16-8 and 16-10. Where a structure is located in an A zone and Fa is to be considered in design, in addition to the load combinations of Equations 16-1 through 16-7, structures and portions thereof shall resist the most critical effects of the load combinations of Equation 16-9 and 16-11. Where ice loads are to be considered in design, the load combinations of Section [2.3.4] 2.3.3 of ASCE 7 shall be used. Refer to the following sections for other load combinations:

Flood Load Combinations:

1.2(D + F) + 1.0W + 2.0Fa + f1L + 1.6H +0.5(Lr or S or R)	(Equation 16-8)

1.2(D + F) + 0.5W+1.0Fa + f1L + 1.6H + 0.5(Lr or S or R)	(Equation 16-9)

0.9D + 1.0W + 2.0Fa +1.6H	(Equation 16-10)

0.9D + 0.5W + 1.0Fa + 1.6H	(Equation 16-11)

1605.3 Load combinations using allowable stress design. Load combinations for allowable stress design shall be in accordance with Section 1605.3.1 or 1605.4.

1605.3.1 Basic load combinations. Where allowable stress design (working stress design), as permitted by this code, is used, structures and portions thereof shall resist the most critical effects resulting from the following combinations of loads:

(Equation 16-12)

(Equation 16-13)

(Equation 16-14)

(Equation 16-15)

(Equation 16-16)

(Equation 16-17)

[0.6 + W + H]

(Equation 16-18)

[0.6 + 0.7E + H]

(Equation 16-19)

(Equation 16-20)

Exceptions:

1.	Crane hook loads need not be combined with roof live load or with more than three-fourths of the snow load or one-half of the wind load.

2.	Flat roof snow loads of 30 psf (1.44 kN/m2) or less and roof live loads of 30 psf (1.44 kN/m2) or less need not be combined with seismic loads. Where flat roof snow loads exceed 30 psf (1.44 kN/m2), 20 percent shall be combined with seismic loads.

3.	Where the effect of H resists the primary variable load effect, a load factor of 0.6 shall be included with H where H is permanent and H shall be set to zero for all other conditions.

4.	In Equation 16-19, the wind load, W, is permitted to be reduced in accordance with Exception 2 of Section 2.4.1 of ASCE 7.

5.	In Equation 16-20, 0.6 D is permitted to be increased to 0.9 D for the design of special reinforced masonry shear walls complying with Chapter 21.

1605.3.1.1 Stress increases. Increases in allowable stresses specified in the appropriate material chapter or the referenced standards shall not be used with the load combinations of Section 1605.3.1, except that increases shall be permitted in accordance with Chapter 23.

1605.3.1.2 Other loads. Where a structure is located in a V zone or Coastal A zone and Fa is to be considered in design, in addition to load combinations of Equations 16-12 through [16-19] 16-20, structures and portions thereof shall resist the most critical effects of load combinations of Equations [16-20] 16-21, [16-22] 16-23 and [16-24] 16-25. Where a structure is located in [a] an A zone and Fa is to be considered in design, in addition to load combinations of Equations 16-12 through [16-19] 16-20, structures and portions thereof shall resist the most critical effects of load combinations of Equations [16-21] 16-22, [16-23] 16-24 and [16-25] 16-26. Where ice loads are to be considered in design, the load combinations of Section 2.4.3 of ASCE 7 shall be used. [Refer to the following sections for other loads:]

Flood Load Combinations:

[(Equation 16-20)]

D + H + F + 0.6W + 1.5Fa	(Equation 16-21)

[(Equation 16-21)]

D + H + F + 0.6W + 0.75Fa	(Equation 16-22)

[(Equation 16-22)]

D + H + F + 0.75(0.6W) + 0.75L + 0.75(Lr or S or R) + 1.5Fa	(Equation 16-23)

[(Equation 16-23)]

D + H + F + 0.75(0.6W) + 0.75L + 0.75(Lr or S or R) + 0.75Fa	(Equation 16-24)

[(Equation 16-24)]

0.6D + 0.6W + H + 1.5Fa	(Equation 16-25)

[(Equation 16-25)]

0.6D + 0.6W + H + 0.75Fa	(Equation 16-26)

1605.4 [Heliports and helistops. Heliport and helistop landing areas shall be designed for the following loads, combined in accordance with Section 1605:]

[1.	Dead load, D, plus the gross weight of the helicopter, Dh, plus snow load, S.]

[2.	Dead load, D, plus two single concentrated impact loads, L, approximately 8 feet (2438 mm) apart applied anywhere on the touchdown pad (representing each of the helicopter’s two main landing gear, whether skid type or wheeled type), having a magnitude of 0.75 times the gross weight of the helicopter. Both loads acting together total 1.5 times the gross weight of the helicopter.]

[3.	Dead load, D, plus a uniform live load, L, of 100 psf (4.79 kN/m2).]

[Exception: Landing areas designed for helicopters with gross weights not exceeding 3,000 pounds (13.34 kN) in accordance with Items 1 and 2 shall be permitted to be designed using a 40 psf (1.92 kN/m2) uniform live load in Item 3, provided the landing area shall be identified with a 3,000-pound (13.34 kN) weight limitation and the 40 psf (1.92 kN/m2) uniform live load shall not be reduced. The landing area weight limitation shall be indicated by the numeral “3” (kips) located in the bottom right corner of the landing area as viewed from the primary approach path. The indication for the landing area weight limitation shall be a minimum 5 feet (1524 mm) in height.]

[1605.5] Structural integrity load combinations—alternate load path method. Where specifically required by Sections [16141624] 1615 through [1616] 1617, elements and components shall be designed to resist the forces calculated using the following combination of factored loads:

[(Equation 16-26)] Equation 16-27

where:

0.25 for buildings in [Structural Occupancy] Risk Category II.

0.5 for buildings in [Structural Occupancy] Risk Category III or IV.

0 for buildings in [Structural Occupancy] Risk Category II.

0.33 for buildings in [Structural Occupancy] Risk Category III or IV.

The live load component  need not be greater than the reduced live load.

[1605.6] 1605.5 Structural integrity load combinations—vehicular impact and gas explosions. Where specifically required by Sections [1615.5] 1616.4 and [1615.6] 1616.5, elements and components shall be designed to resist the forces calculated using the following combination of factored loads:

[(Equation 16-27)] Equation 16-28

[(Equation 16-28)] Equation 16-29

Where Ak is the load effect of the vehicular impact or gas explosion.

[1605.7] 1605.6 Structural integrity load combinations—specific local resistance method. Where the specific local resistance method is used in a key element analysis, the specified local loads shall be used as specified in Section [1616.7] 1617.6.

SECTION BC 1606
DEAD LOADS

1606.1 General. Dead loads are those loads defined in [Section 1602.1] Chapter 2 of this code. Dead loads shall be considered permanent loads.

1606.2 Design dead load. For purposes of design, the actual weights of materials of construction and fixed service equipment shall be used. In the absence of definite information, values used shall be subject to the approval of the commissioner.

SECTION BC 1607
LIVE LOADS

1607.1 General. Live loads are those loads defined in [Section 1602.1] Chapter 2 of this code.

TABLE 1607.1
MINIMUM UNIFORMLY DISTRIBUTED LIVE LOADS, Lo, AND MINIMUM CONCENTRATED LIVE LOADS[f,i]g

| OCCUPANCY OR USE | UNIFORM (psf) | CONCENTRATED [(lbs.)] (pounds) |
| --- | --- | --- |
| 1. Apartments (see residential) | ─ | ─ |
| 2. Access floor systems Office use Computer use | 50 100 | 2,000 2,000 |
| 3. Armories and drill rooms | 150n | ─ |
| 4. Assembly areas [and theaters] Fixed seats (fastened to floor) Follow spot, projections and control rooms Lobbies Movable seats Private assembly spaces, including conference rooms [Stages and platforms] Stage floors [Follow spot, projections and control rooms] Platforms (assembly) [Catwalks] Other assembly spaces | 60m 50 100m 100m 50 [125] 150n [50] 100m [40] [Note h] 100m | ─ |
| 5. Balconies [(exterior)] and Decks[g]h | 1.5 times the live load for the occupancy served. Not required to exceed 100 psf | ─ |
| 6. [Bowling alleys] Catwalks | [75] 40 | [--] 300 |
| 7. Cornices | 60 | ─ |
| 8. Corridors [, except as otherwise indicated] First floor Other floors | 100 Same as occupancy served except as indicated | ─ |
| [9. Dance halls and ballrooms] | [100] | [--] |
| [10.] 9. Dining rooms and restaurants | 100m | ─ |
| [11.] 10. Dwellings (see residential) | ─ | ─ |
| [12.] 11. Elevator machine room and control room grating (on area of [4 in.2] 2 inches by 2 inches) | ─ | 300 |
| [13.] 12. Equipment rooms, including pump rooms, generator rooms, transformer vaults, and areas for switch gear, ventilating, air conditioning, and similar electrical and mechanical equipment | 75 | [--] |
| [14.] 13. Finish light floor plate construction (on area of [1 in.2] 1 inch by 1 inch) | ─ | 200 |
| [15.] 14. Fire escapes (exterior) On single-[and multiple] family dwellings only | 100 40 | ─ |
| [16.] 15. Garages (passenger vehicles only) Trucks and buses | 40o | Note a |
|  | See Section [1607.6] 1607.7 |
| [17. Grandstands (see stadium and arena bleachers)] | [─] | [--] |
| [18. Gymnasiums, main floors and balconies] | [100] | [--] |
| [19.] 16. Handrails, guards and grab bars | See Section [1607.7] 1607.8 |
| 17. Helipads | See Section 1607.6 |
| [20.] 18. Hospitals Corridors above first floor Operating rooms, laboratories Patient Rooms [Private rooms] [Wards] [Corridors above first floor] | 80 60 40 [40] [40] [80] | 1,000 1,000 1,000 [1,000] [1,000] [1,000] |
| [21.] 19. Hotels (see residential) | ─ | ─ |
| [22.] 20. Libraries Corridors above first floor Reading rooms Stack rooms [Corridors above first floor] | 80 60 150b,n [80] | 1,000 1,000 1,000 [1,000] |
| [23.] 21. Manufacturing Heavy Light [Heavy] | 250n 125n [250] | 3,000 2,000 [3,000] |
| [24.] 22. Marquees, except one- and two-family dwellings | 75 | ─ |
| [25.] 23. Office buildings Corridors above first floor File and computer rooms shall be designed for heavier loads based on anticipated occupancy Lobbies and first-floor corridors Offices [Corridors above first floor] | 80 ─ 100 50 [80] | 2,000 ─ 2,000 2,000 [2,000] |
| [26.] 24. Penal institutions Cell blocks Corridors | 40 100 | ─ |
| 25. Recreational uses: Bowling alleys, poolrooms and similar uses Dance halls and ballrooms Gymnasiums Ice skating rink Reviewing stands, grandstands and bleachers Roller skating rink Stadiums and arenas with fixed seats (fastened to floor) | 75m 100m 100m 250n 100c,m 100m 60c,m | ─ |
| [27.] 26. Residential One- and two-family dwellings Uninhabitable attics without storagei Uninhabitable attics with storagei,j,k Habitable attics and sleeping areask Canopies, including marquees All other areas [except balconies and decks] Hotels and multifamily dwellings Private rooms and corridors serving them Public roomsm and corridors serving them | 10 20 30 20 40 40 100 | ─ |
| [28. Reviewing stands, grandstands and bleachers] | [Note c] | [--] |
| [29.] 27. Roofs All roof surfaces subject to maintenance workers Awnings and canopies: Fabric construction supported by a [lightweight rigid] skeleton structure All other construction, except one- and two-family dwellings Ordinary flat, pitched, and curved roofs (that are not occupiable) Primary roof members[,] exposed to a work floor Single panel point of lower chord of roof trusses or any point along primary structural members supporting roofs over manufacturing, storage warehouses, and repair garages All other [occupancies] primary roof members [Roofs used for other special purposes] [Roofs used for promenade purposes] [Roofs used for roof gardens or assembly purposes] Occupiable roofs: Roof gardens Assembly areas All other similar areas | 5m [Nonreducible] 20 20 [Note j] [60] [100] 100 100m Note l | 300 2,000 300 [Note j] Note l |
| [30.] 28. Schools Classrooms Corridors above the first floor First-floor corridors | 40 80 100 | 1,000 1,000 1,000 |
| [31.] 29. Scuttles, skylight ribs and accessible ceilings | ─ | 200 |
| [32.] 30. Sidewalks, vehicular driveways and yards, subject to trucking | 300 d,m | 8,000[d]e or 20,000d |
| [33. Plaza areas (open) accessible to the public (including landscaped portions)] | [100] | [--] |
| [34. Skating rinks] | [100] | [--] |
| [35. Stadiums and arenas Bleachers Fixed seats (fastened to floor)] | [100c] [60c] | [--] |
| [36.] 31. Stairs and exits One- and two-family dwellings All other | [100] 40 100 | [Note e] 300f 300f |
| [37.] 32. Storage warehouses (shall be designed for heavier loads if required for anticipated storage) Heavy Light [Heavy] | 250n 125n [250] | ─ |
| [38.] 33. Stores Retail First floor Upper floors Wholesale, all floors | 100 75 125n | 1,000 1,000 1,000 |
| [39.] 34. Vehicle barriers | See Section [1607.7] 1607.9 |
| [40.] 35. Walkways and elevated platforms (other than exitways) | 60 | ─ |
| [41.] 36. Yards and terraces, pedestrians | 100m | ─ |

[Notes to Table 1607.1]

For SI:

1 inch = 25.4 mm, 1 square inch = 645.16 mm2,

1 square [inch] foot = [645.16 mm2] 0.0929m2,

1 pound per square foot = 0.0479 kN/m2,

1 pound = 0.004448 kN,

1 pound per cubic foot = 16 kg/m3.

a.	Floors in garages or portions of buildings used for the storage of motor vehicles shall be designed for the uniformly distributed live loads of this Table [1607.1] or the following concentrated loads: (1) for garages restricted to passenger vehicles accommodating not more than nine passengers, 3,000 pounds acting on an area of [4.5] 41/2 inches by [4.5] 41/2 inches; (2) for mechanical parking structures without slab or deck which are used for storing passenger vehicles only, 2,250 pounds per wheel.

b.	The loading applies to stack room floors that support nonmobile, double-faced library [bookstacks] book stacks, subject to the following limitations:

- The nominal [bookstack] book stack unit height shall not exceed 90 inches;

- The nominal shelf depth shall not exceed 12 inches for each face; and

- Parallel rows of double-faced [bookstacks] book stacks shall be separated by aisles not less than 36 inches wide.

c.	Design in accordance with [the ICC Standard on Bleachers, Folding and Telescopic Seating and Grandstands] Section 1029.1.

d.	The concentrated wheel load of 20,000 pounds shall be applied as follows 8,000 pounds on an area of 20 square inches, 20,000 pounds on a 20 inch by 10 inch area.

e.	[The concentrated wheel load shall be applied on an area of 20 square inches.] The concentrated wheel load shall be applied on an area of 4.5 inches by 4.5 inches.

[f.]	[Minimum concentrated load on stair treads (on area of 4 square inches) is 300 pounds.]

[g.]f.	[Where snow loads occur that are in excess of the design conditions, the structure shall be designed to support the loads due to the increased loads caused by drift buildup or a greater snow design determined by the commissioner (see Section 1608). For special-purpose roofs, see Section 1607.11.2.2.] The minimum concentrated load on stair treads shall be applied on an area of 2 inches by 2 inches. This load need not be assumed to act concurrently with the uniform load.

[h.]g.	[See Section 1604.8.3 for decks attached to exterior walls.] Where snow loads occur that are in excess of the design conditions, the structure shall be designed to support the loads due to the increased loads caused by drift buildup or a greater snow design determined by the department (see Section 1608).

[i.]h.	[Live loads for assembly spaces other than those described in this table shall be determined from the occupant load requirements as established by Section 1004 of this code using the formula 1,000/(net floor area per occupant) but shall not be less than 50 psf nor more than 100 psf.] See Section 1604.8.3 for decks attached to exterior walls.

[j.]i.	[For establishing live loads for occupancies not specifically listed herein, refer to Referenced Standard ASCE 7 for guidance.] Uninhabitable attics without storage are those where the maximum clear height between the joists and rafters is less than 42 inches, or where there are not two or more adjacent trusses with web configurations capable of accommodating an assumed rectangle 42 inches in height by 24 inches in width, or greater, within the plane of the trusses. This live load need not be assumed to act concurrently with any other live load requirements.

j.	[Roofs used for other special purposes shall be designed for appropriate loads as approved by the commissioner.] Uninhabitable attics with storage are those where the maximum clear height between the joists and rafters is 42 inches or greater, or where there are two or more adjacent trusses with web configurations capable of accommodating an assumed rectangle 42 inches in height by 24 inches in width, or greater, within the plane of the trusses.

The live load need only be applied to those portions of the joists of truss bottom chords where both of the following conditions are met:

i.	The attic area is accessible from an opening not less than 20 inches in width by 30 inches in length that is located where the clear height in the attic is a minimum of 30 inches; and

ii.	The slopes of the joists or truss bottom chords are no greater than two units vertical in 12 units horizontal.

The remaining portions of the joists or truss bottom chords shall be designed for a uniformly distributed concurrent live load of not less than 10 pounds per square foot.

k.	Attic spaces served by stairways other than the pull-down type shall be designed to support the minimum live load specified for habitable attics and sleeping rooms.

l.	Areas of occupiable roofs, other than roof gardens and assembly areas, shall be designed for appropriate loads as approved by the department. Unoccupied landscaped areas of roofs shall be designed in accordance with Section 1607.13.3.

m.	Live load reduction is not permitted.

n.	Live Load reduction is only permitted in accordance with Section 1607.11.1.2 or Item 1 of Section 1607.11.2.

o.	Live Load reduction is only permitted in accordance with Section 1607.11.1.3 or Item 2 of Section 1607.11.2.

1607.2 Loads not specified. For occupancies or uses not designated in Table 1607.1, the live load shall be determined in accordance with a method approved by the commissioner.

1607.2.1 Stage areas using scenery or scenic elements. Scenery battens and suspension systems shall be designed for a load of 30 pounds per linear foot (437.7 N/m) of batten length. Loft block and head block beams shall be designed to support vertical and horizontal loads corresponding to a 4-inch (102 mm) spacing of battens for the entire depth of the gridiron. Direction and magnitude of total forces shall be determined from the geometry of the rigging system including load concentrations from spot line rigging. Locking rails shall be designed for a uniform uplift of 500 psf (3447 kN/m2) with a 1,000 pound (454 kg) concentration. Impact factor for batten design shall be 75 percent and for loft and head block beams shall be 25 percent. A plan drawn to a scale not less than ¼ inch (6.4 mm) equals 1 foot (305 mm) shall be displayed in the stage area indicating the framing plan of the rigging loft and the design loads for all members used to support scenery or rigging. Gridirons over stages shall be designed to support a uniformly distributed live load of 50 psf (2.40 kN/m2) in addition to the rigging loads indicated.

1607.3 Uniform live loads. The live loads used in the design of buildings and other structures shall be the maximum loads expected by the intended use or occupancy but shall in no case be less than the minimum uniformly distributed [unit] live loads [required by] given in Table 1607.1.

1607.4 Concentrated live loads. Floors, roofs and other similar surfaces shall be designed to support the uniformly distributed live loads prescribed in Section 1607.3 or the concentrated [load, in pounds (kilonewtons),] live loads, given in Table 1607.1, whichever produces the greater load effects. Unless otherwise specified, the indicated concentration shall be assumed to be uniformly distributed over an area [2.5] of 2½ feet by [2.5] 2½ feet [(762 mm × 762 mm)] (762 mm by 762 mm) and shall be located so as to produce the maximum load effects in the structural members.

1607.5 Partition loads. In office buildings and in other buildings where partition locations are subject to change, provisions for partition weight shall be made, whether or not partitions are shown on the construction documents, unless the specified live load is 80 psf (3.83 kN/m2) or greater. Weights of all partitions shall be considered, using either actual weights at locations shown on the plans or the equivalent uniform load given in Section 1607.5.2. Partition loads shall be taken as superimposed dead loads.

1607.5.1 Actual loads. Where actual partition weights are used, the uniform design live load may be omitted from the strip of floor area under each partition.

1607.5.2 Equivalent uniform load. The equivalent uniform partition loads in Table 1607.5 may be used in lieu of actual partition weights except for bearing partitions or partitions in toilet room areas (other than in one- and two-family dwellings), at stairs and elevators, and similar areas where partitions are concentrated. In such cases, actual partition weights shall be used in design. [Except as otherwise exempted, equivalent uniform partition loads shall be used in areas where partitions are not definitely located on the plans, or in areas where partitions are subject to rearrangement or relocation.]

TABLE 1607.5
EQUIVALENT UNIFORM PARTITION LOADS

| PARTITION WEIGHT (plf) | EQUIVALENT UNIFORM LOAD (psf) (to be added to floor dead and live loads) |
| --- | --- |
| 50 or less | 0 |
| 51 to 100 | 6 |
| 101 to 200 | 12 |
| 201 to 350 | 20 |
| Greater than 350 | 20 plus a concentrated live load of the weight in excess of 350 plf. |

For SI: 1 pound per linear foot = 0.01459 kN/m2, 1 pound per square foot = 0.0479 kN/m2.

[1607.6 Garages.]

[1607.6.1 Passenger vehicle garages. Areas used for, and restricted by physical limitations of clearance to, the transit or parking of passenger vehicles shall be designed for the uniformly distributed and concentrated loads for parking areas for such vehicles as provided in Table 1607.1 applied without impact. An exception is made for members or constructions which, because of physical limitations, cannot be subjected to direct load from the vehicle or from a jack or hoist used to raise or suspend the vehicle. Such members or constructions shall be designed for the loads corresponding to the actual usage.]

[TABLE 1607.6
UNIFORM AND CONCENTRATED LOADS

| LOADING CLASSa | UNIFORM LOAD (pounds/linear foot of lane) | CONCENTRATED LOAD (pounds)b |
| --- | --- | --- |
|  |  | For moment design | For shear design |
| H20-44 and HS20-44 | 640 | 18,000 | 26,000 |
| H15-44 and HS15-44 | 480 | 13,500 | 19,500 |

For SI: 1 pound per linear foot = 0.0 1459 kN/m, 1 pound = 0.004448 kN, 1 ton = 8.90kN.

- An H loading class designates a two-axle truck with a semitrailer. An HS loading class designates a tractor truck with a semitrailer. The numbers following the letter classification indicate the gross weight in tons of the standard truck and the year the loadings were instituted.

- See Section 1607.6.1 for the loading of multiple spans.]

[1607.6.2 Truck and bus garages. Minimum live loads for garages having trucks or buses shall be as specified in Table 1607.6, but shall not be less than 50 psf (2.40 kN/m2), unless other loads are specifically justified and approved by the commissioner. Actual loads shall be used where they are greater than the loads specified in the table.]

[1607.6.2.1 Truck and bus garage live load application. The concentrated load and uniform load shall be uniformly distributed over a 10-foot (3048 mm) width on a line normal to the centerline of the lane placed within a 12-foot-wide (3658 mm) lane. The loads shall be placed within their individual lanes so as to produce the maximum stress in each structural member. Vertical impact shall be taken as 10 percent of the vertical load. Single spans shall be designed for the uniform load in Table 1607.6 and one simultaneous concentrated load positioned to produce the maximum effect. Multiple spans shall be designed for the uniform load in Table 1607.6 on the spans and two simultaneous concentrated loads in two spans positioned to produce the maximum negative moment effect. Multiple span design loads, for other effects, shall be the same as for single spans.]

1607.6 Helipads. Helipads shall be designed for the following live loads:

1.	A uniform live load, L, as specified in Items 1.1 and 1.2. This load shall not be reduced.

1.1.	40 psf (1.92 kN/m2) where the design basis helicopter has a maximum take-off weight of 3,000 pounds (13.35 kN) or less.

1.2.	60 psf (2.87 kN/m2) where the design basis helicopter has a maximum take-off weight greater than 3,000 pounds (13.35 kN).

2.	A single concentrated live load, L, of 3,000 pounds (13.35 kN) applied over an area of 4.5 inches by 4.5 inches (114 mm by 114 mm) and located so as to produce the maximum load effects on the structural elements under consideration. The concentrated load is not required to act concurrently with other uniform or concentrated live loads.

3.	Two single concentrated live loads, L, 8 feet (2438 mm) apart applied on the landing pad (representing the helicopter’s two main landing gear, whether skid type or wheeled type), each having a magnitude of 0.75 times the maximum take-off weight of the helicopter, and located so as to produce the maximum load effects on the structural elements under consideration. The concentrated loads shall be applied over an area of 8 inches by 8 inches (203 mm by 203 mm) and are not required to act concurrently with other uniform or concentrated live loads.

Landing areas designed for a design basis helicopter with maximum take-off weight of 3,000-pounds (13.35 kN) shall be identified with a 3,000 pound (13.34 kN) weight limitation. The landing area weight limitation shall be indicated by the numeral “3” (kips) located in the bottom right corner of the landing area as viewed from the primary approach path. The indication for the landing area weight limitation shall be a minimum 5 feet (1524 mm) in height.

1607.7 Heavy Vehicle loads.  Floors and other surfaces that are intended to support vehicle loads greater than a 10,000-pound (4536 kg) gross vehicle weight rating shall comply with Sections 1607.7.1 through 1607.7.5.

1607.7.1 Loads. Where any structure does not restrict access for vehicles that exceed a 10,000-pound (4536 kg) gross vehicle weight rating, those portions of the structure subject to such loads shall be designed using the vehicular live loads, including consideration of impact and fatigue, in accordance with the NYSDOT Bridge Manual and the NYSDOT LRFD Bridge Design Specifications.

Alternatively, it shall be acceptable to utilize the design live loads for sidewalks as shown in Table 1607.1.

1607.7.2 Fire truck and emergency vehicles. Where a structure or portions of a structure are designated as fire access roads as defined in Chapter 5 of the New York City Fire Code, the structure shall be designed for the live loading specified in Section 1607.7.1 or those identified in Chapter 5 of the New York City Fire Code, whichever produces the greater load effects.

1607.7.3 Heavy vehicle garages. Garages designed to accommodate vehicles that exceed a 10,000-pound (4536 kg) gross vehicle weight rating, shall be designed using the live loading specified by Section 1607.7.1.  Vertical impact shall be taken as 10 percent of the vertical load.

Exception: The vehicular live loads and load placement are allowed to be determined using the actual vehicle weights for the vehicles allowed onto the garage floors, provided such loads and placement are based on rational engineering principles and are approved by the department, but shall not be less than 50 psf (2.9 kN/m2). This live load shall not be reduced.

1607.7.4 Forklifts and movable equipment. Where a structure is intended to have forklifts or other movable equipment present, the structure shall be designed for the total vehicle or equipment load and the individual wheel loads for the anticipated vehicles as specified by the owner of the facility. These loads shall be posted in accordance with Section 1607.7.5.

1607.7.4.1 Impact and fatigue. Impact loads and fatigue loading shall be considered in the design of the supporting structure. For the purposes of design, the vehicle and wheel loads shall be increased by 30 percent to account for impact.

1607.7.5 Posting. The maximum weight of vehicles allowed into or on a garage or other structure shall be posted by the owner or the owner’s authorized agent in accordance with Article 118 of Chapter 1 of Title 28 of the Administrative Code.

[1607.7] 1607.8 Loads on handrails, guards, grab bars, and seats [and vehicle barrier systems]. Handrails[,] and guards[,] shall be designed and constructed for the structural loading conditions set forth in Section 1607.8.1. [grab] Grab bars, [accessible seats,] shower seats and accessible benches [and vehicle barrier systems] shall be designed and constructed [to] for the structural loading conditions set forth in [this section] Section 1607.8.2.

[1607.7.1] 1607.8.1 [Handrail assemblies] Handrails and guards. [Handrail assemblies] Handrails and guards shall be designed to resist a linear load of 50 [plf] pounds per linear foot (plf) (0.73 kN/m) [applied in any direction at the top and to transfer this load through the supports to the structure] in accordance with Section 4.5.1.1 of ASCE 7. Glass handrail assemblies and guards shall also comply with Section 2407.

Exceptions:

1.	For one- and two-family dwellings, only the single[,] concentrated load required by Section [1607.7.1.1] 1607.8.1.1 shall be applied.

2.	In Group I-3, F, H[,] and S occupancies, for areas that are not accessible to the general public and that have an occupant load no greater than 50, the minimum load shall be 20 pounds per foot (0.29 kN/m).

[1607.7.1.1] 1607.8.1.1 Concentrated load. [Handrail] Handrails and guards shall be [able] designed to resist a [single] concentrated load of 200 pounds (0.89 kN) [, applied in any direction at any point, and have attachment devices and supporting structure to transfer this loading to appropriate structural elements of the building. This load need not be assumed to act concurrently with the loads specified in the preceding paragraph] in accordance with Section 4.5.1.1 of ASCE 7.

[1607.7.1.2] 1607.8.1.2 [Components] Intermediate rails. Intermediate rails (all those except the handrail), balusters and panel fillers shall be designed to [withstand a horizontally applied normal] resist a concentrated load of 50 pounds (0.22 kN) [on an area equal to 1 square foot (0.093 m2), including openings and space between rails] in accordance with Section 4.5.1.1 of ASCE 7, a vertically downward load of 50 pounds per foot (0.73 kN/m), and a concentrated upward load of 50 pounds (0.22 kN) applied at the most critical location. Reactions due to this loading are not required to be applied simultaneously with one another, and are not required to be superimposed with those of Section [1607.7.1] 1607.8.1 or [1607.7.1.1] 1607.8.1.1. The railings, balusters and components shall be designed separately for the effect of wind when the total wind load on the panel or component exceeds 50 pounds (0.22 kN). The wind load need not be combined with any other live load.

[1607.7.2] 1607.8.2 Grab bars, shower seats and dressing room bench seats. Grab bars, shower seats and dressing room bench [seat systems] seats shall be designed to resist a single concentrated load of 250 pounds (1.11 kN) applied in any direction at any point on the grab bar or seat so as to produce the maximum load effects.

[1607.7.3] 1607.9 Vehicle [barrier systems] barriers. Vehicle [barrier systems] barriers for passenger vehicles shall be designed to resist a [single] concentrated load of 6,000 pounds (26.70 kN)[applied horizontally in any direction to the barrier system and shall have anchorage or attachment capable of transmitting this load to the structure. For design of the system, two loading conditions shall be analyzed. The first condition shall apply the load at a height of 1 foot, 6 inches (457 mm) above the floor or ramp surface] in accordance with Section 4.5.3 of ASCE 7.

[The second loading condition shall apply the load at 2 feet, 3 inches (686 mm) above the floor or ramp surface. The more severe load condition shall govern the design of the barrier restraint system. The load shall be assumed to act on an area not to exceed 1 square foot (0.0929 m2), and is not required to be assumed to act concurrently with any handrail or guard loadings specified in Section 1607.7.1.] Garages accommodating trucks and buses shall be designed in accordance with [a recognized] an approved method [acceptable to the commissioner] that contains [provision] provisions for traffic railings.

[1607.7.3.1] 1607.9.1 Columns in parking areas. Unless specially protected, columns in parking areas subject to impact of moving vehicles shall be designed to resist the lateral load due to impact [and this load shall be considered a variable load]. For passenger vehicles, this lateral load shall be taken as a minimum service live load of 6,000 pounds (26.70 kN) applied at least 1 foot 6 inches (457 mm)[;] above the roadway, and acting simultaneously with other design loads. In addition, columns in parking areas shall meet the requirements of Section [1615] 1616 for structural integrity. Vehicle barrier systems in garages accommodating trucks and buses shall be designed in accordance with NYSDOT Bridge Manual and the NYSDOT LRFD Bridge Design Specifications.

[1607.8] 1607.10 Impact loads. The live loads specified in Section 1607.3 through 1607.9 shall be assumed to include adequate allowance for impact conditions. Provisions shall be made in the structural design for uses and loads that involve unusual vibration and impact forces.

[1607.8.1] 1607.10.1 Elevators. [Elevator] Members, elements and components subject to dynamic loads [shall be increased by 100 percent for impact and the structural supports] from elevators shall be designed [within the limits of stress] for impact loads and deflection limits prescribed by ASME A17.1, as modified by Appendix K of this code.

[1607.8.2] 1607.10.2 Machinery. For the purpose of design, the weight of machinery and moving loads shall be increased as follows to allow for impact: (1) [elevator machinery, 100 percent; (2)] light machinery, shaft- or motor-driven, 20 percent; [(3)] and (2) reciprocating machinery or power-driven units, 50 [percent; (4) hangers for floors or balconies, 33] percent. Percentages shall be increased where specified by the manufacturer.

1607.10.3 Elements supporting building maintenance equipment. In addition to any other applicable live loads, structural elements that support hoists for façade access and building maintenance equipment shall be designed for a live load of 2.5 times the rated load of the hoist or the stall load of the hoist, whichever is greater.

Equipment installed temporarily to facilitate construction, demolition, alteration, or inspection shall be subject to the requirements of Chapter 33.

1607.10.4 Fall arrest and lifeline anchorages. In addition to any other applicable live loads, lifeline anchorages and structural elements that support lifeline anchorages shall be designed for a live load of at least 3,100 pounds (13.8 kN) for each attached lifeline, in every direction that a fall arrest load may be applied.

[1607.8.3] 1607.10.5 Railroad equipment. Minimum loads (including vertical, lateral, longitudinal, and impact) and the distribution thereof shall meet the applicable requirements of Chapter 15 of the AREMA Manual for Railway Engineering.

[1607.8.4] 1607.10.6 Assembly structures. Seating areas in grandstands, stadiums, and similar assembly structures shall be designed to resist the simultaneous application of a horizontal swaying load of at least 24 plf (36 kg/m) of seats applied in a direction parallel to the row of the seats, and of at least 10 plf (15 kg/m) of seats in a direction perpendicular to the row of the seats. When this load is used in combination with wind for outdoor structures, the wind load shall be one-half of the design wind load.

[1607.9] 1607.11 Reduction in uniform live loads. Except for uniform live loads at roofs, all other minimum uniformly distributed live loads, Lo, in Table 1607.1 are permitted to be reduced in accordance with Section [1607.9.1] 1607.11.1 or [1607.9.2] 1607.11.2. [Roof uniform] Uniform live loads [, other than special purpose roofs of Section 1607.11.2.2,] at roofs are permitted to be reduced in accordance with Section [1607.11.2] 1607.13.2. [Roof uniform live loads of special purpose roofs are permitted to be reduced in accordance with Section 1607.9.1 or 1607.9.2.]

[1607.9.1] 1607.11.1 [General] Basic uniform live load reduction. Subject to the limitations of Sections [1607.9.1.1] 1607.11.1.1 through [1607.9.1.4] 1607.11.1.4 and Table 1607.1, members for which a value of KLLAT is 400 square feet (37.16 m2) or more are permitted to be designed for a reduced uniformly distributed live load, L, in accordance with the following equation:

[((Equation 16-29))] (Equation 16-30)

where:

Reduced design live load per square foot [(square meter)] (m2) of area supported by the member.

Unreduced design live load per square foot [(square meter)] (m2) of area supported by the member (see Table 1607.1).

Live load element factor (see Table [1607.9.1] 1607.11.1).

Tributary area, in square feet [(square meter)] (m2).

L shall not be less than 0.50Lo for members supporting one floor and L shall not be less than 0.40Lo for members supporting two or more floors.

TABLE [1607.9.1] 1607.11.1
LIVE LOAD ELEMENT FACTOR, KLL

| ELEMENT | KLL |
| --- | --- |
| Interior columns | 4 |
| Exterior columns without cantilever slabs | 4 |
| Edge columns with cantilever slabs | 3 |
| Corner columns with cantilever slabs | 2 |
| Edge beams without cantilever slabs | 2 |
| Interior beams | 2 |
| All other members not identified above including: | 1 |
| Edge beams with cantilever slabs |  |
| Cantilever beams |  |
| One-way slabs |  |
| Two-way slabs |  |
| Members without provisions for continuous shear transfer normal to their span |  |

[1607.9.1.1] 1607.11.1.1 One-way slabs. The tributary area, AT, for use in Equation [16-22] 16-23 for one-way slabs shall not exceed an area defined by the slab span times a width normal to the span of 1.5 times the slab span.

[1607.9.1.2] 1607.11.1.2 Heavy live loads. Live loads that exceed 100 psf (4.79 kN/m2) shall not be reduced.

Exceptions:

1.	The live loads for members supporting two or more floors are permitted to be reduced by a maximum of 20 percent, but the live load shall be not [be] less than L as calculated in Section [1607.9.1] 1607.11.1.

2.	For uses other than storage, where approved, additional live load reductions shall be permitted where shown by the registered design professional that a rational approach has been used and that such reductions are warranted.

[1607.9.1.3] 1607.11.1.3 Passenger vehicle garages. The live loads shall not be reduced in passenger vehicle garages.

Exception: [the] The live loads for members supporting two or more floors are permitted to be reduced by a maximum of 20 percent, but the live load shall not be less than L as calculated in Section [1607.9.1] 1607.11.1.

[1607.9.1.4 Special occupancies. Live loads of 100 psf (4.79 kN/m2) or less at areas where fixed seats are located shall not be reduced in public assembly occupancies or in areas used for retail or wholesale sales.]

[1607.9.1.5] 1607.11.1.4 [Special structural elements] Flat Slab and Flat Plate Construction.[Live loads shall not be reduced for one-way slabs except as permitted in Section 1607.9.1.1.] Live loads shall not be reduced for calculating shear stresses at the heads of columns in flat slab or flat plate construction.

[1607.9.1.6 Roof members. Live loads of 100 psf (4.79 kN/m2) or less shall not be reduced for roof members except as specified in Section 1607.11.2.]

[1607.9.2] 1607.11.2 [Alternate floor] Alternative uniform live load reduction. As an alternative to Section [1607.9.1] 1607.11.1[, floor] and subject to the limitations of Table 1607.1, uniformly distributed live loads are permitted to be reduced in accordance with the following provisions. Such reductions shall apply to slab systems, beams, girders, columns, piers, walls and foundations.

[1.	A reduction shall not be permitted in Group A occupancies.]

[2.] 1.	A reduction shall not be permitted where the live load exceeds 100 psf (4.79 kN/m2) except that the design live load for members supporting two or more floors is permitted to be reduced by a maximum of 20 percent.

Exception: For uses other than storage, where approved, additional live load reductions shall be permitted where shown by the registered design professional that a rational approach has been used and that such reductions are warranted.

[3.] 2.	A reduction shall not be permitted in passenger vehicle parking garages except that the live loads for members supporting two or more floors are permitted to be reduced by a maximum of 20 percent.

[4.] 3.	For live loads not exceeding 100 psf (4.79 kN/m2), the design live load for any structural member supporting 150 square feet (13.94 m2) or more is permitted to be reduced in accordance with Equation [16-27] 16-31.

[5.] 4.	For one-way slabs, the area, A, for use in Equation [16-27] 16-31 shall not exceed the product of the slab span and a width normal to the span of 0.5 times the slab span.

[(Equation 16-30)] (Equation 16-31)

Such reduction shall not exceed the smallest of:

- 40 percent for [horizontal members] members supporting one floor;

- 60 percent for [vertical members] members supporting two or more floors; or

- R as determined by the following equation[.]:

[(Equation 16-31)] (Equation 16-32)

where:

Area of floor or roof supported by the member, square feet (m2).

Dead load per square foot (m2) of area supported.

Unreduced live load per square foot (m2) of area supported.

Reduction in percent.

[1607.10] 1607.12 Distribution of floor loads. Where uniform floor live loads are involved in the design of structural members arranged so as to create continuity, the minimum applied loads shall be the full dead loads on all spans in combination with the floor live loads on spans selected to produce the greatest load effect at each location under consideration. [It shall be] Floor live loads are permitted to [reduce floor live loads] be reduced in accordance with Section [1607.9] 1607.11.

[1607.11] 1607.13 Roof loads. The structural supports of roofs and marquees shall be designed to resist wind and, where applicable, snow and earthquake loads, in addition to the dead load of construction and the appropriate live loads as prescribed in this section, or as set forth in Table 1607.1. The live loads acting on a sloping surface shall be assumed to act vertically on the horizontal projection of that surface.

[1607.11.1] 1607.13.1 Distribution of roof loads. Where uniform roof live loads are reduced to less than 20 psf (0.96 kN/m2) in accordance with Section [1607.11.2.1] 1607.13.2.1 and are applied to the design of structural members arranged so as to create continuity, the reduced roof live [loads] load shall be applied to adjacent spans or to alternate spans, whichever produces the most unfavorable load effect. See Section [1607.11.2] 1607.13.2 for reductions in minimum roof live loads and Section 7.5 of ASCE 7 for partial snow loading.

[1607.11.1.1] 1607.13.1.1 Arches and gabled frames. The following simplification is permissible:

1.	Live load placed on one-half of the span adjacent to one support.

2.	Live load placed on the center one-fourth of the span.

3.	Live load placed on ⅜ of the span adjacent to each support.

[1607.11.2 Reduction in roof live loads] 1607.13.2 General. The minimum uniformly distributed live loads of roofs and marquees, Lo, in Table 1607.1 are permitted to be reduced in accordance with Section [1607.11.2.1 or 1607.11.2.2] 1607.13.2.1.

[1607.11.2.1] 1607.13.2.1 [Flat, pitched and curved] Ordinary roofs, awnings and canopies. Ordinary flat, pitched and curved roofs, and awnings and canopies other than of fabric construction supported by [light-weight rigid] a skeleton [structures] structure, are permitted to be designed for a reduced uniformly distributed roof live load, Lr, as specified in the following equations or other controlling combinations of loads as specified in Section 1605, whichever produces the greater load effect.

In structures such as greenhouses, where special scaffolding is used as a work surface for workers and materials during maintenance and repair operations, a lower roof load than specified in the following equations shall not be used unless approved by the commissioner. [Greenhouses] Such structures shall be designed for a minimum roof live load of 12 psf (0.58 kN/m2).

[(Equation 16-32)] (Equation 16-33)

where:

where:

=	Unreduced roof live load per square foot (m2) of horizontal projection supported by the member (see Table 1607.1).

Reduced live load per square foot (m2) of horizontal projection [in pounds per square foot (kN/m2)] supported by the member.

The reduction factors R1 and R2 shall be determined as follows:

[(Equation 16-33)] (Equation 16-34)

[(Equation 16-34)] (Equation 16-35)

[(Equation 16-35)] (Equation 16-36)

where:

Tributary area (span length multiplied by effective width) in square feet (m2) supported by any structural member, and

for a sloped roof, the number of inches of rise per foot (for SI: F = 0.12 × slope, with slope expressed percentage or for an arch or dome, the rise-to-span ratio multiplied by 32.]

[(Equation 16-36)] (Equation 16-37)

[(Equation 16-37)] (Equation 16-38)

[(Equation 16-38)] (Equation 16-39)

where:

For a sloped roof, the number of inches of rise per foot (for SI: F = 0.12 × slope, with slope expressed as a percentage), or for an arch or dome, the rise-to-span ratio multiplied by 32.

[1607.11.2.2] 1607.13.3 [Special-purpose] Occupiable roofs. [Roofs] Areas of roofs that are occupiable, such as vegetative roofs, roof gardens[, marquees, and roofs used for used] or for [promenade,] assembly or other [special] similar purposes [shall be designed for a minimum live load, Lo, as specified in Table 1607.1. Such live loads], and marquees are permitted to [be] have their uniformly distributed live loads reduced in accordance with Section [1607.9] 1607.11. [Live loads of 100 psf (4.79 kN/m2) or more at areas or roofs classified as Group A occupancies shall not be reduced.]

[1607.11.3 Green roofs. Where roofs utilize a green roof system and are not intended for human occupancy, the uniform design live load in the area covered by the green roof shall be 20 psf (0.958 kN/m2). The weight of the landscaping materials shall be considered as dead load and shall be computed on the basis of saturation of the soil. Where roofs utilize a green roof system and are used for human occupancy, the minimum live load shall be as specified in Table 1607.1 or Section 1607.11.2.2, whichever is greater.]

1607.13.3.1 Vegetative and landscaped roofs. The weight of all landscaping materials shall be considered as dead load and shall be computed on the basis of saturation of the soil as determined in accordance with Section 3.1.4, of ASCE 7. The uniform design live load in unoccupied landscaped areas on roofs shall be 20 psf (0.958 kN/m2). The uniform design live load for occupied landscaped areas on roofs shall be determined in accordance with Table 1607.1.

[1607.11.4] 1607.13.4 Awnings, [,] canopies, and sun control devices. Awnings, canopies, and sun control devices shall be designed for uniform live loads as required in Table 1607.1 as well as for snow loads and wind loads as specified in Sections 1608 and 1609.

[1607.11.5 Hanging loads. Girders and roof trusses (other than joists) over garage areas regularly utilized for the repair of vehicles and over manufacturing floors or storage floors used for commercial purposes shall be capable of supporting, in addition to the specified live and wind loads, a concentrated live load of 2,000 pounds (908 kg) applied at any lower chord panel point for trusses, and at any point of the lower flange for girders.]

1607.13.5 Photovoltaic panel systems. Roof structures that provide support for photovoltaic panel systems shall be designed in accordance with Sections 1607.13.5.1 through 1607.13.5.4, as applicable.

1607.13.5.1 Roof live load. Roof structures that support photovoltaic panel systems shall be designed to resist each of the following conditions:

1.	Applicable uniform and concentrated roof loads with the photovoltaic panel system dead loads.

Exception: Roof live loads need not be applied to the area covered by photovoltaic panels where the clear space between the panels and the roof surface is 24 inches (610 mm) or less.

2.	Applicable uniform and concentrated roof loads without the photovoltaic panel system present.

1607.13.5.2 Photovoltaic panels or modules. The structure of a roof that supports solar photovoltaic panels or modules shall be designed to accommodate the full solar photovoltaic panels or modules and ballast dead load, including concentrated loads from support frames in combination with the loads from Section 1607.13.5.1 and other applicable loads. Where applicable, snow drift loads created by the photovoltaic panels or modules shall be included.

1607.13.5.3 Photovoltaic panels or modules installed as an independent structure. Solar photovoltaic panels or modules that are independent structures and do not have accessible/occupied space underneath are not required to accommodate a roof photovoltaic live load, provided the area under the structure is restricted to keep the public away. All other loads and combinations in accordance with Section 1605 shall be accommodated.

Solar photovoltaic panels or modules that are designed to be the roof, span to structural supports, and have accessible/occupied space underneath shall have the panels or modules and all supporting structures designed to support a roof photovoltaic live load, as defined in Section 1607.13.5.1 in combination with other applicable loads. Solar photovoltaic panels or modules in this application are not permitted to be classified as “not accessible” in accordance with Section 1607.13.5.1.

1607.13.5.4 Ballasted photovoltaic panel systems. Roof structures that provide support for ballasted photovoltaic panel systems shall be designed, or analyzed, in accordance with Section 1604.4; checked in accordance with Section 1604.3.6 for deflections; and checked in accordance with Section 1611 for ponding.

1607.13.6 Hanging loads. Girders and roof trusses (other than joists) over garage areas regularly utilized for the repair of vehicles and over manufacturing floors or storage floors used for commercial purposes shall be capable of supporting, in addition to the specified live and wind loads, a concentrated live load of 2,000 pounds (908 kg) applied at any lower chord panel point for trusses, and at any point of the lower flange for girders.

[1607.12] 1607.14 Crane loads. The crane live load shall be the rated capacity of the crane. Design loads for the runway beams, including connections and support brackets, of moving bridge cranes and monorail cranes shall include the maximum wheel loads of the crane and the vertical impact, lateral and longitudinal forces induced by the moving crane.

[1607.12.1] 1607.14.1 Maximum wheel load. The maximum wheel loads shall be the wheel loads produced by the weight of the bridge, as applicable, plus the sum of the rated capacity and the weight of the trolley with the trolley positioned on its runway at the location where the resulting load effect is maximum.

[1607.12.2] 1607.14.2 Vertical impact force. The maximum wheel loads of the crane shall be increased by the percentages shown below to determine the induced vertical impact or vibration force:

| Monorail cranes (powered) | 25 percent |
| --- | --- |
| Cab-operated or remotely operated bridge cranes (powered) | 25 percent |
| Pendant-operated bridge cranes (powered) | 10 percent |
| Bridge cranes or monorail cranes with hand-geared bridge, trolley and hoist | 0 percent |

[1607.12.3] 1607.14.3 Lateral force. The lateral force on crane runway beams with electrically powered trolleys shall be calculated as 20 percent of the sum of the rated capacity of the crane and the weight of the hoist and trolley. The lateral force shall be assumed to act horizontally at the traction surface of a runway beam, in either direction perpendicular to the beam, and shall be distributed according to the lateral stiffness of the runway beam and supporting structure.

[1607.12.4] 1607.14.4 Longitudinal force. The longitudinal force on crane runway beams, except for bridge cranes with hand-geared bridges, shall be calculated as 10 percent of the maximum wheel loads of the crane. The longitudinal force shall be assumed to act horizontally at the traction surface of a runway beam, in either direction parallel to the beam.

[1607.13] 1607.15 Interior walls and partitions. Interior walls and partitions that exceed 6 feet (1829 mm) in height, including their finish materials, shall have adequate strength and stiffness to resist the loads to which they are subjected but not less than a horizontal load of 5 psf (0.240 kN/m2).

[Exception: Fabric partitions complying with Section 1607.13.1 shall not be required to resist the minimum horizontal load of 5 psf (0.24 kN/m2).]

[1607.13.1] 1607.15.1 Fabric partitions. Fabric partitions that exceed 6 feet (1829 mm) in height, including their finish materials, shall have adequate strength and stiffness to resist the following load conditions:

1.	[A] The horizontal distributed load [of 5 psf (0.24 kN/m2)] need only be applied to the partition framing. The total area used to determine the distributed load shall be the area of the fabric face between the framing members to which the fabric is attached. The total distributed load shall be uniformly applied to such framing members in proportion to the length of each member.

2.	A concentrated load of 40 pounds (0.176 kN) applied to an 8-inch diameter (203 mm) area [50.3 square inches (32 452 mm2)] of the fabric face at a height of 54 inches (1372 mm) above the floor.

1607.15.2 Fire Walls.  In order to meet the structural stability requirements of Section 706.2 where the structure on either side of the wall has collapsed, fire walls and their supports shall be designed to withstand a minimum horizontal allowable stress load of 5 psf (0.240 kN/m2).

SECTION BC 1608
SNOW LOADS

1608.1 General. Design snow loads shall be determined in accordance with Chapter 7 of ASCE 7, but the design roof load shall not be less than that determined by Section 1607.

1608.2 Ground snow loads. The ground snow [load, Pg,] loads to be used in determining the design snow loads for roofs is 25 psf (1.2 kN/m2).

[1608.3 Flat roof snow loads. The flat roof snow load, ρf, on a roof with a slope equal to or less than 5 degrees (0.09 rad) (1 inch per foot = 4.76 degrees) shall be calculated in accordance with Section 7.3 of ASCE 7.]

[1608.3.1 Exposure factor. The value for the snow exposure factor, Ce, used in the calculation of ρf shall be determined from Table 1608.3.1.]

[TABLE 1608.3.1
SNOW EXPOSURE FACTOR, Ce

| TERRAIN CATEGORYa | EXPOSURE OF ROOFa,b |
| --- | --- |
|  | Fully exposedc | Partially exposed | Sheltered |
| A (see Section 1609.4) | N/A | 1.1 | 1.3 |
| B (see Section 1609.4) | 0.9 | 1.0 | 1.2 |
| C (see Section 1609.4) | 0.9 | 1.0 | 1.1 |

For SI: 1 mile = 1609 m.

a.	The terrain category and roof exposure condition chosen shall be representative of the anticipated conditions during the life of the structure. An exposure factor shall be determined for each roof of a structure.

b.	Definitions of roof exposure are as follows:

1.	Fully exposed shall mean roofs exposed on all sides with no shelter afforded by terrain, higher structures or trees. Roofs that contain several large pieces of mechanical equipment, parapets which extend above the height of the balanced snow load, hb, or other obstructions are not in this category.

2.	Partially exposed shall include all roofs except those designated as “fully exposed” or “sheltered.”

3.	Sheltered roofs shall mean those roofs located tight in among conifers that qualify as “obstructions.”

c.	Obstructions within a distance of 10 ho provide “shelter,” where ho is the height of the obstruction above the roof level. If the only obstructions are a few deciduous trees that are leafless in winter, the “fully exposed” category shall be used except for terrain category “A.” Note that these are heights above the roof. Heights used to establish the terrain category in Section 1609.4 are heights above the ground.]

[1608.3.2 Thermal factor. The value for the thermal factor, Ct, used in the calculation of ρf shall be determined from Table 1608.3.2.]

TABLE 1608.3.2
THERMAL FACTOR, Ct

| THERMAL CONDITIONa | Ct |
| --- | --- |
| All structures except as indicated below | 1.0 |
| Structures kept just above freezing and others with cold, ventilated roofs in which the thermal resistance (R-value) between the ventilated space and the heated space exceeds 25h ⋅ ft2 ⋅ °F/Btu | 1.1 |
| Unheated structures | 1.2 |
| Continuously heated greenhousesb with a roof having a thermal resistance (R-value) less than 2.0h ⋅ ft2 ⋅°F/Btu | 0.85 |

For SI: 1 h⋅ft2⋅ °F/Btu = 0.176m2⋅K/W.

- The thermal condition shall be representative of the anticipated conditions during winters for the life of the structure.

b.	A continuously heated greenhouse shall mean a greenhouse with a constantly maintained interior temperature of 50°F or more during winter months. Such greenhouse shall also have a maintenance attendant on duty at all times or a temperature alarm system to provide warning in the event of a heating system failure.

]

[1608.3.3 Snow load importance factor. The value for the snow load importance factor, Is, used in the calculation of ρf shall be determined in accordance with Table 1604.5.2 based on the Structural Occupancy Category determined in accordance with Table 1604.5. Greenhouses that are occupied for growing plants on production or research basis, without public access, shall be included in Structural Occupancy Category I.]

[1608.3.4 Reserved.]

[1608.3.5] 1608.3 Ponding instability.[For roofs with a slope less than ¼ inch per foot (1.19 degrees), the design calculations shall include verification of the prevention of] Susceptible bays of roofs shall be evaluated for ponding instability in accordance with [Section 7.11] Chapters 7 and 8 of ASCE 7.

[1608.3.6 Ice. For ice loads to be used in the design of ice sensitive structures, such as open framed or guyed towers, refer to Chapter 10 of ASCE 7.]

[1608.4 Sloped roof snow loads. The snow load, ps, on a roof with a slope greater than 5 degrees (0.09 rad) (1 inch per foot = 4.76 degrees) shall be calculated in accordance with Section 7.4 of ASCE 7.]

[1608.5 Partial loading. The effect of not having the balanced snow load over the entire loaded roof area shall be analyzed in accordance with Section 7.5 of ASCE 7.]

[1608.6 Unbalanced snow loads. Unbalanced roof snow loads shall be determined in accordance with Section 7.6 of ASCE 7. Winds from all directions shall be accounted for when establishing unbalanced snow loads.]

[1608.7 Drifts on lower roofs. In areas where the ground snow load, Pg, as determined by Section 1608.2, is equal to or greater than 5 psf (0.240 kN/ m2), roofs shall be designed to sustain localized loads from snowdrifts in accordance with Section 7.7 of ASCE 7.]

[1608.8 Roof projections. Drift loads due to mechanical equipment, penthouses, parapets and other projections above the roof shall be determined in accordance with Section 7.8 of ASCE7.]

[1608.9 Sliding snow. The extra load caused by snow sliding off a sloped roof onto a lower roof shall be determined in accordance with Section 7.9 of ASCE 7.]

SECTION BC 1609
WIND LOADS

1609.1 Applications. Buildings, structures and parts thereof shall be designed to withstand the minimum wind loads prescribed herein. Decreases in wind loads shall not be made for the effect of shielding by other structures.

1609.1.1 Determination of wind loads. Wind loads on every building or structure shall be determined in accordance with [Chapter 6] Chapters 26 to 31 of ASCE 7[with the basic]. The type of opening protection required, the basic design wind speed, V, and the exposure category for a site is permitted to be determined in accordance with [Sections 1609.3 through 1609.4] Section 1609.[.] [Wind loads may also be determined using provisions of the alternate methods described in Section 1609.6.] Wind shall be assumed to come from any horizontal direction and wind pressures shall be assumed to act normal to the surface considered.

Exceptions:

- [Reserved] Subject to the limitations of Section 1609.1.1.1, the provisions of ICC 600 shall be permitted for applicable Group R-2 and R-3 buildings.

2.	Subject to the limitations of Section 1609.1.1.1, residential structures using the provisions of [the AF&PA] AWC WFCM.

3.	Subject to the limitations of Section 1609.1.1.1, residential structures using the provisions of AISI S230.

4.	Designs using NAAMM FP 1001[Guide Specification for Design of Metal Flagpoles].

5.	Designs using [TIA/EIA-222] TIA-222 for antenna-supporting structures and antennas.

6.	Wind tunnel tests in accordance with [Section 6.6] ASCE 49 and Sections 31.4 and 31.5 of ASCE 7 [, subject to the limitations in Section 1609.1.1.2].

The wind speeds in Section 1609.3 are basic design wind speeds, V, and shall be converted in accordance with Section 1609.3.1 to allowable stress design wind speeds, Vasd, when the provisions of the standards referenced in Exceptions 4 and 5 are used.

1609.1.1.1 Applicability. The provisions of ICC 600[, AF&PA] are applicable only to buildings located within Exposure B or C as defined in Section 1609.4. The provisions of ICC 600, AWC WFCM and AISI S230 shall not apply to buildings sited on the upper half of an isolated hill, ridge or escarpment meeting the following conditions:

1.	The hill, ridge or escarpment is 60 feet (18 288 mm) or higher if located in Exposure B or 30 feet (9144 mm) or higher if located in Exposure C;

2.	The maximum average slope of the hill exceeds 10 percent; and

3.	The hill, ridge or escarpment is unobstructed upwind by other such topographic features for a distance from the high point of 50 times the height of the hill or [1 mile (1.61 km)] 2 miles (3.22 km), whichever is greater.

[1609.1.1.2 Wind tunnel test limitations. The lower limit on pressures for main wind-force-resisting systems and components and cladding shall be in accordance with Sections 1609.1.1.2.1 and 1609.1.1.2.2.]

[1609.1.1.2.1 Lower limits on main wind-force-resisting system. Base overturning moments determined from wind tunnel testing shall be limited to not less than 80 percent of the design base overturning moments determined in accordance with Section 6.5 of ASCE 7, unless specific testing is performed that demonstrates that lower vaults result from the aerodynamic coefficient of the building, rather than shielding from other structures. The 80-percent limit shall be permitted to be adjusted by the ratio of the frame load at critical wind directions as determined from wind tunnel testing without specific adjacent buildings, but including appropriate upwind roughness, to that determined in Section 6.5 of ASCE 7. In no case shall the limiting value be less than 50 percent of the design base overturning moments determined in accordance with Section 6.5 of ASCE 7.]

[1609.1.1.2.2 Lower limits on components and cladding. The design pressures for components and cladding on walls or roofs shall be selected as the greater of: (i) the wind tunnel test results; or (ii) 80 percent of the pressure obtained for Zone 4 for walls and Zone 1 for roofs, as determined in Section 6.5 of ASCE 7, unless specific testing is performed that demonstrates that lower values result from the aerodynamic coefficient of the building rather than shielding from nearby structures. Alternatively, limited tests at a few wind directions without specific adjacent buildings, but in the presence of an appropriate upwind roughness, shall be permitted to be used to demonstrate that the lower pressures are due to the shape of the building and not to shielding. In no case shall the limiting value be less than 65 percent of the pressure obtained for Zone 4 for walls and Zone 1 for roofs, as determined in Section 6.5 of ASCE 7.]

[1609.1.2 Protection from wind borne debris. The following buildings shall be protected with an impact-resistant covering or glazing in accordance with the Missile Levels and Wind Zones specified in ASTM E 1886 and ASTM E 1996 or other approved test methods and performance criteria:]

[1. Buildings in Structural Occupancy Category IV, as defined in Table 1604.5, located in Exposure C or D, as defined in Section 1609.4;]

[2. Buildings in Structural Occupancy Category III, as defined in Table 1604.5, located in Exposure D, as defined in Section 1609.4, where the glazing of such building encloses places of assembly for 300 or more persons or areas of in-place shelter.]

[Exception: Glazing protection in accordance with Section 1609.1.2 shall not be required if the glazing is located more than 60 feet (18 288 mm) above the ground and more than 30 feet (9144 mm) above aggregate-surfaced roofs, including roofs with gravel or stone ballast located within 1,500 feet (457.2 m) of the building.]

1609.1.2 Protection of openings. In wind-borne debris regions, glazing in buildings shall be impact resistant or protected with an impact-resistant covering meeting the requirements of an approved impact-resistant standard or ASTM E1996 and ASTM E1886 referenced herein as follows:

1.	Glazed openings located within 30 feet (9144 mm) of grade shall meet the requirements of the large missile test of ASTM E1996.

2.	Glazed openings located more than 30 feet (9144 mm) above grade shall meet the provisions of the small missile test of ASTM E1996.

Exceptions:

1.	Wood structural panels with a minimum thickness of 7/16 inch (11.1 mm) and maximum panel span of 8 feet (2438 mm) shall be permitted for opening protection in buildings with a mean roof height of 33 feet (10 058 mm) or less that are classified as a Group R-3 or R-4 occupancy. Panels shall be precut so that they shall be attached to the framing surrounding the opening containing the product with the glazed opening. Panels shall be predrilled as required for the anchorage method and shall be secured with the attachment hardware provided. Attachments shall be designed to resist the components and cladding loads determined in accordance with the provisions of ASCE 7, with corrosion-resistant attachment hardware provided and anchors permanently installed on the building. Attachment in accordance with Table 1609.1.2 with corrosion-resistant attachment hardware provided and anchors permanently installed on the building is permitted for buildings with a mean roof height of 45 feet (13 716 mm) or less where Vasd determined in accordance with Section 1609.3.1 does not exceed 140 mph (63 m/s).

2.	Glazing in Risk Category I or II buildings, including greenhouses that are occupied for growing plants on a production or research basis, without public access shall be permitted to be unprotected.

3.	Glazing in Risk Category III or IV buildings located over 60 feet (18 288 mm) above the ground.

TABLE 1609.1.2
WIND-BORNE DEBRIS PROTECTION FASTENING SCHEDULE FOR WOOD STRUCTURAL PANELSa,b,c,d

| FASTENER TYPE | FASTENER SPACING (inches) |
| --- | --- |
|  | Panel Span ≤ 4 feet | 4 feet < Panel Span ≤ 6 feet | 6 feet < Panel Span ≤ 8 feet |
| No. 8 wood-screw-based anchor with 2-inch embedment length | 16 | 10 | 8 |
| No. 10 wood-screw-based anchor with 2-inch embedment length | 16 | 12 | 9 |
| ¼-inch diameter lag-screw-based anchor with 2-inch embedment length | 16 | 16 | 16 |

For SI: 1 inch = 25.4 mm, 1 foot = 304.8 mm, 1 pound = 4.448 N, 1 mile per hour = 0.447 m/s.

a.	This table is based on 140 mph wind speeds and a 45-foot mean roof height.

b.	Fasteners shall be installed at opposing ends of the wood structural panel. Fasteners shall be located a minimum of 1 inch from the edge of the panel.

c.	Anchors shall penetrate through the exterior wall covering with an embedment length of 2 inches minimum into the building frame. Fasteners shall be located a minimum of 2½ inches from the edge of concrete block or concrete.

d.	Where panels are attached to masonry or masonry/stucco, they shall be attached using vibration-resistant anchors having a minimum ultimate withdrawal capacity of 1,500 pounds.

1609.1.2.1 Louvers. Louvers protecting intake and exhaust ventilation ducts not assumed to be open that are located within 30 feet (9144 mm) of grade shall meet the requirements of [an approved impact-resisting standard or the large missile test of ASTM E 1996] AMCA 540.

1609.1.2.2 Application of ASTM E1996. The text of Section 6.2.2 of ASTM E1996 shall be substituted as follows:

6.2.2 Unless otherwise specified, select the wind zone based on the strength design wind speed, V, as follows:

6.2.2.1 Wind Zone 1—130 mph ≤ basic design wind speed, V < 140 mph.

6.2.2.2 Delete.

6.2.2.3 Delete.

6.2.2.4 Delete.

[1609.1.2.2] 1609.1.2.3 Garage doors. Garage door glazed opening protection for wind-borne debris shall meet the requirements of an approved impact-resisting standard or ANSI/DASMA 115.

1609.1.3 Minimum wind loads. The design wind [loads] pressure, p, used in the design of the main wind-force-resisting system shall not be less than [10 psf (0.479 kN/m2)] 16 psf (0.766 kN/m2) multiplied by the area of the building or structure projected on a vertical plane normal to the wind direction. In the calculation of design wind [loads for] pressure, p, used in the design of components and cladding for buildings, the algebraic sum of the pressures acting on opposite faces shall be taken into account. The design pressure for components and cladding of buildings shall not be less than [20 psf (0.958 kN/m2)] 32 psf (1.533 kN/m2) acting in either direction normal to the surface. The design force for open buildings and other structures shall not be less than [10 psf (0.479 kN/m2)] 16 psf (0.766 kN/m2) multiplied by the area Af.

1609.1.4 Anchorage against overturning, uplift and sliding. Structural members and systems and components and cladding in a building or structure shall be anchored to resist wind-induced overturning, uplift and sliding and to provide continuous load paths for these forces to the foundation.

Where a portion of the resistance to these forces is provided by dead load, the dead load, including the weight of soils and foundations, shall be taken as the minimum dead load likely to be in place during a design wind event.

1609.1.5 Wind and seismic detailing. Lateral-force-resisting systems shall meet seismic detailing requirements and limitations prescribed in this code, even when wind code prescribed load effects are greater than seismic load effects.

1609.1.6 Wind tunnel test limitations. The lower limit on pressures for main wind-force-resisting systems and components and cladding shall be in accordance with Section 1609.1.6.

1609.1.6.1 Lower limits on main wind-force-resisting system. Base overturning moments determined from wind tunnel testing shall be limited to not less than 80 percent of the design base overturning moments determined in accordance with Section 27.2 of ASCE 7 unless the wind tunnel results and testing procedure are peer reviewed by an independent wind tunnel laboratory. In no case shall the limiting value be less than 70 percent of the design base overturning moments determined in accordance with Section 27.2 of ASCE 7.

1609.1.6.2 Lower limits on components and cladding. The design pressures for components and cladding on walls or roofs shall be selected as the greater of: (i) the wind tunnel test results; or (ii) 80 percent of the pressure obtained for Zone 4 for walls and Zone 1 for roofs, as determined in Section 30.5 of ASCE 7, unless the wind tunnel results and testing procedure are peer reviewed by an independent wind tunnel laboratory. In no case shall the limiting value be less than 70 percent of the pressure obtained for Zone 4 for walls and Zone 1 for roofs, as determined in Section 30.5 of ASCE 7.

1609.1.6.3 Scope of peer review by independent wind tunnel laboratory. When applicable, the peer reviewer of the wind tunnel test shall:

1.	Be retained by or on behalf of the owner and shall be independent from the wind tunnel laboratory that performed the tests and the report shall bear no conflict of interest.

2.	Have a minimum of 10 years of technical expertise in the application of wind tunnel studies on buildings comparable to that being reviewed.

3.	Have experience in performing or evaluating boundary layer wind tunnel studies and shall be familiar with the technical issues and regulations governing the wind tunnel procedure in ASCE 49.

4.	Review the wind tunnel report, including but not limited to wind climate data and modeling, data analysis, boundary layer modeling, building modeling, significant influential buildings, resulting wind loads and other relevant issues identified by the reviewer.

5.	Review the wind tunnel report for cladding and envelope pressures, if applicable.

6.	Submit a report to the department summarizing the results of their review, and shall state whether the wind tunnel test and the results meet the industry standard, the New York City Building Code and are appropriate for the project.

1609.2 Definitions. [The following words and terms shall, for] For the purposes of Section 1609[, have the meanings shown herein.] and as used elsewhere in the code, the following terms are defined in Chapter 2:

BUILDINGS AND OTHER STRUCTURES, FLEXIBLE. [Buildings and other structures that have a fundamental natural frequency less than 1 Hz.]

BUILDING, ENCLOSED. [A building that does not comply with the requirements for open or partially enclosed buildings.]

BUILDING, LOW-RISE. [Enclosed or partially enclosed buildings that comply with the following conditions:]

[1.	Mean roof height, h, less than or equal to 60 feet (18 288 mm).]

[2.	Mean roof height, h, does not exceed least horizontal dimension.]

BUILDING, OPEN. [A building having each wall at least 80 percent open. This condition is expressed for each wall by the equation:]

[(Equation 16-39)]

[where:]

[Ao =	Total area of openings in a wall that receives positive external pressure, in square feet (m2).]

[Ag =	The gross area of that wall in which Ao is identified, in square feet (m2).]

BUILDING, PARTIALLY ENCLOSED. [A building that complies with both of the following conditions:]

[1.	The total area of openings in a wall that receives positive external pressure exceeds the sum of the areas of openings in the balance of the building envelope (walls and roof) by more than 10 percent; and]

[2.	The total area of openings in a wall that receives positive external pressure exceeds 4 square feet (0.37 m2) or 1 percent of the area of that wall, whichever is smaller, and the percentage of openings in the balance of the building envelope does not exceed 20 percent. These conditions are expressed by the following equations:]

[(Equation 16-40)]

[(Equation 16-41)]

[where:]

,  are as defined for an open building.]

The sum of the areas of openings in the building envelope (walls and roof) not including Ao, in square feet (m2).]

The sum of the gross surface areas of the building envelope (walls and roof) not including Ag, in square feet (m2).]

BUILDING, SIMPLE DIAPHRAGM. [A building in which wind loads are transmitted through floor and roof diaphragms to the vertical lateral-force-resisting systems.]

COMPONENTS AND CLADDING. [Elements of the building envelope that do not qualify as part of the main wind force-resisting system.]

EAVE HEIGHT, h[:]. [The distance from the ground surface adjacent to the building to the roof eave line at the particular wall. If the distance of the eave varies along the wall, the average distance shall be used.]

EFFECTIVE WIND AREA.[The area used to determine GCp. For component and cladding elements, the effective wind area in Tables 1609.6.2.1(2) and 1609.6.2.1(3) is the span length multiplied by an effective width that need not be less than one-third the span length. For cladding fasteners, the effective wind area shall not be greater than the area that is tributary to an individual fastener.]

HURRICANE-PRONE REGIONS. [New York City is within the hurricane-prone region.]

IMPORTANCE FACTOR, I. [A factor that accounts for the degree of hazard to human life and damage to property.]

MAIN WIND FORCE-RESISTING SYSTEM. [An assemblage of structural elements assigned to provide support and stability for the overall structure. The system generally receives wind loading from more than one surface.]

MEAN ROOF HEIGHT. [The average of the roof eave height and the height to the highest point on the roof surface, except that eave height shall be used for roof angle of less than or equal to 10 degrees (0. 1745 rad).]

WIND-BORNE DEBRIS REGION.[New York City is not in the wind-borne debris region.]

WIND SPEED, V (BASIC).

WIND SPEED, Vasd (ALLOWABLE STRESS DESIGN).

1609.3 Basic design wind speed. The basic design wind speed, V, in mph, for [New York City is 98 mph (43.8m/s). The basic wind speed is measured at 33 feet (10 058 mm) above ground in Exposure C as a 3-second gust speed. This wind speed is based on local wind climate with a nominal annual probability of 0.02 (nominal 50-year mean recurrence interval) which is obtained by dividing the 700 year mean recurrence wind speed by sq rt (1.6).] determining wind speed shall be that of Table 1609.3.

TABLE 1609.3

BASIC DESIGN WIND SPEED

| Risk Category | Basic Design Wind Speed, mph (3-sec gust, 33 ft. for Exposure Category C) | Mean Recurrence Interval, years | Probability of Exceedance in 50 years, % |
| --- | --- | --- | --- |
| I | 110 | 300 | 15 |
| II | 117 | 700 | 7 |
| III | 127 | 1700 | 3 |
| IV | 132 | 3000 | 1.6 |

Note:	Values are ultimate design 3-second gust wind speeds in miles per hour at 33 feet (10 058 mm) above ground for Exposure Category C.

1609.3.1 Wind speed conversion. [When required, the 3-second gust wind speed, V3S can be converted to a fastest-mile wind speed, Vfm using Equation 16-42 below.] Where required, the basic design wind speed, V, of Table 1609.3 shall be converted to allowable stress design wind speed, Vasd, using Equation 16-40.

[	[(Equation 16-42)]

Vasd = 0.79V	(Equation 16-40)

1609.3.2 Wind speed for serviceability design. Table 1609.3.2 presents 3-second gust wind speeds for mean recurrence intervals (MRI) of 10, 25, 50 and 100 years. These wind speeds may be used for serviceability applications such as drift and habitability.

TABLE 1609.3.2

SERVICEABILITY DESIGN WIND SPEED

| Mean Recurrence Interval (years) | Serviceability Design Wind Speed, mph (3-sec gust, 33 ft. for Exposure Category C) |
| --- | --- |
| 10 | 80 |
| 25 | 87 |
| 50 | 93 |
| 100 | 100 |

Note:	Values are 3-second gust wind speeds in miles per hour at 33 feet (10 058 mm) above ground for Exposure Category C.

1609.4 Exposure category. For each wind direction considered, an exposure category that adequately reflects the characteristics of ground surface irregularities shall be determined for the site at which the building or structure is to be constructed. [For a site located in the transition zone between categories, the category resulting in the largest wind forces shall apply.]

Account shall be taken of variations in ground surface roughness that arise from natural topography and vegetation as well as from constructed features.[When applying the simplified wind load method of Section 1609.6, a single exposure category shall be used based upon the most restrictive for any given wind direction.]

1609.4.1 Wind directions and sectors. For each selected wind direction at which the wind loads are to be evaluated, the exposure of the building or structure shall be determined for the two upwind sectors extending 45 degrees (0.79 rad) either side of the selected wind direction. The exposures in these two sectors shall be determined in accordance with Sections 1609.4.2 and 1609.4.3 and the exposure resulting in the highest wind loads shall be used to represent winds from that direction.

1609.4.2 Surface roughness categories. A ground surface roughness within each 45-degree (0.79 rad) sector shall be determined for a distance upwind of the site as defined in Section 1609.4.3 from the categories defined below, for the purpose of assigning an exposure category as defined in Section 1609.4.3.

Surface Roughness B. Urban and suburban areas, wooded areas or other terrain with numerous closely spaced obstructions having the size of single-family dwellings or larger.

Surface Roughness C. Open terrain with scattered obstructions having heights generally less than 30 feet (9144 mm). This category includes flat open country, grasslands, and limited water surfaces per Figure 1609.4.3.

Surface Roughness D. Flat, unobstructed areas and water surfaces[, including areas in hurricane-prone regions]. This category includes smooth mud flats, salt flats and unbroken ice.

1609.4.3 Exposure categories. An exposure category shall be determined in accordance with the following:

Figure 1609.4.3 provides the exposure categories at the shore lines for wind directions approaching over the water within the city boundaries.

Exposure B. For buildings with a mean roof height of less than or equal to 30 feet (9144 mm), Exposure B shall apply where the ground surface roughness [condition], as defined by Surface Roughness B, prevails in the upwind direction for a distance of at least 1,500 feet (457 m). For buildings with a mean roof height greater than 30 feet (9144 mm), Exposure B shall apply where Surface Roughness B prevails in the upwind direction for a distance of at least 2,600 feet (792 m) or 20 times the height of the building, whichever is greater.

[Exception: For buildings whose mean roof height is less than or equal to 30 feet (9144 mm), the upwind distance is permitted to be reduced to 1,500 feet (457 m).]

Exposure C. Exposure C shall apply where it is shown in Figure 1609.4.3 or for all cases where [Exposures] Exposure B or D does not apply.

Exposure D. Exposure D shall apply where the ground surface roughness, as defined by Surface Roughness D, prevails in the upwind direction for a distance of at least 5,000 feet (1524 m) or 20 times the height of the building, whichever is greater. Exposure D shall [extend inland from] also apply where the [shoreline for] ground surface roughness immediately upwind of the site is B or C, and the site is within a distance of 600 feet (183 m) or 20 times the [height of the] building height, whichever is greater, from an Exposure D condition as defined in the previous sentence.

[1609.5 Importance factor. Buildings and other structures shall be assigned a wind load importance factor, I, in accordance with Table 1604.5.2 based on the Structural Occupancy Category determined by Table 1604.5.]

[1609.6 Simplified wind load methods.]

[1609.6.1 Scope. The procedures in Section 1609.6 shall be permitted to be used for determining and applying wind pressures in the design of enclosed buildings as listed below:]

[1.	For buildings with flat, gabled or hipped roofs having a mean roof height not exceeding the least horizontal dimension or 60 feet (18 288 mm), whichever is less, the use of Section 1609.6.2, Simplified Procedure I, is permitted.]

[2.	For buildings located within any Borough with a mean roof height of not more than 200 feet (60 960 mm) not located in Exposure C or D in accordance with Section 1609.4, the use of Section 1609.6.3, Simplified Procedure II, is permitted.]

[3.	For buildings located within the Borough of Manhattan with a mean roof height of not more than 300 feet (91 440 mm) and not located in Exposure C or D in accordance with Section 1609.4, the use of Section 1609.6.3, Simplified Procedure II, is permitted.]

[1609.6.2 Simplified Design Procedure I (for low-rise buildings).]

[1.	The wind shall be assumed to come from any horizontal direction.]

[2.	An importance factor I shall be determined in accordance with Section 1609.5.]

[3.	An exposure category shall be determined in accordance with Section 1609.4.]

[4.	A height and exposure adjustment coefficient, λ, shall be determined from Table 1609.6.2.1(4).]

[1609.6.2.1 Main wind force-resisting system. Simplified design wind pressures, ps, for the main wind force-resisting systems represent the net pressures (sum of internal and external) to be applied to the horizontal and vertical projections of building surfaces as shown in Figure 1609.6.2.1. For the horizontal pressures (Zones A, B, C, D), ps is the combination of the windward and leeward net pressures. ps shall be determined from Equation 16-43).]

[	[(Equation 16-43)]

[where:]

Adjustments factor for building height and exposure from Table 1609.6.2.1(4).]

Importance factor as defined in Section 1609.5.]

=	Simplified design wind pressure for Exposure B, at h = 30 feet (9144 mm), and for I =1.0, from Table 1609.6.2.1(1).]

[

]

[FIGURE 1609.6.2.1
MAIN WINDFORCE LOADING DIAGRAM

For SI: 1 foot = 304.8 mm, 1 degree = 0.0 174 rad.

Notes:

1.	Pressures are applied to the horizontal and vertical projections for Exposure B, at h = 30 feet, for I = 1.0. Adjust to other exposures and heights with adjustment factor λ.

2.	The load patterns shown shall be applied to each corner of the building in turn as the reference corner.

3.	For the design of the longitudinal MWFRS, use θ = 0°, and locate the Zone E/F, G/H boundary at the mid-length of the building.

4.	Load Cases 1 and 2 must be checked for 25° < θ ≤45°. Load Case 2 at 25° is provided only for interpolation between 25° to 30°.

5.	Plus and minus signs signify pressures acting toward and away from the projected surfaces, respectively.

6.	For roof slopes other than those shown, linear interpolation is permitted.

7.	The total horizontal load shall not be less than that determined by assuming PS = 0 in Zones B and D.

8.	The zone pressures represent the following:

Horizontal pressure zones — Sum of the windward and leeward net (sum of internal and external) pressures on vertical projection of:

A – End zone of wall	C – Interior zone of wall

B – End zone of roof	D – Interior zone of roof

Vertical pressure zones — Net (sum of internal and external) pressures on horizontal projection of:

E – End zone of windward roof	G – Interior zone of windward roof

F – End zone of leeward roof	H – Interior zone of leeward roof

9.	Where Zone E or G falls on a roof overhang on the windward side of the building, use EOH and GOH for the pressure on the horizontal projection of the overhang. Overhangs on the leeward and side edges shall have the basic zone pressure applied.

10.	Notation:

a: 10 percent of least horizontal dimension or 0.4h, whichever is smaller, but not less than either 4 percent of least horizontal dimension or 3 feet.

h: Mean roof height, in feet (meters), except that eave height shall be used for roof angles <10°.

θ: Angle of plane of roof from horizontal, in degrees.]

[TABLE 1609.6.2.1(1)
SIMPLIFIED DESIGN WIND PRESSURE (MAIN WINDFORCE-RESISTING SYSTEM), ps30 (Exposure B at h = 30 feet with I = 1.0) (psf)

| ROOF ANGLE (degrees) | ROOF RISE IN 12 | LOAD CASE | ZONES |
| --- | --- | --- | --- |
|  |  |  | Horizontal Pressures | Vertical Pressures | Overhangs |
|  |  |  | A | B | C | D | E | F | G | H | EOH | GOH |
| 0 to 5° | Flat | 1 | 12.0 | -6.0 | 8.0 | -4.0 | -14.0 | -8.0 | -10.0 | -6.0 | -20.0 | -15.0 |
| 10° | 2 | 1 | 22.0 | -9.0 | 15.0 | -5.0 | -23.0 | -14.0 | -16.0 | -11.0 | -33.0 | -26.0 |
| 15° | 3 | 1 | 24.0 | -8.0 | 16.0 | -5.0 | -23.0 | -15.0 | 16.0 | -12.0 | -33.0 | -26.0 |
| 20° | 4 | 1 | 27.0 | -7.0 | 18.0 | -4.0 | -23.0 | -16.0 | 16.0 | -12.0 | -33.0 | -26.0 |
| 25° | 6 | 1 2 | 24.0 — | 4.0 — | 18.0 — | 4.0 — | -11.0 -4.0 | -15.0 -8.0 | -8.0 -1.0 | -12.0 -5.0 | -20.0 — | -17.0 — |
| 30° to 45° | 7 to 12 | 1 2 | 22.0 22.0 | 15.0 15.0 | 17.0 17.0 | 12.0 12.0 | 2.0 9.0 | -13.0 -7.0 | 1.0 7.0 | -12.0 -5.0 | -8.0 -4.0 | -9.0 -9.0 |

For SI: 1 inch = 25.4 mm, 1 foot = 304.8 mm, 1 degree = 0.0174 rad, 1 mile per hour = 0.44 m/s, 1 pound per square foot = 47.9 N/m2.]

[TABLE 1609.6.2.1(2)
NET DESIGN WIND PRESSURE (COMPONENT AND CLADDING), pnet30
(Exposure B at h = 30 feet with I = 1.0 and kzt=1 and 98 mph 3 sec. gust basic wind speed) (psf)

|  | ZONE | EFFECTIVE WIND AREA | PRESSURE / SUCTION |
| --- | --- | --- | --- |
| Roof 0 to77 7 degrees | 1 | 10 | 7.0 | -17.0 |
|  | 1 | 20 | 7.0 | -16.0 |
|  | 1 | 50 | 6.0 | -16.0 |
|  | 1 | 100 | 6.0 | -15.0 |
|  | 2 | 10 | 7.0 | -28.0 |
|  | 2 | 20 | 7.0 | -25.0 |
|  | 2 | 50 | 6.0 | -21.0 |
|  | 2 | 100 | 6.0 | -18.0 |
|  | 3 | 10 | 7.0 | -42.0 |
|  | 3 | 20 | 7.0 | -35.0 |
|  | 3 | 50 | 6.0 | -26.0 |
|  | 3 | 100 | 6.0 | -18.0 |
| Roof > 7 to 27 degrees | 1 | 10 | 10.0 | -15.0 |
|  | 1 | 20 | 9.0 | -15.0 |
|  | 1 | 50 | 8.0 | -14.0 |
|  | 1 | 100 | 7.0 | -14.0 |
|  | 2 | 10 | 10.0 | -27.0 |
|  | 2 | 20 | 9.0 | -25.0 |
|  | 2 | 50 | 8.0 | -22.0 |
|  | 2 | 100 | 7.0 | -20.0 |
|  | 3 | 10 | 10.0 | -39.0 |
|  | 3 | 20 | 9.0 | -37.0 |
|  | 3 | 50 | 8.0 | -33.0 |
|  | 3 | 100 | 7.0 | -31.0 |
| Roof > 27 to 45 degrees | 1 | 10 | 15.0 | -17.0 |
|  | 1 | 20 | 15.0 | -16.0 |
|  | 1 | 50 | 14.0 | -15.0 |
|  | 1 | 100 | 14.0 | -14.0 |
|  | 2 | 10 | 15.0 | -20.0 |
|  | 2 | 20 | 15.0 | -19.0 |
|  | 2 | 50 | 14.0 | -18.0 |
|  | 2 | 100 | 14.0 | -17.0 |
|  | 3 | 10 | 15.0 | -20.0 |
|  | 3 | 20 | 15.0 | -19.0 |
|  | 3 | 50 | 14.0 | -18.0 |
|  | 3 | 100 | 14.0 | -17.0 |
| Wall | 4 | 10 | 17.0 | -18.0 |
|  | 4 | 20 | 16.0 | -18.0 |
|  | 4 | 50 | 15.0 | -17.0 |
|  | 4 | 100 | 14.0 | -16.0 |
|  | 4 | 500 | 13.0 | -14.0 |
|  | 5 | 10 | 17.0 | -22.0 |
|  | 5 | 20 | 16.0 | -21.0 |
|  | 5 | 50 | 15.0 | -19.0 |
|  | 5 | 100 | 14.0 | -18.0 |
|  | 5 | 500 | 13.0 | -14.0 |

For SI: 1 foot = 304.8 mm, 1 degree = 0.0 174 rad, 1 mile per hour = 0.44 m/s, 1 pound per square foot = 47.9 N/m2.

Note: For effective areas between those given above, the load is permitted to be interpolated, otherwise use the load associated with the lower effective area.]

[TABLE 1609.6.2.1(3)
ROOF OVERHANG NET DESIGN WIND PRESSURE (COMPONENT AND CLADDING), pnet30
(Exposure B at h = 30 feet with Iw = 1.0 and 98 mph 3 sec. gust basic wind speed) (psf)

|  | ZONE | EFFECTIVE | PRESSURE/ SUCTION |
| --- | --- | --- | --- |
|  |  | WIND AREA |  |
|  |  | (sq. ft.) |  |
| Roof 0 to 7 degrees | 2 | 10 | -24.0 |
|  | 2 | 20 | -24.0 |
|  | 2 | 50 | -23.0 |
|  | 2 | 100 | -23.0 |
|  | 3 | 10 | -40.0 |
|  | 3 | 20 | -31.0 |
|  | 3 | 50 | -20.0 |
|  | 3 | 100 | -12.0 |
| Roof > 7 to 27 degrees | 2 | 10 | -31.0 |
|  | 2 | 20 | -31.0 |
|  | 2 | 50 | -31.0 |
|  | 2 | 100 | -31.0 |
|  | 3 | 10 | -52.0 |
|  | 3 | 20 | -47.0 |
|  | 3 | 50 | -41.0 |
|  | 3 | 100 | -35.0 |
| Roof > 27 to 45 degrees | 2 | 10 | -28.0 |
|  | 2 | 20 | -28.0 |
|  | 2 | 50 | -26.0 |
|  | 2 | 100 | -26.0 |
|  | 3 | 10 | -28.0 |
|  | 3 | 20 | -28.0 |
|  | 3 | 50 | -26.0 |
|  | 3 | 100 | -26.0 |

For SI: 1 foot = 304.8 mm, 1 degree = 0.0174 rad, 1 mile per hour = 0.45 m/s, 1 pound per square foot = 47.9 N/m2.

Note: For effective areas between those given above, the load is permitted to be interpolated, otherwise use the load associated with the lower effective area.]

[TABLE 1609.6.2.1(4)
ADJUSTMENT FACTOR FOR BUILDING HEIGHT AND EXPOSURE, (λ)

| MEAN ROOF HEIGHT | EXPOSURE |
| --- | --- |
| (feet) | B | C/C1 | D |
| 15 | 1.00 | 1.21 | 1.47 |
| 20 | 1.00 | 1.29 | 1.55 |
| 25 | 1.00 | 1.35 | 1.61 |
| 30 | 1.00 | 1.40 | 1.66 |
| 35 | 1.05 | 1.45 | 1.70 |
| 40 | 1.09 | 1.49 | 1.74 |
| 45 | 1.12 | 1.53 | 1.78 |
| 50 | 1.16 | 1.56 | 1.81 |
| 55 | 1.19 | 1.59 | 1.84 |
| 60 | 1.22 | 1.62 | 1.87 |

For SI: 1 foot = 304.8 mm.

a.	All table values shall be adjusted for other exposures and heights by multiplying by the above coefficients.]

[1609.6.2.1.1 Minimum pressures. The load effects of the design wind pressures from Section 1609.6.2.1 shall not be less than assuming the pressures, ps, for Zones A, B, C and D all equal to + 20 psf (0.96 kN/m2), while assuming Zones E, F, G, and H all equal to 0 psf.]

[1609.6.2.2 Components and cladding.cladding. Net Net design wind pressures, pnet, for the components and cladding of buildings represent the net pressures (sum of internal and external) to be applied normal to each building surface as shown in Figure 1609.6.2.2. The net design wind pressure, pnet, shall be determined from Equation 16-44:]

[	[(Equation 16-44)]

[where:]

Adjustments factor for building height and exposure from Table 1609.6.2.1(4).]

Importance factor as defined in Section 1609.5.]

Net design wind pressure for Exposure B, at h =30 feet (9144 mm), and for Iw =1.0, from Tables 1609.6.2.1(2) and 1609.6.2.1(3).]

FIGURE 1609.6.2.2
COMPONENT AND CLADDING PRESSURE

]

[For SI: 1 foot = 304.8 mm, 1 degree = 0.0174 rad.

Notes:

- Pressures are applied normal to the surface for Exposure B, at h = 30 feet, for Iw = 1.0. Adjust to other exposures and heights with adjustment factor λ.

- Plus and minus signs signify pressures acting toward and away from the surfaces, respectively.

- For hip roofs with θ ≤ 25°, Zone 3 shall be treated as Zone 2.

- For effective areas between those given, the value is permitted to be interpolated, otherwise use the value associated with the lower effective area.

- Notation:

a: 10 percent of least horizontal dimension or 0.4h, whichever is smaller, but not less than either 4 percent of least horizontal dimension or 3 feet.

h: Mean roof height, in feet (meters), except that eave height shall be used for roof angles <10°.

θ: Angle of plane of roof from horizontal, in degrees.]

[1609.6.2.2.1 Minimum pressures. The positive design wind pressures, pnet, from Section 1609.6.2.2 shall not be less than + 20 psf (1.44 kN/m2), and the negative design wind pressures, pnet, from Section 1609.6.2.2 shall not be less than –20 psf (-1.44 kN/m2).]

[1609.6.2.3 Load case. Members that act as both part of the main wind force-resisting system and as components and cladding shall be designed for each separate load case.]

[1609.6.3 Simplified Design Procedure II.]

[1609.6.3.1 Main wind-force-resisting system. Main wind force-resisting systems shall comply with the following:]

[1.	The building shall be designed for the following net lateral wind pressure to be applied to the horizontal projection of the building surfaces:]

[1.1.	From 0 to 100 feet (0 to 30 480 mm) elevation 20 psf (0.96 kN/m2).]

[1.2.	From 100 to 300 feet (30 480 to 91 440 mm) elevation 25 psf (1.2 kN/m2).]

[2.	An importance factor, I, shall be determined in accordance with Section 1609.5 and shall be applied to the pressures indicated above.]

[1609.6.3.2 Design wind load cases. The main wind-force-resisting system of buildings, whose wind loads have been determined pursuant to Section 1609.6.3, shall be designed for wind load cases as defined below:]

[Case 1. Full design wind pressure acting on the projected area perpendicular to each principal axis of the structure, considered separately along each principal axis.]

[Case 2. Seventy-five percent of the design wind pressure acting on the projected area perpendicular to each principal axis of the structure to be applied eccentric to the center of the exposure with eccentricity equal to 15 percent of the exposure width, considered separately for each principal direction.]

[Case 3. Wind loading as defined in Case 1 for each orthogonal direction, but considered to act simultaneously at 75 percent of the specified value.]

[1609.6.3.3 Components and cladding. cladding. Net Net design wind positive and negative pressures (pressure and suction) for the components and cladding of buildings represent the net (sum of internal and external) to be applied normal to each building surface. The net design wind positive and negative shall not be less than 30 psf (1.44 kN/m2), except at the corners of the building with a width equivalent to 10 percent of the building’s width at its side, the net design wind negative pressure for the components and cladding shall not be less than: (i) 45 psf (2.16 kN/m2) for the portion of the building between 200 feet (60.76 meters) to 300 feet (91.14 meters) height above ground and (ii) 40 psf (1.92 kN/m2) for the portion of the building between 100 feet (30.38 meters) to 199 feet (60.66 meters) in height above ground.]

[1609.6.3.4 Roof. The design pressure and suction acting over the entire roof including purlins, roofing, and other roof elements (including their fastenings) shall not be less than 30 psf (1.44 kN/m2).]

[1609.6.3.5 Other building elements. The following building elements of buildings whose wind loads have been determined under the provisions of Section 1609.6.3 shall be designed for wind pressures shown in Section 1609.6.3.1 multiplied by the following shape factors given in Table 1609.6.3.5.]

TABLE 1609.6.3.5 
OTHER BUILDING ELEMENTS

| CONSTRUCTION SHAPE FACTOR |
| --- |
| Signs (and their supports), or portions thereof, having 70 percent or more of solid surface | 1.5 |
| Signs (and their supports), or portions thereof, having less than 70 percent of solid surface | 2.0 |
| Tanks, cooling towers, and similar constructions | 1.5 |
| Square and rectangular chimneys | 1.5 |

[1609.6.3.5.1 Eaves and cornices. Eaves, cornices, and overhanging elements of the buildings shall be designed for upward pressures twice the values given in Section 1609.6.3.1.]

[1609.7] 1609.5 Roof systems. Roof systems shall be designed and constructed in accordance with Sections 1609.5.1 through 1609.5.3, as applicable.

[1609.7.1] 1609.5.1 Roof deck. The roof deck shall be designed to withstand the wind pressures determined [under either the provisions of Section 1609.6 for buildings satisfying the height and other requirements of the simplified methods or] in accordance with Section 1609.1.1 for buildings of any height.

[1609.7.2] 1609.5.2 Roof coverings. Roof coverings shall comply with [the requirements for roof decks pursuant to] Section [1609.7.1] 1609.5.1.

Exceptions:

1.	Rigid tile roof coverings that are air permeable and installed over a roof deck complying with Section [1609.7.1] 1609.5.1 are permitted to be designed in accordance with Section [1609.7.3] 1609.5.3.

2.	Asphalt shingles installed over a roof deck complying with Section [1609.7.1] 1609.5.1 shall comply with the wind-resistance requirements of Section [1507.2.7.1] 1504.1.1.

[1609.7.3] 1609.5.3 Rigid tile. Wind loads on rigid tile roof coverings shall be determined in accordance with the following equation:

Ma = qhCLbLLa(1.0 – GCp)	[(Equation 16-45)] (Equation 16-41)

For SI: Ma = qhCLbLLa(1.0 – GCp) / 1,000

where:

b = 	Exposed width, feet (mm) of the roof tile.

CL = 	Lift coefficient. The lift coefficient for concrete and clay tile shall be 0.2 or shall be determined by test in accordance with Section [1716.2] 1711.2.

GCp = 	Roof pressure coefficient for each applicable roof zone determined from Chapter [6] 30 of ASCE 7. Roof coefficients shall not be adjusted for internal pressure.

L = 	Length, feet (mm) of the roof tile.

La = 	Moment arm, feet (mm) from the axis of rotation to the point of uplift on the roof tile. The point of uplift shall be taken at 0.76L from the head of the tile and the middle of the exposed width. For roof tiles with nails or screws (with or without a tail clip), the axis of rotation shall be taken as the head of the tile for direct deck application or as the top edge of the batten for battened applications. For roof tiles fastened only by a nail or screw along the side of the tile, the axis of rotation shall be determined by testing. For roof tiles installed with battens and fastened only by a clip near the tail of the tile, the moment arm shall be determined about the top edge of the batten with consideration given for the point of rotation of the tiles based on straight bond or broken bond and the tile profile.

Ma = 	Aerodynamic uplift moment, feet-pounds (N-mm) acting to raise the tail of the tile.

qh = 	Wind velocity pressure, psf (kN/m2) determined from Section [6.5.10] 26.10.2 of ASCE 7.

Concrete and clay roof tiles complying with the following limitations shall be designed to withstand the aerodynamic uplift moment as determined by this section.

1.	The roof tiles shall be either loose laid on battens, mechanically fastened, mortar set or adhesive set.

2.	The roof tiles shall be installed on solid sheathing [which] that has been designed as components and cladding.

3.	An underlayment shall be installed in accordance with Chapter 15.

4.	The tile shall be single lapped interlocking with a minimum head lap of not less than 2 inches (51 mm).

5.	The length of the tile shall be between 1.0 and 1.75 feet (305 mm and 533 mm).

6.	The exposed width of the tile shall be between 0.67 and 1.25 feet (204 mm and 381 mm).

7.	The maximum thickness of the tail of the tile shall not exceed 1.3 inches (33 mm).

8.	Roof tiles using mortar set or adhesive set systems shall have at least two-thirds of the tile’s area free of mortar or adhesive contact.

[1609.8 Wind on temporary structures. Wind on temporary structures shall be permitted to be designed for reduced wind loading in accordance with the requirements of Section 1618.]

1609.6 Simplified design procedure. Use of the simplified design procedure shall comply with Sections 1609.6.1 through 1609.6.5.

1609.6.1 Scope. The procedures in Section 1609.6 shall be permitted to be used for determining and applying wind pressures in the design of enclosed buildings in Risk Category I and II as listed below:

1.	For buildings located within any borough with a mean roof height of not more than 200 feet (60 960 mm) and not located in Exposure C or D in accordance with Section 1609.4, the use of Section 1609.6 shall be permitted.

2.	For buildings located within the Borough of Manhattan with a mean roof height of not more than 300 feet (91 440 mm) and not located in Exposure C or D in accordance with Section 1609.4, the use of Section 1609.6 shall be permitted.

1609.6.2 Main windforce-resisting systems. Main windforce-resisting systems shall comply with the following:

1.	The building shall be designed for the following net lateral wind pressure to be applied to the horizontal projection of the building surfaces:

1.1.	From 0 to 100 feet (0 to 30 480 mm) elevation 32 psf (1.54 kN/m2).

1.2.	From 100 to 300 feet (30 480 to 91 440 mm) elevation 40 psf (1.92 kN/m2).

1609.6.3 Design wind load cases. The main windforce-resisting system of buildings, whose wind loads have been determined pursuant to Section 1609.6.1, shall be designed for wind load cases as defined below:

Case 1. Full design wind pressure acting on the projected area perpendicular to each principal axis of the structure, considered separately along each principal axis.

Case 2. Seventy-five percent of the design wind pressure acting on the projected area perpendicular to each principal axis of the structure to be applied eccentric to the center of the exposure with eccentricity equal to 15 percent of the exposure width, considered separately for each principal direction.

Case 3. Wind loading as defined in Case 1 for each orthogonal direction, but considered to act simultaneously at 75 percent of the specified value.

1609.6.4 Components and cladding. Net design wind positive and negative pressures (pressure and suction) for the components and cladding of buildings represent the net pressures (sum of internal and external) to be applied normal to each building surface. The net design wind positive and negative pressures shall not be less than 48 psf (12.30 kN/m2), except at the corners of the building with a width equivalent to 10 percent of the building’s width at its side, the net design wind negative pressure for the components and cladding shall not be less than: (i) 72 psf (3.46 kN/m2) for the portion of the building between 200 feet (60 960 mm) to 300 feet (91 440 mm) height above ground and (ii) 64 psf (3.07 kN/m2) for the portion of the building between 100 feet (30 480 mm) to 199 feet (60 656 mm) in height above ground.

1609.6.5 Roof. The design pressure and suction acting over the entire roof including purlins, roofing, and other roof elements (including their fastenings) shall be not less than 48 psf (2.30 kN/m2).

1609.7 Attached canopies on buildings. Canopies attached to buildings shall comply with Section 1609.7.1 or 1609.7.2, as applicable.

TABLE 1609.7
NET PRESSURE COEFFICIENT, (GCPN) FOR ATTACHED CANOPIES ON BUILDINGS WITH h>60 FT

| Net Pressure Coefficient (GCpn) | h/hc |
| --- | --- |
|  | 2 | 3 | 6 | 12 | 18 | 24 | 30 |
| Upward | -0.60 | -0.70 | -0.95 | -1.04 | -1.16 | -1.3 | -1.3 |
| Downward | 0.90 | 0.90 | 0.90 | 0.90 | 0.90 | 0.90 | 0.90 |

For SI: 1 foot = 304.8 mm.

h

hc

Figure 1609.7 Schematic of attached canopy on buildings with h>60 ft.

1609.7.1 Buildings with h≤60 ft. The design wind pressure for canopies attached to walls of buildings with h≤60 ft. shall follow Chapter 30 of ASCE 7.

1609.7.2 Buildings with h>60 ft. The design wind pressure for canopies attached to walls of buildings with h>60 ft. and hc/h< 0.5, as shown on Figure1609.7, shall be from the following equation:

P= qh(GCpn) (lb/ft2)	(Equation 16-42)

Where:

qh= velocity pressure at mean roof height h per Chapter 26 of ASCE 7.

GCpn= net pressure coefficient for attached canopies given in Table 1609.7.

1609.8 Wind load on structures during construction. Structures during construction shall comply with Sections 1609.8.1 and 1609.8.2.

1609.8.1 Design wind speed. Design wind speed during construction for a construction period of less than 5 years may be reduced as follows:

Unless otherwise directed by the commissioner, the basic design wind speed may be reduced to 110 mph for all risk categories, corresponding to 1.7% probability of exceedance in 5 years. The basic design wind speed refers to the ultimate design 3-second gust wind speed at 33 feet (10 058 mm) above ground for Exposure Category C, as defined in Section 1609.3.

1609.8.2 Frameworks without cladding. For unenclosed frames and elements, the appropriate drag factors and wind effect on successive elements shall be accounted for per recognized standards and references, or in accordance with suitable wind tunnel testing.

SECTION BC 1610
SOIL LATERAL [LOAD] LOADS

1610.1 General. Foundation walls and retaining walls shall be designed to resist lateral soil [and hydrostatic] loads. [The soil] Soil loads specified in Table 1610.1 shall be used as the minimum design lateral soil loads unless [specified] determined otherwise [in] by a geotechnical investigation [report prepared] in accordance with Section [1802] 1803. Foundation walls and other walls in which horizontal movement is restricted at the top shall be designed for at-rest pressure. Retaining walls free to move and rotate at the top [are] shall be permitted to be designed for active pressure. Design lateral pressure from [hydrostatic, dynamic, or] surcharge loads shall be added to the lateral earth pressure load [, as applicable. For hydrostatic lateral pressure, see Section 1806.2]. Design lateral pressure shall be increased if soils at the site are expansive. Foundation walls shall be designed to support the weight of the full hydrostatic pressure of undrained backfill unless a drainage system is installed in accordance with Sections 1805.4.2 and 1805.4.3.

Exception: Foundation walls extending not more than 8 feet (2438 mm) below grade and laterally supported at the top by flexible diaphragms shall be permitted to be designed for active pressure.

TABLE 1610.1
[SOIL] LATERAL SOIL LOAD

| DESCRIPTION OF BACKFILL MATERIALc | UNIFIED SOIL CLASSIFICATION | DESIGN LATERAL SOIL LOADa (pound per square foot per foot of depth) |
| --- | --- | --- |
|  |  | Active pressure | At-rest pressure |
| Well-graded, clean gravels; gravel-sand mixes | GW | 30 | 60 |
| Poorly graded clean gravels; gravel-sand mixes | GP | 30 | 60 |
| Silty gravels, poorly graded gravel-sand mixes | GM | 40 | 60 |
| Clayey gravels, poorly graded gravel-and-clay mixes | GC | 45 | 60 |
| Well-graded, clean sands; gravelly sand mixes | SW | 30 | 60 |
| Poorly graded clean sands; sand-gravel mixes | SP | 30 | 60 |
| Silty sands, poorly graded sand-silt mixes | SM | 45 | 60 |
| Sand-silt clay mix with plastic fines | SM-SC | 45 | 100 |
| Clayey sands, poorly graded sand-clay mixes | SC | 60 | 100 |
| Inorganic silts and clayey silts | ML | 45 | 100 |
| Mixture of inorganic silt and clay | ML-CL | 60 | 100 |
| Inorganic clays of low to medium plasticity | CL | 60 | 100 |
| Organic silts and silt clays, low plasticity | OL | Note b | Note b |
| Inorganic clayey silts, elastic silts | MH | Note b | Note b |
| Inorganic clays of high plasticity | CH | Note b | Note b |
| Organic clays and silty clays | OH | Note b | Note b |

For SI: 1 pound per square foot per foot of depth = 0.157 kPa/m, 1 foot = 304.8 mm.

- Design lateral soil loads are given for moist conditions for the specified soils at their optimum densities. Actual field conditions shall govern. Submerged or saturated soil pressures shall include the weight of the buoyant soil plus the hydrostatic loads.

- Unsuitable as backfill material.

- The definition and classification of soil materials shall be in accordance with ASTM D 2487.

SECTION BC 1611
RAIN LOADS

1611.1 Design rain loads. Each portion of a roof shall be designed to sustain the load of rainwater that will accumulate on it if the primary drainage system for that portion is blocked plus the uniform load caused by water that rises above the inlet of the secondary drainage system at its design flow.

[(Equation 16-46)] (Equation 16-43)

where:

Additional depth of water on the undeflected roof above the inlet of secondary drainage system at its design flow (i.e., the hydraulic head), in inches (mm).

Depth of water on the undeflected roof up to the inlet of secondary drainage system when the primary drainage system is blocked (i.e., the static head), in inches (mm).

Rain load on the undeflected roof, in psf (kN/m2). When the phrase “undeflected roof” is used, deflections from loads (including dead loads) shall not be considered when determining the amount of rain on the roof.

1611.2 Ponding instability. [For roofs with a slope less than ¼ inch per foot [(1.19 degrees (0.0208 rad))], the design calculations shall include verification of adequate stiffness to preclude progressive deflection in accordance with Section 8.4 of ASCE 7.] Susceptible bays of roofs shall be evaluated for ponding instability in accordance with Section 8.4 ASCE 7.

1611.3 Controlled drainage. Roofs equipped with hardware to control the rate of drainage shall be equipped with a secondary drainage system at a higher elevation that limits accumulation of water on the roof above that elevation. Such roofs shall be designed to sustain the load of rainwater that will accumulate on them to the elevation of the secondary drainage system plus the uniform load caused by water that rises above the inlet of the secondary drainage system at its design flow determined from Section 1611.1. Such roofs shall also be checked for ponding instability in accordance with Section 1611.2.

SECTION BC 1612
FLOOD LOADS

1612.1 General. [The requirements for flood loads shall be as specified in Appendix G of this code.] Buildings and other structures located in whole or in part in flood hazard areas shall meet the requirements of Section 5.3 of ASCE 7 and Appendix G of this code. The structural design shall be based on the design loads stated in Section 5.4 of ASCE 7, the load combinations of Section 1605, and Appendix G of this code.

1612.2 Reserved.

1612.3 Reserved.

1612.4 Reserved.

1612.5 Reserved.

SECTION BC 1613
EARTHQUAKE LOADS

1613.1 Scope. Every structure, and portion thereof, including nonstructural components that are permanently attached to structures and their supports and attachments, shall be designed and constructed to resist the effects of earthquake motions in accordance with ASCE 7[-10], excluding Chapter 14 and Appendix 11A. The seismic design category for a structure shall be determined in accordance with either Section 1613 or ASCE 7[-10].

Exceptions:

1.	One- and two-family dwellings three stories or less in height.

2.	The [seismic-force-resisting] seismic force-resisting system of wood-frame buildings that conform to the provisions of Section 2308 are not required to be analyzed as specified in this section.

3.	Agricultural storage structures intended only for incidental human occupancy.

4.	Structures that require special consideration of their response characteristics and environment that are not addressed by this code or ASCE 7[-10] and for which other regulations provide seismic criteria, such as vehicular bridges, electrical transmission towers, hydraulic structures, buried utility lines and their appurtenances and nuclear reactors.

[1613.1.1 Seismic importance factor. The value for the seismic load importance factor, I, used in the calculation of E shall be determined in accordance with Table 1604.5.2 based on the Risk Category determined in accordance with Table 1604.5.]

[1613.1] 1613.2 Definitions. The following [words and terms shall, for the purposes of this section, have the meanings shown herein.] terms are defined in Chapter 2:

DESIGN EARTHQUAKE GROUND MOTION. [The earthquake ground motion that buildings and structures are specifically proportioned to resist in Section 1613.]

MAXIMUM CONSIDERED EARTHQUAKE (MCE) GROUND MOTION. [The most severe earthquake effects considered by this standard more specifically defined in the following two terms.]

MAXIMUM CONSIDERED EARTHQUAKE GEOMETRIC MEAN (MCEG) PEAK GROUND [ACCELERATIONS] ACCELERATION. [The most severe earthquake effects considered by this standard determined for geometric mean peak ground acceleration and without adjustment for targeted risk. The MCEG peak ground acceleration adjusted for site effects (PGAM) is used in this standard for evaluation of liquefaction, lateral spreading, seismic settlements, and other soil-related issues. The PGAM values adjusted for site effects are provided in Table 1813.2.1 or can be derived from the site-specific procedures provided in Section 21.5 of ASCE 7-10.]

[RISK-TARGETED MAXIMUM CONSIDERED EARTHQUAKE (MCER) GROUND MOTION RESPONSE ACCELERATIONS. The most severe earthquake effects considered by this standard determined for the orientation that results in the largest maximum response for horizontal ground motions and with adjustment for targeted risk. The MCER Ground Motion values can be determined from general procedure in Section 1613.5.3 or can be derived from the site specific procedures provided in Sections 21.1 and 21.2 of ASCE 7-10.]

MECHANICAL SYSTEMS. [For the purposes of determining seismic loads in ASCE 7-10, mechanical systems shall also include fire protection, plumbing and fuel gas systems as specified therein.]

ORTHOGONAL. [To be in two horizontal directions, at 90 degrees (1.57 rad) to each other.]

RISK-TARGETED MAXIMUM CONSIDERED EARTHQUAKE (MCER) GROUND MOTION RESPONSE ACCELERATION.

SEISMIC DESIGN CATEGORY.[A classification assigned to a structure based on its risk category and the severity of the design earthquake ground motion at the site.]

[SEISMIC-FORCE-RESISTING] SEISMIC FORCE-RESISTING SYSTEM.[The part of the structural system that has been considered in the design to provide the required resistance to the prescribed seismic forces.]

SITE CLASS. [A classification assigned to a site based on the types of soils present and their engineering properties as defined in Section 1613.5.2.]

SITE COEFFICIENTS.[The values of, Fa, and, Fv, indicated in Tables 1613.5.3(1) and 1613.5.3(2), respectively.]

[1613.3 Reserved.]

[1613.4 Reserved.]

[1613.5] 1613.3 Seismic ground motion values. Seismic ground motion values shall be determined in accordance with this section.

[1613.5.1] 1613.3.1 Mapped acceleration parameters. The mapped maximum considered earthquake spectral response acceleration at short periods (SS) shall be [0.281] 0.296 g and at [1-second] 1-s period (S1) shall be [0.073] 0.061 g. The mapped long-period transition period (TL) shall be [6] 6.0 seconds. Alternatively, electronic values of mapped acceleration parameters Ss and S1 and other seismic design parameters provided at the U.S. Geological Survey (USGS) website at https://doi.org/10.5066/F7NK3C76 may be used as per the guidelines of ASCE 7, Section 11.4.

[1613.5.2] 1613.3.2 Site class definitions. Based on the site soil properties, the site shall be classified as [either] Site Class A, B, C, D, E or F in accordance with [Table 1613.5.2] Chapter 20 of ASCE 7, and this code. Where the soil properties are not known in sufficient detail to determine the site class, Site Class D shall be used unless the commissioner or geotechnical data determines [that] Site Class E or F [soil is] soils are present at the site.

| TABLE 1613.5.2 SITE CLASS DEFINITIONS |
| --- |
| SITE CLASS | SOIL PROFILE NAME | AVERAGE PROPERTIES IN TOP 100 feet, SEE SECTION 1613.5.5 |
|  |  | Soil shear wave velocity, vs, (ft/s) | Standard penetration resistance, N | Soil undrained shear strength, su, (psf) |
| A | Hard rock | vs > 5,0000 | N/A | N/A |
| B | Rock | 2,500 < vs ≤ 5,000 | N/A | N/A |
| C | Very dense soil and soft rock | 1,200 < vs ≤ 2,500 | N > 50 | su ≥ 2,000 |
| D | Stiff soil profile | 600 ≤ vs ≤ 1,200 | 15 ≤ N ≤ 15 | 1,000 ≤ su ≤ 2,000 |
| E | Soft soil profile | vs < 600 | N < 15 | su < 1,000 |
| E | -- | Any profile with more than 10 feet of soil having the following characteristics: 1. Plasticity index PI > 20, 2. Moisture content w ≥ 40%, and 3. Undrained shear strength su < 500 psf |
| F | -- | Any profile containing soils having one or more of the following characteristics: 1. Soils vulnerable to potential failure or collapse under seismic loading such as liquefiable soils, quick and highly sensitive clays, collapsible weakly cemented soils. 2. Peats and/or highly organic clay (H > 10 feet of peat and/or highly organic clay where H = thickness of soil) 3. Very high plasticity clays (H > 25 feet with plasticity index PI > 75) 4. Very thick soft/medium stiff clays (H > 120 feet) |

For SI: 1 foot = 304.8 mm, 1 square foot = 0.0929m2, 1 pound per square foot = 0.0479 kPa. N/A = Not applicable]

[1613.5.3] 1613.3.3 Site coefficients and [risk-targeted] adjusted maximum considered earthquake [(MCER)] spectral response acceleration parameters. The [MCER] maximum considered earthquake spectral response acceleration [parameters] for short periods, SMS, and at 1-second period, SM1, adjusted for site class effects shall be determined by Equations [16-47] 16-44 and [16-48] 16-45, respectively:

[(Equation 16-47)] (Equation 16-44)

[(Equation 16-48)] (Equation 16-45)

where:

Fa = Site coefficient defined in Table [1613.5.3(1)] 1613.3.3(1).

Fv = Site coefficient defined in Table [1613.5.3(2)] 1613.3.3(2).

Ss = The mapped MCER spectral accelerations for short periods as determined in Section [1613.5.1] 1613.3.1.

S1 = The mapped MCER spectral accelerations for a 1-s period as determined in Section [1613.5.1] 1613.3.1.

Exception: When electronic values of mapped acceleration parameters are used as per Section 1613.3.1, the site coefficients, Fa and Fv, cannot be taken from Tables 1613.3.3(1) and 1613.3.3(2). Rather, general procedures in Chapter 11 of ASCE 7 shall be followed to determine Fa and Fv.

TABLE [1613.5.3(1)] 1613.3.3(1)
VALUES OF SITE COEFFICIENT Fa AS A FUNCTION OF SITE
CLASS AND MAPPED SPECTRAL RESPONSE ACCELERATION
AT SHORT PERIODS (SS)a

| SITE CLASS | Fa |
| --- | --- |
| A | 0.80 |
| B (Vs measured) | 0.90 |
| B (Vs unmeasured) | 1.00 |
| C | [1.20] 1.30 |
| D | 1.57 |
| E | [2.37] 2.28 |
| F | Note a |

- Site-specific geotechnical investigation and dynamic site response analyses shall be performed to determine appropriate values, except that for structures with periods of vibration equal or less than 0.5 second, values of Fa for liquefiable soils are permitted to be taken equal to the values for the site class determined without regard to liquefaction in Section [1613.5.5] 1613.3.4.1.

TABLE [1613.5.3(2)] 1613.3.3(2)
VALUES OF SITE COEFFICIENT Fv AS A FUNCTION OF SITE
CLASS AND MAPPED SPECTRAL RESPONSE ACCELERATION
AT 1-SECOND PERIOD (S1)a

| SITE CLASS | Fv |
| --- | --- |
| A | 0.80 |
| B (Vs measured) | 0.90 |
| B (Vs unmeasured) | 1.00 |
| C | [1.70] 1.50 |
| D | 2.40 |
| E | [3.50] 4.20 |
| F | Note a |

a.	Site-specific geotechnical investigation and dynamic site response analyses shall be performed to determine appropriate values, except that for structures with periods of vibration equal or less than 0.5 second, values of Fv for liquefiable soils are permitted to be taken equal to the values for the site class determined without regard to liquefaction in Section [1613.5.5] 1613.3.4.1.

[1613.5.4] 1613.3.4 Design spectral response acceleration parameters. Five-percent damped design spectral response acceleration at short periods, SDS, and at [1-second] 1-s period, SD1, shall be determined from [Equation 16-49] Equations 16-46 and [16-50] 16-47, respectively:

[(Equation 16-49)] (Equation 16-46)

[(Equation 16-50)] (Equation 16-47)

Sms = The MCER spectral response accelerations for short periods as determined in Section [1613.5.3] 1613.3.3.

Sm1 = The MCER spectral response accelerations for a 1-second period as determined in Section [1613.5.3] 1613.3.3.

[1613.5.5] 1613.3.4.1 Site classification for seismic design. Site classification for Site Class C, D or E shall be determined from Table [1613.5.5] 1613.3.4.1. The notations presented below apply to only materials encountered above rock meeting Class 1a, 1b, or 1c as defined in Section [1804] 1803 or rock with shear wave velocity greater than 2500 feet per second (762 meters per second) to a maximum depth of 100 feet (30 480 mm). Profiles containing distinctly different soil and rock layers shall be subdivided into those layers designated by a number that ranges from 1 to n at the bottom where there is a total of n distinct layers in the upper 100 feet (30 480 mm). The symbol i then refers to any one of the layers between 1 and n. For situations in which site investigations, performed in accordance with Chapter 20 of ASCE 7, reveal rock conditions consistent with Site Class B, but site-specific velocity measurements are not made, the site coefficients Fa, Fv, and FPGA shall be taken as unity (1.0).

where:

vsi= The shear wave velocity in feet per second (m/s).

di = The thickness of any layer between 0 and 100 feet (30 480 mm).

[(Equation 16-51)] (Equation 16-48)

where:

Ni is the Standard Penetration Resistance (ASTM D1586) not to exceed 100 blows/foot (328 blows/m) as directly measured in the field without corrections. When refusal is met for a rock layer of Class 1d, Ni shall be less than or equal to 100 blows/foot (328 blows/m) provided that the extent of the Class 1d material is confirmed by a boring to a depth where Class 1c or better rock is determined, not to exceed 100 feet. Alternatively, if this boring is not performed, site classification should be based on all soil material that is above the Class 1d layer.

[(Equation 16-52)] (Equation 16-49)

[(Equation 16-53)] (Equation 16-50)

where:

Use di and Ni for cohesionless soil layers only in Equation [16-42] 16-50.

ds = The total thickness of cohesionless soil layers in the top 100 feet (30 480 mm).

m = The number of cohesionless soil layers in the top 100 feet (30 480 mm).

Sui = The undrained shear strength in psf (kPa), not to exceed 5,000 psf (240 kPa), ASTM

D 2166 or ASTM D 2850.

where:

dc = The total thickness (100-ds) (For SI: 30 480-ds) of cohesive soil layers in the top 100 feet (30 480 mm).

k = The number of cohesive soil layers in the top 100 feet (30 480 mm).

PI = The plasticity index, ASTM D 4318.

w = The moisture content in percent, ASTM D 2216.

Where a site does not qualify under the criteria for Site Class F and there is a total thickness of soft clay greater than 10 feet (3048 mm) where a soft clay layer is defined by su < 500 psf (24 kPa), w > 40 percent, and PI > 20, it shall be classified as Site Class E. The shear wave velocity for rock, Site Class B, shall be either measured on site or estimated by a geotechnical engineer or engineering geologist/seismologist for competent rock with moderate fracturing and weathering. Softer and more highly fractured and weathered rock shall either be measured on site for shear wave velocity or classified as Site Class C. The hard rock category, Site Class A, shall be supported by shear wave velocity measurements either on site or on profiles of the same rock type in the same formation with an equal or greater degree of weathering and fracturing. Where hard rock conditions are known to be continuous to a depth of 100 feet (30 480 mm), surficial shear wave velocity measurements are permitted to be extrapolated to assess vs. The rock categories, Site Classes A and B, shall not be used if there is more than 10 feet (3048 mm) of soil between the rock surface and the bottom of the spread footing or mat foundation.

TABLE [1613.5.5] 1613.3.4.1
SITE CLASSIFICATIONa

| SITE CLASS | vs | N or Nch | sv |
| --- | --- | --- | --- |
| E | < 600 ft/s | < 15 | < 1,000 psf |
| D | 600 to 1,200 ft/s | 15 to 50 | 1,000 to 2,000 psf |
| C | 1,200 to 2,500 ft/s | > 50 | > 2,000 |

For SI: 1 foot per second = 304.8 mm per second, 1 pound per square foot = 0.0479 kN/m2.

a.If the sv method is used and the Nch and sv criteria differ, select the category with the softer soils (for example, use Site Class E instead of D).

[1613.5.5.1] 1613.3.4.1.1 Steps for classifying a site. The following steps shall be performed during the classification of a site:

1.	Check for the four categories of Site Class F requiring site-specific evaluation. If the site corresponds to any of these categories, classify the site as Site Class F and conduct a site-specific evaluation according to ASCE 7[-10] and the requirements of Section [1813] 1815.

2.	Check for the existence of a total thickness of soft clay > 10 feet (3048 mm) where a soft clay layer is defined by: su < 500 psf (24 kPa), w ≥ 40 percent and PI > 20. If these criteria are satisfied, classify the site as Site Class E.

3.	Categorize the site using one of the following three methods with vs, N, [and] or su and computed in all cases as specified.

3.1.	vs for the top 100 feet (30 480 mm) (vs method).

3.2.	N for the top 100 feet (30 480 mm) (N method).

3.3.	Nch for cohesionless soil layers (PI < 20) in the top 100 feet (30 480 mm) and average, su, for cohesive soil layers (PI > 20) in the top 100 feet (30 480 mm) (su method).

[1613.5.6] 1613.3.5 Determination of seismic design category. All structures shall be assigned [to] a seismic design category based on their risk category [determined in accordance with Table 1604.5] and the design spectral response acceleration parameters, SDS and SD1, determined in accordance with Section [1613.5.4] 1613.3.4 or the site-specific procedures of ASCE 7 [-10]. Each building and structure shall be assigned to the [more severe] seismic design category in accordance with Table [1613.5.6(1) or 1613.5.6(2)] 1613.3.5, irrespective of the fundamental period of vibration of the structure, T.

Exception: When electronic values of mapped acceleration parameters are used as per Section 1613.3.1, the seismic design category for Risk Category IV structures shall not differ from the values in Table 1613.3.5.

[TABLE 1613.5.6(1) 
SEISMIC DESIGN CATEGORY BASED ON
SHORT-PERIOD (0.2 SECOND) RESPONSE ACCELERATIONS

| VALUE OF SDS | RISK CATEGORYa |
| --- | --- |
|  | I & II | III | IV |
| SDS < 0.167g | A | A | A |
| 0.167g < SDS < 0.33g | B | B | C |
| 0.33g < SDS < 0.50g | C | C | D |
| 0.50g < SDS | Da | Da | Da |

  - Requirements for Seismic Design Categories E and F have been eliminated from the New York City Building Code as such categories do not apply in New York City. References to these Seismic Design Categories can be found in ASCE 7-10.]

[TABLE 1613.5.6(2) 
SEISMIC DESIGN CATEGORY BASED ON
1-SECOND PERIOD RESPONSE ACCELERATION

| VALUE OF SD1 | RISK CATEGORYa |
| --- | --- |
|  | I & II | III | IV |
| SD1 < 0.067g | A | A | A |
| 0.067g < SD1 < 0.133g | B | B | C |
| 0.133g <SD1 < 0.20g | C | C | D |
| 0.20g ≤ SD1 | Da | Da | Da |

- Requirements for Seismic Design Categories E and F have been eliminated from the New York City Building Code as such categories do not apply in New York City. References to these Seismic Design Categories can be found in ASCE 7-10.]

TABLE 1613.3.5
SEISMIC DESIGN CATEGORY

| Risk Category | Site Class |
| --- | --- |
|  | A | B /C /D | E |
| I /II /III | A | B | C |
| IV | A | C | D |

[1613.5.6.1] 1613.3.5.1 Alternative seismic design category determination. The seismic design category is permitted to be determined from Table [1613.5.6(1)] 11.6-1 of ASCE 7 alone, except for Risk Category IV structures for which Table 1613.3.5 shall be used, when all of the following apply:

1.	In each of the two orthogonal directions, the approximate fundamental period of the structure, Ta, [as] in each of the two orthogonal directions determined in accordance with Section 12.8.2.1 of ASCE 7[-10], is less than 0.8 Ts[, as] determined in accordance with Section [11.4.5] 11.4.6 of ASCE 7[-10].

2.	In each of the two orthogonal directions, the fundamental period of the structure used to calculate the story drift is less than Ts.

3.	Equation 12.8-2 of ASCE 7[-10] is used to determine the seismic response coefficient, Cs.

4.	The diaphragms are rigid[,] or are permitted to be idealized as [defined] rigid in accordance with Section 12.3.1 of ASCE 7[-10] or, for diaphragms [that are] permitted to be idealized as flexible in accordance with Section 12.3.1 of ASCE 7, the distances between [the] vertical elements of the [seismic-force-resisting] seismic force-resisting system do not exceed 40 feet (12 192 mm).

[1613.5.6.2] 1613.3.5.2 Simplified design procedure. Where the alternate simplified design procedure of ASCE 7[-10] is used, the seismic design category shall be determined in accordance with ASCE 7[-10].

[1613.6 Alternatives to ASCE 7-10. The provisions of Section 1613.6 shall be permitted as alternatives to the relevant provisions of ASCE 7-10.]

[1613.6.1 Additional seismic-force-resisting systems for seismically isolated structures. Add the following exception to the end of Section 17.5.4.2 of ASCE 7-10:]

[Exception: For isolated structures designed in accordance with this standard, the Structural System Limitations and the Structural Height Limits in Table 1613.8 for ordinary steel concentrically braced frames (OCBFs) as defined in Chapter 11 of ASCE 7-10 and ordinary moment frames (OMFs) as defined in Chapter 11 of ASCE 7-10 are permitted to be taken as 160 feet (48 768 mm) for structures assigned to Seismic Design Category D, provided that the following conditions are satisfied:]

[1. The value of R1 as defined in Chapter 17 of ASCE 7-10  is taken as 1.]

[2. For OMFs and OCBFs, design is in accordance with AISC 341.]

[1613.7] 1613.4 Structural separations. All structures shall be separated from adjacent structures. When a structure adjoins a property line not common to a public way (typically side or rear lot lines), that structure shall also be set back from the property line by at least 1 inch (25 mm) for each 50 feet (15 240 mm) of height and a minimum of 1 inch (25 mm) for structures with heights less than 50 feet (15 240 mm). For structures in Seismic Design Category D, refer to ASCE 7[-10] for additional requirements.

Exception: Smaller separations or property line setbacks shall be permitted when justified by rational analysis based on maximum expected ground motions with a minimum separation of 1 inch (25 mm) along the full height of the structure.

[1613.7.1] 1613.4.1 Masonry structures. For structures adjacent to existing unreinforced masonry bearing wall structures, the structural separation shall be filed with a material with a minimum compressive strength of 25 psi (172.37 kPa) and a maximum compressive strength of 100 psi (689.74 kPa). Additionally, when the adjacent wall is a party wall, the party wall shall be made secure by the party responsible for the new construction as per Chapter 33.

[1613.7.2] 1613.4.2 Covers. The infill material shall be covered on all sides and shall meet the appropriate provisions of Chapter 26. The covering must be of adequate strength to resist the wind loads for cladding as specified in Chapter 16 and shall conform to all applicable provisions in Chapter 14.

[1613.7.3] 1613.4.3 Covers wider than 5 inches (127 mm). When a building separation wider than 5 inches (127 mm) is created pursuant to Section [1613.7] 1613.4, such separation, at the roof level of the proposed new building, or at the roof level of an existing adjoining building where if that building is lower than the proposed new building, shall have a horizontal cover/closure that conforms with the following:

1.	The cover/closure material shall be noncombustible; and

Exception: The cover/closure material used shall be permitted to be combustible material in accordance with Section [1509.9] 1510.9 if all the material on the appropriate roof conforms to the limitations therein, there are no masonry openings in either wall abutting the building separation, and both buildings are noncombustible.

2.	The cover/closure shall be capable of withstanding the roof live load of 30 psf (1.43 kPa), securely fastened to the new building, and be of a type that would be capable of preventing unauthorized or accidental access to the space.

[1613.8] 1613.5 ASCE 7[-10], Table 12.2-1. Modify ASCE 7[-10], Table 12.2-1 as follows:

TABLE [1613.8] 1613.5

DESIGN COEFFICIENT AND FACTORS FOR BASIC SEISMIC C-FORCE-RESISTING SYSTEMS

|  |  |  |  |  | Structural System Limitations Including Structural Height, hn (ft), Limitsc |
| --- | --- | --- | --- | --- | --- |
| Seismic Force-Resisting System | ASCE 7[-10] Section Where Detailing Requirements Are Specified | Response Modification Coefficient | Overstrength Factor | Deflection Amplification Factor | Seismic Design Category |
| A. BEARING WALL SYSTEMS |  | Ra | Ω0g | Cdb | B | C | Dd |
| 1. Special reinforced concrete shear wallsl,m | 14.2 | 5 | 2.5 | 5 | NL | NL | [NL] 160 |
| 2. Ordinary reinforced concrete shear wallsl | 14.2 | 4 | 2.5 | 4 | NL | NL | NP |
| 3. Detailed plain concrete shear wallsl | 14.2 | 2 | 2.5 | 2 | NL | NP | NP |
| 4. Ordinary plain concrete shear wallsl | 14.2 | 1.5 | 2.5 | 1.5 | NL | NP | NP |
| 5. Intermediate precast shear wallsl | 14.2 | 4 | 2.5 | 4 | NL | NL | 40k |
| 6. Ordinary precast shear wallsl | 14.2 | 3 | 2.5 | 3 | NL | NP | NP |
| 7. Special reinforced masonry shear walls | 14.4 | 5 | 2.5 | 3.5 | NL | NL | [NL] 160 |
| 8. Intermediate reinforced masonry shear walls | 14.4 | 3.5 | 2.5 | 2.25 | NL | NL | NP |
| 9. Ordinary reinforced masonry shear walls | 14.4 | 2 | 2.5 | 1.75 | NL | [NL] 160 | NP |
| 10. Detailed plain masonry shear walls | 14.4 | 2 | 2.5 | 1.75 | NL | NP | NP |
| 11. Ordinary plain masonry shear walls | 14.4 | 1.5 | 2.5 | 1.25 | NL | NP | NP |
| 12. Prestressed masonry shear walls | 14.4 | 1.5 | 2.5 | 1.75 | NL | NP | NP |
| 13. Ordinary reinforced Autoclaved Aerated Concrete (AAC) masonry shear walls | 14.4 | 2 | 2.5 | 2 | NL | 35 | NP |
| 14. Ordinary plain (unreinforced) Autoclaved Aerated Concrete (AAC) masonry shear walls | 14.4 | 1.5 | 2.5 | 1.5 | NL | NP | NP |
| 15. Light-frame (wood) walls sheathed with wood structural panels rated for shear resistance or steel sheets | 14.1 and 14.5 | 6.5 | 3 | 4 | NL | NL | 65 |
| 16. Light-frame (cold-formed steel) walls sheathed with wood structural panels rated for shear resistance or steel sheets | 14.1 | 6.5 | 3 | 4 | NL | NL | 65 |
| 17. Light-frame walls with shear panels of all other materials | 14.1 and 14.5 | 2 | 2.5 | 2 | NL | NL | 35 |
| 18. Light-frame (cold-formed steel) wall systems using flat strap bracing | 14.1 | 4 | 2 | 3.5 | NL | NL | 65 |
| B. BUILDING FRAME SYSTEMS |  | Ra | Ω0g | Cdb | B | C | Dd |
| 1. Steel eccentrically braced frames | 14.1 | 8 | 2 | 4 | NL | NL | [NL] 160 |
| 2. Steel special concentrically braced frames | 14.1 | 6 | 2 | 5 | NL | NL | [NL] 160 |
| 3. Steel ordinary concentrically braced frames | 14.1 | 3.25 | 2 | 3.25 | NL | NL | 35j |
| 4. Special reinforced concrete shear wallsl,m | 14.2 | 6 | 2.5 | 5 | NL | NL | [NL] 160 |
| 5. Ordinary reinforced concrete shear wallsl | 14.2 | 5 | 2.5 | 4.5 | NL | NL | NP |
| 6. Detailed plain concrete shear wallsl | 14.2 and [14.2.2.8] 14.2.2.7 | 2 | 2.5 | 2 | NL | NP | NP |
| 7. Ordinary plain concrete shear wallsl | 14.2 | 1.5 | 2.5 | 1.5 | NL | NP | NP |
| 8. Intermediate precast shear wallsl | 14.2 | 5 | 2.5 | 4.5 | NL | NL | 40k |
| 9. Ordinary precast shear wallsl | 14.2 | 4 | 2.5 | 4 | NL | NP | NP |
| 10. Steel and concrete composite eccentrically braced frames | 14.3 | 8 | [2] 2.5 | 4 | NL | NL | [NL] 160 |
| 11. Steel and concrete composite special concentrically braced frames | 14.3 | 5 | 2 | 4.5 | NL | NL | [NL] 160 |
| 12. Steel and concrete composite ordinary braced frames | 14.3 | 3 | 2 | 3 | NL | NL | NP |
| 13. Steel and concrete composite plate shear walls | 14.3 | 6.5 | 2.5 | 5.5 | NL | NL | [NL] 160 |
| 14. Steel and concrete composite special shear walls | 14.3 | 6 | 2.5 | 5 | NL | NL | [NL] 160 |
| 15. Steel and concrete composite ordinary shear walls | 14.3 | 5 | 2.5 | 4.5 | NL | NL | NP |
| 16. Special reinforced masonry shear walls | 14.4 | 5.5 | 2.5 | 4 | NL | NL | [NL] 160 |
| 17. Intermediate reinforced masonry shear walls | 14.4 | 4 | 2.5 | 4 | NL | NL | NP |
| 18. Ordinary reinforced masonry shear walls | 14.4 | 2 | 2.5 | 2 | NL | [NL] 160 | NP |
| 19. Detailed plain masonry shear walls | 14.4 | 2 | 2.5 | 2 | NL | NP | NP |
| 20. Ordinary plain masonry shear walls | 14.4 | 1.5 | 2.5 | 1.25 | NL | NP | NP |
| 21. Prestressed masonry shear walls | 14.4 | 1.5 | 2.5 | 1.75 | NL | NP | NP |
| 22. Light-frame (wood) walls sheathed with wood structural panels rated for shear resistance | 14.5 | 7 | 2.5 | 4.5 | NL | NL | 65 |
| 23. Light-frame (cold-formed steel) walls sheathed with wood structural panels rated for shear resistance or steel sheets | 14.1 | 7 | 2.5 | 4.5 | NL | NL | 65 |
| 24. Light-frame walls with shear panels of all other materials | 14.1 and 14.5 | 2.5 | 2.5 | 2.5 | NL | NL | 35 |
| 25. Steel buckling-restrained braced frames | 14.1 | 8 | 2.5 | 5 | NL | NL | [NL] 160 |
| 26. Steel special plate shear walls | 14.1 | 7 | 2 | 6 | NL | NL | [NL] 160 |
| C. MOMENT-RESISTING FRAME SYSTEMS |  | Ra | Ω0g | Cdb | B | C | Dd |
| 1. Steel special moment frames | 14.1 and 12.2.5.5 | 8 | 3 | 5.5 | NL | NL | NL |
| 2. Steel special truss moment frames | 14.1 | 7 | 3 | 5.5 | NL | NL | [NL] 160 |
| 3. Steel intermediate moment frames | 14.1 and 12.2.5.7 | 4.5 | 3 | 4 | NL | NL | 35h |
| 4. Steel ordinary steel moment frames | 14.1 and 12.2.5.6 | 3.5 | 3 | 3 | NL | NL | NPi |
| 5. Special reinforced concrete moment framesn | 14.2 and 12.2.5.5 | 8 | 3 | 5.5 | NL | NL | NL |
| 6. Intermediate reinforced concrete moment frames | 14.2 | 5 | 3 | 4.5 | NL | NL | NP |
| 7. Ordinary reinforced concrete moment frames | 14.2 | 3 | 3 | 2.5 | NL | NP | NP |
| 8. Steel and concrete composite special moment frames | 14.3 and 12.2.5.5 | 8 | 3 | 5.5 | NL | NL | NL |
| 9. Steel and concrete composite intermediate moment frames | 14.3 | 5 | 3 | 4.5 | NL | NL | NP |
| 10. Steel and concrete composite partially restrained moment frames | 14.3 | 6 | 3 | 5.5 | [NL] 160 | [NL] 160 | 100 |
| 11. Steel and concrete composite ordinary moment frames | 14.3 | 3 | 3 | 2.5 | NL | NP | NP |
| 12. Cold-formed steel—special bolted moment framep | 14.1 | 3.5 | 3o | 3.5 | 35 | 35 | 35 |
| D. DUAL SYSTEMS WITH SPECIAL MOMENT FRAMES CAPABLE OF RESISTING AT LEAST 25% OF PRESCRIBED SEISMIC FORCES | 12.2.5.1 | Ra | Ω0g | Cdb | B | C | Dd |
| 1. Steel eccentrically braced frames | 14.1 | 8 | 2.5 | 4 | NL | NL | NL |
| 2. Steel special concentrically braced frames | 14.1 | 7 | 2.5 | 5.5 | NL | NL | NL |
| 3. Special reinforced concrete shear wallsl | 14.2 | 7 | 2.5 | 5.5 | NL | NL | NL |
| 4. Ordinary reinforced concrete shear wallsl | 14.2 | 6 | 2.5 | 5 | NL | NL | NP |
| 5. Steel and concrete composite eccentrically braced frames | 14.3 | 8 | 2.5 | 4 | NL | NL | NL |
| 6. Steel and concrete composite special concentrically braced frames | 14.3 | 6 | 2.5 | 5 | NL | NL | NL |
| 7. Steel and concrete composite plate shear walls | 14.3 | 7.5 | 2.5 | 6 | NL | NL | NL |
| 8. Steel and concrete composite special shear walls | 14.3 | 7 | 2.5 | 6 | NL | NL | NL |
| 9. Steel and concrete composite ordinary shear walls | 14.3 | 6 | 2.5 | 5 | NL | NL | NP |
| 10. Special reinforced masonry shear walls | 14.4 | 5.5 | 3 | 5 | NL | NL | NL |
| 11. Intermediate reinforced masonry shear walls | 14.4 | 4 | 3 | 3.5 | NL | NL | NP |
| 12. Steel buckling-restrained braced frames | 14.1 | 8 | 2.5 | 5 | NL | NL | NL |
| 13. Steel special plate shear walls | 14.1 | 8 | 2.5 | 6.5 | NL | NL | NL |
| E. DUAL SYSTEMS WITH INTERMEDIATE MOMENT FRAMES CAPABLE OF RESISTING AT LEAST 25% OF PRESCRIBED SEISMIC FORCES | 12.2.5.1 | Ra | Ω0g | Cdb | B | C | Dd |
| 1. Steel special concentrically braced framesf | 14.1 | 6 | 2.5 | 5 | NL | NL | 35 |
| 2. Special reinforced concrete shear wallsl | 14.2 | 6.5 | 2.5 | 5 | NL | NL | [NL] 160 |
| 3. Ordinary reinforced masonry shear walls | 14.4 | 3 | 3 | 2.5 | NL | [NL] 160 | NP |
| 4. Intermediate reinforced masonry shear walls | 14.4 | 3.5 | 3 | 3 | NL | NL | NP |
| 5. Steel and concrete composite special concentrically braced frames | 14.3 | 5.5 | 2.5 | 4.5 | NL | NL | NL |
| 6. Steel and concrete composite ordinary braced frames | 14.3 | 3.5 | 2.5 | 3 | NL | NL | NP |
| 7. Steel and concrete composite ordinary shear walls | 14.3 | 5 | 3 | 4.5 | NL | NL | NP |
| 8. Ordinary reinforced concrete shear wallsl | 14.2 | 5.5 | 2.5 | 4.5 | NL | NL | NP |
| F. SHEAR WALL-FRAME INTERACTIVE SYSTEM WITH ORDINARY REINFORCED CONCRETE MOMENT FRAMES AND ORDINARY REINFORCED CONCRETE SHEAR WALLSl | 14.2 and 12.2.5.8 | 4.5 | 2.5 | 4 | NL | NP | NP |
| G. CANTILEVERED COLUMN SYSTEMS DETAILED TO CONFORM TO THE REQUIREMENTS FOR: | 12.2.5.2 | Ra | Ω0g | Cdb | B | C | Dd |
| 1. Steel special cantilever column systems | 14.1 | 2.5 | 1.25 | 2.5 | 35 | 35 | 35 |
| 2. Steel ordinary cantilever column systems | 14.1 | 1.25 | 1.25 | 1.25 | 35 | 35 | NPi |
| 3. Special reinforced concrete moment frames n | 14.2 and 12.2.5.5 | 2.5 | 1.25 | 2.5 | 35 | 35 | 35 |
| 4. Intermediate reinforced concrete moment frames | 14.2 | 1.5 | 1.25 | 1.5 | 35 | 35 | NP |
| 5. Ordinary reinforced concrete moment frames | 14.2 | 1 | 1.25 | 1 | 35 | NP | NP |
| 6. Timber frames | 14.5 | 1.5 | 1.5 | 1.5 | 35 | 35 | 35 |
| H. STEEL SYSTEMS NOT SPECIFICALLY DETAILED FOR SEISMIC RESISTANCE, EXCLUDING CANTILEVER COLUMN SYSTEMS | 14.1 | 3 | 3 | 3 | NL | NL | NP |

a.	Response modification coefficient, R, for use throughout the standard. Note R reduces forces to a strength level, not an allowable stress level.

b.	Deflection amplification factor, Cd, for use in Sections 12.8.6, 12.8.7, and [12.9.2] 12.9.1.2 of ASCE 7[-10].

c.	NL = Not Limited and NP = Not Permitted. For metric units use 30.5 m for 100 ft and use 48.8 m for 160 ft.

d.	See Section 12.2.5.4 of ASCE 7[-10] for a description of seismic force-resisting systems limited to buildings with a structural height, hn, of 240 ft (73.2 m) or less.

e.	See Section 12.2.5.4 of ASCE 7[-10] for seismic force-resisting systems limited to buildings with a structural height, hn, of 160 ft (48.8 m) or less.

f.	Ordinary moment frame is permitted to be used in lieu of intermediate moment frame for Seismic Design Categories B or C.

g.	Where the tabulated value of the overstrength factor, Ω0, is greater than or equal to 2½, Ω0 is permitted to be reduced by subtracting the value of 1/2 for structures with flexible diaphragms.

h.	See Section 12.2.5.7 of ASCE 7[-10] for limitations in structures assigned to Seismic Design Category D.

i.	See Section 12.2.5.6 of ASCE 7[-10] for limitations in structures assigned to Seismic Design Category D.

j.	Steel ordinary concentrically braced frames are permitted in single-story buildings up to a structural height, hn, of 60 ft (18.3 m) where the dead load of the roof does not exceed 20 psf (0.96 kN/m2) and in penthouse structures.

k.	An increase in structural height, hn, to 45 ft (13.7 m) is permitted for single story storage warehouse facilities.

l.	In Section [2.2] 2.3 of ACI 318. A shear wall is defined as a structural wall.

m.	In Section [2.2] 2.3 of ACI 318. The definition of “special structural wall” includes precast and cast-in-place construction.

n.	In Section [2.2] 2.3 of ACI 318. The definition of “special moment frame” includes precast and cast-in-place construction.

o.	Alternately, the seismic load effect with overstrength, Emh, is permitted to be based on the expected strength determined in accordance with AISI [S110] S400.

p.	Cold-formed steel – special bolted moment frames shall be limited to one-story in height in accordance with AISI [S110] S400.

1613.6 Ballasted photovoltaic panel systems. Ballasted, roof-mounted photovoltaic panel systems need not be rigidly attached to the roof or supporting structure. Ballasted non-penetrating systems shall be designed and installed only on roofs with slopes not more than one unit vertical in 12 units horizontal. Ballasted nonpenetrating systems shall be designed to resist sliding and uplift resulting from lateral and vertical forces as required by Section 1605, using a coefficient of friction determined by acceptable engineering principles. In structures assigned to Seismic Design Category C or D, ballasted nonpenetrating systems shall be designed to accommodate seismic displacement determined by nonlinear response-history analysis or shake-table testing, using input motions consistent with ASCE 7 lateral and vertical seismic forces for nonstructural components on roofs.

SECTION BC 1614
ATMOSPHERIC ICE LOADS

1614.1 General. Ice-sensitive structures shall be designed for atmospheric ice loads in accordance with Chapter 10 of ASCE 7.

SECTION BC [1614] 1615
STRUCTURAL INTEGRITY DEFINITIONS

[1614.1] 1615.1 Definitions. The following [words and terms shall, for the purposes of this section, have the meanings shown herein.] terms are defined in Chapter 2:

ALTERNATE LOAD PATH. [A secondary or redundant load path capable of transferring the load from one structural element to other structural elements.]

ALTERNATE LOAD PATH METHOD. [A design approach that accounts for an extreme event by providing alternate load paths for elements that are no longer able to carry load. In an alternate load path design, key elements are considered notionally removed, one at a time, and the structure is designed to transfer the loads from the removed element to other structural elements, as required by Section 1616.]

ASPECT RATIO. [The height of any portion of a building divided by its least dimension at the elevation from which the height is being measured.]

COLLAPSE (STRUCTURAL). [Failure of a structural element to the extent that it can no longer support any load.]

ELEMENT (STRUCTURAL). [A structural member or structural assembly.]

KEY ELEMENT. [An element of the structural system, including its connections, that meets one or more of the following criteria:]

[1. An element which when lost, results in more than local collapse.]

[2. An element that braces a key element, the failure of which results in failure of the key element (further secondary elements need not be considered key elements).]

[3. An element whose tributary area exceeds 3,000 square feet (279 square meters) on a single level.]

LOCAL COLLAPSE. [Failure of a structural element that results in the collapse of areas being directly supported by that element and not extending vertically more than three stories.]

RESPONSE RATIO. [The ratio of an ultimate response quantity (e.g., deflection) to its value at yield.]

ROTATION. [The angle, measured at the ends of a member, whose tangent is equal to the deflection of the member at midspan divided by half the length of the member.]

SPECIFIC LOCAL LOAD. [A load applied to a structural element or structural system as specified in Section 1616.7.]

SPECIFIC LOCAL RESISTANCE METHOD. [A design approach that accounts for extreme event loads by providing sufficient strength for elements that may fail. In a specific local resistance design, key elements are designed for specific local loads as required by Section 1616.]

SECTION BC [1615] 1616
STRUCTURAL INTEGRITY—PRESCRIPTIVE REQUIREMENTS

[1615.1] 1616.1 Scope. The intent of these provisions is to enhance structural performance under extreme event scenarios by providing additional overall system redundancy and local robustness. All structures shall be designed to satisfy the prescriptive requirements of this section.

Exception: Structures in [Structural Occupancy] Risk Category I of Table 1604.5 and structures in Occupancy Group R-3 are exempt from the requirements of Sections [1614] 1615 through [1616] 1617.

[1615.2] 1616.2 Continuity and ties. All structural elements shall have a minimum degree of continuity and shall be tied together horizontally and vertically as specified in Chapters 19, 21, and 22 for concrete, masonry and steel, respectively.

[1615.3] 1616.3 Lateral bracing. Floor and roof diaphragms or other horizontal elements shall be tied to the lateral load-resisting system.

[1615.4 Reserved.]

[1615.5] 1616.4 Vehicular impact. Structural columns that are directly exposed to vehicular traffic shall be designed for vehicular impact. Structural columns that are adequately protected by bollards, guard walls, vehicle arrest devices or other elements do not need to be designed for vehicular impact. The load combinations for vehicular impact shall be as specified in Section [1605.6] 1605.5.

Specific loads for vehicular impact shall be as follows:

1.	Exterior corner columns shall be designed for a concentrated load of 40 kips applied horizontally in any direction from which a vehicle can approach at a height of either 18 inches (457 mm) or 36 inches (914 mm) above the finished driving surface, whichever creates the worst effect.

2.	All other exterior columns exposed to vehicular traffic, and columns within loading docks, and columns in parking garages along the driving lane shall be designed for a concentrated load of 20 kips applied horizontally in any direction from which a vehicle can approach at a height of either 18 inches (457 mm) or 36 inches (914 mm) above the finished driving surface, whichever creates the worst effect.

[1615.6] 1616.5 Gas explosions. In buildings with gas piping operating at pressures in excess of 15 psig (103 kPa gauge), all key elements and their connections within 15 feet (4572 mm) of such piping shall be designed to resist a potential gas explosion. The structure shall be designed to account for the potential loss of the affected key elements one at a time by the alternate load path [Alternative Load Path] method. Load combinations for the alternate load path [Alternative Load Path] shall be as specified in Section [1605.5] 1605.4. In lieu of the alternate load path [Alternative Load Path] method, the affected key elements shall be designed to withstand a load of 430 psf (20.6 kPa) applied using the load combinations specified in Section [1605.6] 1605.5. The load shall be applied along the entire length of the element, and shall be applied in the manner and direction that produces the most damaging effect.

Exceptions:

1.	If a structural enclosure designed to resist the specified pressure is provided around the high-pressure gas piping, only the key elements within the structural enclosure need to comply with this section.

2.	A reduced pressure for gas explosions can be used based on an engineering analysis approved by the commissioner.

[1615.6.1] 1616.5.1 Explosion prevention and deflagration venting. The structural design and installation of explosion prevention systems and deflagration venting shall be in accordance with the requirements of Appendices E and G of the New York City Fuel Gas Code, as well as the New York City Fire Code, and the rules and regulations of the department.

SECTION BC [1616] 1617
STRUCTURAL INTEGRITY—KEY ELEMENT ANALYSIS

[1616.1] 1617.1 Scope. A key element analysis shall be performed for the following buildings:

1.	Buildings included in [Structural Occupancy] Risk Category IV as defined in this chapter.

2.	Buildings with the aspect ratios of seven or greater.

3.	Buildings greater than 600 feet (183 m) in height or more than 1,000,000 square feet (92 903 m2) in gross floor area.

4.	Buildings taller than seven stories where any element, except for walls greater than 10 feet (3.048 m) in length, supports in aggregate more than 15 percent of the building area.

5.	Buildings designed for areas with 3,000 or more occupants in one area in close proximity, including fixed seating and grandstand areas.

6.	When specifically ordered by the commissioner.

[1616.2] 1617.2 Load combinations. Where specifically required by Section [1616.1] 1617.1, elements and components shall be designed to resist the forces calculated using the combination specified in Section [1605.5] 1605.4 or [1605.7] 1605.6 as applicable.

[1616.3 Reserved.]

[1616.4] 1617.3 Seismic and wind. When the code-prescribed seismic or wind design produces greater effects, the seismic or wind design shall govern, but the detailing requirements and limitations prescribed in this and referenced sections shall also be followed.

[1616.5] 1617.4 Joints. Where a structure is divided by joints that allow for movement, each portion of the structure between joints shall be considered as a separate structure.

[1616.6] 1617.5 Key element analysis. Where key elements are present in a structure, the structure shall be designed to account for their potential loss one at a time by the alternate load path method or by the specific local resistance method as specified in Section [1616.7] 1617.6.

[1616.7] 1617.6 The specific local resistance method. Where the specific local resistance method is used, key elements shall be designed using specific local loads as follows:

1.	Each compression element shall be designed for a concentrated load equal to 2 percent of its axial load but not less than 15 kips, applied at midspan in any direction, perpendicular to its longitudinal axis. This load shall be applied in combination with the full dead load and 50 percent of the live load in the compression element.

2.	Each bending element shall be designed for the combination of the principal acting moments plus an additional moment, equal to 10 percent of the principal acting moment applied in the perpendicular plane.

3.	Connections of each tension element shall be designed to develop the smaller of the ultimate tension capacity of the member or three times the force in the member.

4.	All structural elements shall be designed for a reversal of load. The reversed load shall be equal to 10 percent of the design load used in sizing the member.

[1616.8] 1617.7 Design criteria. Alternate load path method and/or specific local resistance method for key elements shall conform to the appropriate design criteria as determined from Sections [1616.9, 1616.10 and] 1617.8 through [1616.11] 1617.10. [Load combinations for the alternate load path method shall be as specified in Section 1605.5.]

[1616.9] 1617.8 Analysis procedures. All structural analysis for specific local loads or alternate load paths shall be made by one of the following methods:

[1616.9.1] 1617.8.1 Static elastic analysis. For analysis of this type, dynamic effects of member loss or dynamic effects of specific local loads need not be considered. The structural demand is obtained from linear static analysis. However, structural member capacity is based on ultimate capacity of the entire cross section. The demand/capacity ratio of structural elements shall not exceed one.

[1616.9.2] 1617.8.2 Dynamic inelastic analysis. For analysis of this type, dynamic effects of member loss or specific local loads shall be considered. The structure does not need to remain elastic; however, the response ratio and rotation limits obtained from Table [1616.9.3] 1617.8.3 shall not be exceeded.

1617.8.3 Energy methods. Static inelastic analysis using energy equilibrium may also be used. The structure does not need to remain elastic; however, the response ratio and rotation limits obtained from Table [1616.9.3] 1617.8.3 shall not be exceeded.

TABLE [1616.9.3] 1617.8.3
RESPONSE RATIO AND ROTATION LIMITS

| ELEMENT | RESPONSE RATIO | ROTATION |
| --- | --- | --- |
| Concrete slabs | μ < 10 | θ < 4° |
| Post-tensioned beams | μ < 2 | θ < 1.5° |
| Concrete beams Concrete columns | μ < 20 | θ < 6° |
|  | μ < 2 | θ < 6° |
| Long span acoustical deck | μ < 2 | θ < 3° |
| Open web steel joists | μ < 2 | θ < 6° |
| Steel beams | μ < 20 | θ < 10° |
| Steel columns | μ < 5 | θ < 6° |

For SI: 1 degree = 0.0 1745 rad.

Note: Table [1616.9.3] 1617.8.3 is intended for SDOF and simplified MDOF response calculations and a low level of protection. Table [1616.9.3] 1617.8.3 does not apply for explicit finite element methods that calculate the performance of the structural elements in response to the specified loading intensity. Steel joists: downward loading 6 degrees, upward loading ductility of 2.

[1616.10] 1617.9 Minimum response. Structural response of elements determined using a dynamic inelastic analysis shall not be less than 80 percent of the structural response determined using a static elastic analysis.

[1616.11] 1617.10 Strength reduction factors. For structural design for specific local loads or alternate load paths, all strength reduction factors may be [taken as one] multiplied by 1.1.

BC [1617] 1618
STRUCTURAL PEER REVIEW

[1617.1] 1618.1 General. The provisions of this section specify where structural peer review is required, how and by whom it is to be performed.

[1617.2] 1618.2 Where required. A structural peer review of the primary structure shall be performed and a report provided for the following buildings:

1.	Buildings included in [Structural Occupancy] Risk Category IV as defined in this chapter and more than 50,000 square feet (4645 m2) of framed area.

2.	Buildings with aspect ratios of seven or greater.

3.	Buildings greater than 600 feet (183 m) in height or more than 1,000,000 square feet (92 903 m2) in gross floor area. Rooftop structures may be excluded from building height in accordance with Section 504.3.

4.	Buildings taller than seven stories where any element, except for walls greater than 10 feet (3.048 meters) in length, supports in aggregate more than 15 percent of the building area.

5.	Buildings designed using nonlinear time history analysis or with special seismic energy dissipation systems.

6.	Buildings designed for areas with 3,000 or more occupants in one area in close proximity, including fixed seating and grandstand areas.

[6] 7. Buildings where a structural peer review is requested by the commissioner.

8.	Buildings designed by performance-based methods.

[1617.3] 1618.3 Structural peer review. It shall be verified that the structural design is in general conformance with the requirements of this code.

[1617.4] 1618.4 Geotechnical peer review.  Geotechnical peer reviews are required to be performed in accordance with Section 1815.

1618.5 Structural peer reviewer. The structural peer review shall be performed by a qualified independent structural engineer who has been retained by or on behalf of the owner. A structural peer reviewer shall meet the requirements of the rules of the department.

1618.5.1 Independence. In order to satisfy the requirement that the peer reviewer be independent, the department requires that the peer reviewer must not engage in any activities that may conflict with their objective judgment and integrity, including but not limited to having a financial and/or other interest in the design, construction, installation, manufacture or maintenance of structures or components that they are reviewing.

[1617.5] 1618.6 Extent of the structural peer review. The structural peer review shall comply with Sections 1618.6.1 and 1618.6.2.

[1617.5.1] 1618.6.1 Scope. The structural peer reviewer shall review the plans and specifications submitted with the permit application for general compliance with the structural and foundation design provisions of this code. The reviewing engineer shall perform the following tasks at a minimum:

1.	Confirm that the design loads conform to this code.

2.	Confirm that other structural design criteria and design assumptions conform to this code and are in accordance with generally accepted engineering practice.

3.	Review geotechnical and other engineering investigations that are related to the foundation and structural design and confirm that the design properly incorporates the results and recommendations of the investigations.

4.	Review the structural frame and the load supporting parts of floors, roofs, walls, shallow foundation elements, deep foundation caps, connection of deep foundation elements to deep foundation caps, and permanent rock or soil anchor connection to the structural elements [foundations]. Cladding, cladding framing, stairs, equipment supports, ceiling supports, non-loadbearing partitions, railings and guards, and other secondary structural items shall be excluded.

[4] 5.	Confirm that the structure has a complete load path.

[5] 6.	Perform independent calculations for a representative fraction of systems, members, and details to check their adequacy. The number of representative systems, members, and details verified shall be sufficient to form a basis for the reviewer’s conclusions.

[6] 7.	Verify that performance-specified structural components (such as certain precast concrete elements) have been appropriately specified and coordinated with the primary building structure.

[7] 8.	Verify that the design engineer of record complied with the structural integrity provisions of the code.

9.	Review the structural and architectural plans for the building. Confirm that the structural plans are in general conformance with the architectural plans regarding loads and other conditions that may affect the structural design.

10.	Confirm that major mechanical items are accommodated in the structural plans.

11.	Attest to the general completeness of the structural plans and specifications.

12.	Review performance based design.

[1617.5.2] 1618.6.2 Structural design criteria. If the design criteria and design assumptions are not shown on the drawings or in the computations, the structural engineer of record shall provide a statement of these criteria and assumptions for the reviewer. In addition, the design engineer shall provide information and/or calculations, if requested by the peer reviewer.

[1617.6] 1618.7 Structural peer review report. The structural peer review report shall comply with Sections 1618.7.1 through 1618.7.3.

[1617.6.1] 1618.7.1 General. The reviewing engineer shall submit a report to the department stating whether or not the structural design shown on the plans and specifications generally conforms to the structural and foundation requirements of this code.

[1617.6.2] 1618.7.2 Contents. The report shall demonstrate, at a minimum, compliance with Items 1 through [11] 12 of Section [1617.5.1] 1618.6.1. In addition, the report shall also include the following:

1.	A list of construction documents, including the latest revision dates submitted to the department for approval, as well as geotechnical reports, wind tunnel studies and other reports utilized in the design.

2.	The codes and standards used in the structural design of the project.

[2.] 3.	The structural design criteria, including loads and performance requirements.

[3.] 4.	The basis for design criteria that are not specified directly in applicable codes and standards. This should include reports by specialty consultants such as wind tunnel study reports and geotechnical reports. Generally, the report should confirm that existing conditions at the site have been investigated as appropriate and that the design of the proposed structure is in general conformance with these conditions.

5.	The basis of performance-based design and its appropriateness of use.

6.	A statement that the qualification and independence of the peer reviewer is in accordance with Section 1618.5.

7.	Peer review reports shall provide an unconditional statement that must be either an acceptance or rejection of code compliance of the structural design required to be reviewed by this section.

8.	The structural peer review reports shall contain a statement that geotechnical peer review reports and/or wind tunnel peer review reports, when required, have been received with an unconditional statement of acceptance by the authors of those reports.

[1617.6.3] 1618.7.3 Phased submission. If an application is submitted for a permit for the construction of foundations or any other part of a building before the construction documents for the whole building have been submitted, then the structural peer review and report shall be phased. The structural peer reviewer shall be provided with sufficient information on which to make a structural peer review of the phased submission. In addition to the requirements of this section, phased submission of the report shall include any changes made to the initial structural peer review evaluation.  The geotechnical peer review report need not be submitted concurrently with the structural peer review report.

[1617.7] 1618.8 Responsibility. The responsibilities of the engineer of record and peer reviewer shall be as laid out in Sections 1618.8.1 through 1618.8.4.

[1617.7.1] 1618.8.1 Structural engineer of record. The structural engineer of record shall retain sole responsibility for the structural design. The activities and reports of the structural peer reviewer shall not relieve the structural engineer of record of this responsibility.

[1617.7.2] 1618.8.2 Structural peer reviewer. The structural peer reviewer’s report states his or her opinion regarding the design by the engineer of record. The standard of care to which the structural peer reviewer shall be held in the performance of the structural peer review and report is that level of skill and care [are] consistent with structural peer review services performed by professional engineers licensed in the State of New York for similar type projects. The structural peer reviewer shall not be responsible for the conclusions of the wind and geotechnical peer review reports.

1618.8.3 Revisions of design.  The structural engineer of record shall identify that a new review is required based upon changes to the design documents relevant to the scope of the peer review.  The structural peer reviewer shall review the items that have been affected and shall revise the structural peer review report.

1618.8.4 Disputes. When a dispute arises between the applicant of record and the peer reviewer regarding compliance with Section 1618 that cannot be resolved by these parties, such dispute shall be reported to the department in the form of a letter from the applicant of record. The department may make a final decision or may accept a change of the peer reviewer.

1618.9 Change to peer reviewer. The peer reviewer cannot be changed without the express consent of the department. The current peer reviewer must submit both a written letter to the borough commissioner detailing the reason for the withdrawal request and a report of the structural peer review findings to date. If a change of peer reviewer is approved, a revised submission indicating the replacement peer reviewer shall be filed with the department.

SECTION [1618] 1619
[LOADS ON] TEMPORARY STRUCTURES AND TEMPORARY CONSTRUCTION INSTALLATIONS

[1618.1 General.  Installations governed by this code shall be defined as temporary when such installations are intended to be taken apart or removed after a limited period following their installation, including, but not limited to, tents, scaffolds, sidewalk sheds, cranes, and run back structures.  Temporary installations shall comply with all the provisions of this code, except as described in Sections 1618.1.1 through 1618.3.2.]

[1618.1.1 Duration. Such limited period shall not exceed one year for temporary installations used in construction operations covered by Chapter 33.  For temporary installations covered by Section 3103, the limited period shall not exceed ninety days. The limited period shall be counted from the date the temporary installation is substantially installed.]

[1618.1.1.1 Extension of time. Subject to the approval of the commissioner, a request to extend the time for a temporary installation, subject to the limits in Section 1618.1.1, shall be accompanied by the submission of a report from a registered design professional that certifies the following:]

[1.	Such registered design professional performed an inspection within the last 30 days to confirm that the installation complies with the requirements of the approved construction documents for the temporary installation; and]

[2.	The action plan required by Section 1618.3:]

[2.1.	Is still in effect;]

[2.2.	Has been revised to reflect the current conditions of the installation; or]

[2.3.	Is no longer required, as the installation has been retrofitted to comply with the loads for new construction without any reduction, pursuant to Section 1618.2.]

[1618.1.2 Construction documents.  Any temporary installation utilizing the exemptions and load reductions in the structural design shall be prominently indicated on drawings as temporary, and all reduced loads shall be indicated on the drawings. The environmental load mitigations shall be indicated on the construction documents. The construction documents shall be maintained at the site of the temporary installation and be available to the department upon request.]

[1618.2 Loads. Temporary installations shall be designed and constructed to resist the loads required by Chapter 16 of this code for new construction.]

[Exception:  Temporary installations that are accompanied by an action plan in accordance with Section 1618.3 shall be permitted to reduce the design environmental loads required by Chapter 16 of this code as follows:]

[1.	Seismic. Temporary installations shall be permitted to use 2 percent of the design dead and live load in lieu of the seismic forces required by Section 1614in load combinations including seismic forces.  This load shall be distributed in proportion to the design loads, shall be applied in any horizontal direction and need not be combined with other environmental loads.]

[2.	Wind. The wind design for temporary installations shall be computed as required by Section 1609. The basic wind speed used to design the structure shall be permitted to be reduced by applying a factor of 0.8.]

[3.	Other environmental forces. Other environmental forces, including, but not limited to, snow, flood ice, and temperature differential effects, shall be permitted to be reduced as appropriate for the limited exposure of the installation.]

[1618.3 Action plan. All temporary installations reducing the design environmental loads in accordance with Section 1618.2 shall include environmental load mitigation measures as part of an action plan.  The action plan measures shall be indicated on the drawings.]

[1618.3.1 Implementation. The action plan shall be such that it may be reliably implemented in one day’s notice or less as appropriate for the actions.]

[1618.3.2 Components. The action plan shall, at a minimum, include the following:]

[1. Threshold of predicted environmental loads;]

[2. Method of monitoring environmental loads;]

[3. Party responsible for monitoring loads and determining implementation of action plan;]

[4. Party responsible for effectuating the action plan;]

[5. Evacuation procedures;]

[6. Safety zone, standoff distance or standoff perimeter as appropriate. Safety zone, standoff distance or standoff perimeter shall not extend beyond the property line;]

[7. Any other activities, such as the addition or removal of structural and/or nonstructural elements, removal of loads or creating sacrificial elements so that the structure may resist unreduced forces as required for permanent structures;]

[8. Plan to prevent wind-born debris; and]

[9. Verification that the design and procedures shall not adversely impact other structures.]

1619.1 General. Temporary construction installations that are required by this code to be designed by a registered design professional, and all temporary structures, shall comply with all the provisions of this code, except as described in Sections 1619.3 and 1619.4.

1619.2 Definitions. The following terms are defined in Chapter 2:

TEMPORARY CONSTRUCTION INSTALLATIONS.

TEMPORARY STRUCTURES.

1619.3 Temporary construction installations.  Temporary construction installations shall be subject to the requirements of this section and Chapter 33.

1619.3.1 Design drawings for temporary construction installations.  Design loads, including location and intensity of live loads, shall be indicated on the design drawings for temporary construction installations. Drawings for multilevel temporary construction installations shall indicate the maximum number of levels to be loaded simultaneously and the maximum design loads. Any temporary construction installation utilizing authorized exemptions and load reductions in the structural design shall be indicated on drawings as temporary, and all reduced loads shall be indicated on the drawings. The environmental load mitigations shall be indicated on the design drawings. The design drawings shall be maintained at the site of the temporary construction installation and be made available to the department upon request.

1619.3.2 Loads for temporary construction installations. Temporary construction installations shall be designed and constructed to resist the loads and load combinations required by this chapter for permanent construction and Chapter 33 of the building code. Live loads shall not be less than the code prescribed value or the maximum loads for the use of a temporary construction installation as noted on the design drawings.

Exceptions:

1.	Load reductions may be utilized where permitted by Section 1619.3.3.

2.	Derricks not permanently mounted to a building shall not be subject to the loads and load combinations of this chapter.  Such derricks shall instead be subject to the requirements of Section 3319 and rules promulgated by the commissioner.  However, temporary construction installations used to support such derricks shall be subject to the loads and load combinations of this chapter.

3.	Mobile cranes shall not be subject to the loads and load combinations of this chapter.  Mobile cranes shall instead be subject to the requirements of Section 3319 and rules promulgated by the commissioner.  However, temporary construction installations used to support mobile cranes shall be subject to the loads and load combinations of this chapter.

1619.3.3 Load reductions for temporary construction installations. Temporary construction installations shall be permitted to reduce the design environmental loads required by this chapter in accordance with the specifications below.  An action plan for load reductions shall be required in accordance with Section 1619.5.

1.	Seismic resistance. Temporary construction installations do not need to consider seismic design. These installations, other than supports of excavation, shall be designed for a minimum of 2 percent of the dead and live load as a service level lateral force. This load shall be used in lieu of seismic forces required by Section 1613 in load combinations including seismic forces.  This load shall be distributed in proportion to the design loads, applied in any horizontal direction, and need not be combined with other environmental loads.

2.	Wind. The wind design for temporary construction installations shall be computed as required by Section 1609. The basic wind speed used to design the temporary construction installation shall be permitted to be reduced by applying a factor of 0.8.

Exceptions: The following are exceptions to item 2 concerning load reductions for wind design:

1.	Mast climbers shall not be permitted to reduce wind loads.

2.	Suspended scaffolds shall be designed for an out of service wind speed of at least 45 mph, or a lower speed when so specified by the scaffold manufacturer.

3.	Other environmental forces. Other environmental forces, including  but not limited to snow, flood, ice, and temperature differential effects, shall be permitted to be reduced as appropriate for the limited seasonal exposure of the temporary construction installation.

1619.3.4 Permit renewal for temporary construction installations that utilize an action plan.  Where a temporary construction installation requires an action plan in accordance with Section 1619.5, the application to renew the permit for such temporary construction installation shall be accompanied by the submission of a report from a registered design professional certifying, based on an inspection of the temporary construction installation performed by the registered design professional within 30 days prior to the submittal of the permit renewal application, that the action plan:

1.	Is still in effect;

2.	Has been revised to reflect the current conditions of the temporary structure; or

3.	Is no longer required, as the temporary structure has been retrofitted to comply with the loads for new construction without any reduction, pursuant to Section 1619.3.2.

1619.4 Temporary structures.  Temporary structures shall be subject to the requirements of Section 3103.1 and this section.

1619.4.1 Design drawings for temporary structures.  Design loads, including location and intensity of live loads, shall be indicated on the design drawings for temporary structures. Drawings for multilevel temporary structures shall indicate the maximum number of levels to be loaded simultaneously and the maximum design loads. Any temporary structure utilizing authorized exemptions and load reductions in the structural design shall be indicated on drawings as temporary, and all reduced loads shall be indicated on the drawings. The environmental load mitigations shall be indicated on the design drawings. The design drawings shall be maintained at the site of the temporary structure and be made available to the department upon request.

1619.4.2 Loads for temporary structures. Temporary structures shall be designed and constructed to resist the loads and load combinations required by this chapter. Live loads shall not be less than the code prescribed value or the maximum loads for the use of a temporary structure as noted on the design drawings.

Exception:  Load reductions may be utilized where permitted by Section 1619.4.3.

1619.4.3 Load reductions for temporary structures. Temporary structures shall be permitted to reduce the design environmental loads required by this chapter in accordance with the specifications below.  An action plan for load reductions shall be required in accordance with Section 1619.5.

1.	Seismic resistance. Temporary structures do not need to consider seismic design. Temporary structures shall be designed for a minimum of 2 percent of the dead and live load as a service level lateral force. This load shall be used in lieu of seismic forces required by Section 1613 in load combinations including seismic forces.  This load shall be distributed in proportion to the design loads, applied in any horizontal direction, and need not be combined with other environmental loads.

2.	Wind. The wind design for temporary structures shall be computed as required by Section 1609. The basic wind speed used to design the structure shall be permitted to be reduced by applying a factor of 0.8.

Exception: In lieu of applying a factor of 0.8, temporary structures shall be removed from service at the environmental conditions determined by the manufacturer of the temporary structure.  The threshold for removal of service shall be indicated on the design drawings required by Section 1619.4.1 as well as the action plan required by Section 1619.5.

3.	Other environmental forces. Other environmental forces, including but not limited to snow, flood, ice, and temperature differential effects, shall be permitted to be reduced as appropriate for the limited seasonal exposure of the temporary structure.

1619.4.4 Duration of time for temporary structures.  Temporary structures shall be erected for a limited period not exceeding ninety days in accordance with Article 111 of Title 28 of the New York City Administrative Code.  Such limited period shall be counted from the date the temporary structure is substantially completed.

Exception: Where the commissioner has approved a request to extend the duration of time for a temporary structure in accordance with Section 1619.4.5.

1619.4.5 Extension of time for temporary structures. Subject to the approval of the commissioner, the duration of time for a temporary structure may be extended by increments not to exceed ninety days.  Each request to extend the time for a temporary structure shall be accompanied by the submission of a report from a registered design professional certifying the following:

1.	Such registered design professional performed an inspection within the last 30 days to confirm that the temporary structure complies with the requirements of the approved construction documents for the temporary structure; and

2.	Where an action plan is utilized in accordance with Section 1619.5:

2.1.	It is still in effect;

2.2.	It has been revised to reflect the current conditions of the temporary structure; or

2.3.	It is no longer required, as the temporary structure has been retrofitted to comply with the loads for new construction without any reduction, pursuant to Section 1619.4.2.

1619.5 Action plan. All temporary structures or temporary construction installations with reduced design environmental loads in accordance with Sections 1619.3.3 or 1619.4.3 shall include environmental load mitigation measures as part of an action plan to protect the public.  The action plan measures shall be indicated on the design drawings required by Sections 1619.3.1 or 1619.4.1.

Exception: An action plan is not required for:

1.	Derricks not permanently mounted to a building.  Derricks not permanently mounted to a building shall be secured in accordance with a wind action plan as specified in rules promulgated by the commissioner.

2.	Mobile cranes.  Mobile cranes shall be secured in accordance with a wind action plan as specified in rules promulgated by the commissioner.

3.	A suspended scaffold.  Suspended scaffolds shall be secured in accordance with the requirements of Section 3314; requirements for securing suspended scaffolds shall be indicated on design drawings when required by Section 3314.

1619.5.1 Implementation. The action plan shall be such that it can be reliably implemented within one day of notice or less as appropriate for the actions.

1619.5.2 Components. The action plan shall, at a minimum, include the following:

1.	Threshold of predicted environmental loads;

2.	Method of monitoring environmental loads;

3.	Party responsible for monitoring loads and determining implementation of action plan;

4.	Party responsible for implementing the action plan;

5.	Evacuation procedures;

6.	Safety zone, standoff distance or standoff perimeter as appropriate. Safety zone, standoff distance or standoff perimeter shall not extend beyond the property line;

7.	Any other activities, such as the addition or removal of structural and/or nonstructural elements, removal of loads or creating sacrificial elements so that the structure may resist unreduced forces as required for permanent structures;

8.	Plan to prevent wind-born debris; and

9.	Verification that the design and procedures shall not adversely impact other structures.

§ 18. Chapter 17 of the New York city building code, as amended by local law number 141 for the year 2013, table 1704.3 as amended by local law number 51 for the year 2014, section 1704.33 as amended by local law number 116 for the year 2019, is amended to read as follows:

CHAPTER 17
[STRUCTURAL TESTS AND] SPECIAL INSPECTIONS AND TESTS

SECTION BC 1701
GENERAL

1701.1 Scope. The provisions of this chapter shall govern the inspection of quality, workmanship and requirements for construction. Materials, inspection and testing shall conform to the applicable standards listed in this code or in the rules of the department. See Chapter 1 of Title 28 of the Administrative Code for additional provisions relating to materials, testing and inspections.

1701.2 New materials. See Chapter 1 of Title 28 of the Administrative Code for additional provisions.

1701.3 Used materials. See Chapter 1 of Title 28 of the Administrative Code.

SECTION BC 1702
DEFINITIONS

1702.1 [General. The following words and terms shall, for the purposes of this chapter and as used elsewhere in this code, have the meanings shown herein.] Definitions. The following terms are defined in Chapter 2:

APPROVED AGENCY. [See Chapter 1 of Title 28 of the Administrative Code.]

APPROVED FABRICATOR. [An established and qualified person, firm or corporation approved by the commissioner to custom manufacture or build products or assemblies regulated by this code.]

CERTIFICATE OF COMPLIANCE. [A certificate stating that materials meet specified standards, that work was done in compliance with approved construction documents and other applicable provisions of law, or with respect to specified service equipment, a certificate issued by the department authorizing the operation of such equipment.]

FABRICATED ITEM. [Products and assemblies regulated by this code that are custom manufactured, or built prior to their incorporation into the work at the job site. Fabricated items shall not include listed, labeled or approved products or assemblies.]

INSPECTION CERTIFICATE. [An identification applied on a product by an approved agency containing the name of the manufacturer, the function and performance characteristics, and the name and identification of the approved agency that indicates that the product or material has been inspected and evaluated by such approved agency. An inspection certificate shall also mean a certificate issued by the department upon satisfactory completion of an inspection or test.]

INTUMESCENT FIRE-RESISTANT COATINGS. [Thin film liquid mixture applied to substrates which expands into a protective foamed layer to provide fire-resistant protection of the substrates when exposed to flame or intense heat.]

LABEL. [An identification applied on a product by the manufacturer that contains the name of the manufacturer, the function and performance characteristics of the product or material, and the name and identification of an approved agency and that indicates that a representative sample of the product or material has been tested and evaluated by an approved agency for compliance with nationally recognized standards or tests to determine suitable usage in a specified manner.]

MANUFACTURER’S DESIGNATION. [An identification applied on a product by the manufacturer indicating that a product or material complies with a specified standard or set of rules.]

MARK. [An identification applied on a product by the manufacturer indicating the name of the manufacturer and the function of a product or material.]

MASTIC FIRE-RESISTANT COATINGS. [Liquid mixture applied to a substrate that provides fire-resistant protection of a substrate when exposed to flame or intense heat.]

SPECIAL INSPECTION. [Inspection of selected materials, equipment, installation, fabrication, erection or placement of components and connections, to ensure compliance with approved construction documents and referenced standards as required by this chapter or elsewhere in this code or its referenced standards.]

SPECIAL INSPECTION, CONTINUOUS. [The full-time observation of work requiring special inspection by a special inspector who is continuously present in the area where the work is being performed.]

SPECIAL INSPECTION, PERIODIC. [The intermittent observation of work requiring special inspection by a special inspector who is present in the area where the work has been or is being performed and at the completion of the work. All work requiring special inspection shall remain accessible and exposed until approved by the special inspector.]

SPECIAL INSPECTOR. [See Chapter 1 of Title 28 of the Administrative Code.]

SPRAYED FIRE-RESISTANT MATERIALS. [Cementitious or fibrous materials that are sprayed to provide fire-resistant protection of the substrates.]

SUPERINTENDENT OF CONSTRUCTION. [See Chapter 1 of Title 28 of the Administrative Code.]

SECTION BC 1703
APPROVALS

See Chapter 1 of Title 28 of the Administrative Code.

SECTION BC 1704
RESPONSIBILITIES FOR SPECIAL INSPECTIONS AND TESTS

1704.1 General. Where application is made for construction as described in this section, one or more special inspection agencies meeting the requirements of Sections 28-114.1 and 28-115.1 of the Administrative Code shall be retained by the owner to provide inspections during construction on the types of work listed under Section [1704] 1705 and elsewhere in this code. These inspections are in addition to the other inspections required by Section 110, elsewhere in this code, and Section 28-116 of the Administrative Code. The special inspector shall be acceptable to the registered design professional of record.

Exception: Special inspections are not required for building components unless the design involves the practice of professional engineering or architecture as defined by the Education Law of the State of New York and applicable regulations governing the professional registration and certification of engineers or architects.

1704.1.1 Responsibilities. Special inspection responsibilities of registered design professionals of record, special inspection agencies, and permit holders shall meet the applicable requirements of this section.

1704.1.1.1 Responsibilities of the registered design professional of record. The registered design professional of record shall have the following duties and responsibilities:

1.	[Construction document requirements] Identification of required special inspections. The registered design professional of record shall identify the materials, equipment, installation, fabrication, erection or placement of components and connections, or construction operations for the work indicated on the construction documents that are subject to special inspections on the construction documents and [on forms supplied] in any other form or manner required by the department prior to the approval of the construction documents.

2.	Respond to field discrepancies. The registered design professional of record shall respond to special inspector reports of uncorrected discrepancies and shall approve remedial measures.

3.	Review of shop drawings and other submittals. Where shop or working drawings, and other submittals have been provided, the registered design professional of record shall review such shop drawings for conformance with the approved design. The registered design professional shall acknowledge conformance with the approved design on such documents.

4.	Deviations from approved construction documents. The registered design professional of record shall submit to the department and the special inspection agency written documentation of the professional’s approval of deviations from the approved construction documents. All such deviations approved by the registered design professional of record shall be filed with the department on amended construction documents in accordance with Section 28-104.3 of the Administrative Code.

[1704.1.2] 1704.1.1.2 Responsibilities of the special inspection agency. The special inspection agency shall have the following duties and responsibilities:

1.	Independence. The special inspection agency shall be independent of the contractors responsible for the work being inspected. The registered design professional of record is permitted to act as the approved special inspection agency and such agency’s personnel are permitted to act as special inspectors for the work designed by the registered design professional of record, provided those personnel meet the qualification requirements of this section to the satisfaction of the department.

2.	Qualifications. The special inspection agency shall ensure that qualified special inspectors are provided to perform special inspections in accordance with the rules of the department. Upon request of the registered design professional of record, the special inspection agency shall provide proof of inspectors’ and agency’s qualifications, certifications, and other documents demonstrating compliance with department rules and regulations.

[2.] 3.	Construction documents. The special inspection agency shall examine all approved construction documents that relate to the work that is the subject of the special inspections to confirm that the documents are sufficient to enable the proper performance of the special inspection. The special inspection agency shall confirm that any shop drawings or sketches have been accepted by the registered design professional of record. Acceptance shall be demonstrated in writing by the registered design professional of record on the documents. All approved shop drawings, submittals and/or sketches are to be located on site and accessible to the special inspector at time of inspection.

[3.] 4.	Inspection. The special inspection agency shall observe work subject to special inspection to confirm that the work that is the subject of the special inspection is in compliance with the approved construction documents; with the approved shop drawings, where provided; and with the special inspection requirements of this code and department rules and regulations.

5.	Tests. Where specifically required by this code, the performance of testing shall be by qualified special inspectors working for the special inspection agency. In all other instances, the special inspection agency shall observe testing to confirm that testing activities that are subject to special inspection are in compliance with the prescribed testing procedures.

[4.] 6.	Reports. The special inspection agency shall prepare reports of its inspections and tests, and such reports shall indicate that work inspected was or was not performed in conformance with approved construction documents.

[4.1] 6.1. Format. Special inspection reports and records of special inspections shall be in the form and format supplied by the commissioner.

[4.2] 6.2. Discrepancies. Discrepancies shall be brought to the immediate attention of the contractor and, when applicable, to the attention of the superintendent of construction, for correction. [If the discrepancies are not corrected, the] The discrepancies shall also be brought to the attention of the owner, and the registered design professional of record [prior to the completion of that phase of the work] in a timely manner to allow for correction of the discrepancies.

[4.3] 6.3. Hazardous conditions. The special inspector shall report conditions noted as hazardous to life, safety or health that are not immediately corrected to the immediate attention of the commissioner.

[4.4] 6.4. Final report. Prior to issuance of a certificate of occupancy or letter of completion, a final report documenting the required special inspections, including any required performance or witnessing of tests, and correction of all discrepancies noted in the inspections shall be submitted to the department [, certifying] Such report shall certify compliance with approved construction documents, deviations approved by the registered design professional of record in accordance with Section 1704.1.1.1 Item 4, and the administrative and procedural requirements of this code.

[4.5] 6.5 Approval of partially completed work. Reports of partially completed work shall be accepted when such reports indicate that the inspected work has been completed in accordance with the construction documents, and indicate the extent and the condition of the remaining work.

[4.6] 6.6 Maintain records. The special inspection agency shall [keep] maintain records of inspections for a period of 6 years from the date of [project sign-off] the special inspection agency’s final submittal or report of completed inspection. Such records shall be supplied to the commissioner upon request. The commissioner may require that special inspection reports be filed with the department and/or that such reports be otherwise made accessible for review.

[1704.1.3] 1704.1.1.3 Responsibilities of the permit holder. The permit holder shall have the following duties and responsibilities:

1.	Statement of special inspections. The application for permit shall include a statement of relevant special inspections as a condition for permit issuance on forms supplied by the department. This statement shall include:

  - A complete list of materials and work included in the permit application requiring special inspections by this section and elsewhere in this code and the inspections to be performed on such work and materials; and

  - A list of the special inspection agencies retained by the owner for conducting the special inspections listed on the approved plans. Within each category of work, multiple special inspectors or special inspection agencies may be employed.

2.	Identification of registered design professionals providing design documents for certain construction operations. The registered design professionals responsible for the production of design, sequence of construction operations or shop drawings for projects that require design pursuant to Chapter 33, shall file documentation of their intent to perform those duties on forms supplied by the department. The registered design professionals preparing such documents shall also be subject to the responsibilities of the registered design professional of record required by Section 1704.1.1.1 for the scope of work covered in the design, sequence of construction operations or shop drawings for which they are responsible.

3.	Required notification to special inspection agencies. The holder of a permit covering work requiring a special inspection shall notify the relevant special inspectors or special inspection agencies in writing at least 72 hours before the commencement of any work requiring special inspection. The permit holder shall make available the most current approved construction documents to the special inspection agency.

4.	Access for special inspection. The construction or work for which special inspection is required shall remain accessible and exposed for special inspection purposes until completion of the required special inspections.

5.	[Deficiencies] Resolution of discrepancies. The permit holder shall be responsible for the [correction] resolution of identified [deficiencies] discrepancies. A satisfactory inspection by a special inspection agency or the acceptance by the department of a satisfactory report of an inspection by a special inspection agency shall not be construed to be an approval by the department of a violation of the provisions of this code or of any other provision of law.

1704.2 Inspection of fabricators. Where fabrication of structural members, and other regulated products is performed on the premises of a fabricator’s shop, special inspection and progress inspection of the fabricated items shall be required by this section, the New York City Construction Codes, and [in] Chapter 1 of Title 28 of the Administrative Code.

1704.2.1 Fabrication and implementation procedures. The special inspector shall verify that the fabricator maintains detailed fabrication and quality control procedures that provide a basis for inspection control of the workmanship and the fabricator’s ability to conform to approved construction documents and referenced standards. The special inspector shall review the procedures for completeness and adequacy relative to the code requirements for the fabricator’s scope of work.

Exception: Special inspections and progress inspections as required by Section 1704.2 shall not be required where the fabricator is approved in accordance with [Section 1704.2.2 and with] Chapter 1 of Title 28 of the Administrative Code, except as required by Section 1704.2.2.

1704.2.2 Fabricator approval. Work that is subject to special inspection and performed on the approved fabricator’s premises shall be inspected by the special inspection agency in accordance with Section 1704.2.2.3. Approval of fabricators shall be based upon review of the fabricator’s written procedural and quality control manuals and periodic auditing of fabrication practices by an approved agency.

1704.2.2.1 Certificate of intent to fabricate. For all work where approval is sought based upon Section 1704.2.2, the approved fabricator shall submit a certificate of intent to fabricate such work to the department identifying the work to be performed as an approved fabricator, and that such work shall be performed in accordance with the approved construction documents, referenced standards and applicable provisions of law and for which site the work is being fabricated prior to fabricating any items for such project.

1704.2.2.2 Fabricator’s certificate of compliance. For all fabricated items, the approved fabricator shall submit a certificate of compliance to the department stating that the work was performed in accordance with the approved construction documents, referenced standards and applicable provisions of law.

1704.2.2.3 In-plant special inspections. The owner shall engage [an approved] a registered special inspection agency to perform special inspections for the portion of the work performed in the approved fabricator’s premises. These inspections shall at a minimum include: (i) one visit to the fabricator’s premises during the course of the subject work to verify the fabricator’s compliance with the written and procedural quality control manuals; and (ii) inspection of 5 percent of the subject work to verify compliance with the approved construction documents. [Such inspection is permitted to be performed in either the fabricator’s premises or at the construction site.]

SECTION BC 1705
REQUIRED SPECIAL INSPECTIONS AND TESTS

1705.1 General. Special inspections and tests of structural elements and nonstructural components of buildings and structures shall meet the applicable requirements of this section.

1705.1.1 Special cases. Special inspections shall be required for proposed work that is, in the opinion of the commissioner, unusual in its nature, including, but not limited to:

1.	Construction materials and systems that are alternatives to materials and systems prescribed by this code.

2.	Unusual design applications of materials described in this code.

3.	Materials and systems required to be installed in accordance with manufacturer’s instructions that prescribe additional requirements not contained in this code or in standards referenced by this code.

1705.1.1.1 Qualifications. Where special inspections are required for proposed work in accordance with Section 1705.1.1, the special inspection shall be performed by special inspectors qualified to inspect the work to be inspected. The qualifications of the special inspector shall be acceptable to the commissioner.

[1704.3] 1705.2 Steel construction. The special inspections of new installations and alterations to existing installations of steel elements in buildings and structures shall be as required by [Section [1704.3] this section and Table [1704.3] 1705.2. Where required, special inspection of steel shall also comply with Section [1716] 1711.

Exceptions:

- Special inspection of the steel fabrication process shall not be required where the fabricator does not perform any welding, thermal cutting or heating operation of any kind as part of the fabrication process. In such cases, the fabricator shall be required to submit a detailed procedure for material control that demonstrates the fabricator’s ability to maintain suitable records and procedures such that, at any time during the fabrication process, the material specification, grade and mill test reports for the main stress-carrying elements are capable of being determined.

- [The] When specified by the registered design professional, the special inspector [need not be continuously present] shall have the option to perform periodic inspections during welding of the following items, provided the materials, welding procedures and qualifications of welders are verified prior to the start of the work; periodic inspections are made of the work in progress and a visual inspection of all welds is made prior to completion or prior to shipment of shop welding.

2.1.	Single-pass fillet welds not exceeding 5/16 inch (7.9 mm) in size.

2.2.	Floor and roof deck welding.

2.3.	Welded studs when used for structural diaphragm.

2.4.	Welded sheet steel for cold-formed steel members.

2.5.	Welding of stairs and railing systems.

[TABLE 1704.3
REQUIRED VERIFICATION AND INSPECTION OF STEEL CONSTRUCTION

| VERIFICATION AND INSPECTION | CONTINUOUS | PERIODIC | REFERENCED STANDARDa | BC REFERENCE |
| --- | --- | --- | --- | --- |
| 1. Material verification of high-strength bolts, nuts and washers: |  |  |  |  |
| Identification markings to conform to ASTM standards specified in the approved construction documents. | — | X | Applicable ASTM material specifications; AISC 335, Section A3.4; AISC LRFD, Section A3.3 | — |
| Manufacturer’s certificate of compliance required. | — | X | — | — |
| 2. Inspection of high-strength bolting: |  |  |  |  |
| Bearing-type connections. | — | X Note b | AISC LRFD Section M2.5 | 1704.3.3 |
| Slip-critical connections. | X | X |  |  |
| 3. Material verification of structural steel: |  |  |  |  |
| Identification markings to conform to ASTM standards specified in the approved construction documents. | — | — | ASTM A 6 or ASTM A 568 | 1708.4 |
| Manufacturers’ certified mill test reports. | — | — | ASTM A 6 or ASTM A 568 |  |
| 4. Material verification of weld filler materials: |  |  |  |  |
| Identification markings to conform to AWS specification in the approved construction documents. | — | — | AISC, ASD, Section A3.6; AISC LRFD, Section A3.5 | — |
| Manufacturer’s certificate of compliance required. | — | — | — | — |
| 5. Inspection of welding: a. Structural steel: | — | — |  |  |
| Complete and partial penetration groove welds. | X | — | AWS D1.1 | 1704.3.1 |
| Multipass fillet welds. | X | — |  |  |
| Single-pass fillet welds > 5/16″ | X | — |  |  |
| Single-pass fillet welds ≤ 5/16″ | — | X |  |  |
| Floor and roof deck welds. | — | X | AWS D1.3 | — |
| b. Reinforcing steel: | — | — | AWS D1.4 ACI 318: 3.5.2 | 1903.5.2 |
| Verification of weldability of reinforcing steel other than ASTM A 706. | — | X |  |  |
| Reinforcing steel-resisting flexural and axial forces in intermediate and special moment frames, and boundary elements of special reinforced concrete shear walls and shear reinforcement. | X | — |  |  |
| Shear reinforcement. | X Note a | — |  |  |
| Other reinforcing steel. | — | X |  |  |
| 6. Inspection of steel frame joint details for compliance with approved construction documents: Details such as bracing and stiffening. Member locations. Application of joint details at each connection. | — — — | X — — | — | 1704.3.2 |

For SI: 1 inch = 25.4 mm.

- A minimum of 10 percent of shear studs shall be verified for strength of welded connection. If failure is evident on one or more, then the strength of all shear studs shall be verified.

- Turn of the nut bolting shall be continuously inspected. Exception: Periodic inspection shall be acceptable when the contractor’s procedures have been established and verified for compliance by the special inspector.]

2.6.	Welding of connections where the calculated connection strength is at least twice the required strength of the connection. Such connections shall be specifically indicated on the approved construction documents.

TABLE 1705.2
REQUIRED SPECIAL INSPECTION OF STEEL CONSTRUCTION

| TYPE | CONTINUOUS SPECIAL INSPECTION | PERIODIC SPECIAL INSPECTION | REFERENCED STANDARDa | BC REFERENCE |
| --- | --- | --- | --- | --- |
| 1. Material verification of high-strength bolts, nuts and washers: |
| a. Identification markings to conform to ASTM standards specified in the approved construction documents. | — | X | AISC 360, Section A3.3; applicable ASTM material specifications; and RCSC Specification for Structural Joints Using High-Strength Bolts Section 2 | — |
| b. Manufacturer’s certificate of compliance required. | — | X | RCSC Specification for Structural Joints Using High-Strength Bolts Section 2.1 | — |
| 2. Inspection of high-strength bolting: |
| a. Snug-tight joints. | — | X | AISC 360 Section M2.5; and RCSC Specification for Structural Joints Using High-Strength Bolts Section 9 | 1705.2.3 |
| b. Pre-tensioned and slip-critical joints using turn-of-nut with matchmarking, twist-off bolt or direct tension indicator methods of installation. | — | X |  |  |
| c. Pre-tensioned and slip-critical joints using turn-of-nut without matchmarking or calibrated wrench methods of installation. | X | — |  |  |
| d. Pre-installation verification testing. | X | — | Specification for Structural Joints Using High-Strength Bolts Section 8.2 | 1705.2.3.1 |
| 3. Material verification of structural steel and cold formed steel deck: |
| a. For structural steel, identification markings to conform to AISC 360. | — | X | AISC 360 Sections A3.1, N2.1, N3.2 (a) and (k)(1) | — |
| b. For other steel, identification markings to conform to ASTM standards specified in the approved construction documents. | — | — | Applicable ASTM Standards | — |
| c. Manufacturers’ certified mill test reports. | — | X | Applicable ASTM material standards |  |
| 4. Material verification of weld filler materials: |
| a. Identification markings to conform to AWS specification in the approved construction documents. | — | — | AISC 360 Section A3.5 and N3.2(e), and applicable AWS A5 documents; and AWS D1.1 5.3.1 and approved contract documents | — |
| b. Manufacturer’s certificate of compliance required. | — | — | AISC 360 Section A3.5 | — |
| 5. Inspection of welding: |
| a. Structural steel: | — | — | — | — |
| 1) Complete and partial penetration groove welds. | X | — | AWS D1.1 | 1705.2.1 |
| 2) Multipass fillet welds. | X | — |  |  |
| 3) Single-pass fillet welds > 5/16″. | X | — |  |  |
| 4) Plug and slot welds. | X | — |  |  |
| 5) Single-pass fillet welds ≤ 5/16″. | — | X |  |  |
| 6) Floor and roof deck welds. | — | X | AWS D1.3 | — |
| 7) Cold-formed steel welds. | — | X | AWS D1.3 | — |
| b. Reinforcing steel: | — | — | AWS D1.4 | 1903.6.2 |
| 1) Pre-welding verification of base metal. | — | X |  |  |
| 2) Reinforcing steel-resisting flexural and axial forces in intermediate and special moment frames, and boundary elements of special reinforced concrete shear walls and shear reinforcement. | X | — |  |  |
| 3) Shear reinforcement. | X Note a | — |  |  |
| 4) Other reinforcing steel. | — | X Note b |  |  |
| 6. Inspection of steel frame joint details for compliance with approved construction documents: |  |  | — | 1705.2.2 |
| a. Details such as bracing and stiffening. | — | X |  |  |
| b. Member locations. | — | X |  |  |
| c. Application of joint details at each connection. | — | X |  |  |

For SI: 1 inch = 25.4 mm.

a	A minimum of 10 % of shear studs shall be verified for strength of welded connection. If failure is evident on one or more, then the strength of all shear studs shall be verified.

b.	Welding of indirect and direct butt joints shall be continuously inspected.

[1704.3.1] 1705.2.1 Welding. Welding inspection and welding inspector qualification shall be in compliance with this section and the rules of the department.

[1704.3.1.1] 1705.2.1.1 Structural steel. Welding inspection and welding inspector qualification for structural steel shall be in accordance with AWS D1.1.

[1704.3.1.2] 1705.2.1.2 Cold-formed steel deck. Welding inspection and welding inspector qualification for cold-formed steel floor and roof decks shall be in accordance with [AWS D1.3] SDI QA/QC.

[1704.3.1.3] 1705.2.1.3 Reinforcing steel. Welding inspection and welding inspector qualification for reinforcing steel shall be in accordance with AWS D1.4[and ACI 318].

[1704.3.2] 1705.2.2 Details. The special inspector shall perform an inspection of the steel frame to verify compliance with the details shown on the approved construction documents, such as bracing, stiffening, member locations and proper application of joint details at each connection, including connections designed for seismic effects.

[1704.3.3] 1705.2.3 High-strength bolts. Installation of high-strength bolts shall be inspected in accordance with this section and AISC 360.

Exception: Installation of high strength bolts in bearing type connections where the calculated connection strength is at least twice the required strength of the connection. Inspection of such connections shall be made under Section [1704.3.2] 1705.2.2. Such connections shall be clearly indicated on the approved construction documents.

[1704.3.3.1] 1705.2.3.1 General. While the work is in progress, the special inspector shall determine that the requirements for bolts, nuts, washers and paint; bolted parts and installation and tightening in such standards are met. For bolts requiring pretensioning, the special inspector shall observe the preinstallation testing and calibration procedures when such procedures are required by the installa-tion method or by project plans or specifications; determine that all plies of connected materials have been drawn together and properly snugged and monitor the installation of bolts to verify that the selected procedure for installation is properly used to tighten bolts. For joints required to be tightened only to the snug-tight condition, the special inspector need only verify that the connected materials have been drawn together and properly snugged.

[1704.3.3.2] 1705.2.3.2 Periodic inspection. Inspection of bolt installation for pretensioning is permitted to be performed on a periodic basis when using the turn-of-nut method with matchmarking techniques, the direct tension indicator method or the alternate design fastener (twist-off bolt) method. Joints designated as snug tight need be inspected only on a periodic basis.

[1704.3.3.3] 1705.2.3.3 Continuous inspection. Inspection of bolt installation for pretensioning using the calibrated wrench method or the turn-of-nut method without matchmarking shall be performed on a continuous basis.

1705.2.4 Special inspection for seismic resistance. In addition to the other special inspection requirements of this code, special inspections of structural steel seismic force resistancing systems and structural steel elements shall be performed in accordance with Section 1705.2.4.1 and 1705.2.4.2.

1705.2.4.1 Seismic force-resisting systems. Special inspections of structural steel in the seismic force-resisting systems of buildings and structures assigned to Seismic Design Category B, C, or D shall be performed in accordance with the quality assurance requirements of AISC 341.

Exception: Special inspections per Section 1705.2.4.1 are not required in the seismic force-resisting systems of buildings and structures assigned to Seismic Design Category B or C that are not specifically detailed for seismic resistance, with a response modification coefficient, R, of 3 or less, excluding cantilever column systems.

1705.2.4.2 Structural steel elements. Special inspections of structural steel elements in the seismic force-resisting systems of buildings and structures assigned to Seismic Design Category B, C, or D other than those covered in Section 1705.2.4.1, including struts, collectors, chords and foundation elements, shall be performed in accordance with the quality assurance requirements of AISC 341.

Exception: Special inspections of structural steel elements per Section 1705.2.4.2 are not required in the seismic force-resisting systems of buildings and structures assigned to Seismic Design Category B or C with a response modification coefficient, R, of 3 or less.

1705.2.5 Testing for seismic resistance of structural steel. Nondestructive testing for seismic resistance shall be in accordance with Section 1705.2.5.1 or 1705.2.5.2, as applicable.

1705.2.5.1 Seismic force-resisting systems. Nondestructive testing of structural steel in the seismic force-resisting systems of buildings and structures assigned to Seismic Design Category B, C, or D shall be performed in accordance with the quality assurance requirements of AISC 341.

Exception: Nondestructive testing is not required in the seismic force-resisting systems of buildings and structures assigned to Seismic Design Category B or C that are not specifically detailed for seismic resistance, with a response modification coefficient, R, of 3 or less, excluding cantilever column systems.

1705.2.5.2 Structural steel elements. Nondestructive testing of structural steel elements in the seismic force-resisting systems of buildings and structures assigned to Seismic Design Category B, C, or D other than those covered in Section 1705.2.5.1, including struts, collectors, chords and foundation elements, shall be performed in accordance with the quality assurance requirements of AISC 341.

Exception: Nondestructive testing of structural steel elements is not required in the seismic force-resisting systems of buildings and structures assigned to Seismic Design Category B or C with a response modification coefficient, R, of 3 or less.

[1704.3.4] 1705.2.6 Cold-formed steel construction. Special inspections for prefabricated and site built cold-formed steel [light-frame] construction and assemblies used structurally shall be as required by this section and Table [1704.3.4] 1705.2.6. [The special inspector shall verify the size, quality, framing, erection, and both temporary and permanent bracing.]

| TABLE 1705.2.6 REQUIRED SPECIAL INSPECTION OF COLD-FORMED STEEL CONSTRUCTION |
| --- |
| TYPE | CONTINUOUS SPECIAL INSPECTION | PERIODIC SPECIAL INSPECTION | REFERENCED STANDARD | BC REFERENCE |
| 1. Material Verification: |  |  |  |  |
| a. Verify that identification markings conform to AISI S240and as specified in the approved construction documents. | X |  | AISI S240, Section D6.5 |  |
| b. Verify that material is clean, straight and undamaged. |  | X |  |  |
| 2. Inspection of general framing: |  |  |  |  |
| a. Verify that member sizes conform to the approved construction documents. |  | X | AISI S240 Section C |  |
| b. Verify that member layout conforms to the approved construction documents. |  | X |  |  |
| c. Verify that proper bearing lengths are provided in accordance with approved construction documents. |  | X |  |  |
| d. Verify that punched holes and sheared or flame cut edges of material in members are clean and free from notches and burred edges. |  | X |  |  |
| 3. Inspection of framing connections and anchorages: |  |  |  |  |
| a. Verify that screws, bolts, and other fasteners conform to approved construction document requirements for diameter, length, quantity, spacing, edge distance, and location. |  | X | AISI S240, Section D6.7 |  |
| b. Verify that manufactured connectors, such as joist hangers, caps, straps, clips, ties, hold-downs, and anchors conform to approved construction document requirements for manufacturer, type, gauge, and fastener requirements. |  | X | AISI S240 Section B1.5 and Section C4 |  |
| c. Post-installed connections to concrete. | X |  | AISI S240 Section D6.9 |  |
| 4. Inspection of welding: |  |  |  |  |
| a. Inspect welds in accordance with S240 Section D6.6. |  | X | AWS D1.3, AISI S240 Section D6.6 |  |
| b. Additional requirements for welds performed as a part of a lateral force-resisting system | X Note a |  | AISI S240 Section D6.9 |  |
| 5. Bracing: |  |  |  |  |
| a. Verify that temporary bracing, shoring, jacks, etc., are installed, and not removed until no longer necessary, in accordance with the approved construction documents and approved erection drawings. |  | X | AISI S240 Section E6 |  |
| b. Verify that permanent bracing, web stiffeners, bridging, blocking, wind bracing, etc, are installed in accordance with the approved construction documents and approved erection drawings. |  | X |  |  |
| c. Where a cold-formed steel truss clear span is 60 feet (18 288 mm) or greater, the special inspector shall verify that the temporary installation restraint/bracing and the permanent individual truss member restraint/bracing are installed in accordance with the approved truss submittal package. |  | X |  | 2211.1.3.2 |
| 6. Pre-installation Document Submittals |  | X | AISI S240, Section D3 |  |
| 7. Lateral Force-Resisting System Additional Requirements |  | X | AISI S240 Section D6.9 |  |

Note a:  In accordance with AISI S240 Section D6.9.1, continuous special inspection of weld fit-up in lateral force-resisting systems may be reduced to periodic special inspection upon fulfillment of the conditions of Section D6.9.1.

1705.2.7 Open-web steel joists and joist girders. Special inspections of open web steel joists and joist girders in buildings, structures, and portions thereof shall be in accordance with Table 1705.2.7.

| TABLE 1705.2.7 REQUIRED SPECIAL INSPECTIONS OF OPEN-WEB STEEL JOISTS AND JOIST GIRDERS |
| --- |
| TYPE | CONTINUOUS SPECIAL INSPECTION | PERIODIC SPECIAL INSPECTION | REFERENCED STANDARD | BC REFERENCE |
| 1. Inspection of member sizes and locations. | --- | X |  |  |
| 2. Inspection of end connections – welded or bolted | ---- | X | SJI Specifications | 2207.1 |
| 3. Inspection of standard bridging, horizontal or diagonal | ---- | X | SJI Specifications | 2207.1 |
| 4. Inspection of bridging, horizontal or diagonal, that differs from the SJI specifications listed in Section 2207.1 | ---- | X | SJI Specifications |  |

[1704.4] 1705.3 Concrete construction. The special inspections and verifications for concrete construction shall be as required by this section and Table [1704.4] 1705.3.

Exceptions:

- Special inspection shall not be required when specifically indicated as not required on the approved construction documents for:

[1.1.	Nonstructural concrete slabs supported directly on the ground, including prestressed slabs on grade, where the effective prestress in the concrete is less than 150 psi (1.03 Mpa).]

[1.2.	Concrete foundation(s) for lightweight fences and recreational equipment.]

[1.3.	Concrete patios, site furnishings, garden walls, driveways, sidewalks and similar construction.]

1.1.	Nonstructural concrete slabs supported directly on the ground, including prestressed slabs on grade, where the effective prestress in the concrete is less than 150 psi (1.03 Mpa).

1.2.	Concrete foundation(s) for lightweight fences and recreational equipment.

1.3.	Concrete patios, site furnishings, garden walls, driveways, sidewalks and similar construction.

2.	Testing required by Table [1704.4.1] 1705.3, Item 6, may be waived by the registered design professional who prepared the approved structural construction documents when such waiver is specifically indicated on such construction documents in the following cases:

2.1.	Where the total concrete placement on a given project is less than 50 cubic yards (38  m3).

2.2.	Isolated spread concrete footings of R-3 buildings three stories or less above grade plan that are fully supported on earth or rock.

2.3.	Continuous concrete footings supporting walls of R-3 buildings three stories or less above grade plan that are fully supported on earth or rock where the structural design of the footing is based on a specified compressive strength, f’c, no greater than 2,500 pounds per square inch (psi) (17.2 Mpa), and the compressive strength used in the footing construction is at least 4,000 psi (27.6 Mpa).

[TABLE 1704.4
REQUIRED VERIFICATION AND INSPECTION OF CONCRETE CONSTRUCTION

| VERIFICATION AND INSPECTION | CONTINUOUS | PERIODIC | REFERENCED STANDARD | BC REFERENCE |
| --- | --- | --- | --- | --- |
| 1. Inspection of reinforcing steel, including prestressing tendons and placement. | ___ | X | ACI 3 18:3.5, 7.1 – 7.7 | 1903.5, 1907.1, 1907.7, 1914.4 |
| 2. Inspection of reinforcing steel welding in accordance with Table 1704.3, Item 5b. | ___ | ___ | AWS D1.4 |  |
| 3. Inspect bolts to be installed in concrete prior to and during placement of concrete where allowable loads have been increased. | ACI 318:3.5.2 | 1903.5.2 |  |  |
| 4. Verifying use of required design mix. | X | ___ | ____ | 1912.5 |
| 5. At the time fresh concrete is sampled to fabricate specimens for strength tests, perform slump and air content tests, and determine the temperature of the concrete. | ___ | X | ACI 318: Ch. 4, 5.2-5.4 | 1904, 1905.2-1905.4, |
| 6. Inspection of concrete and shotcrete placement for proper application techniques. | 1914.2, 1914.3 |  |  |  |
| 7. Inspection for maintenance of specified curing temperature and techniques. | X | ___ | ASTM C 172 ASTM C 31 |  |
| 8. Inspection of prestressed concrete: A. Application of prestressing forces. B. Grouting of bonded prestressing tendons in the seismic-force-resisting system. | ACI 318: 5.6,5.8 |  |  |  |
| 9. Erection of precast concrete members. | (Note a, b) | 1905.6, 1914.10 |  |  |
| 10. Verification of in-situ concrete strength, prior to stressing of tendons in post-tensioned concrete and prior to removal of shores and forms from beams and structural slabs. | X | ___ | ACI 318: 5.9, 5.10 | 1905.9, 1905.10, |

a.	Standard sampling rate shall be in accordance with Section 1905.6.2.

b.	Four-inch by 8-inch cylinders may be accepted in lieu of 6-inch by 12-inch cylinders at the option of the engineer of record.]

| TABLE 1705.3 REQUIRED SPECIAL INSPECTIONS AND TESTS OF CONCRETE CONSTRUCTION |
| --- |
| TYPE | CONTINUOUS SPECIAL INSPECTION | PERIODIC SPECIAL INSPECTION | REFERENCED STANDARD | BC REFERENCE | Concrete Special Inspector (Cast-In-Place, Precast, & Prestressed) | Licensed Concrete Testing Laboratory |
| 1. Inspect reinforcement, including prestressing tendons and verify placement. | — | X | ACI 318: 3.5, 7.1 – 7.7 | 1903.6, 1907.1, 1907.7, 1911.4 | X |  |
| 2. Inspection of reinforcing steel welding in accordance with Table 1705.2, Item 5b. | — | — | AWS D1.4 ACI 318: 3.5.2 | 1903.6.2 |  |  |
| 3. Inspect anchors cast in concrete. | X | — | ACI 318: 17.8.2 | 1901.3 | X |  |
| 4. Inspect anchors post-installed in hardened concrete membersc. a. Adhesive anchors installed in horizontally or upwardly inclined orientations to resist sustained tension loads. b. Mechanical anchors and adhesive anchors not defined in 4a. | X | X | ACI 318: 17.8 |  | X |  |
| 5. Verifying use of required design mix. | — | — | ACI 318: Ch. 4, 5.2-5.4 | 1904, 1905.2-1905.4, 1911.3 |  | X |
| 6. Prior to concrete placement, fabricate specimens for strength tests, perform slump and air content tests, and determine the temperature of the concrete. Determine water content when required. | — | — | ASTM C 172 ASTM C 31 ACI 318: 5.6, 5.8 (Note a, b) | 1905.6, 1911.10 |  | X |
| 7. a. Inspect concrete and shotcrete placement for proper application techniques. b. For concrete pumped through a placement boom: Following the lubrication of the concrete placement boom and prior to Contractor’s commencement of the concrete pour, observe and document as part of the special inspection of the concrete placement whether the material exiting the hose is concrete exhibiting a uniform matrix of aggregate. | X | — | ACI 318: 5.9, 5.10 | 1905.9, 1905.10, 1911.6, 1911.7, 1911.8 | X |  |
| 8. Verify maintenance of specified curing temperature and techniques. Monitoring of in-place temperatures per thermal protection plan when required. | — | X | ACI 318: 5.11-5.13 | 1905.11, 1905.13, 1911.9 | X |  |
| 9. Inspect prestressed concrete for: A. Application of prestressing forces; and B. Grouting of bonded prestressing tendons. | X X | — | ACI 318: 18.20 ACI 318: 18.18.4 | — | X |  |
| 10. Inspect erection of precast concrete members. | — | X | ACI 318: Ch. 16 | — | X |  |
| 11. Verify in-situ concrete strength, prior to stressing of tendons in post-tensioned concrete and prior to removal of shores and forms from beams and structural slabs. | — | X | ACI 318: 6.2 | 1906.2 | — | X |
| 12. Inspect formwork for shape, location, and dimensions of the concrete member being formed. | — | X | ACI 318: 6.1.1 | 1906.2 | X |  |

a.	Standard sampling rate shall be in accordance with Section 1905.6.2.

b.	Four-inch by 8-inch cylinders may be accepted in lieu of 6-inch by 12-inch cylinders at the option of the engineer of record.

c.	Specific requirements for special inspection shall be included in the research report for the anchor issued by an approved source in accordance with 17.8.2 in ACI 318, or other qualification procedures.  Where specific requirements are not provided, special inspection requirements shall be specified by the registered design professional and shall be approved by the commissioner prior to the commencement of the work.

[1704.4.1] 1705.3.1 Materials. In the absence of sufficient data or documentation providing evidence of conformance to quality standards for materials in Chapter 3 of ACI 318, the commissioner shall require testing of materials in accordance with the appropriate standards and criteria for the material in Chapters [3] 19 and 20 of ACI 318. Weldability of reinforcement, except that which conforms to ASTM A 706, shall be determined in accordance with the requirements of Section [1903.5.2] 1903.6.2.

[1704.4.2] 1705.3.2 Concrete construction. When the specified compressive strength of concrete in a column is greater than 1.4 times that specified for a floor system, the special inspections for concrete construction shall also comply with the requirements of Section [1908.2.1] 1908.1.4.

[1704.5] 1705.4 Masonry construction. Masonry construction shall be inspected and verified in accordance with the requirements of Sections [1704.5.1] 1705.4.1 through [1704.5.3] 1705.4.3, depending on the [structural occupancy] risk category of the building or structure.

Exception: Special inspections shall not be required for:

1.	[2.]	Masonry fireplaces, masonry heaters or masonry chimneys installed or constructed in accordance with Section 2111, 2112, or 2113, respectively.

2.	Alterations to existing masonry, where the quantity of replaced masonry is less than 10 square feet (0.93 m2) in any 100 square feet (9.3 m2) of wall area, when specifically exempted on the approved construction documents.

[TABLE 1704.3
REQUIRED VERIFICATION AND INSPECTION OF STEEL CONSTRUCTION

| VERIFICATION AND INSPECTION | CONTINUOUS | PERIODIC | REFERENCED STANDARDa | BC REFERENCE |
| --- | --- | --- | --- | --- |
| 1. Material verification of high-strength bolts, nuts and washers: |  |  |  |  |
| a. Identification markings to conform to ASTM standards specified in the approved construction documents. | — | X | AISC 360, Section A3.3 and applicable ASTM material specifications | — |
| b. Manufacturer’s certificate of compliance required. | — | X |  | — |
| 2. Inspection of high-strength bolting: |  |  |  |  |
| a. Snug-tight joints. | — | X Note b | AISC 360 Section M2.5 | 1704.3.3 |
| b. Pre-tensioned and slip-critical joints using turn-of-nut with matchmarking, twist-off bolt or direct tension indicator methods of installation. | — | X |  |  |
| c. Pre-tensioned and slip-critical joints using turn-of-nut without matchmarking or calibrated wrench methods of installation. | X | — |  |  |
| 3. Material verification of structural steel and cold formed steel deck: |  |  |  |  |
| a. For structural steel, identification markings to conform to AISC 360. | — | X | AISC 360, Section M5.5 | — |
| b. For other steel, identification markings to conform to ASTM standards specified in the approved construction documents. | — | — | Applicable ASTM Standards | — |
| c. Manufacturers’ certified mill test reports. | — | X | Applicable ASTM material standards |  |
| 4. Material verification of weld filler materials |  |  |  |  |
| a. Identification markings to conform to AWS specification in the approved construction documents. | — | — | AISC 360, Section A3.5 and applicable AWS A5 documents | — |
| b. Manufacturer’s certificate of compliance required. | — | — |  | — |
| 5. Inspection of welding: |  |  |  |  |
| a. Structural steel, cold-formed steel and cold-formed steel deck: | — | — | — | — |
| 1) Complete and partial penetration groove welds. | X | — | AWS D1.1 | 1704.3.1 |
| 2) Multipass fillet welds. | X | — |  |  |
| 3) Single-pass fillet welds > 5/16″. | X | — |  |  |
| 4) Plug and slot welds. | X | — |  |  |
| 5) Single-pass fillet welds ≤ 5/16″. | — | X |  |  |
| 6) Floor and roof deck welds. | — | X | AWS D1.3 | — |
| 7) Cold-formed steel welds. | — | X | AWS D1.3 | — |
| b. Reinforcing steel: | — | — | AWS D1.4 ACI 318: 3.5.2 | 1903.5.2 |
| 1) Verification of weldability of reinforcing steel other than ASTM A 706 | — | X |  |  |
| 2) Reinforcing steel-resisting flexural and axial forces in intermediate and special moment frames, and boundary elements of special reinforced concrete shear walls and shear reinforcement. | X | — |  |  |
| 3) Shear reinforcement. | X Note a | — |  |  |
| 4) Other reinforcing steel. | — | X |  |  |
| 6. Inspection of steel frame joint details for compliance with approved construction documents: |  |  | — | 1704.3.2 |
| a. Details such as bracing and stiffening. | — | X |  |  |
| b. Member locations. | — | X |  |  |
| c. Application of joint details at each connection. | — | X |  |  |

For SI: 1 inch = 25.4 mm.

a.	A minimum of 10 % of shear studs shall be verified for strength of welded connection. If failure is evident on one or more, then the strength of all shear studs shall be verified.

b.	Turn of the nut bolting shall be continuously inspected.

Exception: Periodic inspection shall be acceptable when the contractor’s procedures have been established and verified for compliance by the special inspector.]

| [TABLE 1704.3.4 REQUIRED VERIFICATION AND INSPECTION OF COLD-FORMED STEEL LIGHT-FRAME CONSTRUCTION] |
| --- |
| [Verification and inspection] | [Continuous] | [Periodic] | [Referenced Standard] | [Code Reference] |
| [1. Material Verification:] |  |  |  |  |
| [a. Verify that identification markings conform to AISI S200 and as specified in the approved construction documents.] |  | [X] | [AISI 200, Section A5.4] |  |
| [b. Verify that material is clean, straight and undamaged.] |  | [X] |  |  |
| [2. Inspection of general framing:] |  |  |  |  |
| [a. Verify that member sizes conform to the approved construction documents.] |  | [X] |  |  |
| [b. Verify that member layout conforms to the approved construction documents.] |  | [X] |  |  |
| [c. Verify that proper bearing lengths are provided in accordance with approved construction documents.] |  | [X] |  |  |
| [d. Verify that punched holes and sheared or flame cut edges of material in members are clean and free from notches and burred edges.] |  | [X] |  |  |
| [3. Inspection of framing connections and anchorages:] |  |  |  |  |
| [a. Verify that screws, bolts, and other fasteners conform to approved construction document requirements for diameter, length, quantity, spacing, edge distance, and location.] |  | [X] | [AISI S200, Section D] |  |
| [b. Verify that manufactured connectors, such as joist hangers, caps, straps, clips, ties, hold-downs, and anchors conform to approved construction document requirements for manufacturer, type, gauge, and fastener requirements.] |  | [X] | [AISI S200, Section D] |  |
| [4. Inspection of welding:] |  |  |  |  |
| [a. Inspect welds in accordance with Table 1704.3.] |  | [X] | [AWS D1.3] |  |
| [5. Bracing:] |  |  |  |  |
| [a. Verify that temporary bracing, shoring, jacks, etc., are installed, and not removed until no longer necessary, in accordance with the approved construction documents and approved erection drawings.] |  | [X] |  |  |
| [b. Verify that permanent bracing, web stiffeners, bridging, blocking, wind bracing, etc, are installed in accordance with the approved construction documents and approved erection drawings.] |  | [X] |  |  |
| [c. Where a cold-formed steel truss clear span is 60 feet (18 288 mm) or greater, the special inspector shall verify that the temporary installation restraint/bracing and the permanent individual truss member restraint/bracing are installed in accordance with the approved truss submittal package.] |  | [X] |  | [2210.3.4] |

[TABLE 1704.4
REQUIRED VERIFICATION AND INSPECTION OF CONCRETE CONSTRUCTION

| VERIFICATION AND INSPECTION | CONTINUOUS | PERIODIC | REFERENCED STANDARD | BC REFERENCE |
| --- | --- | --- | --- | --- |
| 1. Inspection of reinforcing steel, including prestressing tendons and placement. | ___ | X | ACI 318: 3.5, 7.1 – 7.7 | 1903.5, 1907.1, 1907.7, 1913.4 |
| 2. Inspection of reinforcing steel welding in accordance with Table 1704.3, Item 5b. | ___ | ___ | AWS D1.4 ACI 318: 3.5.2 | 1903.5.2 |
| 3. Inspection of bolts to be installed in concrete prior to and during placement of concrete where allowable loads have been increased or where strength design is used. | X | ___ | ACI 318: 8.1.3, 21.2.8 | 1911.5, 1912.1 |
| 4. Inspection of anchors installed in hardened concrete membersc. | — | X | ACI 318: 3.8.6, 8.1.3, 21.2.8 | 1912.1 |
| 5. Verifying use of required design mix. | ___ | X | ACI 318: Ch. 4, 5.2-5.4 | 1904, 1905.2-1905.4, 1913.3 |
| 6. At the time fresh concrete is sampled to fabricate specimens for strength tests, perform slump, unit weight, and air content tests, and determine the temperature of the concrete. Determine water content when required. | X | ___ | ASTM C 172 ASTM C 31 ACI 318: 5.6, 5.8 (Note a, b) | 1905.6, 1913.10 |
| 7. Inspection of concrete and shotcrete placement for proper application techniques. | X | ___ | ACI 318: 5.9, 5.10 | 1905.9, 1905.10, 1913.6, 1913.7, 1913.8 |
| 8. Inspection for maintenance of specified curing temperature and techniques. Monitoring of in-place temperatures per thermal protection plan when required. | ____ | X | ACI 318: 5.11-5.13 | 1905.11, 1905.13, 1913.9 |
| 9. Inspection of prestressed concrete: A. Application of prestressing forces B. Grouting of bonded prestressing tendons in the seismic-force-resisting system. | X X | ____ | ACI 318: 18.20 ACI 318: 18.18.4 | ___ |
| 10. Erection of precast concrete members. | ___ | X | ACI 318: Ch. 16 | ___ |
| 11. Verification of in-situ concrete strength, prior to stressing of tendons in post-tensioned concrete and prior to removal of shores and forms from beams and structural slabs. | ___ | X | ACI 318: 6.2 | 1906.2 |
| 12. Inspection of formwork for shape, location, and dimensions of the concrete member being formed. | ___ | X | ACI 318: 6.1.1 | 1906.2 |

a.	Standard sampling rate shall be in accordance with Section 1905.6.2.

b.	Four-inch by 8-inch cylinders may be accepted in lieu of 6-inch by 12-inch cylinders at the option of the engineer of record.]

[1704.5.1] 1705.4.1 Empirically designed masonry, glass unit masonry and masonry veneer in buildings in structural occupancy category IV. The minimum inspection program for empirically designed masonry, glass unit masonry and masonry veneer designed [by] in accordance with Section 2109, 2110, or Chapter 14, respectively, or by Chapter 5, 6 or 7 of TMS 402[/ACI 530/ASCE 5] as modified by Chapter 21 of this code, in structures classified as [structural occupancy] risk category IV, in accordance with Table 1604.5, shall comply with Table [1704.5.1] 1705.4.1.

TABLE 1704.5.1
LEVEL 1 SPECIAL INSPECTION

| INSPECTION TASK | FREQUENCY OF INSPECTION | REFERENCE FOR CRITERIA |
| --- | --- | --- |
|  | Continuous during task listed | Periodically during task listed | IBC section | ACI 530/ASCE 5/TMS 402a | ACI 530.1/ASCE 6/TMS 602a |
| 1. As masonry construction begins, the following shall be verified to ensure compliance: |  |  |  |  |  |
| Proportions of site-prepared mortar. | — | X | — | — | Art. 2.6A |
| Construction of mortar joints. |  | X |  |  | Art. 3.3B |
| Location of reinforcement, connectors, prestressing tendons and anchorage. |  | X |  |  | Art. 3.4, 3.6A |
| Prestressing technique. | — | X | — | — | Art. 3.6B |
| Grade and size of prestressing tendons and anchorages. | — | X | — | — | Art. 2.4B, 2.4H |
| 2. The inspection program shall verify: |  |  |  |  |  |
| Size and location of structural elements. | — | X | — | — | Art. 3.3G |
| Type, size and location of anchors, including other details of anchorage of masonry to structural members, frames or other construction. | — | X | — | Sec. 4.3.1.6, 2.1.4, 3.1.6 | — |
| Specified size, grade and type of reinforcement. | — | X | — | Sec. 1.12 | Art. 2.4, 3.4 |
| Welding of reinforcing bars. | X | — | — | Sec. 2.1.10.6.2, 3.2.3.4(b) | — |
| Protection of masonry during cold weather (temperature below 40°F) or hot weather (temperature above 90°F). | — | X | Sec. 2104.3, 2104.4 | — | Art. 1.8C, 1.8D |
| f. Application and measurement of prestressing force. | — | X | — | — | Art. 3.6B |
| 3. Prior to grouting, the following shall be verified to ensure compliance: |  |  |  |  |  |
| Grout space is clean. | — | X | — | — | Art. 3.2D |
| Placement of reinforcement and connectors and prestressing tendons and anchorages. |  | X |  | Sec. 1.12 | Art. 3.4 |
| Proportions of site-prepared grout and prestressing grout for bonded tendons. |  | X |  | — | Art. 2.6B |
| Construction of mortar joints. |  | X |  | — | Art. 3.3B |
| 4. Grout placement shall be verified to ensure compliance with code and construction document provisions. | X | — | — | — | Art 3.5 |
| a. Grouting of prestressing bonded tendons. | X | — | — | — | Art. 3.6C |
| 5. Preparation of any required grout specimens, mortar specimens and/or prisms shall be observed. | X | — | Sec. 2105.2.2, 2105.3 | — | Art. 1.4 |
| 6. Compliance with required inspection provisions of the construction documents and the approved submittals shall be verified. | — | X | — | — | Art. 1.5 |

For SI: °C = (°F - 32)/1.8.

a.	The specific standards referenced are those listed in Chapter 35.]

| TABLE 1705.4.1 LEVEL B REQUIRED SPECIAL INSPECTIONS AND TESTS OF MASONRY CONSTRUCTION |
| --- |
| MINIMUM TESTS |
| Verification of Slump flow and Visual Stability Index (VSI) as delivered to the project site in accordance with TMS 602 Article 1.5.B.1.b.3 for self-Consolidating grout. |
| Verification of f’m and f’AAC in accordance with TMS 602 Article 1.4 B prior to construction, except where specifically exempted by this Code. |
| MINIMUM SPECIAL INSPECTION |
| TYPE | FREQUENCY | REFERENCE FOR CRITERIA |
|  | CONTINUOUS SPECIAL INSPECTION | PERIODIC SPECIAL INSPECTION | BC SECTION | TMS 402 | TMS 602 |
| 1. Verify compliance with required inspection provisions of the construction documents and the approved submittals. | — | X | — | — | Art. 1.5 |
| 2. As masonry construction begins, the following shall be verified to ensure compliance: |
| a. Proportions of site-prepared mortar. | — | X | — | — | Art. 2.6A |
| b. Construction of mortar joints. | — | X | — | — | Art. 3.3B |
| c. Grade and size of prestressing tendons and anchorages. | — | X | — | — | Art. 2.4B, 2.4H |
| d. Location of reinforcement, connectors, prestressing tendons and anchorages. | — | X | — | — | Art. 3.4, 3.6A |
| e. Prestressing technique. | — | X | — | — | Art. 3.6B |
| 3. Prior to grouting, the following shall be verified to ensure compliance: |
| a. Grout space. | — | X | — | — | Art. 3.2D |
| b. Grade, type, and size of reinforcement and anchor bolts, and prestressing tendons and anchorages. | — | X | — | — | — |
| c. Placement of reinforcement, connectors, and prestressing tendons and anchorages. | — | X | — | Sec. 1.13 | Art. 3.4 |
| d. Proportions of site-prepared grout and prestressing grout for bonded tendons. | — | X | — | — | Art. 2.6B |
| e. Construction of mortar joints. | — | X | — | — | Art. 3.3B |
| 4. Verify during construction: |
| a. Size and location of structural elements. | — | X | — | — | Art. 3.3F |
| b. Type, size and location of anchors, including other details of anchorage of masonry to structural members, frames or other construction. | — | X | — | Sec. 1.2.1(e), 14.4.3 | — |
| c. Welding of reinforcement. | X | — | — | Sec. 1.2.1(g), 6.1.6.1.2, 6.1.7.3, 13.7 | — |
| d. Preparation, construction and protection of masonry during cold weather (temperature below 40°F) or hot weather (temperature above 90°F). | — | X | Sec. 2104.2, 2104.3, | Sec 3.1.3 | Art. 1.8C, 1.8D |
| e. Preparation of any required grout specimens, mortar specimens and/or prisms shall be observed. | — | X | — | Art. 3.1.3 | Art. 1.4 |
| f. Application and measurement of prestressing force. | X | — | — | — | Art. 3.6B |
| g. Placement of grout and prestressing grout for bonded tendons is in compliance. | X | — | — | — | Art. 3.5, 3.6 C |
| h. Placement of AAC masonry units and construction of thin-bed mortar joints. | Xb | Xc | — | — | Art. 3.3 B.9, 3.3 F.1.b |
| i. Grout space is clean. | — | X | — | — | Art. 3.2D |
| j. Placement of reinforcement and connectors, and prestressing tendons and anchorages. | — | X | — | Sec. 6.1.3 and 10.8 | Art. 3.4 |
| k. Proportions of site-prepared grout and prestressing grout for bonded tendons. | — | X | — | — | Art. 2.6B |
| l. Construction of mortar joints. | — | X | — | — | Art. 3.3B |
| 5. Observe preparation of grout specimen, mortar specimen, and/or prisms. | — | X | — | — | Art: 1.4B2a3, 1.4B2b3, 1.4B2c3, 1.4B3, 1.4B4, 2.1A |

For SI: °C = [(°F) - 32]/1.8.

- The specific standards referenced are those listed in Chapter 35.

b.	Required for the first 5,000 square feet of AAC masonry.

c.	Required after the first 5,000 square feet of AAC masonry.

[1704.5.2] 1705.4.2 Masonry in buildings [less than] three stories or less in height in [structural occupancy] risk category I, II, or III. The minimum special inspection program for structures classified as risk categories I, II, or III, in accordance with Table 1604.5, which are three stories or less in height, shall comply with Table [1704.5.1] 1705.4.1.

| TABLE 1704.5.1 LEVEL 1 REQUIRED VERIFICATION AND INSPECTION OF MASONRY CONSTRUCTION] |
| --- |
| [VERIFICATION AND INSPECTION] | [FREQUENCY OF INSPECTION] | [REFERENCE FOR CRITERIA] |
|  | [Continuous] | [Periodic] | [BC Sectio n] | [TMS 402/ACI 530/ASCE 5a] | [TMS 602/ACI 530.1/ASCE 6a] |
| [1. Compliance with required inspection provisions of the construction documents and the approved submittals shall be verified.] | [—] | [X] | [—] | [—] | [Art. 1.5] |
| [2. Verification of f’m and f’AAC prior to construction except where specifically exempted by this code.] | [—] | [X] | [—] | [—] | [Art. 1.4B] |
| [3. Verification of slump flow and VSI as delivered to the site for self-consolidating grout.] | [X] | [—] | [—] | [—] | [Art. 1.5B.1.b.3] |
| [4. As masonry construction begins, the following shall be verified to ensure compliance:] |
| [a. Proportions of site-prepared mortar.] | [—] | [X] | [—] | [—] | [Art. 2.6A] |
| [b. Construction of mortar joints.] | [—] | [X] | [—] | [—] | [Art. 3.3B] |
| [c. Location of reinforcement, connectors, prestressing tendons and anchorages.] | [—] | [X] | [—] | [—] | [Art. 3.4, 3.6A] |
| [d. Prestressing technique.] | [—] | [X] | [—] | [—] | [Art. 3.6B] |
| [e. Grade and size of prestressing tendons and anchorages.] | [—] | [X] | [—] | [—] | [Art. 2.4B, 2.4H] |
| [5. During construction the inspection program shall verify:] |
| [a. Size and location of structural elements.] | [—] | [X] | [—] | [—] | [Art. 3.3F] |
| [b. Type, size and location of anchors, including other details of anchorage of masonry to structural members, frames or other construction.] | [—] | [X] | [—] | [Sec. 1.2.2(e), 1.16.1] | [—] |
| [c. Specified size, grade and type of reinforcement, anchor bolts, prestressing tendons and anchorages.] | [—] | [X] | [—] | [Sec. 1.15] | [Art. 2.4, 3.4] |
| [d. Welding of reinforcing bars.] | [X] | [—] | [—] | [Sec. 2.1.9.7.2, 3.3.3.4(b)] | [—] |
| [e. Preparation, construction and protection of masonry during cold weather (temperature below 40°F) or hot weather (temperature above 90°F).] | [—] | [X] | [Sec. 2104.3, 2104.4] | [—] | [Art. 1.8C, 1.8D] |
| [f. Application and measurement of prestressing force.] | [X] | [—] | [—] | [—] | [Art. 3.6B] |
| [6. Prior to grouting, the following shall be verified to ensure compliance:] |
| [a. Grout space is clean.] | [—] | [X] | [—] | [—] | [Art. 3.2D] |
| [b. Placement of reinforcement and connectors, and prestressing tendons and anchorages.] | [—] | [X] | [—] | [Sec. 1.13] | [Art. 3.4] |
| [c. Proportions of site-prepared grout and prestressing grout for bonded tendons.] | [—] | [X] | [—] | [—] | [Art. 2.6B] |
| [d. Construction of mortar joints.] | [—] | [X] | [—] | [—] | [Art. 3.3B] |
| [7. Grout placement shall be verified to ensure compliance:] | [X] | [—] | [—] | [—] | [Art. 3.5] |
| [a. Grouting of prestressing bonded tendons.] | [X] | [—] | [—] | [—] | [Art. 3.6C] |
| [8. Preparation of any required grout specimens, mortar specimens and/or prisms shall be observed.] | [—] | [X] | [Sec. 2105.2.2, 2105.3] | [—] | [Art. 1.4] |

[For SI: °C = [(°F) - 32]/1.8.]

[a. The specific standards referenced are those listed in Chapter 35.]

[1704.5.3] 1705.4.3 Masonry in buildings greater than three stories [or more] in height, and engineered masonry in [structural occupancy] risk category IV. The minimum special inspection program for masonry designed [by] in accordance with Section 2107 or 2108, or by chapters other than Chapters 5, 6 or 7 of TMS 402[/ACI 530/ASCE 5] as modified by Chapter 21 of this code, in structures classified as [structural occupancy] risk category IV, in accordance with Table 1604.5, and masonry in buildings [more] greater than three stories in height, shall comply with Table [1704.5.3] 1705.4.3.

Exception: Alterations to existing masonry walls where the quantity of masonry involved in any one given location does not exceed 50 contiguous square feet (4.64 m2) shall be permitted to be subject to level 1 special inspection in accordance with Table [1704.5.1] 1705.4.1 when specifically identified as such on the approved construction documents by the registered design professional of record.

| [TABLE 1704.5.3 LEVEL 2 SPECIAL INSPECTION |
| --- |
| INSPECTION TASK | FREQUENCY OF INSPECTION | REFERENCE FOR CRITERIA |
|  | Continuous during task listed | Periodically during task listed | BC section | ACI 530/ ASCE 5/TMS 402 | ACI 530.1/ASCE 6/TMS 602 |
| 1. From the beginning of masonry construction, the following shall be verified to ensure compliance: |  |  |  |  |  |
| Proportions of site-prepared mortar, grout and prestressing grout for bonded tendons. | — | X | — | — | Art. 2.6A |
| Placement of masonry units and construction of mortar joints. | — | X | — | — | Art. 3.3B |
| Placement of reinforcement, connectors and prestressing tendons and anchorages. | — | X | — | Sec. 1.12 | Art. 3.4, 3.6A |
| Grout space prior to grouting. | X | — | — | — | Art. 3.2D |
| Placement of grout. | X | — | — | — | Art. 3.5 |
| Placement of prestressing grout. | X | — | — | — | Art. 3.6C |
| 2. The inspection program shall verify: |  |  |  |  |  |
| Size and location of structural elements. | — | X | — | — | Art. 3.3G |
| Type, size and location of anchors, including other details of anchorage of masonry to structural members, frames or other construction. | X | — | — | Sec. 1.2.2(e), 2.1.4, 3.1.6 | — |
| Specified size, grade and type of reinforcement. |  | X | — | Sec. 1.12 | Art. 2.4, 3.4 |
| Welding reinforcement. | X | — | — | Sec. 2.1.10.6.2, 3.2.3.4(b) | — |
| Protection of masonry during cold weather (temperature below 40°F) or hot weather (temperature above 90°F). | — | X | Sec. 2104.3, 2104.4 | — |  |
| Application and measurement of prestressing force. | X | — | — | — | Art 3.6B |
| 3. Preparation of any required grout specimens, mortar specimens and/or prisms shall be observed. | X | — | Sec. 2105.2.2, 2105.3 | — | Art 1.4 |
| 4. Compliance with required inspection provisions of the construction documents and the approved submittals shall be verified. | — | X | — | — | Art 1.5] |
| TABLE 1705.4.3 LEVEL C REQUIRED SPECIAL INSPECTIONS AND TESTS OF MASONRY CONSTRUCTION |
| MINIMUM TESTS |
| Verification of f’m and f’AAC in accordance with TMS 602 Article 1.4 B prior to construction and every 5,000 sq. ft. during construction. |
| Verification of proportions of materials in premixed or preblended mortar, prestressing grout, and grout other than self-consolidating grout, as delivered to the project site in accordance with TMS 602 Article 1.5B. |
| Verification of Slump flow and Visual Stability Index (VSI) as delivered to the project site in accordance with TMS 602 Article 1.5.B.1.b.3 for self-consolidating grout. |
| MINIMUM SPECIAL INSPECTION |
| TYPE | Continuous Special Inspection | Periodic Special Inspection | REFERENCE FOR CRITERIA |
|  |  |  | BC Section | TMS 402 | TMS 602a |
| 1. Verify compliance with required inspection provisions of the construction documents and the approved submittals. | — | X | — | — | Art. 1.5 |
| 2. Verify that the following are in compliance: |
| a. Proportions of site-prepared mortar, grout and prestressing grout for bonded tendons. | — | X | — | — | Art. 2.6 A |
| b. Grade, type, and size of reinforcement and anchor bolts, and prestressing grout for bonded tendons. | — |  |  | Sec. 6.1.2, 10.8 | Art. 2.4, 3.4 |
| c. Placement of masonry units and construction of mortar joints. | X | X | — | — | Art. 3.3 B |
| d. Placement of reinforcement, connectors and prestressing tendons and anchorages. | — | X | — | Sec. 6.1.2, 10.8 | Art. 3.4, 3.6 A |
| e. Grout space prior to grouting. | X | — | — | — | Art. 3.2 D |
| f. Placement of grout and prestressing grout for bonded tendons. | X | — | — | — | Art. 3.5 |
| g. Placement of prestressing grout. | X | — | — | — | Art. 3.6 C |
| h. Size and location of structural elements. | — | X | — | — | Art. 3.3 F |
| i. Type, size and location of anchors, including other details of anchorage of masonry to structural members, frames or other construction. | X | — | — | Sec. 1.2.1(e), 14.4.3 | — |
| j. Welding of reinforcement. | X | — | — | Sec. 1.2.1(g), 6.1.6.1.2, 6.1.7.3, 13.7 | — |
| k. Preparation, construction and protection of masonry during cold weather (temperature below 40°F) or hot weather (temperature above 90°F). | — | X | Sec. 2104.2, 2104.3 | — | Art. 1.8 C, 1.8 D |
| l. Application and measurement of prestressing force. | X | — | — | — | Art. 3.6 B |
| m. Placement of AAC masonry units and construction of thin-bed mortar joints. | X | — | — | — | Art. 3.3 B.9, 3.3 F.1.b |
| n. Properties of thin-bed mortar for AAC masonry. | X | — | — | — | Art. 2.1 C.1 |
| 6. Observe preparation of grout specimens, mortar specimens, and/or prisms. | X | — | — | Sec. 3.1.3 | Art. 1.4 |

For SI: °C = [(°F) - 32]/1.8, 1 square foot = 0.0929 m2.

a.	The specific standards referenced are those listed in Chapter 35.

[1704.6] 1705.5 Wood construction. Special inspections of site-built assemblies shall be in accordance with Sections 1705.5.1 through 1705.5.4.  Special inspections of the fabrication process of prefabricated wood structural elements and assemblies shall be in accordance with Section [1704.2] 1705.10. [Special inspections of site-built assemblies shall be in accordance with Section 1704.1.]

[1704.6.1] 1705.5.1 High-load diaphragms. High-load diaphragms designed in accordance with Table [2306.2.1(2)] 2306.2(2) shall be [installed with] subject to special inspections as indicated in Section 1704.1. The special inspector shall inspect the wood structural panel sheathing to ascertain whether it is of the grade and thickness shown on the approved construction documents. Additionally, the special inspector must verify the nominal size of framing members at adjoining panel edges, the nail or staple diameter and length, the number of fastener lines and that the spacing between fasteners in each line and at edge margins agrees with the approved construction documents.

[1704.6.2] 1705.5.2 Metal-plate-connected wood trusses. In addition to the requirements of Section 1704.1, metal-plate-connected wood trusses shall be subject to special inspection in accordance with Section [1704.6.2.1] 1705.5.2.1 and [1704.6.2.2] 1705.5.2.2.

| [TABLE 1704.5.3 LEVEL 2 REQUIRED VERIFICATION AND INSPECTION OF MASONRY CONSTRUCTION] |
| --- |
| [VERIFICATION AND INSPECTION] | [Continuous] | [Periodic] | [REFERENCE FOR CRITERIA] |
|  |  |  | [BC Section] | [TMS 402/ACI 530/ASCE 5a] | [TMS 602/ACI 530.1/ASCE 6a] |
| [1. Compliance with required inspection provisions of the construction documents and the approved submittals.] | [—] | [X] | [—] | [—] | [Art. 1.5] |
| [2. Verification of f’m and f’AAC prior to construction and for every 5,000 square feet during construction.] | [—] | [X] | [—] | [—] | [Art. 1.4B] |
| [3. Verification of proportions of materials in premixed or preblended mortar and grout as delivered to the site.] | [—] | [X] | [—] | [—] | [Art. 1.5B] |
| [4. Verification of slump flow and VSI as delivered to the site for self-consolidating grout.] | [X] | [—] | [—] | [—] | [Art. 1.5B.1.b.3] |
| [5. The following shall be verified to ensure compliance:] |
| [a. Proportions of site-prepared mortar, grout and prestressing grout for bonded tendons.] | [—] | [X] | [—] | [—] | [Art. 2.6A] |
| [b. Placement of masonry units and construction of mortar joints.] | [—] | [X] | [—] | [—] | [Art. 3.3B] |
| [c. Placement of reinforcement, connectors and prestressing tendons and anchorages.] | [—] | [X] | [—] | [Sec. 1.15] | [Art. 3.4, 3.6A] |
| [d. Grout space prior to grout.] | [X] | [—] | [—] | [—] | [Art. 3.2D] |
| [e. Placement of grout.] | [X] | [—] | [—] | [—] | [Art. 3.5] |
| [f. Placement of prestressing grout.] | [X] | [—] | [—] | [—] | [Art. 3.6C] |
| [g. Size and location of structural elements.] | [—] | [X] | [—] | [—] | [Art. 3.3F] |
| [h. Type, size and location of anchors, including other details of anchorage of masonry to structural members, frames or other construction.] | [X] | [—] | [—] | [Sec. 1.2.2(e), 1.16.1] | [—] |
| [i. Specified size, grade and type of reinforcement, anchor bolts, prestressing tendons and anchorages.] | [—] | [X] | [—] | [Sec. 1.15] | [Art. 2.4, 3.4] |
| [j. Welding of reinforcing bars.] | [X] | [—] | [—] | [Sec. 2.1.9.7.2, 3.3.3.4 (b)] | [—] |
| [k. Preparation, construction and protection of masonry during cold weather (temperature below 40°F) or hot weather (temperature above 90°F).] | [—] | [X] | [Sec. 2104.3, 2104.4] | [—] | [Art. 1.8C, 1.8D] |
| [l. Application and measurement of prestressing force.] | [X] | [—] | [—] | [—] | [Art. 3.6B] |
| [6. Preparation of any required grout specimens and/or prisms shall be observed.] | [X] | [—] | [Sec. 2105.2.2, 2105.3] | [—] | [Art. 1.4] |

[For SI: °C = [(°F) - 32]/1.8, 1 square foot = 0.0929m2.]

[a. The specific standards referenced are those listed in Chapter 35.]

[1704.6.2.1] 1705.5.2.1 Erection. The use of all metal-plate-connected wood trusses shall be subject to special inspection for compliance with the approved construction documents, the requirements of Sections 1704.1, and the following:

- All installed materials shall be clean, straight and otherwise undamaged. Members and parts shall not be stretched, bent, or otherwise distorted unless such forming is in the integral part of the design. The special inspector shall ensure that damaged members are not used for construction.

- Profiles of members used structurally shall conform to the dimensions specified in the approved construction documents. The installation shall be inspected for compliance with the approved construction documents regarding locations, positions, beam separators, bearing surfaces, fasteners, screws, bolts and bracing, as applicable.

- Temporary bracing, shoring, jacks, etc., shall not be removed until the special inspector determines that [they are no longer needed] the construction conforms with the approved construction document.

- Where prefabricated metal-plate-connected wood trusses are utilized, such prefabricated wood structural elements and assemblies shall also comply with Section [1704.2] 1705.10. Where any metal-plate connectors are utilized in site-built assemblies, such connections and assemblies shall be subject to special inspection for compliance with the requirements of the approved construction documents and manufacturers’ instructions.

[1704.6.2.2] 1705.5.2.2 Metal-plate-connected wood trusses spanning 60 feet or greater. Where a truss clear span is 60 feet (18 288 mm) or greater, the special inspector shall verify that the temporary installation restraint/bracing and the permanent individual truss member restraint/bracing are installed in accordance with the approved truss submittal package.

[1704.6.3] 1705.5.3 Prefabricated wood I-joists. The fabrication of prefabricated wood I-joists shall be subject to special inspections in accordance with Section [1704.2] 1705.10 and the requirements of Section 2303.1.2.

[1704.6.3.1] 1705.5.3.1 Erection. The erection of prefabricated wood I-joists shall be subject to special inspection for compliance with the approved construction documents, the requirements of Sections 1704.1, and the following:

- All installed materials shall be clean, straight and otherwise undamaged. Members and parts shall not be stretched, bent, or otherwise distorted unless such forming is in the integral part of the design. The special inspector shall ensure that damaged members are not used for construction.

- Profiles of members used structurally shall conform to the dimensions specified in the approved construction documents. The installation shall be inspected for compliance with the approved construction documents regarding locations, positions, beam separators, bearing surfaces, fasteners, screws, bolts and bracing, as applicable.

- The size, location, and number of penetrations shall be inspected for compliance with the approved construction documents and manufacturers’ instructions.

- Temporary bracing, shoring, jacks, etc., shall not be removed until the special inspector determines that they are no longer needed.

[1704.6.4] 1705.5.4 Other structural wood construction. All other structural wood construction shall be subject to progress inspections for the structural frame to the extent required by Section 110.3.3.

1705.5.5 Special inspection for seismic resistance. For the seismic force-resisting systems of structures assigned to Seismic Design Category C or D:

1.	Continuous special inspection shall be required during field gluing operations of elements of the seismic force resisting system.

2.	Periodic special inspection shall be required for nailing, bolting, anchoring and of other elements of the seismic force-resisting system, including wood shear walls, wood diaphragms, drag struts, braces, shear panels and hold-downs.

Exception:

1.	Special inspections are not required for wood shear walls, shear panels and diaphragms, including nailing, bolting, anchoring and other fastening to other elements of the seismic force-resisting system, where the fastener spacing of the sheathing is more than 4 inches (102 mm) on center.

2.	Where adhesive anchors require continuous special inspection elsewhere in this code, continuous special inspection shall be provided.

1705.5.6 Type IV construction. Special inspections of Type IV construction utilizing cross-laminated timber or structural composite lumber elements shall be in accordance with Table 1705.5.6.

| TABLE 1705.5.6 REQUIRED SPECIAL INSPECTIONS OF Type IV construction utilizing cross-laminated timber or structural composite lumber |
| --- |
| Type | Continuous Special Inspection | Periodic Special Inspection | Referenced Standard | Code References |
| 1. Inspection of anchorage and connections of mass timber construction to timber deep foundation systems | — | X |  | 1705.7, 2308.3, 2304.10 |
| 2. Inspect erection of mass timber, including material verification | — | X | PRG-320, ASTM D5456 | 2303.1.4, 2303.1.10 |
| 3. Inspection of connections where installation methods are required to meet design loads |  |  | NDS 11-14 ANSI/ASME Standard B18.2.1, B18.6.1 As per connection manufacturer’s installation instructions | 2304.10, 2304.11.1.1 to 2304.11.4 |
| 3.1. Threaded fasteners | — | X |  |  |
| 3.1.1. Verify use of proper installation equipment |  |  |  |  |
| 3.1.2. Verify use of pre-drilled holes where required |  |  |  |  |
| 3.1.3. Inspect screws, including diameter, length, head type, spacing, installation angle, and depth |  |  |  |  |
| 3.2. Adhesive anchors installed in horizontal or upwardly inclined orientation to resist sustained tension loads | X | — |  |  |
| 3.3. Adhesive anchors not defined in 3.2 | — | X |  |  |
| 3.4. Bolted connections | — | X |  |  |
| 3.5. Concealed connections | — | X |  |  |
| 3.6. Other fastener types | — | X |  |  |
| 4. Inspection of connections where installation methods are required to meet the fire resistance design in 2304.10.8 | — | X | NDS 16.3 |  |

[1704.7] 1705.6 Subsurface conditions. The special inspections for existing subsurface conditions, fill placement [and], load-bearing requirements, subsurface investigations, borings and test pits shall be performed in accordance with [Sections 1704.7.1 through 1704.7.3] this section and Table 1705.6. The approved geotechnical report [required by Section 1802.2,] and construction documents, as applicable, shall be used to determine compliance.  Special inspection reports of borings and/or test pits shall be in accordance with ASTM D 1586, ASTM D 1587 and Section 1803.5.

| TABLE 1705.6 REQUIRED SPECIAL INSPECTIONS OF SUBSURFACE CONDITIONS |
| --- |
| TYPE | CONTINUOUS SPECIAL INSPECTION | PERIODIC SPECIAL INSPECTION |
| 1. Special inspection of subsurface investigations, borings and test pits. Boring and test pit operations, and alternative investigation methods, shall be subject to continuous special inspection to verify compliance with Section 1803. Soil sample recovery operations for test pits shall be subject to continuous special inspection to verify compliance with Section 1803. Exceptions: 1. Cone penetrometer testing used as an alternative investigation method per 1802.5.2 shall be subject to periodic special inspection. 2. Existing boring, test pit and alternative investigation records that have been deemed acceptable to the commissioner in accordance with Section 1803.4.2 are not subject to special inspection. | X | — |
| 2. During fill placement. During placement and compaction of the fill material, the special inspector shall determine that the material being used and the maximum lift thickness comply with the approved geotechnical report, as specified in Section 1804.5. | X | — |
| 3. Evaluation of in-place density. The special inspector shall determine that the in-place dry density of the compacted fill complies with the approved construction documents. | X | — |
| 4. Subgrade inspection. Immediately prior to placement of each and every footing, foundation, fill or other supporting materials, the special inspector shall determine that the site has been prepared and is in accordance with the approved geotechnical report. | — | X |

[1704.7.1 Subgrade inspection. Immediately prior to placement of the footings, foundations, fill or other supporting materials the special inspector shall determine that the site has been prepared and is in accordance with the approved geotechnical report.]

[1704.7.2 During fill placement. During placement and compaction of the fill material, the special inspector shall determine that the material being used and the maximum lift thickness comply with the approved geotechnical report, as specified in Section 1803.5.]

[1704.7.3 Evaluation of in-place density. The special inspector shall determine, at the approved frequency, that the in-place dry density of the compacted fill complies with the approved geotechnical report.]

[1704.7.4 Special inspection of subsurface investigations, borings and test pits. Boring and test pit operations shall be subject to continuous special inspection to verify compliance with Section 1802. Soil sample recovery operations for test pits shall be subject to continuous special inspection to verify compliance with Section 1802.]

[Exception: Existing boring, test pit and subsurface investigation records that have been deemed acceptable to the commissioner in accordance with Section 1802.4.2 are not subject to special inspection.]

[1704.7.4.1 Boring and/or test pit report. The special inspector shall prepare a written report that includes statements attesting to the following: that borings were performed in accordance with the procedures established in Section 1802.5, that 100 percent of the borings and test pits were witnessed directly by the designated special inspection agency, the identification of those borings, the name of the individual special inspectors that witnessed the borings and/or test pits; confirmation that the borings and/or test pits were made and carried to the depths indicated; that to the best of the special inspector’s knowledge and belief, the description and classification of the soils are a true description of the samples recovered from the respective borings and/or test pits: that such samples were recovered at the levels indicated; and that the boring and/or test pit work progressed in such manner that the samples recovered are reasonably representative of the subsurface conditions.]

[1704.8] 1705.7 Deep foundation elements. [The installation] Installation and testing of deep foundation elements shall be subject to special inspections as specified in Table 1705.7. The approved geotechnical report and construction documents prepared by the registered design professionals shall be used to determine compliance. A special inspector shall be present [continuously] during the installation and testing of each deep foundation element [; and also shall be present continuously for all required testing of deep foundation elements. The special inspection agency shall submit to the commissioner records of the installation of each deep foundation element, and where testing is required, the special inspection agency shall also submit records of the testing. The frequency shall be in accordance with the frequency specified in Table 1705.7, Table 1705.7.1, Table 1705.7.2 and Table 1705.7.3, as applicable. Submittal of records of special inspections required by this section shall be in accordance with Section 1705.7.5.

| TABLE 1705.7 REQUIRED SPECIAL INSPECTIONS AND TESTS OF DEEP FOUNDATION ELEMENTS |
| --- |
| INSTALLATION | CONTINUOUS SPECIAL INSPECTION | PERIODIC SPECIAL INSPECTION |
| 1. Verify the identifying designation of the deep foundation element and record the date of installation, including the start and end times. | X | — |
| 2. Verify the size, material, and allowable capacity as specified in the construction documents. | X | — |
| 3. Record the elevation of the minimum required depth of penetration and record the final tip elevation and butt elevation. | X | — |
| 4. Record the elevation of splices and note whether or not the splices were installed and located in compliance with the construction documents. | X | — |
| LOAD TEST |  |  |
| 5. For load test requiring a load or reaction frame, inspect the construction of the load or reaction frame. Record the results of the inspection and note whether or not the frame complies with the construction documents prepared by the registered design professional. | — | X |
| 6. Record the identifying designation for the element being tested, and the date of the testing, including the start and end time. | X | — |
| 7. Record the method of performing the test, including the equipment being used, as well as the test results, noting whether or not the method of testing and the test results comply with the requirements of Sections 1810, 1811, and 1812 and the construction documents. | X | — |

[1704.8.1] 1705.7.1 [Records of] Driven and vibrated deep foundation [element installation] elements. The [record of] installation [of each] and testing of driven and vibrated deep foundation [element] elements shall [include, but not be limited to, the following:] be subject to special inspections as specified in Table 1705.7 and Table 1705.7.1.

| TABLE 1705.7.1 REQUIRED SPECIAL INSPECTIONS OF DRIVEN AND VIBRATED DEEP FOUNDATION ELEMENTS |
| --- |
| INSTALLATION | CONTINUOUS SPECIAL INSPECTION | PERIODIC SPECIAL INSPECTION |
| 1. For driven deep foundation elements, record the type and size of hammer and record the number of blows per foot of penetration from the start of driving until the final blow count required by the construction documents is reached. | X | — |
| 2. For vibrated deep foundation elements, record the equipment and method used for installation and record the time for each foot of penetration from the start of installation until completion. | X | — |

1705.7.2 Drilled deep foundation elements. The installation and testing of drilled deep foundation elements shall be subject to special inspections as specified in Table 1705.7 and Table 1705.7.2.

| TABLE 1705.7.2 REQUIRED SPECIAL INSPECTIONS OF DRILLED DEEP FOUNDATION ELEMENTS |
| --- |
| INSTALLATION | CONTINUOUS SPECIAL INSPECTION | PERIODIC SPECIAL INSPECTION |
| 1. Record the equipment and method used for installation and record the time for each foot of penetration from the start of installation until completion. | X | — |
| 2. For deep foundation elements requiring a rock socket: 2.1. Record the equipment and method of drilling the rock socket. Record the top elevation and bottom elevation of rock socket, as well as the time for each foot of drilling the rock socket. 2.2. Inspect the rock socket to verify rock quality as required by Section 1812 and the construction documents. Record the results of the inspection and note whether or not the rock socket complies with the requirements of Section 1812. | X | — |

[1.	The identifying designation of the deep foundation element and the date of installation, including the start and end times.]

[2.	The size, material, and allowable capacity as specified in the contract drawings.]

[3.	The elevation of the minimum required depth of penetration, and the final tip elevation and butt elevation.]

[4.	For driven piles, record the type and size of hammer and record the number of blows per foot of penetration from the start of driving until the final blow count required by the contract drawings is reached.]

[5.	For driven or drilled piles filled with concrete or grout:]

[5.1.	Prior to placing concrete, inspect the inside of the pile for alignment and damage. Record the results of the inspection, noting whether or not the pile is in compliance with Sections 1808, 1809, and 1810, and contract requirements.]

[5.2	Witness the placement of concrete or grout inside the deep foundation element, and record the volume placed. Note the date and time of placement, and whether or not the concrete or grout was placed in compliance with Sections 1808, 1809, and 1810, and contract requirements.]

[6.	For drilled or vibrated deep foundation elements, record the equipment and method used for installation and record the time for each foot of penetration from the start of installation until completion.]

[7.	For deep foundation elements requiring a rock socket:]

[7.1.	Record the equipment and method of drilling the rock socket. Record the top elevation and bottom elevation of the rock socket, as well as the time for each foot of drilling the rock socket.]

[7.2.	Inspect the rock socket as required by contract drawings. Record the results of the inspection and note whether or not the rock socket complies with the requirements of Sections 1808, 1809, and 1810, and the contract requirements.]

[8.	Record the elevation of splices and note whether or not the splices were installed and located in compliance with the requirements of Sections 1808, 1809, and 1810, and the contract requirements.]

[9.	For methods of deep foundation element installation not covered by Items 1 through 8 above, perform additional inspection as required by the contract drawings and record the results noting whether or not the deep foundation elements comply with the requirements of Sections 1808, 1809, and 1810, and the contract requirements.]

[1704.8.2 Records of testing of deep foundations elements. The records of testing of deep foundation elements shall include but not be limited to the following:]

[1.	For load test requiring a load or reaction frame, inspect the construction of the load or reaction frame. Record the results of the inspection and note whether or not the frame complies with the design drawings for the frame signed and sealed by a registered design professional.]

[2.	The identifying designation for the element being tested, and the date of the testing, including the start and end time.]

[3.	Record the method of performing the test, including the equipment being used, as well as the test results, noting whether or not the method of testing and the test results comply with the requirements of Sections 1808, 1809, and 1810, and the contract requirements.]

1705.7.3 Cast-in-place deep foundation elements. The installation and testing of driven or drilled cast-in-place deep foundation elements shall be subject to special inspections as specified in Table 1705.7, Table 1705.7.1, Table 1705.7.2 and Table 1705.7.3, as applicable.

| TABLE 1705.7.3 REQUIRED SPECIAL INSPECTIONS OF DRIVEN OR DRILLED CAST-IN-PLACE DEEP FOUNDATION ELEMENTS |
| --- |
| INSTALLATION | CONTINUOUS SPECIAL INSPECTION | PERIODIC SPECIAL INSPECTION |
| 1. Prior to placing concrete, inspect the inside of the pile for alignment and damage. Record the results of the inspection, noting whether or not the pile is in compliance with Section 1812 and the construction documents. | X | — |
| 2. Witness the placement of concrete or grout inside the deep foundation element, and record the volume placed. Note the date and time of placement, and whether or not the concrete or grout was placed in compliance with Section 1812 and the construction documents. | X | — |

[1704.8.3] 1705.7.4 Additional inspection. For methods of deep foundation element installation not covered in Section 1705.7, perform an additional inspection as required by the approved construction documents and record the results noting whether or not the deep foundation element installation complies with the requirements of Sections 1810, 1811, and 1812, and the construction documents. For steel deep foundation elements, perform an additional [inspections] inspection in accordance with Section [1704.3.1] 1705.2. For concrete or grout deep foundation elements, and concrete or grout-filled deep foundation elements, perform an additional inspection in accordance with Section [1704.4.1] 1705.3. For concrete or grout, and concrete or grout filled deep foundation elements, perform an additional inspection in accordance with Section [1704.4.1] 1705.3.

[1704.8.4] 1705.7.5 Submittal of records of [installation and testing] special inspections. The special [inspector’s submittal of installation] inspection agency shall submit to the commissioner records [for] of the inspection of the installation of each deep foundation element[, and]. The special inspection agency shall also submit records of testing [records when required,] of deep foundation elements at the request of the commissioner. The submittal shall include the following:

- A location plan showing the designation identifying each deep foundation element, and the [location] locations of required testing, where applicable.

- A written summary of the installation and testing performed, signed by the special inspector, including a statement verifying that all installation and testing [complied with the comply] complies with the requirements of Sections [1808, 1809, and 1810] 1810, 1811, and 1812, and the [contract requirements] construction documents. The special inspector shall document the type and results of tests, and information of the technician and testing agency peroforming the test.

1705.8 Prestressed rock and soil anchors installation and testing and grout inspection. Special inspection for the installation and testing of permanent prestressed rock and soil anchors shall be performed in accordance with Section 1705.8.1 and Table 1705.8.1. Special inspection for the installation and testing of grout inspection shall be performed in accordance with Section 1705.8.2.

1705.8.1 Prestressed rock and soil anchors. The installation and testing of permanent prestressed rock and soil anchors shall be subject to special inspections.  A special inspector shall be present during the installation of each anchor, including all drilling, grouting, tendon splicing (including corrosion protection) and placement, and installation of any accessories such as trumpets and bearing plates.  The special inspector shall also be present for all required load testing and shall create a report containing a log for each element installed and for each load test performed.  The special inspection agency shall submit to the commissioner records of the installation of each rock anchor, and where testing is required, the special inspection agency shall also submit records of the testing. The special inspection agency shall submit to the commissioner records of the installation and testing of each anchor.

| TABLE 1705.8.1 REQUIRED SPECIAL INSPECTIONS OF PRESTRESSED SOIL AND ROCK ANCHORS |
| --- |
| INSTALLATION | CONTINUOUS SPECIAL INSPECTION | PERIODIC SPECIAL INSPECTION |
| 1. Special inspection of Casing Installation. Special inspector shall observe casing installation and confirm that anchors are installed through a fully cased borehole or installed through stable rock in an open hole drill hole. | X | — |
| 2. Special inspection of Anchor Materials. Special inspector shall confirm that the materials used in prestressed rock and soil anchors conform Section 1815.3 and approved construction documents. Inspector shall confirm that bar tendons conform to ASTM A722 and that strand tendons conform to ASTM A416 or A882. | X | — |
| 3. Special inspection of Anchor Installation. Special inspector shall confirm the preparation and installation of each anchor, including placement, type, size and location of anchors, accessories, corrosion protection and grout conforms to PTI DC35.1-4 and the approved construction documents. | X | — |
| 4. Special inspection of Grout. At the time of grout placement, special inspector shall prepare 3” diameter grout cylinders at the intervals specified in Section 1812.1.1.2.1. Cylinders shall be prepared in accordance with ASTM C31/C31M. | X | — |
| 5. Special inspection of Grout. At the time of grout placement, special inspector shall determine the specific gravity of grout in accordance with American Petroleum Institute (API) Recommended Practice 13B-1 or in accordance with ASTM C138. | X | — |
| 6. Special inspection of Grout. The compressive strength of grout cylinders shall be verified using 3” diameter cylinders tested in accordance with ASTM C39 and Section 1812.1.1.2.2. | X | — |
| 7. Special inspection of Load Test. The special inspector shall observe load testing of each anchor and confirm that the test is accordance with PTI DC35.1-14 (Sections 8.1 – 8.9) and Section 1815.5. Inspector shall confirm that testing lock-off, and test loads comply with approved construction documents and PTI DC35.1-14 (Sections 8.1 – 8.9). | X | — |

1705.8.1.1 Records of anchor element installation. The record of installation of each anchor element shall include, but not be limited to, the following:

1.	The identifying designation of the anchor element and the date of installation, including the start and end times.

2.	The size, material, details of corrosion protection, and allowable capacity as specified in the contract drawings.

3.	Unbonded and bonded lengths of tendons, including strata for the bond zone.

4.	The date and time of the witnessing of the placement of grout inside the anchor element, the volume placed, and whether or not the grout was placed in compliance with Section 1815 and contract requirements.

5.	Equipment and method used for installation and record the time for penetration from the start of installation until completion.

1705.8.1.2 Records of testing of anchor elements. The records of testing of anchor elements shall include, but not be limited to, the following:

1.	The results of the inspection and note the lock-off load.

2.	The identifying designation for the element being tested, and the date of the testing, including the start and end time.

3.	The method of performing the test, including the equipment being used, as well as the test results, noting whether or not the method of testing and the test results comply with the requirements of Section 1815.

1705.8.2 Grout inspection. Grout inspection shall be in accordance with Sections 1705.3 and 1815.8.

[1704.9 Vertical masonry foundation elements. Special inspection shall be performed in accordance with Section 1704.5 for vertical masonry foundation elements.]

[Exception: Piers for support of lightweight fences, recreational equipment, site furnishings and similar construction, unless special inspection is specifically noted as required on the approved construction documents.]

[1704.10 Wall panels, curtain walls and veneers. Special inspection is required for exterior architectural wall panels and the anchoring of veneers designed for installation on buildings above a height of 40 feet (12 192 mm). Special inspection of masonry veneer on such structures shall be in accordance with Section 1704.5.]

[Exceptions: Special inspection of wall panels, curtain walls and veneers is not applicable to:]

[1.	Repairs and replacement in kind of gaskets or seals; or]

[2.	Reglazing other than 4-sided structural silicone glazing.]

[1704.10.1Design and installation documents. The special inspector shall become familiar with and retain a copy of the approved construction documents, and the following items, as applicable, approved by the registered design professional of record:]

[1.	Shop drawings,]

[2.	Instructions for the sequence of component installation]

[3.	Samples and/or mock-ups, if supplied.]

[1704.10.2 Inspection program. The special inspector shall field check the site conditions at the time the structure is prepared for component installation, and periodically during component installation, to verify the following work is performed in compliance with the approved construction documents, including that:]

[1.	The supporting structure for components being installed is aligned and within specified tolerances required for the components;]

[2.	Required inserts are installed;]

[3.	Framing components are, installed and aligned as specified, and without structural defects or weakness;]

[4.	Anchors are placed, welded, bolted and finished as specified, as applicable;]

[5.	Weeps, flashings and tubes are installed as specified and functioning;]

[6.	Joinery and end dams are sealed as specified;]

[7.	Sealing materials with specified adhesive and movement capabilities are installed;]

[8.	Gaskets, tapes, seals, insulation, flashing and other materials that are barriers to air and water movement, vapor drive, and heat loss are installed as specified;]

[9.	Joint filler materials that accommodate specified horizontal and vertical movement are installed in accordance with the manufacturers’ instructions; and]

[10.	Any other observations pertinent to safety of performance of the wall system.]

1705.9 Helical pile foundations. Special inspections shall be performed continuously during installation of helical pile foundations. The information recorded shall include installation equipment used, pile dimensions, tip elevations, final depth, final installation torque and other pertinent installation data as required by the registered design professional of record. The approved geotechnical report and the construction documents prepared by the registered design professional and standards established by the commissioner pursuant to Section 28-113.2.2 of the Administrative Code shall be used to determine compliance. The special inspection agency shall submit to the department records of the inspection of the installation of helical piles on forms provided by the department.

1705.10 Reserved.

1705.11 Reserved.

1705.12 Special inspections for seismic resistance. Special inspections for seismic resistance shall be required as specified in Sections 1705.12.1 through 1705.12.5, unless exempted by the exceptions of Section 1704.2.

1705.12.1 Designated seismic systems. For structures assigned to Seismic Design Category C or D, the special inspector shall examine designated seismic systems requiring seismic qualification in accordance with Section 13.2.2 of ASCE 7 and verify that the label, anchorage and mounting conform to the certificate of compliance.

1705.12.2 Access floors. Periodic special inspection is required for the anchorage of access floors in structures assigned to Seismic Design Category D.

1705.12.3 Plumbing, mechanical, fuel gas, and electrical components. Periodic special inspection of plumbing, mechanical and electrical components shall be required for the following:

1.	Anchorage of electrical equipment for emergency and standby power systems in structures assigned to Seismic Design Category C or D.

2.	Installation and anchorage of piping systems designed to carry hazardous materials and their associated mechanical units in structures assigned to Seismic Design Category C or D.

3.	Installation and anchorage of ductwork designed to carry hazardous materials in structures assigned to Seismic Design Category C or D.

4.	Installation and anchorage of vibration isolation systems in structures assigned to Seismic Design Category C or D where the approved construction documents require a nominal clearance of 1/4 inch (6.4 mm) or less between the equipment support frame and restraint.

5.  Installation and anchorage of stainless steel flexible multiple leg hose assemblies in structures assigned to Seismic Design Category C or D.

1705.12.4 Storage racks. Periodic special inspection is required for the anchorage of storage racks that are 8 feet (2438 mm) or greater in height in structures assigned to Seismic Design Category D.

1705.12.5 Seismic isolation systems. Periodic special inspection shall be provided for seismic isolation systems in seismically isolated structures assigned to Seismic Design Category B, C or D during the fabrication and installation of isolator units and energy dissipation devices.

1705.13 Testing for seismic resistance. Testing for seismic resistance shall be required as specified in Sections 1705.13.1 through 1705.13.3, unless exempted from special inspections by the exceptions of Section 1704.2.

1705.13.1 Nonstructural components. For structures assigned to Seismic Design Category B, C, or D where the requirements of Section 13.2.1 of ASCE 7 for nonstructural components, supports or attachments are met by seismic qualification as specified in Item 2 therein, the registered design professional shall specify on the approved construction documents the requirements for seismic qualification by analysis, testing or experience data. Certificates of compliance for the seismic qualification shall be submitted to the commissioner as specified in Section 1705.4.

1705.13.2 Designated seismic systems. For structures assigned to Seismic Design Category C or D and with designated seismic systems that are subject to the requirements of Section 13.2.2 of ASCE 7 for certification, the registered design professional shall specify on the approved construction documents the requirements to be met by analysis, testing or experience data as specified therein. Certificates of compliance documenting that the requirements are met shall be submitted to the commissioner.

1705.13.3 Seismic isolation systems. Seismic isolation systems in seismically isolated structures assigned to Seismic Design Category B, C, or D shall be tested in accordance with Section 17.8 of ASCE 7.

[1704.11] 1705.14 Sprayed fire-resistant materials. Special inspections for sprayed fire-resistant materials applied to floor, roof and wall assemblies and structural members shall be in accordance with Sections [1704.11.1] 1705.14.1 through [1704.11.7] 1705.14.7. Special inspections shall be based on the fire-resistance design as designated [in] by the approved construction documents.  The tests set forth in this section shall be based on samplings from specific floor, roof and wall assemblies and structural members. Special inspections shall be performed after the rough installation of electrical, automatic sprinkler, mechanical and plumbing systems and suspension systems for ceilings, where applicable.

[1704.11.1] 1705.14.1 Physical and visual tests. The special inspections shall include the following tests and observations to demonstrate compliance with the listing and the fire-resistance rating:

1.	Condition of substrates.

2.	Thickness of application.

3.	Density in pounds per cubic foot (kg/m3).

4.	Bond strength adhesion/cohesion.

5.	Condition of finished application.

[1704.11.1 1704.11.2] 1705.14.2 Structural member surface conditions. The surfaces shall be prepared in accordance with the approved fire-resistance design and the written instructions of approved manufacturers. The prepared surface of structural members to be sprayed shall be inspected before the application of the sprayed fire-resistant material.

[1704.11.3] 1705.14.3 Application. The substrate shall have a minimum ambient temperature before and after application as specified in the written instructions of approved manufacturers. The area for application shall be ventilated during and after application as required by the written instructions of approved manufacturers.

[1704.11.4 Thickness. The thickness of the sprayed fire-resistant materials shall comply with the following:]

[1.	No more than 10 percent of the thickness measurements of the sprayed fire-resistant materials applied to floor, roof and wall assemblies and structural members shall be less than the thickness required by the approved fire-resistance design.;]

[2.	In no case shall the thickness be less than the minimum allowable thickness required by Section 1704.11.4.1.]

1705.14.4 Thickness. No more than 10 percent of the thickness measurements of the sprayed fire-resistant materials applied to floor, roof and wall assemblies and structural members shall be less than the thickness required by the approved fire-resistance design, but in no case less than the minimum allowable thickness required by Section 1705.14.4.1.

[1704.11.4.1] 1705.14.4.1 Minimum allowable thickness. For design thicknesses 1 inch (25 mm) or greater, the minimum allowable individual thickness shall be the design thickness minus 1/4 inch (6.4 mm). For design thicknesses less than 1 inch (25 mm), the minimum allowable individual thickness shall be the design thickness minus 25 percent. Thickness shall be determined in accordance with ASTM E 605. Samples of the sprayed fire-resistant materials shall be selected in accordance with Sections [1704.11.4.2] 1705.14.4.2 [and 1704.11.4.3] through 1705.14.4.9.

[1704.11.4.2] 1705.14.4.2 Floor, roof and wall assemblies. The thickness of the sprayed fire-resistant material applied to floor, roof and wall assemblies shall be determined in accordance with ASTM E 605, making not [less] fewer than four measurements for each 1,000 square feet (93 m2) of the sprayed area in each story or portion thereof.

[1704.11.4.2.1] 1705.14.4.3 Cellular decks. Thickness measurements shall be selected from a square area, 12 inches by 12 inches (305 mm by 305 mm) in size. A minimum of four measurements shall be made, located symmetrically within the square area.

[1704.11.4.2.2] 1705.14.4.4 Fluted decks. Thickness measurements shall be selected from a square area, 12 inches by 12 inches (305 mm by 305 mm) in size. [A minimum of] Not fewer than four measurements shall be made, located symmetrically within the square area, including one each of the following: valley, crest and sides. The average of the measurements shall be reported.

[1704.11.4.3] 1705.14.4.5 Structural framing members. The thickness of the sprayed fire-resistant material applied to structural members shall be determined in accordance with ASTM E 605. Thickness testing shall be performed on not less than 25 percent of the structural members on each floor.

[1704.11.4.3.1] 1705.14.4.5.1 Beams and girders. At beams and girders thickness measurements shall be made at nine locations around the beam or girder at each end of [a] one 12-inch (305 mm) length.

[1704.12.4.3.2] 1705.14.4.5.2 Joists and trusses. At joists and trusses, thickness measurements shall be made at seven locations around the joist or truss at each end of [a] one 12-inch (305 mm) length.

[1704.11.4.3.3] 1705.14.4.5.3 Wide-flanged columns. At wide-flanged columns, thickness measurements shall be made at 12 locations around the column at each end of [a] one 12-inch (305 mm) length.

[1704.11.4.3.4] 1705.14.4.5.4 Hollow structural section and pipe columns. At hollow structural section and pipe columns, thickness measurements shall be made at [a minimum of] not fewer than four locations around the column at each end of [a] one 12-inch (305 mm) length.

[1704.11.5] 1705.14.5 Density. The density of the sprayed fire-resistant material shall not be less than the density specified in the approved fire-resistance design. Density of the sprayed fire-resistant material shall be determined in accordance with ASTM E 605. The test samples for determining the density of the sprayed fire-resistant materials shall be selected as follows:

1.	From each floor, roof and wall assembly at the rate of not less than one sample for every 2,500 square feet (232 m2) or portion thereof of the sprayed area in each story, samples shall be taken at a distance of no less than 50 LF from another sample or 10 LF from any starting edge of an application of a specific type of material.

2.	From beams, girders, trusses and columns at the rate of not less than one sample for each type of structural member for each 2,500 square feet (232 m2) of floor area or portion thereof in each story.

[1704.11.6] 1705.14.6 Bond strength. The cohesive/adhesive bond strength of the cured sprayed fire-resistant material applied to floor, roof and wall assemblies and structural members shall not be less than 150 pounds per square foot (psf) (7.18 kN/m2). The cohesive/adhesive bond strength shall be determined in accordance with the field test specified in ASTM E 736 by testing in-place samples of the sprayed fire-resistant material selected in accordance with Sections [1704.11.6.1] 1705.14.6.1 through [1704.11.6.3] 1705.14.6.3.

Exception: For high-rise buildings, as described in Section 403, refer to the requirements for minimum bond strength in Table 403.2.4.

[1704.11.6.1] 1705.14.6.1 Floor, roof and wall assemblies. The test samples for determining the cohesive/adhesive bond strength of the sprayed fire-resistant materials shall be selected from each floor, roof and wall assembly at the rate of not less than one sample for every 2,500 square feet (232 m2) or part thereof of the sprayed area in each story. Samples shall be obtained from locations no less than 50 LF apart or 10 LF from any starting edge of an application of a specific type of material.

[1704.11.6.2] 1705.14.6.2 Structural members. The test samples for determining the cohesive/adhesive bond strength of the sprayed fire-resistant materials shall be selected from beams, girders, joists, trusses, columns and other structural members at the rate of not less than one sample for each type of structural member for each 2,500 square feet (232 m2) of floor area or portion thereof in each story.

[1704.11.6.3] 1705.14.6.3 Primer, paint and encapsulant bond tests. Bond tests to qualify a primer, paint or encapsulant shall be conducted when the sprayed fire-resistant material is applied to a primed, painted or encapsulated surface for which acceptable bond-strength performance between these coatings and the fire-resistant material has not been determined. A bonding agent approved by the SFRM manufacturer shall be applied to a primed, painted or encapsulated surface where the bond strengths are found to be less than required values.

[1704.11.7] 1705.14.7 Inspection of existing sprayed fire-resistant materials during alterations in office spaces and spaces classified in Occupancy Group B. In office spaces and spaces classified in Occupancy Group B, where an alteration exposes any required sprayed fire-resistant materials on structural members or where, pursuant to an alteration, persons are required to enter or access areas in which such sprayed fire-resistant materials are capable of being observed, the existing required sprayed fire-resistant materials shall be subject to special inspection. [Such inspection shall require a determination, based on visual inspection, (i) that the existing sprayed fire-resistant materials as originally applied or installed comply with the applicable requirements of this code, including those for installation methods, materials, thickness and coverage; and (ii) that, since their original application, the integrity of the existing sprayed fire-resistant materials has not been compromised, damaged or displaced. by the current alteration or by any prior alteration or other event.] Such inspection shall require the special inspector to perform a visual inspection and report the existing sprayed fire-resistant materials and conditions to the registered design professional.

[1704.12] 1705.15 Mastic and intumescent fire-resistant coatings. Special inspections and tests for mastic and intumescent fire-resistant coatings applied to structural elements and decks shall be in accordance with AWCI 12-B. Special inspections and tests shall be based on provisions of AWCI 12-B and the fire-resistance design as designated in the approved construction documents.

[1704.13 Exterior insulation and finish systems (EIFS)] 1705.16 Combustible exterior wall coverings. Special inspections shall be required for all exterior wall coverings containing combustible materials installed more than 15 feet (4572 mm) above adjacent finished grades and alterations to existing exterior wall coverings containing combustible materials installed more than 15 feet (4572 mm) above adjacent finished grades. Exterior insulation and finish system (EIFS) applications, metal composite materials (MCM), high-pressure decorative exterior-grade compact laminates (HPL) and exterior wall covering containing combustible veneers, combustible framing, combustible water-resistive barriers and foam plastic insulation installed more than 15 feet (4572 mm) above adjacent finished grades and alterations to existing [EIFS] installations more than 15 feet (4572 mm) above adjacent finished grades shall be inspected in accordance with Section 1705.16.1.

Exceptions

1.	Water-resistive barriers that are the only combustible component in the exterior wall covering satisfying the requirements of Exceptions 1 or 2 of Section 1403.5.1.

2.	Type VB construction up to 40 feet (12 192 mm) or less in height above grade.

[1704.13.1] 1705.16.1 Inspection program. The special inspection shall include verification of[:] compliance with the approved construction documents for the following:[for] attachment to structure[,]; component properties; thicknesses, orientation, cavity sizes and location of thermal barriers, fireblocking and cavity closures; installation of waterproofing membranes, weeps, drains, mold prevention features are as specified; and conformance with the manufacturers’ installation [guidelines] instructions, and NFPA 285 tested assembly design documentation. The special inspector shall verify that individual components required to be labeled in accordance with this code do bear such labels.

[1704.13.2] 1705.16.2 Water-resistive barrier coating. A water-resistive barrier coating complying with ASTM E 2570 requires special inspection of the water-resistive barrier coating when installed over a sheathing substrate. Inspection of water-resistive barrier coating must verify conformance with approved construction documents, manufacturer’s installation instructions, and NFPA 285 tested assembly design documentation.

1705.16.3 Thermal barrier. The special inspector shall confirm the installation of the thermal barrier is in accordance with the approved construction documents, manufacturer’s installation instructions, and NFPA 285 tested assembly design documentation.

Exception: Foam plastic insulation installation on one-story buildings not required to have thermal barrier complying with Section 2603.4.1.4.

1705.16.4 Fireblocking. The special inspector shall confirm the installation of fireblocking is in accordance with Chapter 7 of this code, the approved construction documents, manufacturer’s installation instructions, and NFPA 285 tested assembly design documentation.

Exception: EIFS systems and exterior wall coverings not required to have fireblocking pursuant to Section 718.2.6.1.

[1704.14 Special cases. Special inspections shall be required for proposed work that is, in the opinion of the commissioner, unusual in its nature, such as, but not limited to, the following examples:]

[1.	Construction materials and systems that are alternatives to materials and systems prescribed by this code.]

[2.	Unusual design applications of materials described in this code.]

[3.	Materials and systems required to be installed in accordance with additional manufacturer’s instructions that prescribe requirements not contained in this code or in standards referenced by this code.]

[1704.14.1 Qualifications. Where special inspections are required for proposed work in accordance with Section 1704.14, the special inspection shall be performed by special inspectors qualified to inspect the work to be inspected. The qualifications of the special inspector shall be acceptable to the commissioner.]

1705.17 Fire-resistant penetrations and joints. Special inspections for through-penetrations, membrane penetration firestops, fire-resistant joint systems, and perimeter fire barrier systems that are tested and listed in accordance with Sections 714.3.1.2, 714.4.2, 715.3 and 715.4 shall comply with Sections 1705.17.1 and 1705.17.2.

1705.17.1 Penetration firestops. Inspections of penetration firestop systems that are tested and listed in accordance with Sections 714.3.1.2 and 714.4.2 shall be conducted by an approved special inspection agency in accordance with ASTM E 2174.

1705.17.2 Joint systems. Inspection of fire-resistant joint systems that are tested and listed in accordance with Sections 715.3 and 715.4 shall be conducted by an approved special inspection agency in accordance with ASTM E 2393.

[1704.15 Special inspection for smoke control. Smoke] 1705.18 Testing for smoke control. Testing of smoke control systems shall be [tested] witnessed in its entirety by a special inspector in accordance with Sections [1704.15.1] 1705.18.1 and 909.

Exception: Post-fire smoke purge systems that are not required to function as a smoke control system shall be permitted to be inspected pursuant to the special inspection requirements of Section [1704.16] 1705.21.

[1704.15.1] 1705.18.1 Testing scope. The test scope shall be as follows:

- During erection of ductwork and prior to concealment for the purposes of leakage testing and recording of device location.

2.	Prior to occupancy and after sufficient completion for the purposes of pressure difference testing, flow measurements and detection and control verification.

[1704.15.2 Qualifications. Special inspection agencies for smoke control shall have expertise in fire protection engineering and mechanical engineering and certification as air balancers.]

1705.19 Vertical masonry foundation elements. Special inspection shall be performed in accordance with Section 1705.4 for vertical masonry foundation elements.

Exception: Piers for support of lightweight fences, recreational equipment, site furnishings and similar construction, unless special inspection is specifically noted as required on the approved construction documents.

1705.20 Wall panels, curtain walls and veneers. Special inspection is required for exterior architectural wall panels, curtain walls and the anchoring of veneers for the full height of the installation when any portion of the wall panel, curtain wall and veneer installation exceeds an elevation of 40 feet (12 192 mm) above grade. Special inspection of masonry veneer on such structures shall be in accordance with Section 1705.4. Special inspection of combustible exterior wall covering shall be in accordance with Section 1705.16.

Exceptions: Special inspection of wall panels, curtain walls and the anchoring of veneers is not applicable to:

1.	Repairs and replacement in kind of gaskets or seals; [or]

2.	Reglazing other than 4-sided structural silicone glazing[.] for which a permit is required; or

3.	Where exempted by the rules of the department.

1705.20.1 Design and installation documents. The special inspector shall become familiar with and retain a copy of the approved construction documents, and the following items, as applicable, approved by the registered design professional of record:

1.	Shop drawings.

2.	Instructions for the sequence of component installation.

3.	Samples and/or mock-ups, if supplied.

4.	Required fire-resistance rating and performance standard listings, as applicable.

1705.20.2 Inspection program. The special inspector shall field check the site conditions at the time the structure is prepared for component installation, and periodically during component installation, to verify the following work is performed in compliance with the approved construction documents, including that:

1.	The supporting structure for components being installed is aligned and within specified tolerances required for the components;

2.	Required inserts are installed;

3.	Framing components are installed and aligned as specified, and without structural defects or weakness;

4.	Anchors are placed, welded, bolted and finished as specified, as applicable;

a.	Inspection of welding of anchors shall be inspected in accordance with Section 1705.3. Inspection of bolting of anchors shall be in accordance with Section 1705.4. Inspection of the installation of post-installed anchors shall be in accordance Section 1705.37.

5.	Weeps, flashings and tubes are installed as specified and functioning;

6.	Joinery and end dams are sealed as specified;

7.	Sealing materials with specified adhesive and movement capabilities are installed;

8.	Gaskets, tapes, seals, insulation, flashing and other materials that are barriers to air and water movement, vapor drive, and heat loss are installed as specified;

9.	Joint filler materials that accommodate specified horizontal and vertical movement are installed in accordance with the manufacturers’ instructions; and

10.	Fireblocking and thermal barrier within combustible exterior wall coverings are installed as specified.

[1704.16] 1705.21 Special inspection for mechanical systems. Mechanical systems [regulated which] that require a certificate of compliance in accordance with Section 28-116.4.1 of the Administrative Code shall be inspected for conformance with the approved construction documents.

[1704.16.1] 1705.21.1 Tests for mechanical systems. Tests of mechanical systems shall be performed in accordance with applicable sections of the code including Sections [507.16] 507.6, 1011, 1108 and 1208 of the New York City Mechanical Code. The special inspector shall witness all required tests.

[Exception:] 1705.21.2 Factory built equipment. Listed and labeled self-contained factory-built equipment and appliances deemed by the registered design professional to meet the design, manufacture and factory test requirements of this code shall be field tested in accordance with the manufacturers’ installation and operational test standards.

[1704.16.2] 1705.21.3 Special inspection of mechanical systems. Inspections of mechanical systems shall include the following as applicable to the system:

1.	Visual certification that required components of such systems are complete in accordance with the manufacturers’ installation guidelines and the approved construction documents;

2.	Supports, hangers,[,] and vibration isolation equipment are properly spaced and anchored to supporting structure;

2.1.	Seismic bracing shall be inspected in accordance with Section 1705.12.

3.	Installation of required signage and safety instructions;

4.	Electrical components are installed and electrical sign-off issued;

5.	Ventilation balancing report is complete and in accordance with design documents and the system is operating as designed;

6.	Required labeling, operational instructions and safety signage properly posted;

7.	All related special inspections for such systems are complete;

8.	The installation of exterior mechanical equipment for compliance with the approved construction documents, including, as applicable:

8.1.	Equipment specified;

8.2.	Equipment location;

8.3.	Installation and attachment details;

8.4.	Vibration isolation installation; and

8.5.	Other items specified by the applicant of record for the mechanical equipment design necessary to verify compliance with Section [928.2.1] 313.2.1 of the New York City Mechanical Code.

9.	[Required fire] Fire and smoke dampers are installed and functioning properly.

[1704.17] 1705.22 Special inspection for fuel storage and fuel-piping systems. Fuel-oil storage equipment, including tanks, pumps, valves, transfer, return, fill and vent piping, hangers and bracing, fill and vent terminals, and related systems regulated by Section [1308] 1305 of the New York City Mechanical Code, shall be inspected for conformance with the approved construction documents and the manufacturers’ installation standards. Testing of fuel storage tanks and piping shall be performed in accordance with Section [1308] 1305 of the New York City Mechanical Code. Special inspection of seismic bracing shall be performed in accordance with Section [1707.7] 1705.12.

Exceptions:

- [Testing for listed] Listed fuel oil storage tanks 660 gallons (2498 L) or less in capacity, supplied with a label or manufacturer’s certification attesting that the tank was factory tested to a testing standard indicated in Section 1308.1 of the New York City Mechanical Code.

- Systems and equipment exempt from service equipment certificate of compliance in accordance with Section 28-116.4.1 of the Administrative Code.

[1704.18] 1705.23 High-pressure-steam piping and high temperature hot water piping. High-pressure-steam piping and high temperature hot water piping regulated by Section [1210] 1211 of the New York City Mechanical Code, shall be subject to special inspection in accordance with this section. Special inspection of seismic bracing shall be performed in accordance with Section [1707.7] 1705.12.

[1704.18.1] 1705.23.1 Welding. The special inspector shall verify the qualifications of the welder and the quality of the welding materials and equipment prior to welding operations. The special inspector shall review the proposed welding procedures for compliance with applicable standards listed in Section [1210.2.2] 1211.2.2 of the New York City Mechanical Code.

[1704.18.2] 1705.23.2 Welding operations. The special inspector shall perform periodic inspection of the pipe joining and welding operations in accordance with the above. Radiographic testing shall be applied to connections as indicated in Section [1210.2.2] 1211.2.2 of the New York City Mechanical Code. Unacceptable connections and installations shall be rejected.

[1704.18.3] 1705.23.3 Testing of high-pressure-steam systems and high temperature hot water piping systems. Hydrostatic testing shall be performed on the completed installation of new and altered systems in accordance with Section [1210.2.3] 1211.2.3 of the New York City Mechanical Code. The special inspector shall witness all required hydrostatic tests.

Exception: Testing requirements shall not apply to alteration or repairs to existing piping systems in which the integrity of the piping is not affected. Such alterations shall be visually inspected for compliance with the approved construction documents.

[1704.19] 1705.24 High-pressure-gas piping. High-pressure-gas piping regulated in Section 406 of the New York City Fuel Gas Code shall be subject to special inspection in accordance with this section. Special inspection of seismic bracing shall be performed in accordance with Section [1707.7] 1705.12.

[1704.19.1] 1705.24.1 Welding. The special inspector shall verify the qualifications of the welder, the quality of the welding materials and equipment prior to welding operations. The special inspector shall review the proposed welding procedures for compliance with applicable standards listed in Section 406 of the New York City Fuel Gas Code.

[1704.19.2] 1705.24.2 Welding operations. The special inspector shall perform periodic special inspection for the pipe joining and welding operations in accordance with the above. Radiographic testing shall be performed to the connections as indicated in Section [406.4] 406 of the New York City Fuel Gas Code.

[1704.19.3] 1705.24.3 Testing of high-pressure-gas piping. Pressure testing shall be performed on the completed installation of new and altered systems in accordance with Section [406.4] 406 of the New York City Fuel Gas Code. The special inspector shall witness all required pressure tests.

[1704.20] 1705.25 Structural stability. [Special inspection for structural stability] Special inspection for structural stability is an inspection of a structure to verify the ability of such structural system to remain in position, or revert to the original position or another stable equilibrium position acceptable by this code, without incurring damage to the structural system from the activity or load to which it had been subjected until the completion of construction. Such special inspection shall be required for construction work as specified in this section or elsewhere in this code. Structural materials and methods of construction utilized in temporary protections shall be subject to special inspection when such materials and methods of construction would be subject to special inspection as a permanent installation in accordance with the applicable sections of this chapter, including but not limited to special [inspection] inspections for concrete, [welding] structural steel, and [pile driving.] deep foundation installation. The registered design professional responsible for plans for a new building, alteration, or other work requiring structural stability inspections shall identify those areas on the plans submitted to the department in accordance with Section 1704.1.1.1. The means and methods of implementing the structural stability measures shall be prepared by a registered design professional and filed with the department where required in this section and elsewhere in this code.

Exception: Alterations consisting of the replacement of existing exterior [window or door] lintels located less than 75 feet (22 860 mm) above curb level spanning less than 4 feet (1219 mm) and existing interior headers spanning less than 4 feet (1219 mm), provided the size of the existing span is not increased, shall be exempt from special inspection for structural stability.

[1704.20.1 Soil percolation tests. Soil percolation tests shall be performed at the site of a proposed individual on-site private sewage disposal system installation to determine the suitability of the soil and site. Such test shall be performed under the supervision of a special inspector. The results of the percolation tests shall be filed on forms provided by the department, stating the suitability of the site and the capacity of the subsoil for the proposed use. The registered design professional of record for the dry-well system shall be notified immediately if the results of the percolation test demonstrate that the approved system may not function as designed.]

[1704.20.1 Structural stability of] 1705.25.1 Alterations to existing [buildings] structures. Alterations to existing structures in which loads are transferred from one structural system of structural elements to another, such as installation of columns or girders, replacement of existing bearing walls, the creation of openings or slots in existing walls, girders or floors, alteration of arches, rigid frames, trusses in frame buildings,  where the stability or integrity of a structural system is to be temporarily diminished, or where otherwise required by the commissioner, shall be subject to special inspections in accordance with Sections [1704.20.6] 1705.25.7  through [1704.20.10] 1705.25.10.

[1704.20.1.1] 1705.25.2 Construction operations influencing adjacent strucures. Where construction operations have the potential to affect structurally the condition or occupancy of the subject structure and/or an adjacent structure, the structural stability of [the] such structures shall be subject to special inspections in accordance with Sections [1704.20.6] 1705.25.7  through [1704.20.10] 1705.25.10.

[1704.20.2] 1705.25.3 Excavations. Methods employed to protect the sides of excavations meeting the requirements of Item 1 of Section 3304.4.1, and blasting for the purpose of excavation shall be subject to special inspections in accordance with Sections [1704.20.6] 1705.25.7  through [1704.20.10] 1705.25.10.

[1704.20.2.1] 1705.25.3.1 Slurry. The proportions and installation of slurry mixtures to protect the sides of excavations shall be subject to special inspection. Slurry mix proportions and installation procedures shall be provided by a registered design professional, and the special inspection agency shall verify compliance with the approved procedures.

1705.25.3.2 New foundations. In addition to the special inspection for structural stability, any new foundation elements installed as part of support of excavation operations shall be subject to special inspection as a permanent installation in accordance with the applicable sections of this chapter, including, but not limited to, special inspection for concrete, structural steel, and deep foundation installation.

1705.25.3.3 Effect of blasting. Adjoining properties shall be subject to special inspection for structural stability due to the effects of blasting when blasting is utilized for excavation.

[1704.20.3] 1705.25.4 Underpinning and alternate methods of support of buildings and adjacent property. Underpinning of structures and alternate methods of support of buildings and adjacent property shall be subject to special inspections in accordance with Sections [1704.20.6] 1705.25.7 through [1704.20.10] 1705.25.10.

[1704.20.3.1] 1705.25.4.1 New foundations. In addition to the special inspection for structural stability, any new foundation elements installed as part of underpinning operations shall be subject to special inspection as a permanent installation in accordance with the applicable sections of this chapter, including, but not limited to, special inspection for concrete, [welding] structural steel, and [pile driving] deep foundation installaton.

[1704.20.4] 1705.25.5 Demolition. Demolition operations shall be subject to special inspection in accordance with Sections 1705.25.5.1 and 1705.25.5.2 as applicable to the operations.

1705.25.5.1 Mechanical means and methods of demolition. Where mechanical demolition equipment, other than handheld devices, is to be used in the full or partial demolition of a building from within the building, or is to be used within the building to remove debris or move material, such demolition operation shall be subject to special inspection in accordance with Sections [1704.20.6] 1705.25.7 through [1704.20.10] 1705.25.10. The special inspector shall visit the site a minimum of three times: before demolition operations start, during demolition, and at the conclusion of demolition. Additionally, the special inspector shall visit the site at minimum intervals identified in the design documents and set forth in Section 1705.25.8.2.

1705.25.5.2 Other means of demolition. Where full or partial demolition of a weakened structure as specified in Section 3306.7 or the demolition of a masonry wall with a height to thickness ratio of 16 or greater is proposed, or the demolition of a floor structure directly supported by such wall, such demolition operation shall be subject to special inspection in accordance with Sections 1705.25.7 through 1705.25.10. The special inspector shall visit the site a minimum of three times: before demolition operations start, during demolition, and at the conclusion of demolition. Additionally, the special inspector shall visit the site at minimum intervals identified in the design documents and set forth in Section 1705.25.8.2.

[1704.20.5] 1705.25.6 Raising and moving of a building. A periodic special inspection shall be required in accordance with Sections 1704.20.6] 1705.25.7  through [1704.20.10] 1705.25.10 where the lowest above-grade floor or the lowest subgrade floor of a building is to be raised, lifted, elevated or moved.

[1704.20.6] 1705.25.7 Inspection program. Prior to commencement of work requiring special inspection per Section 1705.25, the special inspector shall review the approved construction documents, related reports, and contractor’s [proposed] sequence of operations and [determine the] confirm that all areas of work [that require] requiring special inspection per Section 1705.25 have design documents addressing the structural stability temporary protections and sequence. A written statement shall be [prepared, mutually acceptable to the contractor and the special inspector] included in the design documents prepared in accordance with Section 1705.25.8, indicating:

1.	The portions of work requiring design documents in accordance with Section [1704.20.7] 1705.25.8.

2.	The names and addresses of the licensed professionals that have been engaged to supply design documents for applicable work.

3.	[The approximate dates for delivery of] Where filing of plans is required, the application and permit numbers for the design documents for the applicable work.

4.	A schedule of [periodic] special inspections, at agreed intervals, including adequate frequency to assure the contractor’s continued compliance with the proposed designs and sequence of construction operations. At a minimum, the site must be inspected twice, once at a pre-construction meeting with the contractor and once during construction operations.

[1704.20.7] 1705.25.8 Design documents. Design documents, including shop drawings, sketches and written descriptions of proposed work regarding structural stability in construction operations shall be prepared by a registered design professional in the employ of the owner or the contractor. [Such] Where required by this section or elsewhere in this code, the work associated with the structural stability protection methods shall be filed with the department. When filing of the design of protection methods is not required, such designs may be revised at any time by the registered design professional. Copies of the special inspection log book, the design documents and revisions thereof, shall be maintained at the job site, and at the office of the special inspector, available for use and review at all reasonable times, until the work subject to special inspection is complete. In the case of alteration to existing structures, the structural stability design documents shall be reviewed by the registered design professional of record.

[1704.20.7.1] 1705.25.8.1 Monitoring. The design documents for structural stability shall include any requirements for monitoring of the subject structure and/or adjacent structures, as determined by the registered design professional responsible for the design. The monitoring plan shall be specific to the buildings to be monitored and operations to be undertaken, and shall specify the scope and frequency of monitoring, acceptable tolerances, and reporting criteria for when tolerances are exceeded, including when the department is required to be notified. The monitoring plan shall include provisions for daily monitoring, at a minimum, until the structural stability protection methods are no longer necessary. Such monitoring can be accomplished by remote means, in-person monitoring or any combination thereof.

1705.25.8.1.1  Additional monitoring requirements for demolition. The design documents for structural stability shall identify and specify the monitoring required for the demolition operation and be specific to all phases of the demolition operation. These specifications must be part of the requirements identified for special inspection.

1705.25.8.2 Additional requirements for design documents for demolition. Design documents for demolition shall indicate a project-specific required minimum interval for special inspections. A written statement of what the special inspection must include shall be provided on the design documents. The minimum special inspection interval must be incorporated into the demolition sequence. Building components and phases of demolition deemed to be structurally critical must be identified for inspection. A monitoring protocol must be provided in accordance with the requirements of Section 1705.25.8.1.1.

1705.25.8.3 Additional requirements for design documents for underpinning and alternate methods of support of buildings and adjacent property. Design documents for underpinning and alternate methods of support of buildings and adjacent property shall comply with the requirements of Section 1817. Such drawings shall indicate a project-specific required minimum interval for special inspections. A written statement of what the special inspection must include shall be provided on the design documents. The minimum special inspection interval must be incorporated into the sequence of operations. Building components and phases of operations deemed to be structurally critical must be identified for inspection. A monitoring protocol must be provided in accordance with the requirements of Section 1705.25.8.1.1. At a minimum, underpinning shall be subject to continuous special inspection for structural stability of the structure being underpinned while work is occurring.

1705.25.8.4 Additional requirements for design documents for protection of the sides of excavations and blasting. Design documents for protection of the sides of excavations and blasting methods of support of buildings and adjacent property shall indicate a project-specific required minimum interval for special inspections. A written statement of what the special inspection must include shall be provided on the design documents. The minimum special inspection interval must be incorporated into the sequence of operations. Building components and phases of operations deemed to be structurally critical must be identified for inspection. A monitoring protocol must be provided in accordance with the requirements of Section 1705.25.8.1.1. At a minimum protection of the sides of excavations and blasting work shall be subject to continuous special inspection for structural stability of the structure or adjacent property being affected while work is occurring.

[1704.20.8] 1705.25.9 Inspection during construction operations. The special inspector shall visit the jobsite at agreed intervals, assess the ongoing work and verify that operations conform with the design documents. Deficiencies shall be reported as required by Section 1704.1.2. In the event unsafe conditions are discovered, the commissioner and the registered design professional employed by the contractor shall be immediately notified by the special inspector.

[1704.20.9] 1705.25.10 Records of special inspections. The special inspection logbook shall be maintained at the special inspector’s office and shall contain the following information:

1.	Project identification, application number and address.

2.	Date and time of each inspection.

3.	Names of personnel who performed each inspection.

4.	Dates of on-site and off-site meetings, names of the participants and a summary of the conversations.

5.	Any significant observations or instructions given related to structural stability in any of the following:

5.1.	Deviations from the design documents.

5.2.	Anticipated field conditions.

5.3.	Proper execution of the work.

5.4.	Safe jobsite conditions.

5.5.	Precautions taken to maintain safe conditions, if work is stopped for any reason.

1705.26 Tenant protection plan compliance.  When alteration, partial demolition, or construction operations are performed at occupied multiple dwellings, the special inspector shall periodically verify compliance with a tenant protection plan as provided for in Chapter 1 of Title 28 of the Administrative Code and Section 3303.10.  Special inspections for compliance with the tenant protection plan shall comply with Sections 1705.26.1 and 1705.26.2.

Exceptions: Special inspection for tenant protection plan compliance is not required where the scope of the work is limited to:

1.	A three-family home;

2.	The interior of a single dwelling unit of an occupied multiple dwelling with no disruption to the essential services of other units, where such dwelling is owner-occupied. For a dwelling unit within a property that is owned by a condominium or held by a shareholder of a cooperative corporation under a proprietary lease, the unit must be occupied by the owners of record for such unit; or

3.	The interior of a single dwelling unit of an occupied multiple dwelling 3 stories or less in height.

1705.26.1 Inspection frequency.  Special inspections shall be performed throughout the duration of the tenant protection plan at sufficient periodic intervals to verify compliance with the tenant protection plan throughout the course of work.  At a minimum, inspections shall be performed:

1.	Prior to the start of construction and/or demolition to document conditions prior to work;

2.	At the start of construction and/or demolition;

3.	Once per week during construction and/or demolition;

4.	After a tenant protection violation has been issued to verify that the violation was corrected;

5.	When the location of the alteration or construction operations performed in conjunction with the tenant protection plan has moved to another location; and

6.	Whenever construction or demolition operations have changed, requiring changes in methods of protection.

1705.26.2 Reporting.  A written record of the special inspections performed for the tenant protection plan shall be maintained in a log prepared by the special inspector.  The log shall include an entry for each inspection and shall indicate that the alteration or construction operation is being performed in accordance with the tenant protection plan.  Copies of the special inspection log book shall be maintained at the job site, and at the office of the special inspector, and shall be available for use and review at all reasonable times, until the work subject to special inspection is complete.

[1704.21] 1705.27 Private on-site storm water disposal systems and detention facilities. Storm water detention and retention systems required to comply with Section 1114 of the New York City Plumbing Code, and roof detention facilities shall be inspected for compliance with the provisions of this [sections] section.

[1704.21.1] 1705.27.1 Subsurface investigation special inspection. Soil borings, testpits and soil percolation testing shall be subject to the special inspection requirements of this section.

[1704.21.1.1] 1705.27.1.1 Soil borings and testpits. Prior to the approval of construction documents, soil borings and testpits shall be performed in accordance with the provisions of Section 1114.2.1 of the New York City Plumbing Code. Soil borings and testpits shall be performed under the supervision of a special inspector. The results of the soil borings and testpits shall be filed on forms provided by the department.

[1704.21.1.2] 1705.27.1.2 Soil percolation tests. Prior to the approval of construction documents, soil percolation tests shall be performed in accordance with the provisions of Section 1114.2.2 of the New York City Plumbing Code at the site of a proposed on-site stormwater drainage and detention facility installation to determine the suitability of the soil and site. Such test shall be performed under the supervision of a special inspector. The results of the percolation tests shall be filed on forms provided by the department, stating the suitability of the site and the capacity of the subsoil for the proposed use. The registered design professional of record for the dry-well system shall be notified immediately if the results of the percolation test demonstrate that the system may not function as designed.

[1704.21.2] 1705.27.2 Installation special inspection. Private on-site stormwater disposal systems and detention facilities shall be inspected for conformance with the approved construction documents. Minor variations, based on actual site conditions, shall be acceptable at the discretion of the registered design professional of record. Verification shall include:

1.	Materials of construction.

2.	[Bedding] Compliance of bedding, per Section 306 of the New York City Plumbing Code, of pipe and facilities.

3.	Placement and installation of fill materials.

4.	Volume of drywell and detention facilities.

5.	Installation of volume flow control devices.

6.	Workmanship and quality of installation.

7.	Overall conformance with the approved construction documents.

8.	Detention tanks, and roofs used for stormwater detention, shall be filled with water to demonstrate water tightness for a 2-hour duration or as specified by the registered design professional or the manufacturer’s specifications.

[1704.22] 1705.28 Individual on-site private sewage disposal systems. Individual on-site private sewage disposal systems shall be inspected in accordance with the rules of the department.

[1704.23] 1705.29 Sprinkler system special inspection. New and altered sprinkler [system] systems shall be inspected in accordance with Sections 903 and [1704.23.1] 1705.29.1. The permit holder responsible for the sprinkler work shall perform all required acceptance tests, complete and sign the appropriate contractor’s material and test certifications. The special inspector shall witness all required tests and shall verify that all installations of all materials, fittings, hangers, assemblies and signage are in accordance with the approved construction documents, that painting of the sprinkler system required by Section 903.6 of this code has been performed and that the contractor has transmitted required maintenance literature and instruction to the owner. The special inspector shall verify that the material and test certification forms have been transmitted to the Fire Department and the Department of Buildings. Seismic bracing shall be inspected in accordance with Section [1707.7] 1705.12.

Exception: [The special inspection agency need not witness the hydrostatic pressure test when such test is witnessed by the department.] If the department witnesses a hydrostatic pressure test, it need not be witnessed by the special inspection agency.

[1704.23.1] 1705.29.1 Hydrostatic pressure testing. All new or altered sprinkler systems in buildings shall undergo successful hydrostatic pressure testing by a licensed master plumber or licensed fire suppression piping contractor in accordance with the requirements of this code, including Section 901.5, and NFPA 13.

Exceptions: Modification of 6 or fewer sprinklers:

1.	May be tested under working pressure in lieu of hydrostatic testing, or

2.	Need not be witnessed by a special inspection when the hydrostatic test is performed by the licensed installing contractor.

[1704.24] 1705.30 Standpipe system special inspection. New and altered standpipe systems shall be inspected in accordance with Sections 905 and [1704.24.1] 1705.30.1. Fire pump tests associated with standpipe systems shall be tested in accordance with Section 1705.30.2. The permit holder responsible for the standpipe work shall perform all required acceptance tests, and complete and sign the appropriate contractor’s material and test certifications. The special inspector shall witness all required tests, verify that installation of all materials, fittings, hangers, assemblies and signage are in accordance with the approved construction documents, that painting of the standpipe system required by Section 905.11 of this code has been performed and that the contractor has transmitted required maintenance literature and instruction to the owner. The special inspector shall verify that the material and test certification forms have been transmitted to the Fire Department and the Department of Buildings. Seismic bracing shall be inspected in accordance with Section [1707.7] 1705.12.

Exception: The special inspection agency need not witness the hydrostatic pressure test [shall not be required] when such test is witnessed by the department.

[1704.24.1] 1705.30.1 Hydrostatic pressure testing. All new or altered standpipe systems in buildings shall undergo successful hydrostatic pressure testing by a licensed master plumber or licensed fire suppression piping contractor in accordance with the requirements of this code, including Section 901.5, Sections [.1.1] [1704.24.1.1] 1705.30.1.1 through [.1.5] [1704.24.1.5] 1705.30.1.5 and NFPA 14.

Exception: When the standpipe system is exposed to freezing conditions, a hydrostatic pressure test required by this section may be postponed until such conditions no longer exist, notwithstanding any requirement that the standpipe be maintained in a state of readiness, provided that the system undergoes an interim test with dry nitrogen or air using a compressor in accordance with NFPA 14. Any such air pressure tests shall be witnessed by the special inspector unless witnessed by the department.

[1704.24.1.1] 1705.30.1.1 New buildings under construction. For standpipes required to comply with Section 3303.8 of this code, an initial hydrostatic pressure test of the entire system shall be performed when the building reaches a height of 75 feet (22 860 mm) and additional successful hydrostatic pressure tests of the entire system shall be performed at 175 feet (53 340 mm), and at every 100 feet (30 480 mm) in height thereafter. The permit holder shall perform a final acceptance test of the completed system in accordance with the requirements of Section 901.5 of this code.

[1704.24.1.2] 1705.30.1.2 Enlargements or additions to existing system. Where there is an enlargement that triggers a new standpipe system or there is an addition to an existing standpipe system, hydrostatic pressure tests of the entire system shall be performed for every 75 feet (22 860 mm) of additional height added to the system. The permit holder shall perform a final acceptance test of the completed system in accordance with the requirements of Section 901.5 of this code.

[1704.24.1.3] 1705.30.1.3 Removal of stories, including full demolitions. Where stories are removed from a building served by an existing standpipe system, hydrostatic pressure tests of the entire system shall be performed prior to the commencement of work.

[1704.24.1.4] 1705.30.1.4 Alterations. For alterations not covered under Sections [1704.24.1.2] 1705.30.1.2 or [1704.24.1.3] 1705.30.1.3 above, the permit holder shall perform a final acceptance test of the completed system in accordance with the requirements of Section 901.5 of this code.

[1704.24.1.5] 1705.30.1.5 Readiness. No standpipe system shall be considered in readiness until there has been a successful hydrostatic pressure test.

1705.30.2 Fire pump tests. Fire pump tests associated with standpipe systems shall be tested in accordance with Section 913.5. The special inspector shall witness all required tests and shall verify that all installations comply with NFPA 20 and are in accordance with the approved construction documents.

[1704.25] 1705.31 Heating systems. Special inspection shall be required for new and altered boilers and heating systems. All boilers and heating systems, including chimney connectors, shall be inspected for compliance with the approved construction documents. New heating systems shall be tested in accordance with Section 1011 of the New York City Mechanical Code. Alterations to heating systems shall be subjected to applicable tests for the altered portions of the system and to verify its satisfactory operation within the existing system. Special inspection of seismic bracing shall be performed in accordance with Section [1707.7] 1705.12.

Exception: Tests and inspections need not duplicate any valid tests or inspections previously certified by the commissioner or a duly authorized insurance company.

[1704.26] 1705.32 Chimneys and vents. New and altered chimneys and vents, replacing an existing appliance in accordance with Section 503.5.6 of the New York City Fuel Gas Code, or change in appliance in accordance with Section 507 of the New York City Fuel Gas Code and Section 807 of the New York City Mechanical Code shall be subject to special inspection. The chimney or vent shall be inspected to verify compliance with the approved construction documents, and proper clearance or isolation from adjacent combustible construction. Testing of the chimney or vent shall be performed as applicable in accordance with Section 810 of the New York City Mechanical Code and Section 503.5.6 of the New York City Fuel Gas Code. Special inspection of seismic bracing shall be performed in accordance with Section [1707.7] 1705.12.

Exception: [A pressurized smoke test need not be performed on an existing negative pressure chimney if the lining of such chimney is not affected by alterations and the registered design professional specifies on the approved construction documents that such test does not need to be performed on such chimney. Refer to Section 810 of the New York City Mechanical Code and Section 503.5.6 of the New York City Fuel Gas Code for smoke test requirements.] A pressurized smoke test need not be performed on existing and new Listed Type B gas vents and Type L vents.  Listed Type B gas vents and Type L vents shall be visually inspected for the presence of a continuous inner wall, proper installation, and no damage or deterioration via readily accessible areas of the vent system, such as the appliance, tee caps, cleanout openings, or termination. The vent system shall be inspected for proper clearances, protection and damage.

1705.32.1 Reuse of existing chimneys.  When a new heating system appliance is installed, the special inspector shall verify the condition of the existing chimney lining and breaching. Deficiencies shall be reported as required by Section 1704.1.1.2.

[1704.27 Fire-resistant penetrations and joints. Special inspections for through-penetrations, membrane penetration firestops, fire-resistant joint systems, and perimeter fire barrier systems that are tested and listed in accordance with Sections 713.4.1.1.2, 713.4.1.2, 714.3 and 714.4 shall comply with Sections 1704.27.1 and 1704.27.2.]

[1704.27.1 Penetration firestops. Inspections of penetration firestop systems that are tested and listed in accordance with Sections 713.4.1.1.2 and 713.4.1.2 shall be conducted by an approved special inspection agency in accordance with ASTM E 2174.]

[1704.27.2 Joint systems. Inspection of fire-resistant joint systems that are tested and listed in accordance with Sections 714.3 and 714.4 shall be conducted by an approved special inspection agency in accordance with ASTM E 2393.]

[1704.28] 1705.33 Aluminum construction. The special inspections for structural aluminum elements of buildings and structures shall be as required by Section [1704.28.1] 1705.33.1.

[1704.28.1] 1705.33.1 Welding operations. All welding operations of aluminum elements shall be subject to special inspection for compliance with this code, AA ADM, and AWS D1.2.

Exception: Welding operations in connections where the calculated stresses in the welds are less than 50 percent of the basic allowable values. Such connections shall be specifically indicated on the approved construction documents.

[1704.29] 1705.34 Flood zone compliance. Special inspection for flood zone compliance shall be as required by Appendix G of this code.

[1704.30 Photoluminescent] 1705.35 Luminous exit path markings. The installation of [photoluminescent egress] luminous exit path markings shall be subject to special inspection in accordance with the requirements of Section 1025.8. The special inspector shall verify that approved [photoluminescent egress] luminous exit path markings were provided and installed in accordance with [department rules and regulations] Section 1704, the approved construction documents, and manufacturer’s instructions.

[1704.31] 1705.36 Emergency and standby power systems (generators). The installation of generators as part of emergency and standby power systems shall be subject to special inspection. The special inspector shall: perform visual inspections; verify that the installations of all materials, equipment and signage complies with the installation standards; and verify that the installation of the generator and associated connections complies with the approved construction documents. The special inspector shall witness tests that verify the automatic operation of the emergency or standby power system in accordance with NFPA 110 and NFPA 111[, as such standards may have been amended by the New York City Electrical Code or this code]. Deficient results shall be rejected, and deficiencies shall be corrected and successfully retested in the presence of the special inspector prior to sign-off of the emergency or standby power system special inspection. Special inspection of seismic bracing shall be performed in accordance with Section [1707.7] 1705.12.

[1704.32] 1705.37 Post-installed anchors. The installation of post-installed mechanical anchors, adhesive anchors, and screw anchors shall comply with Table [1704.32] 1705.37. The special inspection shall include the verification of compliance with approved construction documents and standards established by the commissioner pursuant to Section 28-113.2.2 of the Administrative Code.

TABLE [1704.32] 1705.37
REQUIRED VERIFICATION AND INSPECTION OF POST-INSTALLED ANCHORS

| [VERIFICATION AND INSPECTION] TYPE | CONTINUOUS SPECIAL INSPECTION | PERIODIC SPECIAL INSPECTION | REFERENCED STANDARD | BC REFERENCE |
| --- | --- | --- | --- | --- |
| 1. Preparation, placement, type, size and location of anchors, including other details of anchors, installed in hardened concrete, and installed to hardened concrete and to another construction. | [—] | [X] | [ACI 318: 3.8.6, 8.1.3, 15.8.3, 21.1.8] | [1912.1, 1908.1.9] 1901.1 |
| a. Adhesive anchors installed horizontally or upwardly inclined orientations to resist sustained tension loads. | X | — | ACI 318 17.8.2.4 ACI 318-11 D.9.2.4 | 1901.1 |
| b. Mechanical anchors and adhesive anchors not defined in 1.a. | — | X | ACI 318 17.9.2 | 1901.1 |
| 2. Preparation, placement, type, size and location of anchors, including other details of anchors, installed in masonry, and installed to masonry and to another construction. | ___ | X | Manufacturer’s specifications and installation instructions | Applicable department procedures |
| 3. Preparation, placement, type, size and location of anchors, including other details of anchors, installed in stone, and installed to stone and to another construction. | ___ | X | Manufacturer’s specifications and installation instructions |  |

[1704.33 Tenant protection plan. When alteration, partial demolition, or construction operations are performed at occupied multiple dwellings, the department shall periodically verify compliance with a tenant protection plan as provided for in Chapter 1 of Title 28 of the Administrative Code and Section 3303.10.]

1705.38 Special inspection for nonpotable water systems. Testing and inspection of nonpotable water systems shall be in accordance with Chapter 13 of the New York City Plumbing Code. The special inspector shall witness all required tests in accordance with Chapter 13 of the New York City Plumbing Code.

1705.38.1 Tests for nonpotable water systems. Tests of nonpotable water systems shall be performed in accordance with Sections 1705.38.1.1 through 1705.38.1.2.

1704.38.1.1 Water storage tanks.  Water storage tanks shall be tested in accordance with Sections 1302.12.2 and 1303.15.4 of the New York City Plumbing Code.

1705.38.1.2 Roofwashers. Roofwashers shall be tested in accordance with Section 1303.15.2 of the New York City Plumbing Code.

1705.38.2 Special inspection of nonpotable water systems. Inspections of nonpotable water systems shall include the following as applicable to the system:

1705.38.2.1 Visual inspection that components of such systems are complete in accordance with the  manufacturers’ instructions and the approved construction documents;

1705.38.2.2 Required labeling, operational instructions and safety signage properly posted.

1705.38.2.3 Inspection of vermin and insect protection. Inlets and vents to the system shall be inspected in accordance with Sections 1302.12.5 and 1303.15.7 of the New York City Plumbing Code.

1705.39 Special inspection for exhaust and vent systems in plenums and ducts. Chimneys, vents, and exhaust systems under positive pressure that penetrate ducts or plenums installed in accordance with exceptions 1 and 2 of Section 601.4 of the New York City Mechanical Code shall be inspected for conformance with the approved construction documents.

1705.39.1 Visual inspection.  Visual inspection shall confirm that joints, seams, and connections of covered mechanical systems are securely fastened and sealed with welds, gaskets, mastics (adhesives), mastic-plus-embedded-fabric systems, liquid sealants or tapes.

1705.39.2 Smoke test. The special inspection shall include witnessing the system smoke test performed in accordance with Section 810 of the New York City Mechanical Code.

[SECTION BC 1705]
[RESERVED]

[SECTION BC 1706]
[RESERVED]

[SECTION BC 1707]
[SPECIAL INSPECTIONS FOR SEISMIC RESISTANCE]

[1707.1 Reserved.]

[1707.2 Reserved.]

[1707.3 Reserved.]

[1707.4 Reserved.]

[1707.5 Reserved.]

[1707.6 Reserved.]

[1707.7 Mechanical, plumbing, fuel gas, and electrical components. Special inspection for mechanical, plumbing, fuel gas, and electrical systems and equipment shall be as follows:]

[1.	Periodic special inspection is required during the anchorage of electrical equipment for emergency or standby power systems in structures assigned to Seismic Design Category C or D.]

[2.	Periodic special inspection is required during the installation of piping systems intended to carry flammable, combustible or highly toxic contents and their associated mechanical units in structures assigned to Seismic Design Category C or D.]

[3.	Periodic special inspection is required during the installation of HVAC ductwork that will contain hazardous materials in structures assigned to Seismic Design Category C or D.]

[1707.8 Seismic isolation system. There shall be periodic special inspection during the fabrication and installation of isolator units and energy dissipation devices if used as part of the seismic isolation system.]

[SECTION BC 1708]
[RESERVED]

[SECTION BC 1709]
[RESERVED]

[SECTION BC 1710]
[RESERVED]

SECTION BC [1711] 1706
DESIGN STRENGTHS OF MATERIALS

[1711.1] 1706.1 Conformance to standards. The design strengths and permissible stresses of any structural material that are identified by a manufacturer’s designation as to manufacture and grade by mill tests, or the strength and stress grade is otherwise confirmed to the satisfaction of the commissioner shall conform to the specifications and methods of design of accepted engineering practice or the rules of the department in the absence of applicable standards.

[1711.2] 1706.2 New materials. For materials that are not specifically provided for in this code, the design strengths and permissible stresses shall be established by tests as provided for in Section [1712] 1707.

SECTION BC [1712] 1707
ALTERNATIVE TEST PROCEDURE

[1712.1] 1707.1 General. In the absence of rules or other approved standards, and upon special application by a registered design professional the commissioner shall make, or cause to be made, the necessary tests and investigations; or the commissioner shall accept duly authenticated reports from approved agencies in respect to the quality and manner of use of new materials or assemblies as provided for in Article 113 of Chapter 1 of Title 28 of the Administrative Code. The cost of all tests and other investigations required under the provisions of this code shall be borne by the permit applicant.

[SECTION BC 1713]
[TEST SAFE LOAD]

[1713.1 Where required. Where proposed construction is not capable of being designed by approved engineering analysis, or where proposed construction design method does not comply with the applicable material design standard, the system of construction or the structural unit and the connections shall be subjected to the tests prescribed in Section 1715. The commissioner shall accept certified reports of such tests conducted by an approved testing agency, provided that such tests meet the requirements of this code and approved procedures.]

SECTION BC [1714] 1708
IN-SITU LOAD TESTS

[1714.1] 1708.1 General. Whenever there is a reasonable doubt as to the stability or load-bearing capacity of a completed building, structure or portion thereof for the expected loads, an engineering assessment shall be required. The engineering assessment shall involve either a structural analysis or an in-situ load test, or both. The structural analysis shall be based on actual material properties and other as-built conditions that affect stability or load-bearing capacity, and shall be conducted in accordance with the applicable design standard. If the structural assessment determines that the load-bearing capacity is less than that required by the code, load tests shall be conducted in accordance with Section [1714.2] 1708.2. If the building, structure or portion thereof is found to have inadequate stability or load-bearing capacity for the expected loads, modifications to ensure structural adequacy or the removal of the inadequate construction shall be required.

[1714.2] 1708.2 Test standards. Structural components and assemblies shall be tested in accordance with the appropriate material standards listed in Chapter 35. In the absence of a standard that contains an applicable load test procedure, the test procedure shall be developed by a registered design professional and approved. The test procedure shall simulate loads and conditions of application that the completed structure or portion thereof will be subjected to in normal use.

[1714.3] 1708.3 In-situ load tests. In-situ load tests shall be conducted in accordance with Section [1714.3.1] 1708.3.1 or [1714.3.2] 1708.3.2 and shall be supervised by a registered design professional. The test shall simulate the applicable loading conditions specified in Chapter 16 as necessary to address the concerns regarding structural stability of the building, structure or portion thereof.

[1714.3.1] 1708.3.1 Load test procedure specified. Where a standard listed in Chapter 35 contains an applicable load test procedure and acceptance criteria, the test procedure and acceptance criteria in the standard shall apply. In the absence of specific load factors or acceptance criteria, the load factors and acceptance criteria in Section [1714] 1708.3.2 shall apply.

[1714.3.2] 1708.3.2 Load test procedure not specified. In the absence of applicable load test procedures contained within a standard referenced by this code or acceptance criteria for a specific material or method of construction, such existing structure shall be subjected to a test procedure developed by a registered design professional that simulates applicable loading and deformation conditions. For components that are not a part of the seismic-load-resisting system, the test load shall be equal to two times the unfactored design loads. The test load shall be left in place for a period of 24 hours. The structure shall be considered to have successfully met the test requirements where the following criteria are satisfied:

- Under the design load, the deflection shall not exceed the limitations specified in Section 1604.3.

- Within 24 hours after removal of the test load, the structure shall have recovered not less than 75 percent of the maximum deflection.

- During and immediately after the test, the structure shall not show evidence of failure.

SECTION BC [1715] 1709
PRECONSTRUCTION LOAD TESTS

[1715.1] 1709.1 General. In evaluating the physical properties of materials and methods of construction that are not capable of being designed by approved engineering analysis or do not comply with applicable material design standards listed in Chapter 35, the structural adequacy shall be predetermined based on the load test criteria established in this section.

[1715.2] 1709.2 Load test procedures specified. Where specific load test procedures, load factors and acceptance criteria are included in the applicable design standards listed in Chapter 35, such test procedures, load factors and acceptance criteria shall apply. In the absence of specific test procedures, load factors or acceptance criteria, the corresponding provisions in Section [1715.3] 1709.3 shall apply.

[1715.3] 1709.3 Load test procedures not specified. Where load test procedures are not specified in the applicable design standards listed in Chapter 35, the load-bearing and deformation capacity of structural components and assemblies shall be determined on the basis of a test procedure developed by a registered design professional that simulates applicable loading and deformation conditions. For components and assemblies that are not a part of the seismic-load-resisting system, the test shall be as specified in Section [1715.3.1] 1709.3.1. Load tests shall simulate the applicable loading conditions specified in Chapter 16.

[1715.3.1] 1709.3.1 Test procedure. The test assembly shall be subjected to an increasing superimposed load equal to not less than two times the superimposed design load. The test load shall be left in place for a period of 24 hours. The tested assembly shall be considered to have successfully met the test requirements if the assembly recovers not less than 75 percent of the maximum deflection within 24 hours after the removal of the test load. The test assembly shall then be reloaded and subjected to an increasing superimposed load until either structural failure occurs or the superimposed load is equal to two and one-half times the load at which the deflection limitations specified in Section [1715.3.2] 1709.3.2 were reached, or the load is equal to two and one-half times the superimposed design load. In the case of structural components and assemblies for which deflection limitations are not specified in Section [1715.3.2] 1709.3.2, the test specimen shall be subjected to an increasing superimposed load until structural failure occurs or the load is equal to two and one-half times the desired superimposed design load. The allowable superimposed design load shall be taken as the lesser of:

1.	The load at the deflection limitation given in Section [1715.3.2] 1709.3.2.

2.	The failure load divided by 2.5.

3.	The maximum load applied divided by 2.5.

[1715.3.2] 1709.3.2 Deflection. The deflection of structural members under the design load shall not exceed the limitations in Section 1604.3.

[1715.4] 1709.4 Wall and partition assemblies. Load-bearing wall and partition assemblies shall sustain the test load both with and without window framing. The test load shall include all design load components. Wall and partition assemblies shall be tested both with and without door and window framing.

[1715.5] 1709.5 Exterior window and door assemblies. The design pressure rating of exterior windows and doors in buildings shall be determined in accordance with Section [1715.5.1] 1709.5.1 or [1715.5.2] 1709.5.2.

Exception: Structural wind load design pressures for window units smaller than the size tested in accordance with Section [1715.5.1] 1709.5.1 or [1715.5.2] 1709.5.2 shall be permitted to be higher than the design value of the tested unit provided such higher pressures are determined by accepted engineering analysis. All components of the small unit shall be the same as the tested unit. Where such calculated design pressures are used, they shall be validated by an additional test of the window unit having the highest allowable design pressure.

[1715.5.1] 1709.5.1 Exterior windows and doors. Exterior windows and doors shall be tested and labeled as conforming to AAMA/WDMA/CSA 101/I.S.2/A440. The label shall state the name of the manufacturer, the approved labeling agency and the product designation as specified in AAMA/WDMA/CSA 101/I.S.2/A440. Products tested and labeled as conforming to [AAMA/NWWDA 101/I.S.2] AAMA/WDMA/CSA 101/I.S.2/A440 shall not be subject to the requirements of Sections 2403.2 and 2403.3.

[1715.5.2] 1709.5.2 Exterior windows and door assemblies not provided for in Section [1715.5.1] 1709.5.1. Exterior window and door assemblies shall be tested in accordance with ASTM E 330. Structural performance of garage doors shall be determined in accordance with either ASTM E 330 or ANSI/DASMA 108, and shall meet the acceptance criteria of ANSI/DASMA 108. Exterior window and door assemblies containing glass shall comply with Section 2403. The design pressure for testing shall be calculated in accordance with Chapter 16. Each assembly shall be tested for 10 seconds at a load equal to 1.5 times the design pressure.

1709.6 Skylights and sloped glazing. Skylights and sloped glazing shall comply with the requirements of Chapter 24.

[1715.6] 1709.7 Test specimens. Test specimens and construction shall be representative of the materials, workmanship and details normally used in practice. The properties of the materials used to construct the test assembly shall be determined on the basis of tests on samples taken from the load assembly or on representative samples of the materials used to construct the load test assembly. Required tests shall be conducted or witnessed by an approved agency.

SECTION BC 1710
TEST SAFE LOAD

1710.1 Where required. Where proposed construction is not capable of being designed by approved engineering analysis, or where proposed construction design method does not comply with the applicable material design standard, the system of construction or the structural unit and the connections shall be subjected to the tests prescribed in Section 1711. The commissioner shall accept certified reports of such tests conducted by an approved testing agency, provided that such tests meet the requirements of this code and approved procedures.

SECTION BC [1716] 1711
MATERIAL AND TEST STANDARDS

[1716.1] 1711.1 Test standards for joist hangers and connectors. Test standards for joist handlers and connectors shall be in accordance with Sections 1711.1.1 through 1711.2.2.

[1716.1.1] 1711.1.1 Test standards for joist hangers. The vertical load-bearing capacity, torsional moment capacity and deflection characteristics of joist hangers shall be determined in accordance with ASTM D 1761, using lumber having a specific gravity of 0.49 or greater, but not greater than 0.55, as determined in accordance with AF&PA NDS for the joist and headers.

Exception: The joist length shall not be required to exceed 24 inches (610 mm).

[1716.1.2] 1711.1.2 Vertical load capacity for joist hangers. The vertical load capacity for the joist hanger shall be determined by testing a minimum of three joist hanger assemblies as specified in ASTM D 1761. If the ultimate vertical load for any one of the tests varies more than 20 percent from the average ultimate vertical load, at least three additional tests shall be conducted. The allowable vertical load of the joist hanger shall be the lowest value determined from the following:

1.	The lowest ultimate vertical load for a single hanger from any test divided by three (where three tests are conducted and each ultimate vertical load does not vary more than 20 percent from the average ultimate vertical load).

2.	The average ultimate vertical load for a single hanger from all tests divided by six (where six or more tests are conducted).

3.	The average from all tests of the vertical loads that produce a vertical movement of the joist with respect to the header is 0.125 inch (3.2 mm).

4.	The sum of the allowable design loads for nails or other fasteners utilized to secure the joist hanger to the wood members and allowable bearing loads that contribute to the capacity of the hanger.

5.	The allowable design load for the wood members forming the connection.

[1716.1.3] 1711.1.3 Torsional moment capacity for joist hangers. The torsional moment capacity for the joist hanger shall be determined by testing at least three joist hanger assemblies as specified in ASTM D 1761. The allowable torsional moment of the joist hanger shall be the average torsional moment at which the lateral movement of the top or bottom of the joist with respect to the original position of the joist is 0.125 inch (3.2 mm).

[1716.1.4] 1711.1.4 Design value modifications for joist hangers. Allowable design values for joist hangers that are determined by Item 4 or 5 in Section [1716.1.2] 1711.1.2 shall be permitted to be modified by the appropriate duration of loading factors as specified in AF&PA NDS but shall not exceed the direct loads as determined by Item 1, 2 or 3 in Section [1716.1.2] 1711.1.2. Allowable design values determined by Item 1, 2 or 3 in Section [1716.1.2] 1711.1.2 shall not be modified by duration of loading factors.

[1716.2] 1711.2 Concrete and clay roof tiles. Concrete and clay roof tiles shall be tested in accordance with Sections 1711.2.1 and 1711.2.2.

[1716.2.1] 1711.2.1 Overturning resistance. Concrete and clay roof tiles shall be tested to determine their resistance to overturning due to wind in accordance with ICC SBCCI SSTD 11 and Chapter 15.

[1716.2.2] 1711.2.2 Wind tunnel testing. When roof tiles do not satisfy the limitations in Chapter 16 for rigid tile, a wind tunnel test shall be used to determine the wind characteristics of the concrete or clay tile roof covering in accordance with ICC SBCCI SSTD 11 and Chapter 15.

§ 19. Chapter 18 of the New York city building code as added by local law number 141 for the year 2013, is amended to read as follows:

CHAPTER 18
SOILS AND FOUNDATIONS

SECTION BC 1801
GENERAL [AND DEFINITIONS]

1801.1 Scope. The provisions of this chapter shall apply to building and foundation systems in those areas not subject to scour or water pressure by wind and wave action. Buildings and foundations subject to such scour or water pressure loads shall be designed in accordance with Chapter 16 and Appendix G. [(Note: Where the text in this Code refers to ASCE 7, the 2005 edition shall be used; and where the text in this Code refers to ASCE 7-10, the 2010 edition shall be used.)]

1801.2 Design. Allowable bearing pressures, allowable stresses and design formulas provided in this chapter shall be used with the allowable stress design load combinations specified in Section 1605.3. The quality and design of materials used structurally in excavations and foundations shall [conform to] comply with the requirements specified in Chapters 16, 19, 21, 22 and 23. Excavations and fills shall also comply with Chapter 33.

1801.2.1 Foundation design for seismic overturning. Where foundations are proportioned using the load combinations of Sections 1605.2 or 1605.3.1 and the computation of seismic overturning effects is by equivalent lateral force or modal analysis, the proportioning shall be in accordance with Section 12.13.4 of ASCE [7-10] 7.

SECTION BC 1802
DEFINITIONS

[1801.3 Definitions.] 1802.1 General. The following terms [shall, for the purposes of this chapter, have the meanings shown herein.] are defined in Chapter 2:

Augered-cast-in-place piles. [Augered-cast-in-place piles are constructed by pumping grout into an augered hole during the withdrawal of the auger. The pile is reinforced with a single reinforcing bar, a reinforcing steel cage or a structural steel section.]

Caisson piles. [Steel cased piles constructed by advancing a steel shell seated into rock and drilling of an uncased socket within the rock. The shell and socket are filled with a steel core section or steel reinforcing, and concrete or grout.]

Compacted concrete piles. [Compacted concrete piles are constructed by filling a driven casing with low-strength concrete and compacting the concrete as the casing is withdrawn.]

Composite Piles. [Composite piles consist of two or more approved pile types joined together.]

Concrete-filled steel pipe and tube piles. [Concrete-filled steel pipe and tube piles are constructed by driving a steel pipe or tube section into the soil and filling the pipe or tube section with concrete. The steel pipe or tube section is left in place during and after the deposition of the concrete.  For the purposes of this code these piles shall be considered driven piles.]

DAMPPROOFING. [Dampproofing is a protective measure applied to building foundation walls and slabs to prevent moisture from passing into interior spaces.]

DEEP FOUNDATIONS. [Deep foundations are comprised of concrete, grout, wood or steel structural elements either driven, drilled or jacked into the ground or cast in place. Deep foundations are relatively slender in comparison to their length, with lengths exceeding 12 times the least horizontal dimension. Deep foundations derive their load-carrying capacity through skin friction, end bearing, or a combination thereof.]

DRILLED DISPLACEMENT PILES.

Driven uncased piles. [Driven uncased piles are constructed by driving a steel shell into the soil to shore an unexcavated hole that is later filled with concrete. The steel casing is lifted out of the hole during the deposition of the concrete. Driven uncased piles are not permitted under the provisions of this code.]

Enlarged base piles. [Enlarged base piles are cast-in-place concrete piles constructed with a base that is larger than the diameter of the remainder of the pile. The enlarged base is designed to increase the load-bearing area of the pile in end bearing. Enlarged base piles include piles installed by driving a precast concrete tip or by compacting concrete into the base of the pile to form an enlarged base.]

[Helical Piles. Helical piles are manufactured deep foundation steel elements consisting of a shaft and one or more helical bearing plates (helices) screwed into the ground by application of torque on the shaft.  The various products marketed as screw piles, torque anchors, and helical piers are considered helical piles.]

[H-piles. Steel H-piles are constructed by driving a steel H-shaped section into the ground.]

FIXED HEADED PILE (DEEP FOUNDATION). [A pile connected to a pile cap in a manner that prevents rotation of the pile head.]

FREE HEADED PILE. [A pile with a head that is free to rotate.]

GEOTECHNICAL CAPACITY OF DEEP FOUNDATIONS. [The load that can be supported by the soil or rock surrounding deep foundation as determined using a recognized method of analysis or as established by load tests.  The geotechnical capacity can be developed through skin friction, end bearing, or a combination thereof.]

HELICAL PILES.

H-PILES.

LIQUEFACTION. [For granular soils, liquefaction is defined as the loss of shear strength in soils resulting from increased pore-water pressure and reduced effective stress that may develop as a result of cyclic loading during earthquakes.  For cohesive soils with a plasticity index of less than 20, liquefaction is defined as any transient softening and increased cyclic shear strains that may occur during earthquakes.]

Micropile. [A micropile is a drilled and grouted deep foundation element with a diameter that measures 5-inches (127 mm) to 14-inches (356 mm) that develops its load-carrying capacity by means of a bond zone in soil (also commonly known as a minipile).]

PERMANENT PRESTRESSED ROCK AND SOIL ANCHORS.

PIER FOUNDATION. [A pier foundation is a shallow foundation element of masonry or cast-in-place concrete construction. Piers are relatively short in comparison to their width, with lengths less than or equal to 12 times the least horizontal dimension of the pier. Piers derive their load-carrying capacity from end bearing on soil or rock.]

RETAINING WALL. [A wall that resists lateral or other forces caused by soil, rock, water or other materials, thereby limiting lateral displacement and the movement of the supported materials. Basement walls and vault walls that are parts of buildings and underground structures, including but not limited to utility vault structures, tunnels and transit stations, are not considered retaining walls.]

SHALLOW FOUNDATION. [A shallow foundation is an individual or strip footing, a mat foundation, a slab-on-grade foundation or a similar foundation element.]

UNDERPINNING. [The alteration of an existing foundation to transfer loads to a lower bearing stratum using new piers, piles, or other structural support elements installed below the existing foundation.]

WATERPROOFING. [Waterproofing is a protective measure applied to building foundation walls and slabs to prevent moisture and liquid water from passing into interior spaces.]

SECTION BC [1802] 1803
GEOTECHNICAL INVESTIGATIONS AND MATERIAL CLASSIFICATIONS

[1802.1] 1803.1 General. Geotechnical investigations shall be subject to special inspections in accordance with Sections [1704.7, 1704.8 and 1704.9] 1705.6, 1705.7 and 1705.19 and be conducted in [conformance] accordance with Sections [1802.2] 1803.2 through [1802.7] 1803.7. An engineer shall scope, supervise and approve the subsurface investigation and the classification of the soil and rock encountered.

[1802.2] 1803.2 Where required. A geotechnical investigation shall be performed and report shall be prepared [conducted] for:

1.	New structures;

2.	Horizontal enlargements;

3.	Vertical enlargements or alterations necessitating new foundations or resulting in additional loading that exceeds 5 percent of the existing foundation design capacity; or

4.	As required by the commissioner or applicant of record.

The geotechnical investigation shall be performed in accordance with Sections [1802.4] 1803.4 through [1802.6] 1803.6.  For structures in Seismic Design Category C or D, the requirements of Sections [1802.2.1] 1803.2.1 and [1802.2.2] 1803.2.2 shall also apply.

[1802.2.1] 1803.2.1 Seismic Design Category C. [Where a structure is determined to be in] For structures assigned to Seismic Design Category C in accordance with Section 1613, the geotechnical investigation shall include an evaluation of the following potential geologic and seismic hazards [resulting from earthquake motions: slope instability, liquefaction and surface rupture due to faulting or lateral spreading. Peak ground acceleration for use in liquefaction analyses shall be determined in accordance with Section 1813.2.1.]:

1.	Slope instability.

2.	Liquefaction. Peak ground accelerations for use in such analyses shall be determined in accordance with Section 1816.2.1.

3.	Total and differential settlement.

4.	Surface displacement due to faulting or seismically induced lateral spreading or lateral flow.

[1802.2.2] 1803.2.2 Seismic Design Category D. [Where a structure is determined to be in] For structures assigned to Seismic Design Category D in accordance with Section 1613, the [requirements for Seismic Design Category C, given in] geotechnical investigation shall meet the requirements of Section [1802.2.1, shall be met. In addition, the following shall be conducted] 1803.2.1 and the following as applicable:

1.	A determination of dynamic seismic lateral earth pressures on [basement, cellar,] foundation walls and retaining walls supporting more than 6 feet (1830 mm) of in situ soil or backfill height due to design earthquake ground motions. Peak ground acceleration for use in lateral pressure analyses shall be determined in accordance with Section [1813.2.1] 1816.2.1.

2.	The potential for liquefaction and soil strength loss evaluated for site peak ground acceleration, earthquake magnitude and source characteristics consistent with the maximum considered earthquake ground motions. Peak ground accelerations for use in such analyses shall be determined in accordance with Section 1816.2.1.

3.	An assessment of potential consequences of [any] liquefaction and soil strength loss[,] including [estimation of differential settlement, lateral movement or reduction in foundation soil-bearing capacity. Mitigation measures shall be addressed. Such measures shall be given consideration in the design of the structure and shall include, but are not limited to, ground stabilization, selection of appropriate foundation type and depths, selection of appropriate structural systems to accommodate anticipated displacements or any combination of these measures.], but not limited to, the following:

3.1.	Estimation of differential settlement.

3.2.	Lateral soil movement.

3.3.	Lateral soil loads on foundations.

3.4.	Reduction in foundation soil-bearing capacity and lateral soil reaction

3.5.	Soil downdrag and reduction in axial and lateral soil reaction for pile foundations.

3.6.	Increases in soil lateral pressures on retaining walls.

3.7.	Flotation of buried structures.

4.	Discussion of mitigation measures such as, but not limited to, the following:

4.1.	Selection of appropriate foundation type and depths.

4.2.	Selection of appropriate structural systems to accommodate anticipated displacements and forces.

4.3.	Ground stabilization.

4.4.	Any combination of these measures and how they shall be considered in the design of the structure.

[1802.3] 1803.3 Material classification. Soil and rock classification shall be based on materials disclosed by borings, test pits or other subsurface exploration methods. Soil classifications shall be determined in accordance with ASTM D2487 (refer to Table [1802.3] 1803.3) and the supplemental definitions contained herein. Rock classifications shall be determined in accordance with generally accepted engineering practice and the supplemental definitions contained herein.  Laboratory tests shall be conducted to ascertain these classifications where deemed necessary by the engineer responsible for the geotechnical investigation or the commissioner.

BEDROCK.

1.	Hard sound rock (Class 1a). Includes crystalline rocks, such as gneiss, granite, diabase and mica schist. Characteristics are as follows: the rock rings when struck with pick or bar; the rock does not disintegrate after exposure to air or water; the rock breaks with sharp fresh fracture; cracks are unweathered, less than ⅛-inch (3.2 mm) wide, and generally no closer than 3 feet (914 mm) apart; and the RQD (rock quality designation) with a double tube, NX-size diamond core barrel is generally 85 percent or greater for each 5-foot (1524 mm) run; or core recovery with BX-size core is generally 85 percent or greater for each 5-foot (1524 mm) run.

2.	Medium hard rock (Class 1b). Includes crystalline rocks of paragraph (1) of this subdivision, plus marble and serpentinite. Characteristics are as follows: all those listed in paragraph (1) of this subdivision, except that cracks may be ¼-inch (6.4 mm) wide and slightly weathered, generally spaced no closer than 2 feet (610 mm) apart; and the RQD with a double tube, NX-size diamond core barrel is generally between 50 and 85 percent for each 5-foot (1524 mm) run; or core recovery with BX-size core is generally 50 to 85 percent for each 5-foot (1524 mm) run.

3.	Intermediate rock (Class 1c). Includes rocks described in paragraphs (1) and (2) of this subdivision, plus cemented shales and sandstone. Characteristics are as follows: the rock gives dull sound when struck with pick or bar; does not disintegrate after exposure to air or water; broken pieces may show moderately weathered surfaces; may contain fracture and moderately weathered zones up to 1 inch (25 mm) wide spaced as close as 1 foot (305 mm) apart; and the RQD with a double tube, NX-size diamond core barrel is generally 35 to 50 percent for each 5-foot (1524 mm) run; or a core recovery with BX-size core of generally 35 to 50 percent for each 5-foot (1524 mm) run.

4.	Soft rock (Class 1d). Includes rocks described in paragraphs (1), (2), and (3) of this subdivision in highly weathered condition, plus talc schist and poorly cemented shales and sandstones. Characteristics are: rock may soften on exposure to air or water; may contain highly weathered zones up to 3 inches (76 mm) wide but filled with stiff soil; and either the RQD with a double tube, NX-size diamond core barrel is less than 35 percent for each 5-foot (1524 mm) run or core recovery with BX-size core of generally less than 35 percent for each 5-foot (1524 mm) run, or a [standard penetration resistance more] value of N60 greater than 50 blows per foot (0.3 meters).

SANDY GRAVEL AND GRAVELS. Consists of coarse-grained material with more than half of the coarse fraction larger than the #4 size sieve and contains little or no fines (GW and GP). The density of these materials shall be determined in accordance with the following:

Dense (Class 2a). These materials have [a standard penetration test N-value] a value of N60 greater than 30 blows per 1 foot (0.3 meter).

Medium (Class 2b). These materials have [a standard penetration test N-value] a value of N60 between 10 and 30 blows per 1 foot (0.3 meter).

Loose (Class 6). These materials have [a standard penetration test N-value] a value of N60 less than 10 blows per 1 foot (0.3 meter). These materials shall be considered nominally unsatisfactory bearing materials.

GRANULAR SOILS. These materials are coarse-grained soils consisting of gravel and/or sand with appreciable amounts of fines[,] and gravel. Soil types include GM, GC, SW, SP, SM, and SC. The density of granular materials shall be determined in accordance with the following:

Dense (Class 3a). These materials have [a standard penetration test N-value of] a value of N60 greater than 30 blows per 1 foot (0.3 meter).

Medium (Class 3b). These materials have [a standard penetration test N-value of] a value of N60 between 10 and 30 blows per 1 foot (0.3 meter).

Loose (Class 6). These materials have [standard penetration test N-value of fewer] a value of N60 less than 10 blows per 1 foot (0.3 meter). These materials shall be considered nominally unsatisfactory bearing materials.

CLAYS. For soil types SC, CL and CH in the absence of sufficient laboratory data, the consistency of clay materials shall be determined in accordance with the following:

Hard (Class 4a). Clay requiring picking for removal, a fresh sample of which cannot be molded by pressure of the fingers; or having an unconfined compressive strength in excess of 4 TSF (383 kPa); or having a [standard penetration test where the N-value is] value of N60 greater than 30 blows per 1 foot (0.3 meter).

Stiff (Class 4b). Clay that can be removed by spading, a fresh sample of which requires substantial pressure of the fingers to create an indentation; or having an unconfined compressive strength of between 1 TSF (96 kPa) and 4 TSF (383 kPa); or having a [standard penetration test where the N-value is] value of N60 between 8 and 30 blows per 1 foot (0.3 meter).

Medium (Class 4c). Clay that can be removed by spading, a fresh sample of which can be molded by substantial pressure of the fingers; or having an unconfined compressive strength of between 0.5 TSF (48 kPa) and 1 TSF (96 kPa); or having a [standard penetration test where the N-value is] value of N60 between 4 and 8 blows per 1 foot (0.3 meter).

Soft (Class 6). Clay, a fresh sample of which can be molded with slight pressure of the fingers; or having an unconfined compressive strength of less than 0.5 TSF (48 kPa); or having a [standard penetration test where the N-value is fewer] a value of N60 less than 4 blows per 1 foot (0.3 meter). This material shall be considered nominally unsatisfactory bearing material.

SILTS AND CLAYEY SILTS. For soil types ML and MH in the absence of sufficient laboratory data, the consistency of silt materials shall be determined in accordance with the following:

Dense (Class 5a). Silt with a standard penetration test where the [N-value is] value of N60 greater than 30 blows per 1 foot (0.3 meter).

Medium (Class 5b). Silt with a standard penetration test where the [N-value is] value of N60 between 10 and 30 blows per 1 foot (0.3 meter).

Loose (Class 6). Silt with a standard penetration test where the [N-value is] value of N60 fewer than 10 blows per 1 foot (0.3 meters).  This material shall be considered nominally unsatisfactory bearing material.

TABLE [1802.3] 1803.3
UNIFIED SOIL CLASSIFICATION (Including Identification and Description)

[1802.4] 1803.4 Investigation. An engineer shall scope and supervise the geotechnical investigation. The geotechnical investigation shall be sufficient for evaluating soil and rock conditions including, but not limited to, material classification, stratigraphy, groundwater, slope stability, soil and rock strength, adequacy of load-bearing soils and rock, the effect of moisture variation on soil-bearing capacity, compressibility, liquefaction and expansiveness. The investigation shall comply with Sections [1802.4.1] 1803.4.1 through [1802.4.4] 1803.4.4.

[1802.4.1] 1803.4.1 Scope of investigation. The scope of the geotechnical investigation, including the number, types and depths of borings, the number of test pits or the number of alternative test methods; the equipment used to drill and sample; the in-situ testing; and the laboratory testing program shall be determined by the engineer responsible for the investigation, subject to the requirements of this chapter.

1.	Borings shall be uniformly distributed under the structure or distributed in accordance with load patterns imposed by the structure.

2.	[As] At a minimum, investigations for structures shall include:

2.1.	One exploratory boring for built-over areas up to and including 750 square feet (69.7 m2).

2.2.	Two exploratory borings for built-over areas greater than 750 square feet (69.7 m2) but less than 5,000 square feet (465 m2), and at least one additional boring for each additional 2,500 square feet (233 m2), or part thereof, of built-over areas up to 20,000 square feet [(1860 m2)] (1858 m2).

2.3.	At least one boring for each additional 5,000 square feet (465 m2), or part thereof, of built-over areas in excess of 20,000 square feet [(1860 m2)] (1858 m2).

3.	At a minimum, investigations for retaining walls greater than 10 feet [(3.05 m)] (3048 mm) in height shall include one exploratory boring for every 50 linear feet [(15.24 m)] (15 240 mm) of wall.

4.	Borings shall be taken into bedrock, or to an adequate depth below the top of the load-bearing strata to demonstrate that the foundation loads have been sufficiently dissipated and to evaluate global stability of retaining walls.

5.	For structures having an average area load (dead plus live) of 1,000 pounds per square foot (47.9 kN/m2) or more, at least one boring for every 10,000 square feet (930 m2) of footprint area shall penetrate at least 100 feet (30 480 mm) below the curb grade or 5 feet (1524 mm) into bedrock of Class 1c or better, whichever is less.

6.	At least one-half of the borings satisfying this requirement shall be located within the limits of the built-up area and the remainder shall be within 25 feet (7620 mm) of the built-up area limits.

7.	For structures to be supported on deep foundations, the required number of borings shall be not less than two borings, and based on a minimum of one boring per 2,000 square feet [(609.6 m2)] (186 m2) for the first 20,000 square feet [(1860 m2)] (1858 m2) and one boring per every additional 4,000 square feet [(609.6 m2)] (372 m2) thereafter.

8.	All boring, sampling, and in-situ testing operations shall be subject to special inspection in accordance with [Section 1704.7.4] Table 1705.6.

Exception: Test pits may be substituted for borings for one and two-story structures[, and may be used only to establish the top of rock, where practical, for taller structures. For taller structures, the engineer shall submit a test pit observation report to the commissioner; for one and two-story structures, the]. The registered design professional shall [may] submit a test pit observation report to the commissioner.

[1802.4.2] 1803.4.2 Existing data. [At the request of the engineer responsible for the geotechnical investigation, the suitable] Suitable borings, test pits, probings, and the logs and records that were obtained as part of earlier exploration programs by an engineer other than the engineer performing the geotechnical investigation and that meet the requirements of this section may only be used as partial fulfillment of the requirements of [this section, subject to the approval of the commissioner] Section 1803.4.1. [Additional borings shall be made at the direction of the engineer responsible for the geotechnical investigation when uncertainty exists as to the accuracy of the available information or specific new project or loading conditions indicate the need for additional information.] Additional boring(s) shall be made to fulfill the requirements of Section 1803.4.1, with a minimum of one additional boring required.

[1802.4.3] 1803.4.3 Groundwater table. The geotechnical investigation shall determine the existing groundwater table.

[1802.4.4] 1803.4.4 Compressible soils. In areas containing compressible soils, the geotechnical investigation shall determine the extent of these soils in the plan area of the structure and shall be subject to the requirements of Section [1802.3] 1803.3.

[1802.5] 1803.5 Soil and rock sampling. The soil boring and sampling procedures and apparatus shall be in accordance with ASTM D1586 and ASTM D1587 and generally accepted engineering practice. The rock coring, sampling procedure and apparatus shall be in accordance with ASTM D2113 and generally accepted engineering practice. Rock cores shall be obtained with a double-tube core barrel with a minimum outside diameter of 2⅞ inches (73 mm). With the approval of the engineer responsible for the geotechnical investigation, smaller-diameter double-tube core barrels may be used under special circumstances such as telescoping casing to penetrate boulders, or space limitations requiring the use of drill rigs incapable of obtaining large-diameter cores.

[1802.5.1] 1803.5.1 Bedrock support. Where the foundation design relies on rock to support footings, [piles] deep foundations or caisson sockets, or permanent prestressed rock anchors, a sufficient number of rock corings shall [extend at least 10 feet (3048 mm) below the lowest level of bearing to provide assurance of the rock soundness] be drilled to sufficient depths to assess the competency of the rock and its load-bearing capacity, but no less than 10 feet (3048 mm) below the lowest level of bearing. [Where foundations are to rest on bedrock and such rock is exposed over a part or all of the area of the building, borings are not required in those areas where rock is exposed, provided the following requirements are met:]

[1.	The presence of defects or the inclination of bedding planes in the rock are of such size and location so as not to affect stability of the foundation.]

[2.	The foundation is not designed for bearing pressures exceeding those permitted in Table 1802.3.]

[1802.5.2] 1803.5.2 Alternative investigative methods. The engineer responsible for the geotechnical investigation may engage specialized technicians to conduct alternative investigative methods such as cone penetrometer testing (CPT) performed in accordance with ASTM D3441 or ASTM D5778. Data from these investigations may be used to (1) supplement soil boring and rock coring information, provided there is a demonstrated correlation between the findings, and (2) determine material properties for static and seismic or liquefaction analyses. [Subject to the approval of the commissioner, alternate exploration methods] CPTs may replace borings on a one [and one-half for] to one basis, but in no case shall there be fewer than half the required standard borings as per Section [1802.4.1] 1803.4.1, and no less than two standard borings. The boring depth requirements of Section [1802.4.1] 1803.4.1 shall be accomplished with borings. The alternative investigative methods must be capable of extending to the depths of the required borings. Other in-situ testing methods, such as geophysical, vane shear, and [pressure meter] pressuremeter, may be used to determine engineering design parameters, but may not be used as a substitute for the required number of borings.

[1802.5.3] 1803.5.3 Material disposition. Soil and rock samples shall be maintained in an accessible location by the permit holder or owner and made available to the engineer responsible for the geotechnical investigation and to the department, until the foundation work has been completed and accepted, or until 1 year after the investigation is complete, whichever is longer.

[1802.6 Reports.]

[1802.6.1 Conditions requiring geotechnical reports. The owner or applicant of record shall submit a written report to the commissioner for any of the following conditions:]

[1.	Any load-bearing value greater than those in Section 1804 is claimed.]

[2.	The structure is determined to be in Seismic Design Category C or D in accordance with Section 1613.]

[3.	Test pits are implemented in lieu of borings as per Section 1802.4.1.]

[4.	The structure will bear on or above compressible soils (see Section 1804.2.2), uncontrolled fill (see Section 1804.2.3), or artificially treated soils (see Section 1804.2.4).]

[5.	As required by the commissioner.]

1803.6 Geotechnical reports. A geotechnical engineering report shall be prepared for all sites and submitted to the commissioner.

Exception: One- and two-family dwellings no more than three stories in height shall not require a geotechnical report except where any of the following exist:

1.	Shallow foundations are used that bear on or above compressible soils (see Section 1803.4.4), uncontrolled fill (see Section 1806.2.3), or artificially treated soils (see Section 1806.2.4);

2.	Underpinning is required;

3.	The structure is within the special flood hazard area;

4.	Dewatering is required;

5.	Test pits are implemented in lieu of borings as per Section 1803.4.1; or

6.	As required by the commissioner.

[1802.6.2] 1803.6.1 Information required in geotechnical reports. The geotechnical report shall be prepared by the engineer responsible for the geotechnical investigation and shall be signed and sealed. The geotechnical report submitted to the commissioner shall include the foundation system shown on the drawings submitted to the department. The report shall include, but need not be limited to, the following information:

1.	A description of the planned structure.

2.	A plot showing the location of test borings, excavations, probes, and/or other exploration techniques.

3.	A complete record of the soil and/or rock sample descriptions.

4.	A record of the soil and/or rock profile.

5.	Elevation of the groundwater table[,] (if encountered), base flood elevation (if applicable), and design flood elevation.

6.	Results of in-situ or geophysical testing.

7.	Results of laboratory testing.

8.	Recommendations for foundation type and design criteria, including but not limited to allowable bearing capacity of natural or compacted soil and/or rock; soil stiffness parameters required for design of the foundations; mitigation of the effects of liquefaction (if applicable); site class; Mapped MCER spectral acceleration parameters (SS and S1); design spectral response acceleration parameters (SDS and SD1); site adjusted peak ground acceleration (PGAM); differential settlement and varying soil and/or rock strength; and the effects of adjacent loads.

9.	Design lateral earth pressures on foundation walls and other retaining walls.

10.	Recommendations for the evaluation of adjacent properties potentially impacted by the proposed construction.

11.	Where dewatering is required, recommendations for the maximum permissible drawdown outside the site.

[9.] 12.	Expected total and differential settlement.

[10.] 13.		Special design and construction provisions for footings or foundations founded on expansive soils, as necessary.

[11.] 14.		Compacted fill material properties and testing in accordance with Section [1803.5] 1804.6.

[12.] 15.		Controlled low-strength material properties and testing in accordance with Section [1803.6] 1804.7.

[13.] 16.		A list of anticipated special inspections required for construction of earthwork and foundations.

[14.] 17.		For deep foundations reports, the requirements outlined in Section [1808.2.2] 1810.2.2.

18.	For permanent prestressed rock and soil anchor reports, the requirements outlined in Section 1815.2.

19.	Soil and rock parameters to be used to determine the safe slope of temporary excavations pursuant to Section 3304.4.1.

[1802.7] 1803.7 Construction documents. Construction documents shall be prepared in accordance with Section 106.7.1.

SECTION BC [1803] 1804
EXCAVATION, GRADING AND FILL

[1803.1] 1804.1 Excavations near foundations. Excavations for any purpose shall not [remove] reduce vertical or lateral support [from] for any foundation without first evaluating if underpinning or protecting the foundation against [settlement or lateral translation] detrimental lateral or vertical movement, or both, is required. Where required, underpinning or shoring shall be provided in accordance with Section [1814] 1817.

[1803.2] 1804.2 Placement of backfill. The excavation outside the foundation shall be backfilled with soil that is free of organic material, construction debris, or boulders. A controlled low-strength material (CLSM) can be used as backfill in lieu of soil. Soil backfill shall be placed in lifts and compacted in a manner that does not damage the foundation or the waterproofing or dampproofing material.

Exception: Controlled low-strength material need not be compacted.

1804.3 Surcharge. No fill or other surcharge loads shall be placed adjacent to any building or structure unless such building or structure is capable of withstanding the additional loads caused by the fill or the surcharge.

Exception: Grading for landscaping purposes shall be permitted where done with walk-behind equipment where the grade is not increased more than one foot (305 mm) from original design grade, or where approved by the commissioner.

[1803.3] 1804.4 Site grading. The ground immediately adjacent to the foundation shall be sloped away from the structure as needed, or an approved alternate method of diverting water away from the foundation shall be used, where surface water would detrimentally affect the foundation material (soil and/or rock). Grading shall not be detrimental to the bearing material of adjacent structures.  Site grading shall also comply with Section 1101.11 of the New York City Plumbing Code.

[1803.3.1] 1804.4.1 Seepage. In an excavation where soil and groundwater conditions are such that an inward or upward seepage might be produced in materials intended to provide vertical or lateral support for foundation elements or for adjacent foundations, excavating methods shall control or prevent the inflow of ground water to prevent disturbance of the soil material in the excavation or beneath existing buildings. No foundation shall be placed on soil that has been disturbed by seepage unless remedial measures have been taken.

[1803.4] 1804.5 Grading and filling in flood hazard areas. Grading and/or filling in areas of special flood hazard shall not be permitted except as permitted in Appendix G.

[1803.5] 1804.6 Compacted fill material. Where foundations will bear on compacted fill material, the compacted fill shall comply with the provisions of a geotechnical report prepared, signed and sealed by the engineer, which shall contain the following:

1.	Specifications for the preparation of the site prior to placement of compacted fill material.

2.	Specifications for material to be used as compacted fill.

3.	Test method(s) to be used to determine the maximum dry density and optimum moisture content of the material to be used as compacted fill.

4.	Maximum allowable thickness of each lift of compacted fill material.

5.	Field test method(s) for determining the in-place dry density of the compacted fill.

6.	Minimum acceptable in-place dry density expressed as a percentage of the maximum dry density determined in accordance with Item 3.

7.	Number and frequency of field tests required to determine compliance with Item 6.

8.	Acceptable types of compaction equipment for the specified fill materials.

[1803.6] 1804.7 Controlled low-strength material (CLSM). Where footings will bear on controlled low-strength material (CLSM), the CLSM shall comply with the provisions of a geotechnical report prepared, signed and sealed by the engineer, which shall contain the following:

1.	Specifications for the preparation of the site prior to placement of the CLSM.

2.	Specifications for the CLSM.

3.	Laboratory or field test method(s) to be used to determine the compressive strength or bearing capacity of the CLSM.

4.	Test methods for determining the acceptance of the CLSM in the field.

5.	Number and frequency of field tests required to determine compliance with Item 4.

SECTION BC 1805
DAMPPROOFING AND WATERPROOFING

1805.1 Where required. Walls or portions thereof that retain soil or rock and enclose interior spaces and floors below grade shall be waterproofed or dampproofed in accordance with this section, with the exception of those spaces containing occupancy groups other than residential and institutional where such omission is not detrimental to the building or occupancy. Ventilation for crawl spaces shall comply with Section 1203.3.

1805.1.1 Flood hazard areas. Buildings and structures in areas of special flood hazard shall comply with Appendix G.

1805.2 Dampproofing required. Where hydrostatic pressure will not occur as determined by Section 1803, floors and walls for other than wood foundation systems shall be dampproofed in accordance with this section. Wood foundation systems shall be constructed in accordance with AWC TR7.

1805.2.1 Floors. Dampproofing materials for floors shall be installed between: (i) the floor and (ii) the base course required by Section 1805.4.1 or the sub-floor. Subgrade for the dampproofing material shall be prepared in accordance with manufacturer’s recommendations. Dampproofing material shall be installed in accordance with manufacturer’s recommendations and protected after placement.  Any damaged areas and punctures must be repaired prior to placement of slab.  All penetrations shall be sealed as per manufacturer’s recommendations.

1805.2.2 Walls. Dampproofing materials for walls shall be installed on the exterior surface of the wall, and shall extend from the top of the footing to above ground level as determined by the registered design professional and shall be installed in accordance with manufacturer’s recommendations.  Dampproofing at walls shall overlap or extend past the slab dampproofing such that there are no gaps or breaches in the dampproofing system.

1805.3 Waterproofing required. Where the geotechnical investigation required by Section 1803 indicates that a hydrostatic pressure condition exists, walls and floors shall be waterproofed in accordance with this section.

1805.3.1 Floors. Floors required to be waterproofed shall be designed and constructed to withstand the hydrostatic pressures to which the floors will be subjected. Waterproofing shall be accomplished by creating a continuous water seal below the floor using appropriate waterproofing materials. Joints, penetrations and other interruptions shall be sealed in accordance with manufacturer’s recommendations.  Floor waterproofing must be transitioned to accomplish a complete tie-in with the foundation wall waterproofing.

1805.3.2 Walls. Walls required to be waterproofed shall be designed and constructed to withstand the hydrostatic pressures and other lateral loads to which the walls will be subjected. Waterproofing shall be applied from the bottom of the wall to not less than 12 inches (305 mm) above the maximum elevation of the groundwater table or as directed by the registered design professional.  The remainder of the wall shall be dampproofed in accordance with Section 1805.2.2. Joints, penetrations and other interruptions shall be sealed in accordance with manufacturer’s recommendations.

1805.3.3 Joints and penetrations. Joints in or between walls and floors, and penetrations of walls and floors shall be sealed utilizing methods and materials approved by the registered design professional. Joints, penetrations and other interruptions shall be sealed in accordance with the manufacturer’s recommendations.

1805.4 Subsoil drainage system. Where it is determined that there is a potential for infiltration or seepage, a subsoil drainage system shall be permitted to be used to control this inflow, provided that:

1.	The below ground space is waterproofed or dampproofed per Sections 1805.2 and 1805.3; and

2.	The estimated discharge from the drainage system is less than or equal to the amount allowed by the agency having jurisdiction.

1805.4.1 Drainage course. A drainage course shall consist of washed gravel, crushed natural stone or other suitable drainage medium acceptable to the engineer.  Recycled concrete aggregate is not acceptable for use in a drainage course where a subsoil drainage system is used.

1805.4.2 Foundation drain. A foundation drain shall be installed where required by the registered design professional.  The foundation drain, including layout, materials, and cleanouts, shall be designed by the registered design professional.

1805.4.3 Drainage discharge. The drainage course and foundation drain shall discharge by gravity or mechanical means into an approved drainage system that complies with the New York City Plumbing Code and any other laws or requirements of agencies having jurisdiction.

1805.5 In situ walls. In situ walls (such as slurry walls, tangent pile walls, and secant pile walls) with joints sealed by grouting or other methods acceptable to the engineer shall not require waterproofing or dampproofing unless required by the engineer.

SECTION BC [1804] 1806
ALLOWABLE LOAD-BEARING VALUES OF SOILS AND ROCK

[1804.1] 1806.1 Design. The allowable bearing pressures provided in Table [1804.1] 1806.1 shall be used with the allowable stress design load combinations specified in Section 1605.3.

| TABLE [1804.1] 1806.1 ALLOWABLE BEARING PRESSURES |
| --- |
| CLASS OF MATERIALS (Notes 1 and 3) | MAXIMUM ALLOWABLE BEARING PRESSURE (TSF) | MAXIMUM ALLOWABLE BEARING PRESSURE (kPa) |
| 1. Bedrock (Notes 2 and 7) |  |  |
| 1a Hard sound rock | 60 | 5,746 |
| 1b Medium rock | 40 | 3,830 |
| 1c Intermediate rock | 20 | 1,915 |
| 1d Soft rock | 8 | 766 |
| 2. Sandy gravel and gravel (GW, GP) (Notes [3,] 4, 8, and 9) |  |  |
| 2a Dense | 10 | 958 |
| 2b Medium | 6 | 575 |
| 3. Granular soils (GC, GM, SW, SP, SM, and SC) (Notes 4, 5, 8, and 9) |  |  |
| 3a Dense | 6 | 575 |
| 3b Medium | 3 | 287 |
| 4. Clays (SC, CL, and CH) (Notes 4, 6, 8, and 9) |  |  |
| 4a Hard | 5 | 479 |
| 4b Stiff | 3 | 287 |
| 4c Medium | 2 | 192 |
| 5. Silts and silty soils (ML and MH) (Notes 4, 8, and 9) |  |  |
| 5a Dense | 3 | 287 |
| 5b Medium | 1.5 | 144 |
| 6.[.] Nominally Unsatisfactory Bearing Materials: Loose granular soils Soft clay soils Loose silt [●] All organic silts, organic clay, peats, soft clays, granular soils and varved silts | See [1804.2.1 1806.2.1 | See [1804.2.1 1806.2.1 |
| 7. Controlled and uncontrolled fills | See [1804.2.2 or 1804.2.3] 1806.2.2 or 1806.2.3 | See [1804.2.2 or 1804.2.3] 1806.2.2 or 1806.2.3 |

Notes:

- Where there is doubt as to the applicable classification of a soil or rock stratum, the allowable bearing pressure applicable to the lower class of material to which the given stratum might conform shall apply.

- The tabulated values of allowable bearing pressures apply only for massive rocks, or for sedimentary or foliated rocks where the strata are level or nearly so, and then only if the area has ample lateral support. The allowable bearing pressure for tilted strata and their relation to nearby slopes or excavations shall be evaluated by the engineer responsible for the geotechnical investigation. The tabulated values for Class 1a materials (hard sound rock) may be increased by 25 percent provided the engineer performs additional tests and/or analyses substantiating the increase.

- For intermediate conditions, values of allowable bearing pressure shall be estimated by interpolation between indicated extremes.

- Footing embedment in soils shall be in accordance with Section [1805.3] 1809.3 and the width of the loaded area shall not be less than 18 inches (457 mm), unless analysis demonstrates that the proposed construction will have a minimum factor of safety of 2.0 against shear failure of the soil.

- Estimates of settlements shall govern the allowable bearing pressure, subject to the maximums given in this table, and as provided in Section [1804.2] 1806.2.

- Allowable bearing pressure of clay soils shall be established on the basis of the strength of such soils as determined by field or laboratory tests and shall provide a factor of safety against failure of the soil of not less than 2.0 computed on the basis of a recognized procedure of soils analysis, shall account for probable settlements of the building and shall not exceed the tabulated maximum values.

- Allowable bearing pressure may be increased due to embedment of the foundation. The allowable bearing pressure for intermediate rock (1c), medium hard rock (1b), and hard sound rock (1a) shall apply where the loaded area is on the rock surface. Where the loaded area is below the rock surface and is fully confined by the adjacent rock mass and provided that the adjacent rock mass above the bearing surface is of [the same] rock class 1c or better, and the rock mass has not been shattered by blasting or otherwise is or has been rendered unsound, the allowable bearing pressure  may be increased 10 percent of the base value for each 1 foot (0.3 meters) of embedment below the surface of the adjacent rock surface in excess of 1 foot (0.3 meters), but shall not exceed 200 percent of the values.

- The allowable bearing pressure for soils of Classes 2, 3, 4, and 5 determined in accordance with Notes 3, 4, and 5 above, shall apply where the loaded area is embedded 4 feet (1219 mm) or less in the bearing stratum. Where the loaded area is embedded more than 4 feet (1219 mm) below the adjacent surface of the bearing stratum, and is fully confined by the weight of the adjacent soil, the allowable bearing pressure may be increased 5 percent of the base value for each 1-foot (305 mm) additional embedment, but shall not exceed twice the values. Increases in allowable bearing pressure due to embedment shall not apply to soft rock, clays, silts and soils of Classes 6 and 7.

- The allowable bearing pressure for soils of Classes 2, 3, 4, and 5 determined in accordance with this table and the notes thereto, may be increased up to ⅓ where the density of the bearing stratum below the bottom of the footings increases with depth and is not underlain by materials of a lower allowable bearing pressure. Such allowable bearing pressure shall be demonstrated by a recognized means of analysis that the probable settlement of the foundation due to compression, and/or consolidation does not exceed acceptable limits for the proposed building.

10.	The maximum toe pressure for eccentrically loaded footings may exceed the allowable bearing pressure by up to 25 percent if it is demonstrated that the heel of the footing is not subjected to tension.

[1804.2] 1806.2 Allowable bearing pressure. The allowable bearing pressure for supporting soil and rock [at or near the surface] shall not exceed the values specified in Table [1804.1] 1806.1, unless data to substantiate the use of a higher value are developed and contained in the engineer’s geotechnical report, and the commissioner approves such value. Allowable bearing pressure shall be considered to be the pressure at the base of a foundation in excess of the [stabilized overburden pressure] effective stress existing at the same level prior to construction operations.

[1804.2.1] 1806.2.1 Nominally unsatisfactory bearing material. Organic silts, organic clays, peats, soft clays, loose granular soils, loose silts, and varved silts shall be considered nominally unsatisfactory bearing material. The allowable bearing pressure shall be determined independently of Table [1804.1] 1806.1 subject to the following:

1.	For varved silts, the soil bearing pressure produced by the proposed building shall not exceed 2 tons per square foot (192 kPa), except that for desiccated or over consolidated soils, higher bearing pressures are allowed subject to approval by the commissioner.

2.	For organic silts or clays, peats, soft clays, loose granular soils, or loose silts, the engineer responsible for the geotechnical investigation shall establish the allowable soil bearing pressure based upon the soil’s specific engineering properties. This may require that the soils be preconsolidated, artificially treated or compacted.

3.	A report prepared, signed and sealed by the engineer is required to be filed with the department to substantiate the design soil pressures to be used on soil materials and shall contain, at a minimum:

3.1.	Sufficient laboratory test data on the compressible material to indicate the soil strength and the preconsolidation pressure, coefficient of consolidation, coefficient of compressibility, permeability, secondary compression characteristics, and Atterberg limits.

3.2.	Where the design contemplates improvement of the natural bearing capacity and/or reduction in settlements by virtue of preloading, cross sections showing the amount of fill and surcharge to be placed, design details showing the required time for surcharging, and computations showing the amount of settlement to be expected during surcharging and the estimated amount and rate of settlement expected to occur after the structure has been completed, including the influence of dead and live loads of the structure.

3.3.	A detailed analysis showing that the anticipated future settlement will not adversely affect the performance of the structure.

3.4.	Where strip drains, sand drains, or stone columns are to be used, computations showing the diameter, spacing, and anticipated method of installation of such drains.

3.5.	Records of settlement plate elevations and pore pressure readings, before, during, and after surcharging.

[1804.2.2] 1806.2.2 Controlled fills. Fills shall be considered as satisfactory bearing material of the applicable class when placed in accordance with the following procedures and subject to the special inspection provisions of Chapter 17:

1.	Area to be filled shall be stripped of all organic materials, rubbish and debris.

2.	Fill shall not be placed when frozen or on frozen or saturated subgrade.

3.	The special inspection agency shall approve the subgrade prior to fill placement.

4.	Fill material shall consist of gravel, crushed rock, recycled concrete aggregate, well-graded sand or a mixture of these, or equivalent materials with a maximum particle size of 3 inches (76.2 mm) and a maximum of 10 percent passing the #200 sieve.

5.	Fill shall be placed and compacted in lifts, not exceeding 12 inches (305 mm), at its optimum moisture content, plus or minus 2 percent, and to not less than a density of 95 percent of the optimum density as determined by ASTM D1557.

6.	Fill density shall be verified by in-place tests made on each lift.

[1804.2.2.1] 1806.2.2.1 Allowable bearing pressure of controlled fills. Provided the capacity of the underlying soil is not exceeded, the allowable bearing pressure of controlled fill shall be limited to:

1.	6 tons per square foot [(766 kPa)] (575 kPa) for gravel and crushed rock.

- 3 tons per square foot [(383 kPa)] (287 kPa) for recycled concrete aggregate and well-graded sand.

[1804.2.3] 1806.2.3 Uncontrolled fills. Fills other than controlled fill may be considered as satisfactory bearing material of applicable class, subject to the following:

1.	Where spread footings will be used, the soil within the built-up area shall be explored using test pits at every column. All test pits shall extend to depths equal to the smaller width of the footing and at least one test pit shall penetrate at least 8 feet (2438 mm) below the level of the bottom of the proposed footings. All test pits shall be backfilled with properly compacted fill. Borings may be used in lieu of test pits, provided that continuous samples of at least 3 inches (76 mm) in diameter are recovered. Where mat foundations will be used, one test pit or minimum 3 inch (76 mm) diameter sampler boring shall be provided for every 1,000 square feet [(232.3 m2)] (92.9 m2) of building footprint area.  For continuous concrete footings, one test pit or minimum 3 inch (76 mm) diameter sampler boring shall be provided for every 25 linear feet [(7.62 m)] (7620 mm).

2.	The building area shall be additionally explored using one standard boring for every 2,500 square foot (232.3 m2) of building footprint area. These borings shall be carried to a depth sufficient to penetrate into natural ground, but not less than 20 feet (6096 mm) below grade.

3.	The fill shall be composed of material that is free of voids and free of extensive inclusions of mud and organic materials such as paper, wood, garbage, cans, or metallic objects and debris.

4.	The allowable soil bearing pressure on satisfactory uncontrolled fill material shall not exceed 2 tons per square foot (192 kPa). One and two-family dwellings may be founded on satisfactory uncontrolled fill provided the dwelling site has been explored using at least one test pit, penetrating at least 8 feet (2438 mm) below the level of the bottom of the proposed footings, and the fill has been found to be composed of material that is free of voids and generally free of mud and organic materials, such as paper, garbage, cans, or metallic objects, and debris. Test pits shall be backfilled with properly compacted fill.

[1804.2.4] 1806.2.4 Artificially treated soils. Nominally unsatisfactory soil materials that are artificially compacted, cemented, or preconsolidated may be used for the support of buildings, and nominally satisfactory soil materials that are similarly treated may be used to resist soil bearing pressures in excess of those indicated in Table [1804.1] 1806.1. The engineer shall develop treatment plans and procedures and post-treatment performance and testing requirements, and submit such plans, procedures, and requirements to the commissioner for approval. After treatment, a sufficient amount of sampling and/or in-situ tests shall be performed in the treated soil to demonstrate the efficacy of the treatment for the increased bearing pressure.

[1804.3 Reserved.]

SECTION BC 1807
RETAINING WALLS AND OTHER RETAINING STRUCTURES

1807.1 General. Retaining walls shall be designed in accordance with Section 1807.2.

1807.2 Design. Retaining walls shall be designed to ensure stability against overturning, sliding, excessive foundation pressure and the effects of water pressure, including uplift. Where a keyway is extended below the wall base with the intent to engage passive pressure and enhance sliding stability, lateral soil pressures on both sides of the keyway shall be considered in the sliding analysis.

1807.2.1 Design lateral soil loads. Retaining walls shall be designed for the lateral soil loads set forth in Section 1605.

Exception: Where the structural design of a retaining wall is based on load factor design, the load factors in Section 1605.2 may be modified as follows: where water can freely flow over the top of the wall, the wall may be designed for a water pressure equal to that caused by a groundwater table elevation at the top of the wall.  For this condition, the load factor for the groundwater pressure may be reduced to 1.2.  The load factor for the lateral earth pressure shall remain at 1.6.

1807.2.2 Safety factor. Retaining walls shall be designed to resist the lateral action of soil to produce sliding and overturning with a minimum safety factor of 1.5 in each case. The load combinations of Section 1605 shall not apply to this requirement. Instead, design shall be based on 0.7 times nominal earthquake loads, 1.0 times other nominal loads, and investigation with one or more of the variable loads set to zero. The safety factor against lateral sliding shall be taken as the available soil resistance at the base of the retaining wall foundation divided by the net lateral force applied to the retaining wall.

Exception: Where earthquake loads are included, the minimum safety factor for retaining wall sliding and overturning shall be 1.1.

1807.3 Temporary retaining structures. Structural members for temporary retaining structures may be designed with a 20 percent increase in the allowable bending stress only.

SECTION BC 1808
RESERVED

SECTION BC [1805] 1809
SHALLOW FOUNDATIONS

[1805.1] 1809.1 General. Shallow foundations shall be designed and constructed in accordance with Sections [1805.1] 1809.1 through [1805.9] 1809.6. Shallow foundations shall be constructed on suitable bearing materials established in accordance with the requirements of Sections [1803] 1804 and [1804] 1806.

[1805.2] 1809.2 Stepped footings. The top surface of footings shall be level. The bottom surface of footings [is] shall be permitted to have a slope not exceeding one unit vertical in 10 units horizontal (10 percent slope). Footings shall be stepped where necessary to change the elevation of the top surface of the footing or where the surface of the ground slopes more than one unit vertical in 10 units horizontal (10 percent slope).

[1805.3] 1809.3 Depth of footings. The minimum depth of shallow foundations below the undisturbed ground surface shall be 12 inches (305 mm). Where applicable, the depth of shallow foundations shall also conform to Section [1805.3.1] 1809.3.1.

[1805.3.1] 1809.3.1 Frost protection. Except where otherwise protected from frost, shallow foundations, pile caps, and other permanent supports of buildings and structures shall be protected from frost by one or more of the following methods:

1.	Extending a minimum of 4 feet (1219 mm) below the lowest adjacent permanent exposed grade;

Exception: Grade beams shall be embedded a minimum of 18 inches (457 mm) below the lowest adjacent permanent exposed grade.

2.	Constructing in accordance with [ASCE-32] ASCE 32; or

3.	Erecting on solid rock.

Exception: Free-standing buildings meeting all of the following conditions [are not] shall not be required to be frost protected:

1.	Classified in Structural Occupancy Category I (see Table 1604.5);

2.	Area of 400 square feet (37 m2) or less; and

3.	Eave height of 10 feet (3048 mm) or less.

[1805.3.2] 1809.3.2 Foundations on frozen soil. Shallow foundations shall not bear on frozen soil.

Exception: Temporary structures may bear on frozen soil if the soil is maintained in a frozen condition throughout the service life of the temporary structures being supported. The method of maintaining the soil in a frozen condition shall be approved by the commissioner.

[1805.4] 1809.4 Shallow foundations at different levels. Where shallow foundations are supported at different levels, or are at different levels from the shallow foundations of adjacent structures, the influence of the pressures under the higher foundation on the stability of the lower foundations shall be considered in the design. The design shall consider the requirements for lateral support of the material supporting the higher foundation, the additional load imposed on the lower foundations, and assessment of the effects of dragdown on [piles] deep foundations supporting adjacent buildings or compression of soils supporting adjacent buildings.

[1805.5] 1809.5 Shallow foundations. Shallow foundations shall be designed and constructed in accordance with Sections [1805.5.1] 1809.5.1 through [1805.5.6] 1809.5.8.

[1805.5.1] 1809.5.1 Design. Shallow foundations shall be designed so that the allowable bearing capacity of the soil is not exceeded, and that differential settlements are within the allowable limits for the structure. The minimum width of shallow foundations shall be 18 inches (457 mm).

[1805.5.1.1] 1809.5.1.1 Design loads. Shallow foundations shall be designed for the most unfavorable effects due to the combinations of loads specified in Section 1605.3. The dead load shall include the weight of shallow foundations and overlying fill. Reduced live loads, as specified in Section [1607.9] 1607.11, are permitted to be used in the design of shallow foundations.

[1805.5.1.2] 1809.5.1.2 Vibratory loads. Where machinery operations or other vibrations are transmitted through the shallow foundations, consideration shall be given in the shallow foundation design to prevent detrimental disturbances of the soil.

[1805.5.1.3] 1809.5.1.3 Shifting or moving soils. When the possibility of shifting or moving soil exists, the short and long term impact of such soils shall be considered in the design of shallow foundations.

[1805.5.2] 1809.5.2 Concrete shallow foundations. The design, materials and construction of concrete shallow foundations shall comply with Sections [1805.5.2.1] 1809.5.2.1 through [1805.5.2.5] 1809.5.2.5 and the provisions of Chapter 19.

[1805.5.2.1] 1809.5.2.1 Concrete strength. Concrete in shallow foundations shall have a specified compressive strength (f’c) of not less than 2,500 pounds per square inch (psi) [(17 237 kPa)] (17.24 MPa) at 28 days.

[1805.5.2.2] 1809.5.2.2 Footing seismic ties. Where a structure is assigned to Seismic Design Category D in accordance with Section 1613, individual spread footings founded on soil defined in Section [1613.5.2] 1613.3.2 as Site Class E or F shall be interconnected by ties. Ties shall be capable of carrying, in tension or compression, a force equal to the product of the larger footing load times the seismic coefficient SDS divided by 10 unless it is demonstrated that equivalent restraint is provided by reinforced concrete beams within slabs on grade or reinforced concrete slabs on grade.

[1805.5.2.3] 1809.5.2.3 Plain concrete footings. The thickness of plain concrete footings supporting walls of other than light-frame construction shall not be less than 8 inches (203 mm) where placed on soil.

Exception: For plain concrete footings supporting Group R-3 occupancies, the thickness is permitted to be 6 inches (152 mm), provided that the footing does not extend beyond a distance greater than the thickness of the footing on either side of the supported wall.

[1805.5.2.4] 1809.5.2.4 Placement of concrete. Concrete shallow foundations shall not be placed through water unless a tremie or other method approved by the commissioner is used. Where placed under or in the presence of water, the concrete shall be deposited by approved means to ensure minimum segregation of the mix and negligible turbulence of the water.

[1805.5.2.5] 1809.5.2.5 Protection of concrete. No shallow foundation shall be placed on frozen soils unless the soils are maintained in frozen condition throughout the service life of the structure being supported. No foundation shall be placed in freezing weather unless provision is made to maintain the underlying soil free of frost. Concrete shallow foundations shall be protected from freezing during depositing and for a period of not less than five days thereafter. Water shall not be allowed to flow through the deposited concrete.

[1805.5.3] 1809.5.3 Masonry-unit footings. The design, materials and construction of masonry-unit footings shall comply with the provisions of Chapter 21.

[1805.5.4] 1809.5.4 Steel grillage footings. Grillage footings of structural steel [shapes] elements shall be separated with approved steel spacers and be entirely encased in concrete with at least 6 inches (152 mm) on the bottom and at least 4 inches (102 mm) at all other points. The spaces between the [shapes] elements shall be completely filled with concrete or cement grout.

[1805.5.5] 1809.5.5 Timber footings. Refer to Chapter 23.

[1805.5.6] 1809.5.6 Wood foundations. Refer to Chapter 23.

[1805.5.7] 1809.5.7 Pier foundations. The design, materials, and construction of pier foundations shall conform to the requirements of Sections [1805.5.2] 1809.5.2, [1805.5.3] 1809.5.3, and [1805.5.7.1] 1809.5.7.1 through [1805.5.7.6] 1809.5.7.6.

Exception: Piers shall be load tested as a deep foundation in accordance with the applicable portions of Section [1808] 1810 when the bearing stratum is not physically available for inspection during construction as required by Chapter 17.

[1805.5.7.1] 1809.5.7.1 Dimensions and height. The minimum horizontal dimension of piers shall be 2 feet (610 mm), and the height shall not exceed 12 times the least horizontal dimension.

[1805.5.7.2] 1809.5.7.2 Concrete design. Where adequate lateral support is furnished by the surrounding materials defined in Section [1808.7] 1810.7, piers may be constructed of plain or reinforced concrete and the requirements of ACI 318 shall apply.

Exception: Where adequate lateral support is not provided, and the ratio of unsupported height to least horizontal dimension does not exceed three, piers of plain concrete shall be designed and constructed as pedestals in accordance with ACI 318. Where the unsupported height to least horizontal dimension exceeds three, piers shall be constructed of reinforced concrete, and shall conform to the requirements for columns in ACI 318.

[1805.5.7.3] 1809.5.7.3 Reinforcement placement. Reinforcement shall be tied and placed as a unit in the pier prior to placement of concrete.

Exception: Steel dowels embedded 5 feet (1524 mm) or less in the pier may be placed individually.  Reinforcement is permitted to be wet set and the concrete cover that is otherwise required to measure a minimum of 2½ inches (64 mm) may be reduced to 2 inches (51 mm) for Groups R-3 and U occupancies not exceeding two stories of light-frame construction, provided the construction method is approved by the commissioner.

[1805.5.7.4] 1809.5.7.4 Concrete placement. Concrete shall be placed in such a manner as to ensure the exclusion of any foreign matter and to fill the full lateral dimensions of each pier. Concrete shall not be placed through water except where a tremie or other approved method is used. When depositing concrete from the top of the pier, the concrete shall not be chuted directly into the pier but shall be poured in a rapid and continuous operation through a funnel hopper centered at the top of the pier.

[1805.5.7.5] 1809.5.7.5 Steel shell. Where concrete piers are entirely encased within a circular steel shell, and the area of the shell steel is considered reinforcing steel, the steel shall be protected under the conditions specified in Section [1808.2.12] 1810.2.12. Horizontal joints in the shell shall be spliced to comply with Section [1808.2.11] 1810.2.11.

[1805.5.7.6] 1809.5.7.6 Dewatering. Where piers are carried to depths below the groundwater level, the piers shall be constructed by a method that will provide accurate preparation and inspection of the subgrade in dry conditions.

[1805.5.8] 1809.5.8 Foundation walls. Concrete and masonry foundation walls shall be designed in accordance with Chapter 19 or 21, respectively.

[1805.5.8.1] 1809.5.8.1 Foundation wall thickness. The minimum thickness of concrete and masonry foundation walls shall comply with Section [1805.5.8.1.1] 1809.5.8.1.1.

[1805.5.8.1.1] 1809.5.8.1.1 Thickness based on walls supported. The thickness of foundation walls shall not be less than the thickness of the wall supported, except that foundation walls of at least 8 inch (203 mm) nominal width are permitted to support brick-veneered frame walls and 10 inch wide (254 mm) cavity walls.

[1805.5.8.2] 1809.5.8.2 Foundation wall drainage. Foundation walls shall be designed to support the weight of the full hydrostatic pressure of undrained backfill unless a drainage system is installed in accordance with Sections [1807.4.2] 1805.4.2 and [1807.4.3] 1805.4.3.

[1805.5.8.3 Reserved.]

[1805.6 Reserved.]

[1805.7 Reserved.]

[1805.8 Reserved.]

[1805.9] 1809.6 Seismic requirements. For structures assigned to Seismic Design Category C or D, provisions of ACI 318 [Section 21.12] 18.13, as modified by Section [1805] 1908 of this code, shall apply when not in conflict with the provisions of Section [1805] 1809 of this code. Concrete shall have a specified compressive strength of not less than 3,000 psi (20.68 MPa) at 28 days.

Exceptions:

1.	Group R or U occupancies of light-framed construction and two stories or fewer in height are permitted to use concrete with a specified compressive strength of not less than 2,500 psi (17.2 MPa) at 28 days.

2.	One and two-family dwellings not more than three stories in height are not required to comply with the provisions of ACI 318, [Sections 21.10.1 through 21.10.3] Section 18.11, as modified by Section 1908 of this code.

[SECTION BC 1806]
[RETAINING WALLS AND OTHER RETAINING STRUCTURES]

[1806.1 General. Retaining walls shall be designed in accordance with Sections 1806.2.]

[1806.2 Design. Retaining walls shall be designed to ensure stability against overturning, sliding, excessive foundation pressure and water uplift. Where a keyway is extended below the wall base with the intent to engage passive pressure and enhance sliding stability, lateral soil pressures on both sides of the keyway shall be considered in the sliding analysis.]

[1806.2.1 Design lateral soil loads. Retaining walls shall be designed for the lateral soil loads set forth in Section 1605.]

[Exception: Where the structural design of a retaining wall is based on load factor design, the load factors in Section 1605.2 may be modified as follows: where water can freely flow over the top of the wall, the wall may be designed for a water pressure equal to that caused by a groundwater table elevation at the top of the wall. For this condition, the load factor for the groundwater pressure may be reduced to 1.2. The load factor for the lateral earth pressure shall remain at 1.6.]

[1806.2.2 Safety factor. Retaining walls shall be designed to resist the lateral action of soil to produce sliding and overturning with a minimum safety factor of 1.5 in each case. The load combinations of Section 1605 shall not apply to this requirement. Instead, design shall be based on 0.7 times nominal earthquake loads, 1.0 times other nominal loads, and investigation with one or more of the variable loads set to zero. The safety factor against lateral sliding shall be taken as the available soil resistance at the base of the retaining wall foundation divided by the net lateral force applied to the retaining wall.]

[Exception: Where earthquake loads are included, the minimum safety factor for retaining wall sliding and overturning shall be 1.1.]

[1806.3 Temporary retaining structures.  Structural members for temporary retaining structures may be designed with a 20 percent decrease in the computed bending moment only.]

[SECTION BC 1807]
[DAMPPROOFING AND WATERPROOFING]

[1807.1 Where required. Walls or portions thereof that retain soil or rock and enclose interior spaces and floors below grade shall be waterproofed or dampproofed in accordance with this section, with the exception of those spaces containing occupancy groups other than residential and institutional where such omission is not detrimental to the building or occupancy. Ventilation for crawl spaces shall comply with Section 1203.3.]

[1807.1.1 Flood hazard areas. Buildings and structures in areas of special flood hazard shall comply with Appendix G.]

[1807.2 Dampproofing required. Where hydrostatic pressure will not occur as determined by Section 1802, floors and walls for other than wood foundation systems shall be dampproofed in accordance with this section. Wood foundation systems shall be constructed in accordance with AF&PA TR7.]

[1807.2.1 Floors. Dampproofing materials for floors shall be installed between: (i) the floor and (ii) the base course required by Section 1807.4.1 or the sub-floor. Subgrade for the dampproofing material shall be prepared in accordance with manufacturer’s recommendations. Dampproofing material shall be installed in accordance with manufacturer’s recommendations, and protected after placement.  Any damaged areas and punctures must be repaired prior to placement of slab.  All penetrations shall be sealed as per manufacturer’s recommendations.]

[1807.2.2 Walls. Dampproofing materials for walls shall be installed on the exterior surface of the wall, and shall extend from the top of the footing to above ground level as determined by the registered design professional and shall be installed in accordance with manufacturer’s recommendations.  Dampproofing at walls shall overlap or extend past the slab dampproofing such that there are no gaps or breaches in the dampproofing system.]

[1807.3 Waterproofing required. Where the geotechnical investigation required by Section 1802 indicates that a hydrostatic pressure condition exists, walls and floors shall be waterproofed in accordance with this section.]

[1807.3.1 Floors. Floors required to be waterproofed shall be designed and constructed to withstand the hydrostatic pressures to which the floors will be subjected. Waterproofing shall be accomplished by creating a continuous water seal below the floor using appropriate waterproofing materials. Joints, penetrations and other interruptions shall be sealed in accordance with manufacturer’s recommendations.  Floor waterproofing must be transitioned to accomplish a complete tie-in with the foundation wall waterproofing.]

[1807.3.2 Walls. Walls required to be waterproofed shall be designed and constructed to withstand the hydrostatic pressures and other lateral loads to which the walls will be subjected. Waterproofing shall be applied from the bottom of the wall to not less than 12 inches (305 mm) above the maximum elevation of the groundwater table or as directed by the registered design professional.  The remainder of the wall shall be dampproofed in accordance with Section 1807.2.2. Joints, penetrations and other interruptions shall be sealed in accordance with manufacturer’s recommendations.]

[1807.3.3 Joints and penetrations. Joints in or between walls and floors, and penetrations of walls and floors shall be sealed utilizing methods and materials approved by the registered design professional. Joints, penetrations and other interruptions shall be sealed in accordance with the manufacturer’s recommendations.]

[1807.4 Subsoil drainage system. Where it is determined that there is a potential for infiltration or seepage, a subsoil drainage system shall be permitted to be used to control this inflow, provided that:]

[1.	The below ground space is waterproofed or dampproofed per Sections 1807.2 and 1807.3; and]

[2.	The estimated discharge from the drainage system is less than or equal to the amount allowed by the agency having jurisdiction.]

[1807.4.1 Drainage course. A drainage course shall consist of washed gravel, crushed natural stone or other suitable drainage medium acceptable to the engineer.  Recycled Concrete Aggregate is not acceptable for use in a drainage course where a subsoil drainage system is used.]

[1807.4.2 Foundation drain. A foundation drain shall be installed where required by the registered design professional.  The foundation drain, including layout, materials, and cleanouts, shall be designed by the registered design professional.]

[1807.4.3 Drainage discharge. The drainage course and foundation drain shall discharge by gravity or mechanical means into an approved drainage system that complies with the New York City Plumbing Code and any other laws or requirements of agencies having jurisdiction.]

[1807.5 In situ walls. In situ walls (such as slurry walls, tangent pile walls, and secant pile walls) with joints sealed by grouting or other methods acceptable to the engineer shall not require waterproofing or dampproofing unless required by the engineer.]

SECTION BC [1808] 1810
DEEP FOUNDATIONS

[1808.1] 1810.1 Scope. Deep foundation elements, including but not limited to timber piles, precast concrete piles, structural steel piles, cast-in-place concrete piles, caisson piles, drilled displacement piles, composite piles, and helical piles, shall comply with Section [1808. In addition,] 1810; driven piles shall comply with Section [1809] 1811; cast-in-place concrete piles shall comply with Section [1810] 1812; composite piles shall comply with Section [1811] 1813; and helical piles shall comply with Section [1812] 1814.

[1808.2 Piles] 1810.2 Deep foundations—general requirements.

[1808.2.1] 1810.2.1 General. [Piles] Deep foundations shall be designed and installed in accordance with the requirements of the geotechnical investigation and report required by Section [1802] 1803 and Sections [1808] 1810 through [1812] 1814.

[1808.2.2] 1810.2.2 Additional geotechnical investigation and report requirements. Where [pile] deep foundations are used, the geotechnical investigation and report provisions of Section [1802] 1803 shall be expanded to include, but not be limited to, consideration of the following:

1.	[Suitable pile] Recommended deep foundation types and [installed] their capacities.

2.	Designation of bearing stratum or strata.

3.	Suitable center-to-center spacing of deep foundation elements.

[3.	Driving criteria.]

4.	Reductions for group action, where necessary.

5.	Load test requirements.

6.	Durability of pile materials.

[4.] 7.	Installation procedures.

8.	Protection of adjacent structures due to installation.

[5.] 9.	Field inspection and reporting procedures (to include procedures for verification of the installed bearing capacity where required).

[6.	Pile load test requirements.]

[7.	Durability of pile materials.]

[8.	Designation of bearing stratum or strata.]

[9.	Reductions for group action, where necessary.]

[1808.2.3] 1810.2.3 Special inspection. Special inspections for deep foundations shall be performed by an engineer in accordance with Sections [1704.8] 1705.7 and [1704.9] 1705.19.

[1808.2.4] 1810.2.4 Pile caps. Pile caps shall be of reinforced concrete, and shall include all elements to which [piles] deep foundations are connected, including grade beams and mats. The soil immediately below the pile cap shall not be considered as carrying any vertical load. The tops of [piles] deep foundations shall be embedded not fewer than 3 inches (76 mm) into pile caps and the caps shall extend at least 4 inches (102 mm) beyond the outermost edges of [piles] the deep foundation elements. The tops of [piles] deep foundations shall be cut back to sound material before capping.  Pile caps shall be protected from the effects of frost in accordance with Section [1805.3.1] 1809.3.1.

[1808.2.5] 1810.2.5 More than one [pile] type, [pile] capacity or method of [pile] installation for deep foundations. In the conditions described below, the several parts of the building supported on the different [pile] types or different [pile] capacities[,] of deep foundations shall be separated by suitable joints providing for differential movement, or analysis shall be prepared by the engineer, establishing to the satisfaction of the commissioner that the proposed construction is adequate and safe, and showing that the probable settlements and differential settlements to be expected will be tolerable to the structure and not result in instability of the building.

The load test requirements of Section [1808.4] 1810.4 shall apply separately and distinctly to each [different] deep foundation type, [or] capacity [of piling or equipment used], or method of installation, except where analysis of the probable, comparative behavior of the different type or capacity of the [piling] deep foundation or the method of installation indicates that data on one type or capacity of [piling] deep foundation permit a reliable extrapolation of the probable behavior of [the piling of] other types or capacities of deep foundations. The requirements of this section apply to the following proposed conditions:

1.	Construction of a foundation for a building incorporating [utilizing piles of] more than one type or capacity of deep foundations;

2.	Modification of an existing foundation by the addition of [piles of a] deep foundations differing from the type or capacity [other than those of] used in the existing [piling] foundation;

3.	Construction or modification of a foundation utilizing different methods or more than one method of installation, or using different types or capacities of equipment (such as different types of hammers having markedly different striking energies or speeds); or

4.	Support of part of a building on [piles] deep foundations and part on [footings] shallow foundations.

[1808.2.6] 1810.2.6 Settlement analysis. The settlement of an individual [piles] deep foundation or groups of [piles] deep foundations shall be estimated based on approved methods of analysis. The predicted settlement shall cause neither harmful distortion of, nor instability in, the structure, nor cause any stresses to exceed allowable values.

[1808.2.7] 1810.2.7 Use of existing [piles] deep foundations. [Piles] Deep foundations left in place where a structure has been demolished shall not be used for the support of new construction unless the [piles] existing deep foundations are load tested in accordance with Section 1810.4, original installation and testing records of the existing deep foundations are available, or the new loads are no more than half the calculated previous loads on the [piles] existing deep foundations. The engineer shall determine and certify that the [piles] existing deep foundations are sound and meet the requirements of this code.

[1808.2.8] 1810.2.8 Special types of [piles] deep foundations. The use of types of [piles] deep foundations not specifically mentioned herein is permitted, subject to the approval of the commissioner, upon the submission of acceptable test data, calculations and other information relating to the structural properties and load capacity of such [piles] deep foundations. The allowable stresses shall not in any case exceed the limitations specified herein.

[1808.2.9] 1810.2.9 Minimum spacing of [piles] deep foundations. Minimum spacing of [piles] deep foundations shall: (i) provide for adequate distribution of the load on the [pile] deep foundation group into the supporting soil or rock, (ii) account for installation effects, and (iii) be in accordance with the recommendations of Section [1808.2.2] 1810.2.2.

[1808.2.10 Piles] 1810.2.10 Deep foundations located near a lot line. [Piles] Deep foundations located near a lot line shall be designed on the assumption that the adjacent lot will be excavated to a depth of 10 feet (3048 mm) below the nearest legally established curb level. Where such excavation would reduce the embedded length of the [pile] deep foundation, the portion of the [pile] deep foundation exposed shall be deemed to provide no lateral or vertical support, and the load-carrying determination shall discount the resistance offered by the soil that is subject to potential excavation.

[1808.2.11] 1810.2.11 Splices. Splices shall be constructed so as to provide and maintain true alignment and position of the component parts of the [pile] deep foundation element during installation and thereafter and shall be of adequate strength to transmit the vertical and lateral loads (including tensions) and the moments occurring in the [pile] deep foundation section at the location of the splice without exceeding the allowable stresses for such materials as established in Table [1808.8] 1810.8. In all cases, splices shall develop at least 50 percent of the bending capacity of the [pile in bending] deep foundation. In all cases, [pile] splices situated in the upper 10 feet (3048 mm) of the [pile] deep foundation shall be capable of resisting (at allowable working stresses) the applied moments and shears. For individual [piles] deep foundation elements or groups comprised of two [piles] deep foundation elements, splices in the upper 10 feet (3048 mm) also shall be capable of resisting the moment and shear that would result from an assumed eccentricity of the [pile] load on the deep foundation of 3 inches (76 mm). For [piles] deep foundations located near a lot line, the applied moment and shears of such [piles] deep foundations shall be determined on the basis that the adjacent site will be excavated to a depth of 10 feet (3048 mm) below the nearest established curb level as required in Section [1808.2.10] 1810.2.10.

Exception: For caissons core beams, the splice shall develop the lesser of 50 percent of the capacity of the core in bending or twice the design bending moment carried by the core at the location of the splice, provided that the core splice is not within two caisson diameters of any splice in the casing.

[1808.2.12] 1810.2.12 Protective treatment of [pile] deep foundation materials. Where boring records or site conditions indicate possible deleterious action on [pile materials] deep foundation elements because of soil constituents or other aggressive environmental factors (such as chemical seepage, the presence of salt water, electrical current, changing water levels or other factors), the [pile materials] deep foundation elements shall be adequately protected by materials, methods or processes approved by the engineer. Protective materials shall be applied to the [piles] deep foundations so as not to be rendered ineffective by driving. The effectiveness of such protective measures for the particular purpose shall have been thoroughly established by satisfactory service records or other evidence.

[Piles] Deep foundations installed in ash, garbage, or cinder fills; [piles] deep foundations that are free-standing in or near a seawater environment; [piles] deep foundations used for the support of chemical plants or coal storage; [piles] deep foundations under similar conditions of chemical seepage or aggressive action; and [piles] deep foundations that are used for support of electrical generating plants, shall be investigated regarding the need for special protective treatment. Where special protective treatment is indicated by the engineer, such [piles] deep foundations shall be protected against deterioration by encasement, coating or other device acceptable to the engineer.

[1808.2.13] 1810.2.13 Minimum concrete cover. The minimum concrete cover for cast-in-place and precast concrete piles shall be as shown in Table [1808.2.13] 1810.2.13.

| TABLE [1808.2.13] 1810.2.13 MINIMUM CONCRETE COVER FOR CAST IN PLACE AND PRECAST CONCRETE PILESa |
| --- |
| FOUNDATION ELEMENT OR CONDITION | MINIMUM COVER |
| 1. Precast nonprestressed deep foundation elements Exposed to seawater Not manufactured under plant conditions Manufactured under plant control conditions | 3 inches 2 inches In accordance with Section [7.7.3] 20.6.1.3.3 of ACI 318 |
| 2. Precast prestressed deep foundation elements Exposed to seawater Other | 2.5 inches In accordance with Section [7.7.3] 20.6.1.3.3 of ACI 318 |
| 3. Cast-in-place deep foundation elements not enclosed by a steel pipe, tube or permanent casing | 2.5 inches |
| 4. Cast-in-place deep foundation elements enclosed by a steel pipe, tube or permanent casing | 1 inch |
| 5. Structural steel core within a steel pipe, tube or permanent casing | 2 inches |
| 6. Cast-in-place drilled shafts enclosed by a stable rock socket | 1.5 inches |

For SI: 1 inch = 25.4 mm.

a.	The concrete cover provided for prestressed and nonprestressed reinforcement in foundations shall be no less than the largest applicable value specified in Table [1808.2.13] 1810.2.13. Longitudinal bars spaced less than 1½ inches (38 mm) clear distance apart shall be considered bundled bars for which the concrete cover provided shall also be no less than that required by Section [7.7.4] 20.6.1.3.4 of ACI 318. Concrete cover shall be measured from the concrete surface to the outermost surface of the steel to which the cover requirement applies. Where concrete is placed in a temporary or permanent casing or a mandrel, the inside face of the casing or mandrel shall be considered the concrete surface.

[1808.3] 1810.3 Allowable [pile] deep foundation loads. Allowable [pile] deep foundation loads shall be determined in accordance with Sections [1808.3.1] 1810.3.1 through [1808.3.5] 1810.3.5.

[1808.3.1] 1810.3.1 Determination of allowable individual axial compressive loads. The allowable individual axial compressive loads on [piles] deep foundations shall be the lesser of the allowable structural capacity of the element [and] or the allowable geotechnical capacity of the element. This allowable load shall be determined by an engineer experienced in geotechnical engineering and shall be approved by the commissioner as described below:

1.	The allowable structural capacity of the [pile] deep foundation shall be determined in accordance with Sections [1808] 1810 through [1813 of this code] 1816.

2.	The allowable geotechnical capacity of the [pile] deep foundation shall be calculated using a recognized method of analysis[,] and a minimum factor of safety of 2 with respect to failure.

3.	The allowable geotechnical capacity shall be demonstrated by load tests.

Exceptions:

1.	Allowable loads for [piles] deep foundations installed by jacking shall be determined in accordance with Section [1808.3.2] 1810.3.2.

2.	[Caissons] Caisson piles socketed into Class 1a through 1c material as defined in Table [1804.1] 1806.1.

3.	Driven [piles] deep foundations with allowable loads less than or equal to 40 tons (356 kN) (30 tons (267 kN) for timber piles).

4.	Micropiles with allowable loads less than or equal to 20 tons (178 kN), provided all of the following criteria are satisfied:

4.1.	The maximum allowable bond stress between the soil and the grout is less than or equal to 4 psi (27.6 kPa).

4.2.	The minimum bond zone diameter is greater than or equal to 9 inches (228.6 mm).

4.3.	The bond zone is formed entirely in Class 3b or better soils.

[1808.3.1.1] 1810.3.1.1 Group effects. The allowable load determined in Section [1808.3.1] 1810.3.1 shall account for [pile] group effects on deep foundations. The analysis of group effects shall be performed by an engineer experienced in geotechnical engineering and calculated using recognized methods of analysis.  This analysis shall include a bearing capacity and settlement analysis of the anticipated [pile groups] group(s) of deep foundations and shall consider the presence of weaker soil strata that may be present below the deep foundation element.

[1808.3.1.2] 1810.3.1.2 Down-drag. Where [piles] deep foundations are installed through subsiding fills or other subsiding strata and derive support from underlying firmer materials, consideration shall be given to the downward frictional forces that may be imposed on the [piles] deep foundations by the subsiding upper strata.

[1808.3.1.3] 1810.3.1.3 Bearing stratum. The plans for the proposed work shall establish, in accordance with the requirements relating to allowable bearing pressure, the bearing stratum to which the [piles] deep foundations in the various sections of the building must penetrate and the approximate elevations of the top of such bearing stratum. Where penetration of a given distance into the bearing strata is required for adequate distribution of the loads, such penetration shall be shown on the plans. The indicated elevations of the top of the bearing strata shall be modified by such additional data as may be obtained during construction. All [piles] deep foundations shall penetrate to or into the designated bearing stratum.

[1808.3.2 Piles] 1810.3.2 Deep foundations installed by jacking or other static forces. The allowable capacity of a [pile] deep foundation installed by jacking or other static forces shall be not more than 50 percent of the load or force used to install the [pile] deep foundation to the required penetration, except for [piles] deep foundations jacked into position for underpinning. The allowable capacity of each deep foundation used for permanent underpinning [pile] shall not exceed the larger of the following values: ⅔ of the total jacking force used to obtain the required penetration if the load is held constant for 7 hours without measurable settlement; or ½ of the total jacking force at final penetration if the load is held for a period of 1 hour without measurable settlement. The jacking resistance used to determine the working load shall not include the resistance offered by nonbearing soils, soils which are to be excavated or soils where support will dissipate with time.

[1808.3.3] 1810.3.3 Helical piles. The allowable axial compressive load for helical piles shall be in accordance with the requirements of Section [1812] 1814.

[1808.3.4] 1810.3.4 Allowable uplift load. Where required by the design, the allowable uplift load for a single [pile] deep foundation shall be determined in accordance with accepted engineering practices based on a minimum factor of safety of three or by uplift load tests performed in accordance with Section [1808.4.2.1] 1810.4.2.1. Where uplift load tests are performed, the maximum allowable uplift load shall not exceed the ultimate load capacity divided by a factor of safety of two. The allowable uplift load for a [pile] deep foundation group shall not exceed the sum of the allowable uplift loads of the individual [piles] deep foundations in the group, nor the uplift capacity calculating the group action of the [pile] deep foundation in accordance with accepted engineering practice where the calculated ultimate group capacity is divided by a safety factor of 2.5.

[1808.3.5] 1810.3.5 Allowable lateral load. The allowable lateral load of a single [pile] deep foundation element or a [pile] group thereof shall be determined by an approved method of analysis in accordance with accepted engineering practice.  The maximum allowable lateral load of a [pile] deep foundation shall be 1 ton (8.9 kN), unless verified by lateral load test. Load testing, where required, shall be in accordance with Section [1808.4.3] 1810.4.3. See Sections [1808.4.3.1] 1810.4.3.1 and [1808.4.3.2] 1810.4.3.2 for determining the allowable lateral load from the results of lateral load tests.

[1808.3.5.1] 1810.3.5.1 Group effects.  Lateral capacities for [pile] deep foundation groups shall be modified to account for group effects in accordance with accepted engineering practice.

[1808.4] 1810.4 Load tests. Where required, [piles] deep foundations shall be load tested in accordance with the requirements of Sections [1808.4.1] 1810.4.1 through [1808.4.3] 1810.4.3.

[1808.4.1] 1810.4.1 Compressive load tests. Where load tests are required per Section [1808.3] 1810.3 or [1808.4.1.1.1] 1810.4.1.1.1, the [piles] deep foundations shall be load tested in accordance with the applicable section.

[1808.4.1.1] 1810.4.1.1 Required number of load tests. Where load tests are required, at least one test shall be performed in each area of the foundation site within which the subsurface soil conditions are “substantially similar” in character, as determined by the engineer, and at least one test shall be performed for each [pile] deep foundation type for the entire foundation installation of the building or group of buildings on a site occupying a total area of 5,000 square feet (465 m2) or less. Where load tests are required, at least two load tests shall be performed for a site having a footprint between 5,000 square feet (465 m2) and 30,000 square feet (2787 m2), and one additional load test shall be performed for each 20,000 square feet (1860 m2) of added footprint area.  For conditions where multiple [pile] deep foundation types or capacities are used, refer to Section [1808.2.5] 1810.2.5.

[1808.4.1.1.1] 1810.4.1.1.1 Additional load tests. Where [installed pile] load bearing capacities of the installed deep foundations are in doubt, [the piles] are considered non-conforming by the engineer, or [as] where required by the commissioner, additional [piles] deep foundation elements shall be load tested to establish the allowable capacity. For friction-based deep foundations [piles] where the actual production [pile] deep foundation lengths vary more than 25 percent from that of the [test pile] deep foundations initially installed and load tested, the engineer shall determine if additional load tests are required to establish the allowable [pile] capacity of the deep foundation.  The number of additional load tests shall be determined by the engineer or commissioner.

[1808.4.1.2] 1810.4.1.2 Load test apparatus and inspection requirements. The apparatus and structure to be used in making the load test shall be designed by an engineer.  Load tests shall be performed under the observation of the special inspector.  A complete record of such tests shall be filed with the commissioner.

[1808.4.1.3] 1810.4.1.3 Compressive load test procedures. Compressive load tests shall be conducted in accordance with ASTM D1143 standard procedures and the following conditions:

1.	Dial extensometer gages shall provide readings to the nearest 0.001 inch (0.025 mm). Electrical transducers may be used to make settlement observations, provided that backup measurements are made utilizing dial extensometers as described herein at sufficient times to validate the transducer readings.

2.	If the allowable axial compressive load is less than or equal to the Basic Maximum Allowable [Pile Load] Loads on Deep Foundations in Table [1808.4.1.3] 1810.4.1.3, the total test load shall remain in place for a minimum of 12 hours, and shall be held until the average rate of settlement as measured over a 12-hour period does not exceed 0.001 inches (0.025 mm) per hour.[.] The total load shall be removed in decrements not exceeding 25 percent of the total load at 1 hour intervals or longer.  For cases where the allowable [pile] load on the deep foundation is greater than the values prescribed in Table [1808.4.1.3] 1810.4.1.3, refer to Section [1808.4.1.5] 1810.4.1.5.

3.	In addition to observations required by ASTM D1143, settlement observations shall be performed 24 hours after the entire test load has been removed.

Exception:  A static load test for drilled [piles] deep foundations using an embedding load transfer mechanism shall be considered acceptable, provided that the test is performed in general accordance with ASTM D1143 – Quick Load Test Method.  The [pile] deep foundation shall be suitably instrumented to evaluate the load transfer through soil or rock at multiple locations along the shaft.

4.	Any temporary supporting capacity that the soil might provide to the [pile] deep foundation during a load test, but which would be dissipated with time, shall be eliminated by casing off or by other suitable means, such as increasing the total test load to account for such temporary capacity.

| TABLE [1808.4.1.3] 1810.4.1.3 BASIC MAXIMUM ALLOWABLE PILE LOADS |
| --- |
| TYPE OF PILE | MAXIMUM ALLOWABLE PILE LOAD (TONS) |
| Caisson Piles | No upper limit |
| Open-end pipe (or tube) piles bearing on rock of Class 1a, 1b, or 1c | 18-in O.D. and greater 250 14-in to 18-in O.D. 200 12-in to 14-in O.D. 150 10-in to 12-in O.D. 100 8-in to 10-in O.D. 60 |
| Closed-end pipe (or tube) piles, H-piles, cast-in-place concrete, enlarged base piles, and precast concrete piles bearing on rock of Class 1a, 1b, or 1c | 150 |
| Piles (other than timber or helical piles) bearing on soft rock of Class 1d | 80 |
| Piles (other than timber or helical piles) that receive their principal support other than by direct bearing on rock of Class 1a through 1d | 75 |
| Timber piles bearing on rock of Class 1a through 1d | 25 |
| Timber piles bearing in suitable soils | 40 tons maximum permissible with load test, 30 tons maximum without load test. |
| Helical piles | 30 tons maximum permissible |

For SI: 1 ton = 907.18 kg.

[1808.4.1.4] 1810.4.1.4 High strain, dynamic compressive test methods. High strain, dynamic compressive test methods performed in accordance with ASTM D4945 shall be permitted to be used where [three] two or more load tests are required and subject to the approval of the commissioner. In such case, at least one high strain dynamic test shall be performed as a calibration on a static load tested [pile] deep foundation or nearby [pile] deep foundation driven to comparable resistance. No more than one-half of the required number of load tests may be performed by high strain dynamic methods. High strain dynamic tests shall be performed under the supervision of an engineer experienced in the methods used. The number of high strain dynamic tests shall be at least twice the number of replaced static load tests.

[1808.4.1.5] 1810.4.1.5 Acceptance criteria. The allowable [pile] load of a deep foundation shall be the lesser of the two values computed as follows:

1.	Fifty percent of the applied load causing a net settlement of the [pile] tested deep foundation of not more than 1/100 of 1 inch per ton (0.25 mm per 8.9 kN) of applied load.  Net settlement in this paragraph is defined as gross settlement due to the total test load minus the rebound after removing 100 percent of the test load.

2.	Fifty percent of the applied load causing a net settlement of the [pile] tested deep foundation of ¾ inch (19 mm). Net settlement in this paragraph is defined as the gross settlement due to the total test load less the amount of elastic shortening in the [pile] deep foundation section due to total test load. The elastic shortening shall be calculated as if the [pile] deep foundation is designed [as an] for end-bearing [pile] or [as a] friction [pile]. Alternatively, the net settlement may be measured directly using a telltale or other suitable instrumentation.

[1808.4.1.5.1] 1810.4.1.5.1 Substantiation of higher allowable loads. The basic maximum allowable [pile] loads of deep foundations tabulated in Table [1808.4.1.3] 1810.4.1.3 may be exceeded where a higher value can be substantiated on the basis of load tests and analysis, except for the loads for timber and helical piles. The provisions of Section [1808.4.1] 1810.4.1 shall be supplemented, as follows: the final load increment shall remain in place for a total of not less than 24 hours; single [test piles] tested deep foundations shall be subjected to cyclical loading in accordance with ASTM D1143 or suitably instrumented with telltales and strain gauges so that the movements of the [pile] tip and butt of the deep foundation may be independently determined and load transfer to the soil evaluated. A complete record demonstrating satisfactory performance of the test shall be submitted to the commissioner.

[1808.4.2] 1810.4.2 Uplift load test.  Where uplift load tests are required, one uplift load test shall be conducted in each area of substantially similar subsurface conditions up to 5,000 square feet (465 m2) of building footprint where [piles] deep foundations are subjected to uplift, and not less than two uplift load tests shall be conducted for each area of building footprint where [piles] deep foundations are subjected to uplift between 5,000 square feet (465 m2) and 30,000 square feet (2787 m2) and for such area one additional [upload] uplift load test shall be conducted for each 20,000 square feet (1860 m2) of additional area of building footprint where [piles] deep foundations are subject to uplift. For conditions where multiple [pile] types or capacities of deep foundations are used, refer to Section [1808.2.5] 1810.2.5.

[1808.4.2.1] 1810.4.2.1 Uplift load test procedures. Uplift load tests shall be conducted in accordance with ASTM D3689 standard procedures and the following conditions:

1.	Dial extensometer gages shall provide readings to the nearest 0.001 inch (0.025 mm). Electrical transducers may be used to make settlement observations provided that backup measurements are made utilizing dial extensometers as described herein at sufficient times to validate the transducer readings.

2.	Any temporary supporting capacity that the soil might provide to the [pile] deep foundation during a load test, but which would be dissipated with time, shall be eliminated by casing off or by other suitable means, such as increasing the total test load to account for such temporary capacity.

[1808.4.2.2] 1810.4.2.2 Uplift load test apparatus and inspection requirements. The apparatus and structure to be used in making the load test shall be designed by an engineer. Load tests shall be performed under the observation of the special inspector. A complete record of such tests shall be filed with the commissioner.

[1808.4.3] 1810.4.3 Lateral load tests. Where testing is required, lateral load tests shall be performed in accordance with ASTM D3966. A minimum of two [piles] deep foundations shall be tested for every area of similar subsurface conditions. For conditions where multiple [pile] types or capacities of deep foundations are used, refer to Section [1808.2.5] 1810.2.5.

[1808.4.3.1] 1810.4.3.1 Free headed [piles] deep foundations. For [piles] deep foundations whose heads are to be designed to be free to rotate in the final structure, the maximum test load shall be at least twice the proposed design working load. In the absence of specific project requirements as determined by the engineer, the resulting allowable load shall not be more than one-half of that test load that produces a gross lateral movement of 1 inch (25 mm) of the deep foundation at the ground surface.

[1808.4.3.2] 1810.4.3.2 Fixed headed [piles] deep foundations. For [piles] deep foundations whose heads are designed to be fixed in the final structure, the results of the load test shall be used to verify the input parameters used in the lateral load analysis.  In the absence of specific project requirements as determined by the engineer, the allowable load shall be the load that produces a gross lateral movement of ⅜ [of an] inch (9.5 mm) of the deep foundation at the ground surface in the lateral load analysis.

[1808.4.3.3] 1810.4.3.3 Lateral load test procedures. Lateral load tests shall be conducted in accordance with ASTM D3966 standard procedures. In addition, dial extensometer gages shall provide readings to the nearest 0.001 inch (0.025 mm). Electrical transducers may be used to make deflection observations, provided that backup measurements are made utilizing dial extensometers as described herein at sufficient times to validate the transducer readings.

[1808.4.3.4] 1810.4.3.4 Load test apparatus and inspection requirements. The apparatus and structure to be used in making the load test shall be designed by an engineer. Lateral load tests shall be performed under the observation of the special inspector. A complete record of such tests shall be filed with the commissioner.

[1808.5] 1810.5 Installation. Installation of [piles] deep foundations shall be subject to the requirements of Sections [1808.5.1] 1810.5.1 through [1808.5.8] 1810.5.8.

[1808.5.1] 1810.5.1 Protection of [piles] deep foundations during installation. [Piling] Deep foundations shall be handled and installed to the required penetration and resistance by methods that leave the [piles’] deep foundations’ strength unimpaired and that develop and retain the [piles’] deep foundations’ required load-bearing resistance. Any damaged [pile] deep foundation shall be satisfactorily repaired or the [pile] deep foundation shall be rejected. As an alternative and subject to the approval by the commissioner, deep foundations that are damaged [or], misaligned [piles or piles], or do not [reaching] reach their design tip elevation may be used at a reduced fraction of the design load based on an analysis by the engineer.

[1808.5.2] 1810.5.2 Equipment. Equipment and methods of installation shall be such that [piles] deep foundations are installed in their proper position and alignment[,] without damage. Equipment shall be maintained in good working order.

[1808.5.3] 1810.5.3 Preexcavation. The use of jetting, augering or other methods of preexcavation shall be subject to the approval of the commissioner. Where permitted, preexcavation shall be carried out in the same manner as used for [piles] deep foundation elements subject to load tests and in such a manner that will not impair the carrying capacity of the [piles] deep foundation elements already in place or damage adjacent structures. [Pile] The element tips of deep foundations shall be [driven] advanced below the preexcavated depth until the required resistance or penetration is obtained.

[1808.5.4] 1810.5.4 Minimum [pile penetrations] penetration of deep foundations. [Piles] Deep foundations shall penetrate the minimum distance required to develop the required load capacity of the [pile] deep foundation as established by the required penetration resistance and load tests as applicable.

[1808.5.5] 1810.5.5 Damage to adjacent structures or [piles] deep foundations. [Piles] Deep foundations shall be installed in such a manner and sequence as to prevent distortion or damage that affects the structural integrity of the [piles] deep foundations being installed, or previously installed adjacent [piles] deep foundations. The sequence of the installation shall avoid compacting the surrounding soil to the extent that other [piles] deep foundations cannot be installed properly, and shall prevent ground movements that are capable of damaging adjacent structures. [Piles] Deep foundations shall be installed with adequate provision for the protection of adjacent buildings and property.

[1808.5.6] 1810.5.6 Identification. All [pile materials] deep foundation elements shipped or delivered to the job site shall be identified for conformity to the specified grade and this identification shall be maintained continuously from the point of manufacture to the point of installation. Such shipment or delivery shall be accompanied by a certification from the material supplier or manufacturer indicating conformance with the construction documents. Such certification shall be made available to the engineer of record and the department. In the absence of adequate data, [pile materials] deep foundation elements shall be tested by an approved agency to determine conformity t o the specified grade. The approved agency shall furnish a certification of compliance to the engineer of record, or upon request to the commissioner.

[1808.5.7 Pile] 1810.5.7 Deep foundation location plan. A plan showing the location and designation of [piles] deep foundations by an identification system shall be filed with the commissioner prior to installation of such [piles] deep foundations. Detailed records for individual [piles] deep foundations shall bear an identification corresponding to that shown on the plan.

[1808.5.8] 1810.5.8 Installation of [piles] deep foundations. [Piles] Deep foundations within the area of influence of a given, satisfactorily tested [pile] deep foundation shall be installed to the same installation criteria as the [successful test pile] satisfactorily tested deep foundation. The same equipment that was used to install the [test pile] satisfactorily tested deep foundation, identically operated in all aspects, shall be used to install the [piles] deep foundation. All [piles] deep foundation shall be of the same type, size and shape as the [test pile] satisfactorily tested deep foundation. All [piles] deep foundations within the area of influence as represented by a given satisfactorily tested [test pile] deep foundation shall bear in, or on, the same bearing stratum as the [test pile] satisfactorily tested deep foundation.

[1808.6] 1810.6 Tolerances.  Tolerances for [piles] deep foundations shall be in accordance with the requirements of Sections [1808.6.1] 1810.6.1 through [1808.6.4] 1810.6.4.

[1808.6.1] 1810.6.1 Tolerance in the location of the head of the [pile] deep foundation. A tolerance of 3 inches (76 mm) from the designed location shall be permitted in the installation of each [pile] deep foundation as measured from [the pile] its head, without reduction in load capacity of the [pile] deep foundation group unless otherwise noted on the foundation plans.  When [piles] deep foundations are installed outside of this tolerance, the true loading on such [piles] deep foundations shall be analytically determined from a survey that defines the actual location of the [piles] deep foundations as installed and using the actual eccentricity in the [pile] deep foundation group with respect to the line of action of the applied load.

[1808.6.2] 1810.6.2 Out of plumb tolerance. If the axis of any [pile] deep foundation is installed out of plumb or deviates from the specified batter by more than 4 percent, the design of the foundation shall be modified to resist the resulting vertical and lateral forces. In types of [piles] deep foundations for which subsurface inspection is not possible, this determination shall be made on the exposed section of the [pile] deep foundation, which [section,] at the time of checking axial alignment, shall not be less than 2 feet (610 mm) in length. In [pile] deep foundations that can be checked for axial alignment below the ground surface, the sweep of the [pile] deep foundation axis shall not exceed 4 percent of the embedded length.

[1808.6.3] 1810.6.3 [Bent piles] Deep foundations that are bent during installation. The load-bearing capacity of [piles] deep foundations discovered to have a sharp or sweeping bend shall be determined using an approved method of analysis by the engineer responsible for the [pile] deep foundation design in accordance with accepted engineering practice or by load testing a representative [pile] deep foundation.

[1808.6.4] 1810.6.4 [Mislocated piles] Deep foundations that are mislocated during installation. The maximum compressive load on any [pile] deep foundation due to mislocation shall not exceed 110 percent of the allowable design load.  If the total load on any [pile] deep foundation, so determined, is in excess of 110 percent of the allowable load-bearing capacity, correction shall be made by installing additional [piles] deep foundations or by other methods of load distribution as required to reduce the maximum [pile] load to 110 percent of the allowable [pile] deep foundation capacity.

[1808.7] 1810.7 Lateral support. Lateral support for [piles] deep foundation elements shall be in accordance with the requirements of Sections [1808.7.1] 1810.7.1 through [1808.7.4] 1810.7.4.

[1808.7.1] 1810.7.1 Buckling of [piles] deep foundations. Any soil other than soil with no shear strength shall be deemed to afford sufficient lateral support to the [pile] deep foundation to prevent buckling and to permit the design of the [pile] deep foundation in accordance with accepted engineering practice and the applicable provisions of this code.

[1808.7.2] 1810.7.2 Unbraced [piles] deep foundations. [Piles] Deep foundation elements standing unbraced in air, water or soils with no shear strength shall be designed as columns in accordance with the provisions of this code. Such [piles] deep foundations driven into firm ground can be considered fixed and laterally supported at 5 feet (1524 mm) below the ground surface and in soft material at 10 feet (3048 mm) below the ground surface unless otherwise prescribed by the engineer.

[1808.7.3] 1810.7.3 Bracing at tops of [piles] deep foundations. [Piles] Deep foundations shall be braced to provide lateral stability and resist eccentric loads and moments in all directions. Three or more [piles] deep foundations connected by a rigid cap shall be considered braced, provided that the [pile] deep foundations are located in radial directions from the centroid of the group not less than 60 degrees (1 rad) apart. A [two-pile] group of two deep foundation elements in a rigid cap shall be considered to be braced along the axis connecting the two [piles] deep foundations. Methods used to brace [piles] deep foundations shall be subject to the approval of the commissioner.

[Piles] Deep foundations supporting walls shall be driven alternately in lines spaced at least 1 foot (305 mm) apart and located symmetrically under the center of gravity of the wall load carried, unless effective measures are taken to provide for eccentricity and moments due to lateral forces, or the [wall piles] deep foundations supporting the wall are adequately braced. A single row of [piles] deep foundations without bracing is permitted for one and two-family dwellings and lightweight construction not exceeding two stories or 35 feet (10 668 mm) in height, provided the centers of the [piles] deep foundations are located within the width of the wall.

[1808.7.4] 1810.7.4 Bracing of short [piles] deep foundations. All pile caps supported by [piles] deep foundations that penetrate less than [ten feet] 10 feet (3048 mm) below cutoff level or less than [ten feet] 10 feet (3048 mm) below ground level shall be braced against lateral movement.  Such bracing may consist of connection to other pile caps that encompass [piles] deep foundations embedded more than [ten feet] 10 feet (3048 mm) below those levels. The heads of the [piles] deep foundations shall be fixed in the cap. In no case shall more than fifty percent of the [piles] deep foundations in the foundation of any building penetrate less than [ten feet] 10 feet (3048 mm) below cut-off level or less than [ten feet] 10 feet (3048 mm) below ground level.

Exception: The requirements of this section shall not apply to caisson piles.

[1808.7.4.1 Piles] 1810.7.4.1 Deep foundations located near a lot line.  Where the embedded length of [piles] deep foundations located near a lot line would be reduced to less than [ten feet] 10 feet (3048 mm) by excavation of the adjacent site to a depth of [ten feet] 10 feet (3048 mm) below the nearest established curb level, the provisions of Section [1808.7.4] 1810.7.4 shall apply.

[1808.8] 1810.8 Allowable stresses.  Allowable stresses for [piles] deep foundations shall be as listed in Table [1808.8] 1810.8.

[1808.8.1 Allowable stresses for piles. Allowable stresses for designing piles shall be as specified in Table 1808.8.]

Exception: Allowable stresses greater than those specified in Table [1808.8] 1810.8 in Sections [1809] 1811 and [1810] 1812 shall be permitted where supporting data justifying such higher stresses are filed and approved by the commissioner.

| TABLE [1808.8] 1810.8 ALLOWABLE AXIAL STRESSES FOR MATERIALS USED IN [PILES] DEEP FOUNDATION ELEMENTSa |
| --- |
| MATERIAL TYPE AND CONDITION | MAXIMUM ALLOWABLE STRESS[a]b |
| 1. Concrete or grout in compression[b]c |  |
| Cast-in-place with a permanent casing in accordance with Section [1810.5.2] 1812.5.2 | 0.4 f’c |
| Cast-in-place in a pipe, tube, other permanent casing or rock | 0.33 f’c |
| Cast-in-place without a permanent casing | 0.3 f’c |
| Precast nonprestressed | 0.33 f’c |
| Precast prestressed | 0.33 f’c – 0.27fpc |
| 2. Nonprestressed reinforcement in compression | 0.4fy ≤ 30,000 psi |
| 3. Structural steel in compression |  |
| Cores within concrete-filled pipes or tubes | 0.5Fy ≤ 32,000 psi |
| Pipes, tubes or H-piles, where justified in accordance with Section [1808.2.10] 1810.4.1.5.1 | 0.5Fy ≤ 32,000 psi |
| Pipes or tubes for micropiles or caissons less than 14 inches in diameter | 0.4Fy ≤ 32,000 psi |
| Other pipes, tubes or H-piles | 0.35Fy ≤ 16,000 psi |
| Helical piles | 0.6Fy ≤ 0.5 Fu |
| 4. Nonprestressed reinforcement in tension |  |
| Within micropiles or caissons less than 14 inches in diameter | 0.6fy |
| Other conditions | 0.5fy ≤ 24,000 psi |
| 5. [Structural steel] Steel in tension |  |
| Structural steel cores in caisson piles | 0.5Fy ≤ 32,000 psi |
| Pipes, tubes or H-piles, where justified in accordance with Section [1808.2.10] 1810.4.1.5.1 | 0.5Fy ≤ 32,000 psi |
| Other pipes, tubes or H-piles | 0.35Fy ≤ 16,000 psi |
| Helical piles | 0.6Fy ≤ 0.5 Fu |
| 6. Timber | See Section [1809.5.4] 1811.5.4 |

For SI:  1 pound per square inch = 6.895 kPa.

a.	For combined stresses, the structural capacity shall be computed in accordance with AISC 360 for steel piles and ACI 318 for concrete piles.

[a]b.	f’c is the specified compressive strength of the concrete or grout; fpc is the compressive stress on the gross concrete section due to effective prestress forces only; fy is the specified yield strength of reinforcement; Fy is the specified minimum yield stress of [structural] steel; Fu is the specified minimum tensile stress of [structural] steel.

[b]c.	The stresses specified apply to the gross cross-sectional area [within the concrete surface.] for precast concrete piles. The stresses specified shall apply to the concrete cross-sectional area for all other deep foundation elements. Where a temporary or permanent casing is used, the inside face of the casing shall be considered the concrete surface.

[1808.9 Seismic Design Categories C & D.]

[1808.9.1] 1810.9 Seismic design of [piles] deep foundations. Seismic design of [piles] deep foundation elements for structures assigned to Seismic Design Categories C & D shall be performed in accordance with Sections [1808.9.1 through 1808.9.3] 1810.9.1 and 1810.9.2.

[1808.9.2] 1810.9.1 Seismic Design Category C. Where a structure is assigned to Seismic Design Category C in accordance with Section 1613, individual pile caps or [piles] deep foundations shall be interconnected by ties. Ties shall be capable of carrying, in tension and compression, a force equal to the lesser of: (i) the product of the larger of the pile cap or column design gravity load times the seismic coefficient, SDS, divided by 10, or (ii) 25 percent of the smaller of the [pile] deep foundation or column design gravity load, unless it can be demonstrated that equivalent restraint is provided by reinforced concrete beams within slabs on grade, reinforced concrete slabs on grade, or confinement by competent rock, hard cohesive soils or very dense granular soils.

[1808.9.2.1] 1810.9.1.1 Connection to pile cap. For structures assigned to Seismic Design Category C or D in accordance with Section 1613, [concrete] deep foundation elements consisting of concrete shall be connected to the pile cap by embedding the element reinforcement or field-placed dowels anchored in the element into the pile cap for a distance equal to their development length in accordance with ACI 318. It shall be permitted to connect precast, prestressed [piles] deep foundations to the pile cap by developing the element prestressing strands into the pile cap, provided the connection is ductile. For deformed bars, the development length is the full development length for compression, or tension in the case of uplift, without reduction for excess reinforcement in accordance with Section 25.4.10 of ACI 318. Alternative measures for laterally confining concrete and maintaining toughness and ductile-like behavior at the top of the element shall be permitted, provided the design is such that any hinging occurs in the confined region. The minimum transverse steel ratio for confinement shall not be less than one-half of that required for columns.

For resistance to uplift forces, anchorage of steel pipes, tubes or H-piles to the pile cap shall be made by means other than concrete bond to the bare steel section. Concrete-filled steel pipes or tubes shall have reinforcement of not less than 0.01 times the cross sectional area of the concrete fill, developed into the cap and extending into the concrete fill a length equal to two times the required cap embedment, but not less than the development length in tension of the reinforcement.

Exception: Anchorage of concrete-filled steel pipe piles is permitted to be accomplished using deformed bars developed into the concrete portion of the [pile] deep foundation. Splices of [pile] deep foundation segments shall develop the full strength of the [pile] deep foundation, but the splice need not develop the nominal strength of the [pile] deep foundation in tension, shear and bending when the splice has been designed to resist axial and shear forces and moments from the load combinations of Section 12.4 of ASCE 7[-10].

[1808.9.2.2] 1810.9.1.2 Design details. [Pile moments] Moments, shears and lateral deflections used for design of deep foundations shall be established considering the nonlinear interaction of the shaft and soil, as recommended by the engineer. Where the ratio of the depth of embedment of the [pile -to-pile] center-to-center diameter or width of deep foundations is less than or equal to six, the [pile] deep foundation may be assumed to be rigid. [Pile group] Group effects from soil on lateral [pile] deep foundation nominal strength shall be included where [pile] deep foundation center-to-center spacing in the direction of lateral force is less than eight [pile] diameters. [Pile group] Group effects on vertical nominal strength of deep foundations shall be included where [pile] deep foundation center-to-center spacing is less than three [pile] diameters. The [pile] uplift soil nominal strength of deep foundations shall be taken as the [pile] uplift strength as limited by the frictional force developed between the soil and the [pile] deep foundation.

Where a minimum length for reinforcement or the extent of closely spaced confinement reinforcement is specified at the top of the [pile] deep foundation, provisions shall be made so that those specified lengths or extents are maintained after [pile] deep foundation cutoff.

[1808.9.3] 1810.9.2 Seismic Design Category D. Where a structure is assigned to Seismic Design Category D in accordance with Section 1613, the requirements for Seismic Design Category C given in Section [1808.9.2] 1810.9.1 shall be met. Provisions of ACI 318, Section [21.12.4] 18.13.4, shall also apply when not in conflict with the provisions of Sections [1808] 1810 through [1813] 1816. Concrete shall have a specified compressive strength of not less than 3,000 psi (20.68 MPa) at 28 days.

Exceptions:

1.	Group R or U occupancies of light-framed construction and two stories or less in height are permitted to use concrete with a specified compressive strength of not less than 2,500 psi (17.2 MPa) at 28 days.

2.	Detached one and two-family dwellings of light-frame construction and two stories or less in height are not required to comply with the provisions of ACI 318, Section [21.12.4] 18.13.4.

3.	Section [21.12.4.4(a)] 18.13.4.4(a) of ACI 318 shall not apply to concrete piles.

[1808.9.3.1] 1810.9.2.1 Design details for [piles] deep foundations and grade beams. Design details for deep foundations and grade beams shall comply with the following:

[Piles] 1.	Deep foundations shall be designed and constructed to withstand maximum imposed curvatures from earthquake ground motions and structure response. Curvatures shall include free-field soil strains modified for soil-pile-structure interaction coupled with [pile] deformations of deep foundations induced by lateral [pile] resistance of deep foundations to structure seismic forces.

2.	Concrete piles on Site Class E or F sites, as determined in Section [1613.5.2] 1613.3.2 of this code, shall be designed and detailed in accordance with Sections [21.12.4.1, 21.12.4.2 and 21.12.4.3] 1813.4.1 and 1813.4.2 of ACI 318 within a distance of seven [pile] diameters of the deep foundation element of the pile cap and the interfaces of soft to medium stiff clay or liquefiable strata. For precast prestressed concrete piles, detailing provisions as given in Sections [1809.6.3.2.1] 1811.6.3.2 and [1809.6.3.2.2] 1811.6.3.2.2 of this code shall apply.

3.	Grade beams shall be designed as beams in accordance with ACI 318, Chapter [21] 18. When grade beams have the capacity to resist the forces from the load combinations in Section 1605.4, they need not conform to ACI 318, Chapter [21] 18.

[1808.9.3.2] 1810.9.2.2 Connection to pile cap. For [piles] deep foundations required to resist uplift forces or provide rotational restraint, design of anchorage of [piles] deep foundations into the pile cap shall be provided considering the combined effect of axial forces due to uplift and bending moments due to fixity to the pile cap. Anchorage into the pile cap shall be capable of developing the following:

1.	In the case of uplift, the lesser of the nominal tensile strength of the longitudinal reinforcement in a concrete pile, or the nominal tensile strength of a steel pile, or the [pile] deep foundation uplift soil nominal strength factored by 1.3 or the axial tension force resulting from the load combinations of Section 12.4 of ASCE 7[-10].

2.	In the case of rotational restraint, the lesser of the axial and shear forces, and moments resulting from the load combinations of Section 12.4 of ASCE 7[-10] or development of the full axial, bending and shear nominal strength of the [pile] deep foundation.

[1808.9.3.3] 1810.9.2.3 Flexural strength. Where the vertical, lateral-force-resisting elements are columns, the grade beam or pile cap flexural strengths shall exceed the column flexural strength.

[1808.9.3.4] 1810.9.2.4 [Batter piles] Battered deep foundations. The connection between [batter piles] deep foundations that are battered and grade beams or pile caps shall be designed to resist the nominal strength of the [pile] deep foundation acting as a short column. [Batter piles] Battered deep foundations and their connections shall be capable of resisting forces and moments from the load combinations of Section 12.4 of ASCE 7[-10].

SECTION BC [1809] 1811
DRIVEN [PILES] DEEP FOUNDATIONS

[1809.1] 1811.1 General. Driven [piles] deep foundations shall be designed and installed in accordance with Sections [1808] 1810 and [1809.2] 1811.2 through [1809.7] 1811.7. Driven deep foundation elements shall be designed and manufactured in accordance with accepted engineering practice to resist all stresses induced by handling, driving and service loads.

[1809.2] 1811.2 Equipment. Equipment and methods of installation shall be such that [piles] deep foundations are installed in their proper position and alignment, without damage. Equipment shall be maintained in good working order.

[1809.2.1 Pile driving] 1811.2.1 Driving hammer for deep foundations. The hammer to be used to drive [piles] deep foundations shall deliver a maximum energy consistent with the size, strength and weight of the driven [piles] deep foundations. The [pile-driving] hammer shall travel freely in the leads. The hammer shall deliver its rated energy, and measurements shall be made of the fall of the ram or other suitable data shall be obtained at intervals necessary to verify the actual energy delivered during the final 20 blows of the hammer.

[1809.2.2] 1811.2.2 Cushion or cap block. The cushion or cap block shall be a solid block of hardwood with its grains parallel to the axis of the [pile] deep foundation and enclosed in a tight-fitting steel housing, or other accepted equivalent assembly. If laminated materials are used, their type and construction shall be such that their strength is equal to or greater than hardwood. Wood chips, pieces of rope, hose, shavings, automobile tires or similar materials shall not be used. Cap block cushions shall be replaced if burned, crushed, or otherwise damaged. Other cushion materials may be used subject to the approval of the engineer. The introduction of fresh hammer cushion or [pile] pile-driving cushion material just prior to final penetration is not permitted.

[1809.2.3] 1811.2.3 Followers. Followers shall not be used unless permitted in writing by the engineer responsible for the [pile] driving operation of the deep foundation. The required driving resistance shall account for the losses of driving energy transmitted to the [pile] deep foundation because of the follower. The follower shall be a single length section, be provided with a socket or hood carefully fitted to the top of the [pile] deep foundation to minimize loss of energy and to prevent damage to the [pile] deep foundation, and have sufficient rigidity to prevent “whip” during driving.

[1809.3] 1811.3 Driving criteria. The allowable compressive load on steel and concrete piles, where determined solely by the application of an approved wave equation analyses approved by the engineer, shall not exceed 40 tons (356 kN). The allowable compressive loads on timber piles, where determined solely by the wave equation analyses approved by the engineer, shall not exceed 30 tons (267 kN). For allowable loads greater than these values, the wave equation method of analysis may be used to establish initial driving criteria, but final driving criteria and the allowable load shall be verified by load tests in accordance with Section [1808.4] 1810.4.  Minimum driving resistance and hammer energy may be determined in accordance with Tables [1809.3(a)] 1811.3(a) and [1809.3(b)] 1811.3(b).

| TABLE [1809.3(a)] 1811.3(a) MINIMUM DRIVING RESISTANCE AND MINIMUM HAMMER ENERGY FOR STEEL H-PILES, PIPE PILES, PRECAST AND CAST-IN-PLACE CONCRETE PILES AND COMPOSITE PILES (other than timber) |
| --- |
| MINIMUM DRIVING RESISTANCE a, c, d, e |
| Pile Capacity (tons) | Hammer Energyb (ft. lbs.) | Friction Piles (blows/ft.) | Piles Bearing on Soft Rock (Class 1d) (blows/ft.) | Piles Bearing on Rock (Class 1a, 1b, and 1c) |
| Up to 20 | 15,000 | 19 | 48 | 5 Blows per ¼ inch (Minimum hammer energy of 15,000 ft. lbs.) |
|  | 19,000 | 15 | 27 |  |
|  | 24,000 | 11 | 16 |  |
| 30 | 15,000 | 30 | 72 |  |
|  | 19,000 | 23 | 40 |  |
|  | 24,000 | 18 | 26 |  |
| 40 | 15,000 | 44 | 96 |  |
|  | 19,000 | 32 | 53 |  |
|  | 24,000 | 24 | 34 |  |
| > 40 | AS PER SECTION [1809.3] 1811.3 |  |

For SI: 1 foot = 304.8 mm, 1 ton = 907.18 kg.

a.	Final driving resistance shall be the sum of tabulated values plus resistance exerted by nonbearing materials. The driving resistance of nonbearing materials shall be taken as the resistance experienced by the pile during driving, but which will be dissipated with time and may be approximated as described in Section [1809.3] 1811.3.

b.	The hammer energy indicated is the rated energy.

c.	Sustained driving resistance. Where piles are to bear in soft rock, the minimum driving resistance shall be maintained for the last 6 inches, unless a higher sustained driving resistance requirement is established by load test. Where piles are to bear in soil Classes 2 through 5, the minimum driving resistance shall be maintained for the last twelve inches unless load testing demonstrates a requirement for higher sustained driving resistance. No pile needs to be driven to a resistance that penetrates in blows per inch (blows per 25 mm) more than twice the resistance indicated in this table, nor beyond the point at which there is no measurable net penetration under the hammer blow.

d.	The tabulated values assume that the ratio of total weight of pile to weight of striking part of the hammer does not exceed 3.5. If a larger ratio is to be used, or for other conditions for which no values are tabulated, the driving resistance shall be as approved by the commissioner.

e.	For intermediate values of pile capacity, minimum requirements for driving resistance may be determined by straight line interpolation.

| TABLE [1809.3(b)] 1811.3(b) MINIMUM DRIVING RESISTANCE AND HAMMER ENERGY FOR TIMBER PILES |
| --- |
| PILE CAPACITY (TONS) | MINIMUM DRIVING RESISTANCE (BLOWS/IN.) TO BE ADDED TO DRIVING RESISTANCE EXERTED BY NONBEARING MATERIALS (NOTES 1, 3, 4) | HAMMER ENERGY (ft./lbs.) (Note 2) |
| Up to 20 | Formula in Note 4 shall apply | 7,500-12,000 |
| Over 20 to 25 |  | 9,000-12,000 |
|  |  | 14,000-16,000 |
| Over 25 to 30 |  | 12,000-16,000 (single-acting hammers) |
| Greater than 30 |  | 15,000-20,000 (double-acting hammers) |

For SI: 1 ton = 907.18 kg, 1 inch = 25.4 mm.

Notes:

1.	The driving resistance exerted by nonbearing materials is the resistance experienced by the pile during driving, but which will be dissipated with time and may be approximated as described in Section [1809.3] 1811.3.

2.	The hammer energy indicated is the rated energy.

3.	Sustained driving resistance. Where piles are to bear in soft rock, the minimum driving resistance shall be maintained for the last 6 inches (152.4 mm), unless a higher sustained driving resistance requirement is established by load test. Where piles are to bear in soil Classes 2 through 5, the minimum driving resistance measured in blows per inch (blows per 25 mm) shall be maintained for the last 12 inches unless load testing demonstrates a requirement for higher sustained driving resistance. No pile need be driven to a resistance that penetrates in blows per inch (blows per 25 mm) more than twice the resistance indicated in this table nor beyond the point at which there is no measurable net penetration under the hammer blow.

4.	The minimum driving resistance shall be determined by the following formula:

or

where:

P =	Allowable pile load in pounds.

Wp =	Weight of pile in pounds.

Wh =	Weight of striking part of hammer in pounds.

H =	Actual height of fall of striking part of hammer in feet.

E =	Rated energy delivered by the hammer per blow in foot/lbs.

S =	Penetration of pile per blow, in inches, after the pile has been driven to a depth where successive blows produce approximately equal net penetration.

The value of Wp shall not exceed three times Wh.

[1809.3.1] 1811.3.1 Capacity as indicated by resistance to penetration. Where subsurface investigation and general experience in the area indicate that the soil that must be penetrated by the [pile] deep foundation consists of glacial deposits containing boulders, or fills containing rip-rap, excavated detritus, masonry, concrete or other obstructions in sufficient numbers to present a hazard to the installation of the [piles] deep foundations, the selection of type of [pile] deep foundation and penetration criteria shall be subject to the approval of the commissioner, but in no case shall the minimum penetration resistance be less than that stated in Tables [1809.3(a)] 1811.3(a) and [1809.3(b)] 1811.3(b).

[1809.4] 1811.4 Installation of driven [piles] deep foundations. Driven [pile] deep foundations shall be installed in accordance with Section [1808.2.6] 1810.2 and Sections [1809.4.1] 1811.4.1 through [1809.4.3] 1811.4.3.

[1809.4.1] 1811.4.1 Driving near fresh concrete. [Piles] Deep foundations shall not be driven adjacent to fresh concrete that is less than 3 days old without approval by the engineer.

[1809.4.2] 1811.4.2 Heaved [piles] deep foundations. [Piles] Deep foundations that have heaved during the driving of adjacent [piles] deep foundations shall be redriven as necessary to develop the required capacity and penetration, or the capacity of the [pile] deep foundation shall be verified by load tests in accordance with Section [1808.4] 1810.4.

[1809.4.3] 1811.4.3 Use of vibratory drivers. Vibratory drivers shall only be used to install [piles] deep foundation elements where the [pile] deep foundation is subsequently seated by an impact hammer to the final driving criteria established in accordance with Section [1809.3] 1811.3.

[1809.5] 1811.5 Timber piles. Timber piles shall be designed in accordance with the [AF&PA NDS] AWC NDS.

[1809.5.1] 1811.5.1 Materials. Round timber piles shall conform to ASTM D 25. Sawn timber piles shall conform to DOC PS-20.

[1809.5.2] 1811.5.2 Preservative treatment. Timber piles used to support permanent structures shall be treated in accordance with this section unless it is established that the tops of the untreated timber piles will be below the lowest groundwater level assumed to exist during the life of the structure as specified in Section [1808.2.12] 1810.2.12. Preservative and minimum final retention shall be in accordance with AWPA [C3] U1 (Commodity Specification E, Use Category 4C) for round timber piles and AWPA [C24] U1 (Commodity Specification A, Use Category 4B) for sawn timber piles. Preservative-treated timber piles shall be subject to a quality control program administered by an approved agency. [Pile cuts] Cuts to timber piles shall be treated in accordance with AWPA M4.

[1809.5.3] 1811.5.3 Defective timber piles. Any sudden decrease in driving resistance of a timber pile shall be investigated [with regard to the possibility of] for possible damage. If the sudden decrease in driving resistance cannot be correlated to load-bearing data, the timber pile shall be removed for inspection[,] or rejected.

[1809.5.4] 1811.5.4 Sizes of timber piles. [Piles] Timber piles shall be of adequate size to resist the applied loads without creating stresses in the timber pile material in excess of 1,200 psi (8.27 MPa) for piles of southern pine, Douglas fir, oak, or other wood of comparable strength; or 800 psi (5.52 MPa) for timber piles of cedar, Norway pine, spruce or other wood of comparable strength. [Piles] Timber piles of 25 tons (222.5 kN) of capacity or more shall have a minimum 8-inch tip (203 mm) with uniform taper. [Piles] Timber piles of less than 25 tons (222.5 kN) of capacity shall have a minimum 6-inch (152 mm) tip with uniform taper. All timber piles, regardless of capacity, driven to end bearing on bedrock of Classes 1a to 1d and compact gravels and sands of Class 2a shall have a minimum 8-inch (203 mm) tip and a uniform taper. Any species of wood may be used for timber piles that conforms to ASTM D 25 and that will stand the driving stresses.

[1809.5.5] 1811.5.5 Lagged or inverted timber piles. The use of lagged or inverted timber piles is permitted. Double lagging shall be adequately connected to the basic timber pile material to transfer the full [pile] load from the basic timber pile material to the lagging without exceeding values of allowable stress as established in Chapter 23. The connection for single lagging shall be proportioned for half the timber pile load. The diameter of any inverted timber pile at any section shall be adequate to resist the applied load without exceeding the stresses specified in Section [1809.5.4] 1811.5.4, but in no case shall it be less than 8 inches (203 mm).

[1809.6] 1811.6 Precast concrete piles.

[1809.6.1] 1811.6.1 General. The materials, reinforcement and installation of precast concrete piles shall conform to Sections [1809.6.1.1] 1811.6.1.1 through [1809.6.1.4] 1811.6.1.3.

[1809.6.1.1 Design and manufacture. Piles shall be designed and manufactured in accordance with accepted engineering practice to resist all stresses induced by handling, driving and service loads.]

[1809.6.1.2] 1811.6.1.1 Minimum dimension. The minimum horizontal dimension shall be 8 inches (203 mm). Corners of square precast concrete piles shall be chamfered.

[1809.6.1.3] 1811.6.1.2 Reinforcement. Longitudinal steel shall be arranged in a symmetrical pattern and be laterally tied with steel ties or wire spiral spaced not more than 4 inches (102 mm) apart, center to center, for a distance of 2 feet (610 mm) from the ends of the precast concrete pile; and not more than 6 inches (152 mm) elsewhere except that at the ends of each precast concrete pile, the first five ties or spirals shall be spaced 1 inch (25 mm) center to center. The gage of ties and spirals shall be as follows:

1.	For precast concrete piles having a least horizontal dimension of 16 inches (406 mm) or less, wire shall not be smaller than 0.22 inch (5.6 mm) (No. 5 gage).

2.	For precast concrete piles having a least horizontal dimension of more than 16 inches (406 mm) and less than 20 inches (508 mm), wire shall not be smaller than 0.238 inch (6 mm) (No. 4 gage).

3.	For precast concrete piles having a least horizontal dimension of 20 inches (508 mm) and larger, wire shall not be smaller than ¼ inch (6.4 mm) round or 0.259 inch (6.6 mm) (No. 3 gage).

[1809.6.1.4] 1811.6.1.3 Installation. [Piles] Precast concrete piles shall be handled and driven so as not to cause injury or overstressing in a manner that affects durability or strength. A precast concrete pile shall not be driven before the concrete has attained a compressive strength of at least 75 percent of the 28-day specified compressive strength (f’c), and not less than the strength sufficient to withstand handling and driving forces.

[1809.6.2] 1811.6.2 Precast nonprestressed concrete piles. Precast nonprestressed concrete piles shall conform to Sections [1809.6.2.1] 1811.6.2.1 through [1809.6.2.4] 1811.6.2.4.

[1809.6.2.1] 1811.6.2.1 Materials. Concrete shall have a 28-day specified compressive strength (f’c) of not less than 3,000 psi (20.68 MPa).

[1809.6.2.2] 1811.6.2.2 Minimum reinforcement. The minimum amount of longitudinal reinforcement shall be 0.8 percent of the concrete section and consist of at least four bars.

[1809.6.2.2.1] 1811.6.2.2.1 Seismic reinforcement in Seismic Design Category C. Where a structure is assigned to Seismic Design Category C in accordance with Section 1613, longitudinal reinforcement with a minimum steel ratio of 0.01 shall be provided throughout the length of precast concrete piles. Within [three pile diameters] a distance equivalent to three times the diameter of the deep foundation element of the bottom of the pile cap, the longitudinal reinforcement shall be confined with closed ties or spirals of a minimum ⅜-inch (9.5 mm) diameter. Ties or spirals shall be provided at a maximum spacing of eight times the diameter of the smallest longitudinal bar, not to exceed 6 inches (152 mm). Throughout the remainder of the precast nonprestressed concrete pile, the closed ties or spirals shall have a maximum spacing of 16 times the smallest longitudinal-bar diameter, not to exceed 6 inches (152 mm).

[1809.6.2.2.2] 1811.6.2.2.2 Seismic reinforcement in Seismic Design Category D. Where a structure is assigned to Seismic Design Category D in accordance with Section 1613, the requirements of Seismic Design Category C shall apply, except that transverse reinforcement shall comply with requirements of Section [1810.1.2.5] 1812.1.2.5.

[1809.6.2.3] 1811.6.2.3 Allowable stresses.  For allowable stresses, see Table [1808.8] 1810.8.

[1809.6.2.4] 1811.6.2.4 Concrete cover. For concrete cover requirements, see Table [1808.2.13] 1810.2.13.

[1809.6.3] 1811.6.3 Precast prestressed concrete piles. Precast prestressed concrete piles shall conform to the requirements of Sections [1809.6.3.1] 1811.6.3.1 through [1809.6.3.4] 1811.6.3.4.

[1809.6.3.1] 1811.6.3.1 Materials. Prestressing steel shall conform to ASTM A 416. Concrete shall have a 28-day specified compressive strength (f’c) of not less than 5,000 psi (34.48 MPa).

[1809.6.3.2] 1811.6.3.2 Design. Precast prestressed concrete piles shall be designed to resist stresses induced by handling and driving as well as by loads. The effective prestress [in the pile] shall not be less than 400 psi (2.76 MPa) for precast prestressed concrete piles less than 30 feet (9144 mm) in length, 550 psi (3.79 MPa) for precast prestressed concrete piles between 30 and 50 feet (9144 mm and 15 240 mm) in length and 700 psi (4.83 MPa) for precast prestressed concrete piles greater than 50 feet (15 240 mm) in length. Effective prestress shall be based on an assumed loss of 30,000 psi (207 MPa) in the prestressing steel. The tensile stress in the prestressing steel shall not exceed the values specified in ACI 318.

[1809.6.3.2.1] 1811.6.3.2.1 Design in Seismic Design Category C. Where a structure is assigned to Seismic Design Category C in accordance with Section 1613, precast prestressed concrete piles shall have transverse reinforcement in accordance with this section. The minimum volumetric ratio of spiral reinforcement shall not be less than the amount required by the following formula for the upper 20 feet (6096 mm) of the precast prestressed concrete pile.

[(Equation 18-4)] (Equation 18-1)

where:

Ag =	Pile cross-sectional area square inches (mm2).

f’c =	Specified compressive strength of concrete, psi (MPa).

fyh =	Yield strength of spiral reinforcement ≤ 85,000 psi (586 MPa).

P =	Axial load on pile, pounds (kN), as determined from Equations 16-5 and 16-7.

ρs =	Spiral reinforcement index (vol. spiral/vol. core).

[At least] Not less than one-half the volumetric ratio required by Equation [18-4] 18-1 shall be provided below the upper 20 feet (6096 mm) of the pile.

[The pile cap connection by means of dowels as indicated in Section 1808.9 is permitted. Pile cap connection by means of developing pile reinforcing strand is permitted provided that the pile reinforcing strand results in a ductile connection.]

Exception: The minimum spiral reinforcement index required by Equation 18-1 shall not apply in cases where the design includes full consideration of load combinations specified in ASCE 7, Section 2.3.6 and the applicable overstrength factor, Ω0. In such cases, minimum spiral reinforcement index shall be as specified in Section 1811.6.1.2.

[1809.6.3.2.2] 1811.6.3.2.2 Design in Seismic Design Category D. Where a structure is assigned to Seismic Design Category D in accordance with Section [1613.5.6] 1613.3.5, the requirements for Seismic Design Category C in Section [1809.6.3.2.1] 1811.6.3.2.1 shall be met, in addition to the following:

1.	Requirements in ACI 318, Chapter [21] 18, do not apply, unless specifically referenced.

2.	Where the total [pile] length of the deep foundation in the soil is 35 feet (10 668 mm) or less, the lateral transverse reinforcement in the ductile region shall occur through the length of the precast prestressed concrete pile. Where the precast prestressed concrete pile length exceeds 35 feet (10 668 mm), the ductile [pile] region of the deep foundation shall be taken as the greater of 35 feet (10 668 mm) or the distance from the underside of the pile cap to the point of zero curvature plus three times the least [pile] dimension of the precast prestressed concrete pile.

3.	In the ductile region, the center-to-center spacing of the spirals or hoop reinforcement shall not exceed one-fifth of the least [pile] dimension of the deep foundation element, six times the diameter of the longitudinal strand[,] or 8 inches (203 mm), whichever is smaller.

4.	Circular spiral reinforcement shall be spliced by lapping one full turn and bending the end of the spiral to a 90-degree (1.6-rad) hook or by use of a mechanical or welded splice complying with Section 25.5.7 of ACI 318.

5.	Where the transverse reinforcement consists of circular spirals, the volumetric ratio of spiral transverse reinforcement in the ductile region shall comply with the following:

[]	[(Equation 18-5)]

[]

[but not less than:]

(Equation 18-2)

[]	[(Equation 18-6)]

[]

[and need] but not exceed:

[(Equation 18-7)] (Equation 18-3)

where:

Ag =	Pile cross-sectional area, square inches(mm2).

[Ach =	Core area defined by spiral outside diameter, square inches (mm2).]

f’c =	Specified compressive strength of concrete, psi (MPa)

fyh =	Yield strength of spiral reinforcement ≤ 85,000 psi (586 MPa).

P =	Axial load on pile, pounds (kN), as determined from Equations 16-5 and 16-7.

ρs =	Volumetric ratio (vol. spiral/ vol. core).

This required amount of spiral reinforcement is permitted to be obtained by providing an inner and outer spiral.

Exception: The minimum spiral reinforcement required by Equation 18-2 shall not apply in cases where the design includes full consideration of load combinations specified in ASCE 7, Section 2.3.6 and the applicable overstrength factor, Ω0. In such cases, minimum spiral reinforcement index shall be as specified in Section 1811.6.1.2.

6.	When transverse reinforcement consists of rectangular hoops and cross ties, the total cross-sectional area of lateral transverse reinforcement in the ductile region with [spacings] spacing, s, and perpendicular to dimension, hc, shall conform to:

[(Equation 18-8)] (Equation 18-4)

but not less than:

[(Equation 18-9)] (Equation 18-5)

where:

fyh =	Yield strength of transverse reinforcement ≤ 70,000 psi (483 MPa).

hc =	Cross-sectional dimension of pile core measured center to center of hoop reinforcement, inch (mm).

s =	Spacing of transverse reinforcement measured along length of pile, inch (mm).

Ash =	Cross-sectional area of transverse reinforcement, square inches (mm2).

f’c =	Specified compressive strength of concrete, psi (MPa).

The hoops and cross ties shall be equivalent to deformed bars not less than No. 3 in size. Rectangular hoop ends shall terminate at a corner with seismic hooks.

Outside of the length of the pile requiring transverse confinement reinforcing, the spiral or hoop reinforcing with a volumetric ratio not less than one-half of that required for transverse confinement reinforcing shall be provided.

[1809.6.3.3] 1811.6.3.3 Allowable stresses. For allowable stresses, see Table [1808.8] 1810.8.

[1809.6.3.4] 1811.6.3.4 Concrete cover. For concrete cover requirements, see Table [1808.2.13] 1810.2.13.

[1809.7] 1811.7 Structural steel piles. Structural steel piles shall conform to the requirements of Sections [1809.7.1] 1811.7.1 through [1809.7.4] 1811.7.6.

[1809.7.1] 1811.7.1 Materials. Structural steel [piles, steel pipe and fully welded] H-piles and structural steel sheet piling shall conform to the material requirements in ASTM A6. Steel pipe piles shall conform to the material requirements in ASTM A252. Welded built-up steel piles shall be fabricated from plates [shall] that conform to the material requirements in ASTM A 36, [ASTM A 252,] ASTM A283, ASTM A572, ASTM A588, or ASTM A690 [, ASTM A 913 or ASTM A 992].

1811.7.1.1 Structural steel pipe piles to be welded. Structural steel pipe piles to be fabricated or spliced by welding shall be subject to qualification requirements of AWS D1.1 for unlisted base metals. Structural steel pipe piles to be welded shall have a carbon equivalency (CE) not exceeding 0.45 as defined by AWS D1.1 and a sulfur content not exceeding 0.05%. Carbon equivalency and sulfur content shall be determined by mill certificates or by chemical analysis, for a minimum of two samples per 1,000 lineal feet of pipe or part thereof, where mill certificates are unavailable.

1811.7.1.2 High strength pipe. High strength pipe meeting the strength requirements of API 5L (N80) and API 5CT (N80) shall be permitted for use as structural steel pipe piles. All such pipe and casing shall meet the minimum tensile requirements of ASTM A252, Grade 3 with a minimum elongation of 15%, except that the yield strength shall be a minimum of 80 ksi (552 MPa). The following requirements shall also apply:

1.	Mill certificates shall be provided.

2.	Where mill certificates are not available, a minimum of two coupon tests per 1,000 lineal feet of pipe or part thereof shall be performed. Testing procedures shall meet the requirements set forth in Section 18 of ASTM A252.

3.	Welding shall be in accordance with Section 1811.7.1.1.  In addition, welded seams and splices shall be complete joint penetration welds. Reinforcing steel shall not be welded to high strength pipe.

[1809.7.2] 1811.7.2 Allowable stresses. For the allowable stresses for materials used in structural steel piles see Table [1808.8] 1810.8.

[1809.7.3] 1811.7.3 Dimensions of Structural Steel H-piles. Sections of structural steel H-piles shall comply with the requirements for HP shapes in ASTM A6 or the following:

1.	The flange projections shall not exceed 14 times the minimum thickness of metal in either the flange or the web and the flange widths shall not be less than 80 percent of the depth of the section.

2.	The nominal depth in the direction of the web shall not be less than 8 inches (203 mm).

3.	Flanges and web shall have a minimum nominal thickness of ⅜ inch (9.5 mm).

[1809.7.4] 1811.7.4 Dimensions of structural steel pipe piles. [Steel] Structural steel pipe piles driven open ended shall have a nominal outside diameter of not less than 8 inches (203 mm). The pipe shall have a minimum of 0.34 square [inch] inches (219 mm2) of steel in cross section to resist each 1,000 foot-pounds (1356 N×m) of [pile hammer] energy from the hammer used to install deep foundation elements or the equivalent strength for steels having a yield strength greater than 35,000 psi (241 MPa), or the wave equation analysis shall be permitted to be used to assess compression stresses induced by driving to evaluate if the structural steel pipe pile section is appropriate for the selected hammer. Where pipe wall thickness less than 0.188 inch (4.8 mm) is driven open ended, a suitable cutting shoe shall be provided.

1811.7.5 Built-up structural steel piles fabricated from plates. Built-up sections of steel piles fabricated from welded plates shall comply with the following:

1.	 The flange projections shall not exceed 14 times the minimum thickness of metal in either the flange or the web and the flange widths shall not be less than 80 percent of the depth of the section.

2.	The nominal depth in the direction of the web shall not be less than 8 inches (203 mm).

3.	Flanges and web shall have a minimum nominal thickness of ⅜ inch (9.5 mm).

1811.7.6 Structural steel sheet piling. Individual sections of structural steel sheet piling shall conform to the profile indicated by the manufacturer, and shall conform to the general requirements specified by ASTM A6.

SECTION BC [1810] 1812
CAST-IN-PLACE CONCRETE PILES

[1810.1] 1812.1 General. The materials, reinforcement and installation of cast-in-place concrete piles shall conform to Sections [1810.1.1] 1812.1.1 through [1810.1.3] 1812.1.3.

[1810.1.1] 1812.1.1 Materials. Concrete or grout shall have a 28-day specified compressive strength (f’c) of not less than 2,500 psi (17.24 MPa), except in micropiles and caisson piles where the minimum compressive strength shall be 4,000 psi [(27 580 kPa)] (27.58 MPa). Where concrete is placed through a funnel hopper at the top of the cast-in-place concrete pile, the concrete mix shall be designed and proportioned so as to produce a cohesive workable mix having a slump of not less than 4 inches (102 mm) and not more than 6 inches (152 mm). Where concrete [or grout] is to be pumped, the mix design shall be such that material produced is suitable for pumping.

Grout shall consist of a pumpable mixture of portland cement, water, and any required fine aggregate, supplemental cementitious materials, or admixtures as permitted by Chapter 19. Grout proportioning shall be determined from trial mixes or on the basis of field experience using documented test results provided that such test results are not older than 24 months.  The water to cement ratio of grout shall not exceed 0.45. The required average compressive strength of grout shall be determined in a manner consistent with the procedures outlined in ACI 301 as utilized for concrete. The evaluation of grout compressive strength shall be in accordance with procedures established for concrete in Chapter 19.  All grout mix design shall be submitted for review and approval of the registered design professional of record.  Copies of the grout mix design shall be submitted to the department.

1812.1.1.1 Concrete sampling and testing.  Sampling and testing of concrete shall be in accordance with Chapter 19.

1812.1.1.2 Grout sampling and testing.  Sampling and testing of grout shall be in accordance with Section 1812.1.1.2.1 through 1812.1.1.2.3.

1812.1.1.2.1 Interval. Grout samples shall be collected and testing shall be performed for the lesser of the following conditions:

1.	each element installed;

2.	each batch of site-mixed grout; or

3.	each load of ready-mixed grout used.

1812.1.1.2.2 Compressive strength.  Compressive strength tests shall be performed using cylinders having a maximum diameter of 3 inches. Grout shall be tested in accordance with ASTM C39.  A minimum of six (6) samples shall be prepared for each test group.

1812.1.1.2.3 Specific gravity.  Specific gravity testing shall be performed using the American Petroleum Institute (API) Recommended Practice 13B-1 or in accordance with ASTM C138.

[1810.1.2] 1812.1.2 Placement of reinforcement. Reinforcement, where required, shall be placed in accordance with Section [1810.3.4] 1812.3.4 and shall be assembled, tied together, and placed in the cast-in-place concrete pile as a unit before concrete or grout is placed.

Exceptions: Where approved by the engineer, reinforcement may be placed after the cast-in-place concrete piles are filled with concrete or grout under the following situations:

1.	Tied reinforcement in augered uncased cast-in-place concrete piles, while the concrete or grout is still in a semifluid state.

2.	Tied reinforcement in cast-in-place concrete piles filled with grout, while the grout is in a semifluid state.

3.	Steel dowels embedded 5 feet (1524 mm) or less in the cast-in-place concrete pile while the concrete or grout is still in a semifluid state.

[1810.1.2.1] 1812.1.2.1 Design cracking moment. The design cracking moment (ØMn) for a cast-in-place deep foundation element not enclosed by a structural steel pipe or tube shall be determined using the following equation:

[(Equation 18-11)] (Equation 18-6)

For SI:

where:

f’c =	Specified compressive strength of concrete or grout, psi

Sm =	Elastic section modulus, neglecting reinforcement and casing, cubic inches

[1810.1.2.2] 1812.1.2.2 Required reinforcement. Where subject to uplift, or where the required moment strength determined using the load combinations of Section 1605.2 exceeds the design cracking moment determined in accordance with Section [1810.1.2.1] 1812.1.2.1, cast-in-place concrete piles not enclosed by a structural steel pipe or tube shall be reinforced.

[1810.1.2.3] 1812.1.2.3 Reinforcement in Seismic Design Categories C & D. Where a structure is assigned to Seismic Design Category C in accordance with Section 1613, reinforcement shall be provided in accordance with Section [1810.1.2.4] 1812.1.2.4. Where a structure is assigned to Seismic Design Category D, reinforcement shall be provided in accordance with Section [1810.1.2.5] 1812.1.2.5.

[1810.1.2.4] 1812.1.2.4 Seismic reinforcement in Seismic Design Category C. For structures assigned to Seismic Design Category C in accordance with Section 1613, cast-in-place [deep foundation] concrete pile elements shall be reinforced as specified in this section. Reinforcement shall be provided where required by analysis. A minimum of four longitudinal bars, with a minimum longitudinal reinforcement ratio of 0.0025, shall be provided throughout the minimum reinforced length of the element as defined below starting at the top of the element. The minimum reinforced length of the element shall be the greatest of the following:

1.	One-third of the element length;

2.	A distance of 10 feet (3048 mm);

3.	Three times the least element dimension; or

4.	The distance from the top of the element to the point where the design cracking moment determined in accordance with Section [1810.1.2.1] 1812.1.2.1 exceeds the required moment strength determined using the load combinations of Section 1605.2.

Transverse reinforcement shall consist of closed ties or spirals with a minimum diameter of ⅜ inch (9.5 mm). Spacing of transverse reinforcement shall not exceed the smaller of 6 inches (152 mm) or 8-longitudinal-bar diameters, within a distance of three times the least element dimension from the bottom of the pile cap. Spacing of transverse reinforcement shall not exceed 16 longitudinal bar diameters throughout the remainder of the reinforced length.

Exceptions:

1.	The requirements of this section shall not apply to concrete cast in structural steel pipes or tubes.

2.	A spiral-welded metal casing of a thickness not less than manufacturer’s standard No. 14 gage (0.068 inch) (1.73 mm) is permitted to provide concrete confinement in lieu of the closed ties or spirals. Where used as such, the metal casing shall be protected against possible deleterious action due to soil constituents, changing water levels or other factors indicated by boring records of site conditions.

[1810.1.2.5] 1812.1.2.5 Seismic reinforcement in Seismic Design Category D. For structures assigned to Seismic Design Category D in accordance with Section 1613, cast-in-place [deep foundation] concrete pile elements shall be reinforced as specified in this section. Reinforcement shall be provided where required by analysis. A minimum of four longitudinal bars, with a minimum longitudinal reinforcement ratio of 0.005, shall be provided throughout the minimum reinforced length of the element as defined below starting at the top of the element.

The minimum reinforced length of the element shall be the greatest of the following:

1.	One-half of the element length;

2.	A distance of 10 feet (3048 mm);

3.	Three times the least element dimension; or

4.	The distance from the top of the element to the point where the design cracking moment determined in accordance with Section [1810.3.9.1] 1812.1.2.1 exceeds the required moment strength determined using the load combinations of Section 1605.2.

Transverse reinforcement shall consist of closed ties or spirals no smaller than No. 3 bars for elements with a least dimension of up to 20 inches (508 mm), and No. 4 bars for larger elements. Throughout the remainder of the reinforced length outside the regions with transverse confinement reinforcement, as specified in Section [1810.1.2.5.1] 1812.1.2.5.1 or [1810.1.2.5.2] 1812.1.2.5.2, the spacing of transverse reinforcement shall not exceed the least of the following:

1.	12 longitudinal bar diameters;

2.	One-half the least dimension of the element; or

3.	12 inches (305 mm).

Exceptions:

1.	The requirements of this section shall not apply to concrete cast in structural steel pipes or tubes.

2.	A spiral-welded metal casing of a thickness not less than manufacturer’s standard [gage] No. 14 gage (0.068 inch) (1.73 mm) is permitted to provide concrete confinement in lieu of the closed ties or spirals. Where used as such, the metal casing shall be protected against possible deleterious action due to soil constituents, changing water levels or other factors indicated by boring records of site conditions.

[1810.1.2.5.1] 1812.1.2.5.1 Site Classes A through D. For Site Class A, B, C and D, transverse confinement reinforcement shall be provided in the element in accordance with Sections [21.6.4.2] 18.7.5.2, through [21.6.4.4] 18.7.5.4 of ACI 318 within three times the least element dimension of the bottom of the pile cap. A transverse spiral reinforcement ratio of not less than one-half of that required in Section [21.6.4.4(a)] 18.7.5.4(a) of ACI 318 shall be permitted.

[1810.1.2.5.2] 1812.1.2.5.2 Site Classes E and F. For Site Class E or F, transverse confinement reinforcement shall be provided in the element in accordance with Sections [21.6.4.2] 18.7.5.2 through [21.6.4.4] 18.7.5.4 of ACI 318 within seven times the least element dimension of the pile cap and within seven times the least element dimension of the interfaces of strata of Class 4b or better and strata that are liquefiable or are composed of material meeting Class 4c or 6.

[1810.1.3] 1812.1.3 Concrete or grout placement. Concrete or grout shall be placed in such a manner as to ensure the exclusion of any foreign matter and to secure a full-sized shaft. Concrete or grout shall not be placed through water except where a tremie or other approved method is used. When depositing concrete from the top of the cast-in-place concrete pile, the concrete shall not be chuted directly into the cast-in-place concrete pile but shall be poured in a rapid and continuous operation through a funnel hopper centered at the top of the cast-in-place concrete pile. Grout for auger cast piles shall be pumped through a hollow stem auger and shall be maintained as fluid throughout placement.

[1810.2] 1812.2 Enlarged base piles. Enlarged base piles shall conform to the requirements of Sections [1810.2.1] 1812.2.1 through [1810.2.5] 1812.2.5.

[1810.2.1] 1812.2.1 Materials. The maximum size of coarse aggregate for concrete shall be ¾ inch (19.1 mm). Concrete to be compacted shall have a zero slump.

[1810.2.2] 1812.2.2 Allowable stresses.  For allowable stresses, see Table [1808.8] 1810.8.

[1810.2.3] 1812.2.3 Installation. Enlarged bases formed either by compacting concrete or driving a precast base shall be formed in or driven into granular soils. [Piles] Enlarged base piles shall be constructed in the same manner as successful [prototype test piles driven] enlarged base test piles installed for the project. [Pile] Enlarged base pile shafts extending through peat or other organic soil shall be encased in a permanent steel casing. Where a cased shaft is used, the shaft shall be adequately reinforced to resist column action or the annular space around the enlarged base pile shaft shall be filled sufficiently to re-establish lateral support by the soil. Where [pile] heave of an enlarged base pile or other deep foundation occurs, the enlarged base pile or other deep foundation, shall be replaced unless it is demonstrated that the enlarged base pile or other deep foundation is undamaged and capable of carrying twice its design load.

[1810.2.4] 1812.2.4 Load-bearing capacity. [Pile] The load-bearing capacity of enlarged base piles shall be verified by load tests in accordance with Section [1808.4] 1810.4.

[1810.2.5] 1812.2.5 Concrete and grout cover. For minimum concrete and grout cover requirements, see Table [1802.13] 1803.13.

[1810.3] 1812.3 Drilled, drilled displacement, or augered uncased piles. Drilled, drilled displacement, or augered uncased piles shall conform to Sections [1810.3.1] 1812.3.1 through [1810.3.5] 1812.3.5.

[1810.3.1] 1812.3.1 Allowable stresses. For allowable stresses, see Table [1808.8] 1810.8.

[1810.3.2] 1812.3.2 Dimensions. The minimum diameter of drilled or drilled displacement piles shall be 8 inches (203 mm). The minimum diameter of augered uncased piles shall be 12 inches (305 mm).

[1810.3.3] 1812.3.3 Installation. Where [pile] shafts for drilled piles are formed through unstable soils and concrete is placed in an open-drilled hole, a steel liner shall be inserted in the hole prior to placing the concrete. Where the steel liner is withdrawn during concreting, the level of concrete shall be maintained above the bottom of the liner at a sufficient height to offset any hydrostatic or lateral soil pressure.

Where drilled displacement piles are used, the auger segments shall be installed into the ground with both a vertical force and a torque such that the soil is displaced laterally within the ground.  The void created after installation shall be filled with grout or concrete.

Where grout is placed by pumping through a hollow-stem auger, the auger shall be permitted to rotate in a clockwise direction during withdrawal. An initial head of grout shall be established and maintained on the auger flights before withdrawal. The auger shall be withdrawn in a continuous manner in increments of about 12 inches (305 mm) each. Grout pumping pressures shall be measured and maintained high enough at all times to offset hydrostatic and lateral earth pressures. Grout volumes shall be measured to ensure that the volume of grout placed in each drilled pile is equal to or greater than the theoretical volume of the hole created by the auger. Where the installation process of any drilled pile is interrupted or a loss of grout pressure occurs, the drilled pile shall be re-drilled to 5 feet (1524 mm) below the elevation of the tip of the auger when the installation was interrupted or grout pressure was lost and reformed.

Augered cast-in-place piles shall not be installed within [six pile diameters center to center of a] a distance equivalent to the center-to-center spacing equivalent to six times the diameter of a drilled pile filled with concrete or grout less than 12 hours old, unless approved by the engineer. The level at which return of the grout occurs during withdrawal shall be recorded. If the grout level in any completed drilled pile drops during installation of an adjacent drilled pile, the drilled pile shall be replaced. The installation shall be performed under the direct supervision of the engineer. The engineer shall certify to the commissioner that the drilled piles were installed in compliance with the approved construction documents.

[1810.3.4] 1812.3.4 Reinforcement. For drilled piles installed with a hollow-stem auger, where full-length longitudinal steel reinforcement is placed without lateral ties, the reinforcement shall be placed through ducts in the auger prior to filling the drilled pile with concrete. Concrete cover for [pile] reinforcement of the drilled pile shall be in accordance with Table [1808.2.13] 1810.2.13.

Exception: Where physical constraints do not allow the placement of the longitudinal reinforcement prior to filling the drilled pile with concrete or where partial-length longitudinal reinforcement is placed without lateral ties, the reinforcement is allowed to be placed after the drilled piles are completely concreted but while concrete is still in a semifluid state.

[1810.3.5] 1812.3.5 Reinforcement in Seismic Design Category C or D. Where a structure is assigned to Seismic Design Category C or D in accordance with Section 1613, the corresponding requirements of Sections [1810.1.2.3] 1812.1.2.3 through [1810.1.2.5] 1812.1.2.5 shall be met.

[1810.4] 1812.4 Driven uncased piles. Driven uncased piles shall not be permitted.

[1810.5] 1812.5 Steel-cased piles. Steel-cased piles shall comply with the requirements of Sections [1810.5.1] 1812.5.1 through [1810.5.4] 1812.5.4.

[1810.5.1] 1812.5.1 Materials. [Pile shells] Shells or casings for steel cased piles shall be of steel and be sufficiently strong to resist collapse and sufficiently water tight to exclude any foreign materials during the placing of concrete. Steel shells shall have a sealed tip with a diameter of not less than 8 inches (203 mm).

[1810.5.2] 1812.5.2 Allowable stresses. For allowable stresses, see Table [1808.8] 1810.8.

[1810.5.2.1] 1812.5.2.1 Shell thickness. The thickness of the steel shell shall not be less than manufacturer’s standard No. 14 gage (0.068 inch) (1.75 mm) minimum.

[1810.5.2.2] 1812.5.2.2 Shell type. The shell shall be seamless or provided with seams of strength equal to the basic material and be of a configuration that will provide confinement to the cast-in-place concrete.

[1810.5.2.3] 1812.5.2.3 Strength. The ratio of steel yield strength (fy) to 28-day specified compressive strength (f’c) shall not be less than six.

[1810.5.2.4] 1812.5.2.4 Diameter. The nominal [pile] diameter of steel cased piles shall not be greater than 16 inches (406 mm).

[1810.5.3] 1812.5.3 Installation. Steel shells shall be mandrel driven for their full length in contact with the surrounding soil.  The steel shells shall be driven in such order and with such pacing as to ensure against distortion of or injury to steel cased piles already in place. A steel cased pile shall not be driven within four and one-half average [pile] diameters of a steel cased pile filled with concrete less than 24 hours old unless approved by the commissioner. Concrete shall not be placed in steel shells within heave range of driving.

[1810.5.4] 1812.5.4 Reinforcement. Reinforcing shall be required for unsupported [pile] lengths of steel cased piles or where the steel cased pile is designed to resist uplift or unbalanced lateral loads. For minimum concrete cover requirements, see Table [1808.2.13] 1810.2.13.

[1810.5.4.1] 1812.5.4.1 Seismic reinforcement. Where a structure is assigned to Seismic Design Category C or D in accordance with Section 1613, the reinforcement requirements of Sections [1810.1.2.3] 1812.1.2.3 through [1810.2.5] 1812.1.2.5 shall be met.

[1810.6] 1812.6 Concrete-filled steel pipe and tube piles. Concrete-filled steel pipe and tube piles shall conform to the requirements of Sections [1810.6.1] 1812.6.1 through [1810.6.5] 1812.6.5.

[1810.6.1] 1812.6.1 Materials. Steel pipe and tube sections used for concrete-filled steel pipe and tube piles shall conform to ASTM A252 or ASTM A283. Concrete shall conform to Section [1810.1.1] 1812.1.1. The maximum coarse aggregate size shall be ¾ inch (19.1 mm).

[1810.6.2] 1812.6.2 Allowable stresses. For allowable stresses, see Table [1808.8] 1810.8.

[1810.6.3] 1812.6.3 Minimum dimensions. [Piles] Concrete-filled steel pipe and tube piles shall have a nominal outside diameter of not less than 8 inches (203 mm) and a minimum wall thickness in accordance with Section [1809.3.4] 1811.7.4. For [mandrel-driven pipe piles] concrete-filled steel pipe and tube piles driven with a mandrel, the minimum wall thickness shall be 1/10 inch (2.5 mm).

[1810.6.4] 1812.6.4 Reinforcement. Reinforcement steel shall conform to Section [1810.1.2] 1812.1.2. For minimum concrete cover requirements see Table [1808.2.13] 1810.2.13.

[1810.6.4.1] 1812.6.4.1 Seismic reinforcement. Where a structure is assigned to Seismic Design Category C or D in accordance with Section 1613, minimum reinforcement no less than 0.01 times the cross-sectional area of the [pile] concrete within the concrete-filled steel pipe and tube piles shall be provided in the top of the [pile] concrete-filled steel pipe and tube piles with an embedment length equal to two times the required cap embedment anchorage into the pile cap, but not less than the tension development length of the reinforcement. The wall thickness of the steel pipe shall not be less than 3/16 inch (5 mm).

[1810.6.5] 1812.6.5 Placing concrete. The placement of concrete shall conform to Section [1810.1.3] 1812.1.3.

[1810.7] 1812.7 Caisson piles. Caisson piles shall conform to the requirements of Sections [1810.7.1] 1812.7.1 through [1810.7.7] 1812.7.7.

[1810.7.1] 1812.7.1 Construction. Caisson piles shall consist of a shaft section of concrete or grout-filled pipe, extending to bedrock, with an uncased socket drilled into bedrock of Class 1c or better and filled with concrete or grout. The caisson pile shall have a full-length structural steel core, full length steel reinforcing, or a stub core or steel reinforcing installed in the rock socket and extending into the pipe portion a distance equal to the socket depth. The minimum outside diameter of the caisson pile shall be 7 inches (194 mm), and the diameter of the rock socket shall be approximately equal to the inside diameter of the caisson pile.

1812.7.1.1 Drilling with air. Where existing structures may be affected by subsurface disturbances, air drilling shall be prohibited.

[1810.7.2] 1812.7.2 Materials. Pipe and steel cores for caisson piles shall conform to the material requirements in Section [1809.3] 1811.7. Pipes shall have a minimum wall thickness of ⅜ inch (9.5 mm) and shall be fitted with a suitable steel-driving shoe or cutting teeth welded to the bottom of the pipe. Concrete or grout shall have a 28-day specified compressive strength (f’c) of not less than 4,000 psi (27.58 MPa).

[1810.7.2.1] 1812.7.2.1 Reinforcing bars. For the purposes of Section [1810.7] 1812.7, threaded bars conforming to ASTM A615 and ASTM A722 shall be considered the same as deformed reinforcing bars.

[1810.7.3] 1812.7.3 Rock socket design. The depth of the rock socket in Class 1c rock or better shall be sufficient to develop the full load-bearing capacity of the caisson pile based upon the sum of the allowable bearing pressure on the bottom of the socket in accordance with Table [1804.1] 1806.1 plus an allowable bond stress of 200 psi (1379 kPa) on the sides of the socket. The depth of the socket in Class 1c rock or better below the bottom of the pipe shall not be less than 3 feet (914 mm) [of] or the outside diameter of the pipe.

[1810.7.3.1] 1812.7.3.1 Increased allowable bond stress. Load tests, with instrumentation in the rock socket to demonstrate the transfer of force to the rock, shall be performed to justify the use of bond stresses above 200 psi (1379 kPa).  [The number of load tests shall be in accordance with the requirements of Section 1808.4.1.1.] A minimum factor of safety of 2 shall be applied to the ultimate test load where an increase in allowable bond stress is sought. A report summarizing the methods and results of the load test shall be submitted to the commissioner for approval.

1812.7.3.2 Minimum number of load tests. In each area of the foundation site within which the subsurface soil and rock conditions are “substantially similar” in character, as determined by the engineer, at least one load test shall be performed for the largest caisson pile diameter used on a site occupying a total area of 80,000 square feet (7432 m2) or less. For sites greater than 80,000 square feet (7432 m2), an additional load test shall be performed for every 80,000 square feet (7432 m2) of added footprint area.

[1810.7.4] 1812.7.4 Structural core and steel reinforcing. The gross cross-sectional area of the structural steel core or bundled center reinforcing shall not exceed 30 percent of the gross area of the caisson pile. For reinforcing placed at the perimeter of the caisson pile, the area of the reinforcing shall not exceed 8 percent of the area inside the casing.  Minimum concrete cover shall be in accordance with Table [1808.2.13] 1810.2.13.

[1810.7.4.1] 1812.7.4.1 Splicing of steel reinforcing. Steel reinforcing shall be spliced in accordance with the requirements of ACI 318.

[1810.7.4.2] 1812.7.4.2 Seismic reinforcement.  Where a structure is assigned to Seismic Design Category C or D in accordance with Section 1613, the reinforcement requirements of Section [1810.6.4.1] 1812.6.4.1 shall be met.

[1810.7.5] 1812.7.5 Allowable stresses. For allowable stresses, see Table [1808.8] 1810.8.

[1810.7.6] 1812.7.6 Installation. The rock socket and [pile] steel pipe shall be thoroughly cleaned of foreign materials before filling with concrete or grout. Steel cores shall be set within 6 inches (125 mm) above the base of the rock socket.  Concrete shall not be placed through water except where a tremie or other method approved by the commissioner is used.

1812.7.6.1 Drilling with air.  Where existing structures may be affected by subsurface disturbances, air drilling shall be prohibited.

[1810.7.7] 1812.7.7 Rock socket inspection. Caisson pile rock sockets shall be subject to special inspection in accordance with Section [1704.9] 1705.19. All caisson pile rock sockets shall be inspected to verify rock quality. Inspection may be accomplished by direct observation, by video methods or by a core boring performed prior to the drilling of the socket.

[1810.8] 1812.8 Micropiles. Micropiles shall conform to Sections [1810.8.1] 1812.8.1 through [1810.8.6] 1812.8.6.

[1810.8.1] 1812.8.1 Materials. Reinforcement shall consist of deformed reinforcing bars in accordance with ASTM A615 Grade 60 or 75 or ASTM A722 Grade 150.  The steel pipe or casing shall have a minimum yield strength of 45,000 psi (310 MPa) and a minimum elongation of 15 percent as shown by mill certifications or two coupon test samples per 40,000 pounds (18 160 kg) of pipe or casing.

[1810.8.2] 1812.8.2 Dimensions. Micropiles shall have an outside diameter of between 5 and 14 inches (127 and 356 mm). [The minimum diameter set forth elsewhere in Section 1810.3.5 shall not apply to micropiles.] The steel pipe shall have a minimum wall thickness of 3/16 inch (4.8 mm).

[1810.8.3] 1812.8.3 Design. Micropiles shall develop their load-carrying capacity by means of a bond zone in soil. The design of micropiles shall not consider end bearing. Micropiles shall be grouted and have either a steel pipe or steel reinforcement at every section along the length. It shall be permitted to transition compression loads from the steel pipe to the deformed reinforcing bars by extending the bars into the pipe section by at least their development length in tension, in accordance with ACI 318.

[1810.8.3.1] 1812.8.3.1 Reinforcement. For micropiles or portions thereof grouted inside a temporary or permanent casing or a hole drilled with grout, the steel pipe or steel reinforcement shall be designed to carry at least 40 percent of the design compression load. Micropiles or portions thereof grouted in an open hole in soil without temporary or permanent casing and without suitable means of verifying the hole diameter during grouting shall be designed to carry the entire compression load in the reinforcing steel. Where a steel pipe is used for reinforcement, the portion of the grout enclosed within the pipe is permitted to be included in the determination of the allowable stress in the grout.

[1810.8.3.2] 1812.8.3.2 Seismic reinforcement. For structures assigned to Seismic Design Category C, a permanent steel casing shall be provided from the top of the micropile down to the point of zero curvature. For structures assigned to Seismic Design Category D, the micropile shall be approved by the commissioner in accordance with Section 28-113.2 of the New York City Administrative Code. The alternative system design, supporting documentation and test data shall be submitted to the commissioner for review and approval.

[1810.8.4] 1812.8.4 Splices. Splices in reinforcing bars shall be made in accordance with ACI 318.  Splices in the steel pipe or casing shall be made by use of flush threaded joints, or by welded joints.  Reductions for the structural capacity of the threaded joint casing at splice locations shall be accounted for in the design.

[1810.8.5] 1812.8.5 Installation. Micropile [deep foundation] elements shall be permitted to be formed in holes advanced by rotary or percussive drilling methods, with or without casing. The elements shall be grouted with a fluid cement grout. The grout shall be pumped through a tremie pipe extending to the bottom of the element until grout of suitable quality returns at the top of the element. The following requirements apply to specific installation methods:

1.	For micropiles grouted inside a temporary casing, the reinforcing bars shall be inserted prior to withdrawal of the casing. The casing shall be withdrawn in a controlled manner with the grout level maintained at the top of the element to ensure that the grout completely fills the drill hole.

[2.	For a micropile or portion thereof grouted in an open drill hole in soil without a temporary casing, the minimum design diameter of the drill hole shall be verified by a suitable device prior to grouting.]

[3.] 2.	Subsequent micropiles shall not be drilled near elements that have been grouted until the grout has had sufficient time to harden.

[4.] 3.	Micropiles shall be grouted as soon as possible after drilling is completed.

[5.] 4.	For micropiles designed with a full-length casing, the casing shall be pulled back to the top of the bond zone and reinserted or some other suitable means employed to assure grout coverage outside the casing.

[1810.8.5.1] 1812.8.5.1 Drilling with air. Where existing structures may be affected by subsurface disturbances, air drilling shall be prohibited.

[1810.8.6] 1812.8.6 Pressure grouted bond zone. Micropiles shall be installed with a pressure grouted bond zone. The bond zone shall be formed entirely in soil of Class 4 or better and the grout shall be placed under pressure exceeding 1.5 times the existing total [overburden pressure] stress at the midpoint of the bond zone. The bond zone shall be formed by extending the casing to the bottom of the bond zone and withdrawing the casing while the grout is being pumped under pressure.  The casing above the bond zone shall remain in place permanently. Reinforcing to the bond zone shall be placed in the casing to the depth of the bond zone prior to placing grout.

SECTION BC [1811] 1813
COMPOSITE PILES

[1811.1] 1813.1 General. Composite piles shall conform to the requirements of Sections [1811.2] 1813.2 through [1811.5] 1813.5.

[1811.2] 1813.2 Design. Composite piles consisting of two or more approved [pile] types of deep foundations shall be designed to meet the conditions of installation.

[1811.3] 1813.3 Limitation of load. The maximum allowable load shall be limited by the capacity of the weakest section incorporated in the composite pile.

[1811.4] 1813.4 Splices. Splices between concrete and steel or wood sections shall be designed to prevent separation both before and after the concrete portion has set, and to ensure the alignment and transmission of the total [pile] load on the composite pile. Splices shall be designed to resist uplift caused by upheaval during driving of adjacent [piles] deep foundations, and shall develop the full compressive strength and not less than 50 percent of the tension and bending strength of the weaker section.

[1811.5] 1813.5 Seismic reinforcement. Where a structure is assigned to Seismic Design Category C or D, in accordance with Section 1613 and where concrete and steel are used as part of the composite pile assembly, the concrete reinforcement shall comply with Sections [1810.1.2.3] 1812.1.2.3 and [1810.1.2.5] 1812.1.2.5 and the steel section shall comply with Section [1809.7.4] 1811.7.4 or [1810.6.4.1] 1812.6.4.1.

SECTION BC [1812] 1814
HELICAL PILES

[1812.1] 1814.1 General. Helical piles may be used to support axial compression, or resist axial tension and lateral loads. All helical pile foundation systems shall be approved by the commissioner in accordance with Section 28-113.2 of the Administrative Code.

[1812.2] 1814.2 Design. Design of helical pile foundations shall be based on a geotechnical investigation in accordance with Sections [1802] 1803 and [1808.2] 1810.2 with the following additional conditions stated in Sections [1812.2.1] 1814.2.1 and [1812.2.2] 1814.2.2.

Exception: For the repair of residential porches, stoops and slab on grades, helical test probes may be used to substitute for test borings, provided the helical pile has a torque to capacity ratio approved in accordance with Section 28-113.2.1 of the Administrative Code.

[1812.2.1] 1814.2.1 Corrosion testing requirements. Tests shall be performed in each soil layer for soil resistivity, soil pH, organic content and sulphate concentration.  The device or system shall not be used in conditions that are indicative of a potential helical pile corrosion situation, as defined by soil resistivity less than 1,000 ohm-cm, pH less than 5.5, soils with high organic content, sulfate concentrations greater than 1,000 ppm, landfills, or mine waste.

[1812.2.2] 1814.2.2 Protective treatment.  In addition to the protective treatment requirements of Section [1808.2.12] 1810.2.12, helical pile design shall consider the abrasive action inherent in the installation process when protective exterior treatment is specified as helical pile protection.

[1812.3] 1814.3 Determination of allowable loads. The allowable load of helical piles shall be in accordance with the applicable provisions of Section [1808.3] 1810.3.  In addition, the requirements of this section shall apply.

[1812.3.1] 1814.3.1 Allowable axial tension and compression. The allowable axial tension and compression load shall not exceed 30 tons (267 kN).

[1812.3.2] 1814.3.2 Allowable lateral load. The allowable lateral load resisted by a helical pile shall not exceed 3 tons [(29.4 kN)] (26.7 kN).

[1812.4] 1814.4 Load tests.  Load tests shall be in accordance with Sections [1808.4] 1810.4 and [1812.4.1] 1814.4.1 through [1812.4.4] 1814.4.4.

[1812.4.1] 1814.4.1 Compression load test procedures. The allowable axial compression load of a helical pile shall be verified by load tests in accordance with the requirements of Section [1808.4] 1810.4, except that ASTM D1143 may be conducted using the Quick Load Test Loading Procedure.  Following each compression load test, the [test] helical pile being tested shall be removed by unscrewing and inspected for any deformations to the helices[,] to verify the structural integrity of the shaft and its connections.

[1812.4.1.1] 1814.4.1.1 Required number of axial compression load tests. The number of axial compression load tests shall satisfy Section [1808.4] 1810.4.

Exception: [Pile load] Load tests on helical piles shall not be required, provided the following conditions are satisfied:

      - The helical pile has a torque to capacity ratio approved in accordance with Section 28-113.2.1 of the Administrative Code;

      - The torque correlation shall demonstrate a factor of safety (FS) of 2.5 on the allowable load; and

      - The maximum allowable axial compression load on the helical pile shall be 10 tons [(98 kN)] (89 kN).

[1812.4.1.2] 1814.4.1.2 Acceptance criteria. The allowable [pile load] load on the helical pile shall be computed in accordance with Section [1808.4.1.5] 1810.4.1.5.

[1812.4.2] 1814.4.2 Axial tension load test procedures. The allowable axial tension load of a helical pile shall be verified by load testing in accordance with Section [1808.4] 1810.4; however, it shall be permitted to use the Quick Load Test Loading Procedure of ASTM D3689. Following the tension load test, the helical pile shall be removed by unscrewing, and shall be inspected for any deformations to the helices and to verify the structural integrity of the shaft and connections.

[1812.4.2.1] 1814.4.2.1 Required number of axial tension load tests. The number of axial tension load tests shall satisfy Section [1808.4] 1810.4, but with a minimum of one test.

[1812.4.3] 1814.4.3 Lateral load test procedures. The allowable lateral load of a helical pile shall be verified with load testing in accordance with Section [1808.4] 1810.4. Following the lateral load test, the helical pile shall be removed by unscrewing and inspected for any deformations to the helices[,] to verify the structural integrity of the shaft and connections.

[1812.4.3.1] 1814.4.3.1 Required number of lateral load tests. The number of lateral load tests shall satisfy Section [1808.4] 1810.4, but shall not be fewer than one test.

[1812.4.3.2] 1814.4.3.2 Acceptance criteria.  The allowable lateral [pile] load on the helical pile shall be computed in accordance with Sections [1808.4.3.1] 1810.4.3.1 and [1808.4.3.2] 1810.4.3.2.

[1812.4.4] 1814.4.4 Additional load tests. Additional axial compression, axial tension and lateral load tests shall be performed for questionable construction as required by Section [1808.4.1.1.1] 1810.4.1.1.1.

[1812.5] 1814.5 Minimum installation torque. Where load tests are required, the [test pile] helical pile being tested shall be used to determine the minimum required site-specific torque for installation of production helical piles.  For each helical pile, the special inspector shall measure and log the installation torque for each foot of depth and the final torque in the helice’s soil-bearing zone. The shaft advancement shall equal or exceed 85 percent of helix pitch per revolution at time of final torque measurement. Where load tests are not required, installation torque shall be in accordance with the exception defined under Section [1812.4.3] 1814.4.3.

[1812.6 Pile internal] 1814.6 Internal stability of helical piles to resist overturning and translation. Where bracket assemblies or structural eccentric forces cause bending, the resulting moment [pile] design of the helical pile shall ensure stability in accordance with Section [1808.2.5] 1810.2.5 and general engineering practice.  Where side-mount brackets are used and a stability analysis indicates that there is insufficient internal stability to resist overturning and translation, helical piles shall be installed staggered or other means shall be designed to provide stability and prevent rotation of the foundation.

[1812.7] 1814.7 Buckling. When helical piles are embedded in soils of Classes 6 and 7, a buckling analysis shall be performed by a recognized method. The allowable axial compressive load shall be not more than two-thirds of the calculated load-causing buckling.  The additional bending moments due to bracket assemblies, structural eccentric forces and coupling rigidity shall be appropriately included in the buckling analysis.

[1812.8] 1814.8 Shaft flexural capacity. Where a moment is transmitted to a single helical pile, a structural analysis shall be conducted to verify that the shaft is capable of resisting the moment with acceptable deflection.

[1812.9] 1814.9 Side-mount bracket assembly test. Where side-mount brackets are used, each bracket assembly shall be proof-tested to a minimum 110 percent of allowable load to demonstrate that the bracket assembly is capable of transferring the loads to the helical pile. The load shall be applied in six equal increments. The 110 percent test load shall be held for a minimum 30 minutes without bracket assembly distortion or deformation. Side-mount brackets for permanent applications shall be encased in concrete with a minimum embedment of 3 inches (76.2 mm). Concrete used to encase side-mount brackets shall meet the requirements of Sections 1903, 1904, 1905 and 1906.

[1812.10] 1814.10 Minimum spacing of helical piles. Minimum spacing between the center lines of helical piles shall be four times the largest helix plate diameter.

[1812.11] 1814.11 Installation. Equipment used for the installation of helical piles shall be as recommended by the helical pile manufacturer.

[1812.12] 1814.12 Special inspection. The installation of helical piles shall be subject to the special inspection requirements in Section [1704.8] 1705.7 and the following requirements:

1.	The special inspector shall prepare a report of special inspections of helical piles[,] and submit such report to the department in a manner acceptable to the commissioner. In addition to the requirements of Section [1704.8] 1705.7, this report shall also include, at a minimum, the following:

1.1.	Helical pile type and product specification sheet for [the] each helical pile installed as published by the manufacturer.

1.2.	Make and model of the equipment used for installation.

1.3.	Make and model number of the torque indicator used to measure installation torque.

1.4.	Calibration records for the torque indicators used to install the helical piles.

1.5.	The installation speed (rpm) of the helical pile.

1.6.	From axial load tests and the site specific torque to capacity relationship, the minimum torque required to achieve the allowable [pile] load of the helical pile in tension or compression.

1.7.	For each helical pile, the installation torque for each foot of depth and the final torque in the helice’s soil-bearing zone. The shaft advancement shall equal or exceed 85 percent of helix pitch per revolution at time of final torque measurement.

2.	Field welds performed in the installation of a helical pile foundation system shall additionally be subject to the special inspection requirements of Section [1704.3] 1705.2.

SECTION BC 1815
PERMANENT PRESTRESSED ROCK AND SOIL ANCHORS

1815.1 General. Rock and soil anchors discussed in this document are cement grouted, prestressed tendons (bars or strands) that are installed in soil or rock. Permanent prestressed rock and soil anchors shall be designed and constructed in accordance with Sections 1815.2 through 1815.8 and PTI DC35.1.

1815.2 Additional geotechnical investigation and report requirements. Where prestressed rock and soil anchors are used, the geotechnical investigation and report provisions of Section 1803.6 shall be expanded to include, but not be limited to, consideration of the following:

1.	Recommended anchor types and capacities.

2.	Suitable center-to-center spacing of anchor elements.

3.	Minimum unbonded and bonded lengths of tendons, including appropriate rock or soil stratum or strata for the bond zone.

4.	The effects of groundwater or voids including grout loss and reduced grout to ground bond.

5.	Installation procedures.

6.	Durability of anchor materials and minimum corrosion protection requirements.

7.	Lock-off load and lift-off load requirements.

8.	Reductions for group action, where necessary.

9.	Protection of adjacent structures due to anchor installation.

1815.3 Materials.  Materials used in prestressed rock and soil anchors shall conform to the following:

1.	Bar tendons. Bar tendons shall conform to the requirements of ASTM A722 or shall be comprised of tested materials not covered by ASTM A722 but have mechanical properties meeting or exceeding those specified by ASTM A722 and which have been cold stressed and stress relieved.

2.	Strand tendons. Strand tendons shall conform to the requirements of ASTM A416 or ASTM A882.

3.	Grout. Grout shall consist of a pumpable mixture of portland cement, water, and any required fine aggregate, supplemental cementitious materials, or admixtures as permitted by Chapter 19. Grout shall have a minimum unconfined compressive strength (f’c) equal to 4,000 psi.

4.	Corrosion protection. All anchors shall meet PTI DC35.1 requirements for Class I protection (Encapsulated Tendons).

1815.4 Design.  Anchors shall be designed in accordance with Sections 1815.4.1 through 1815.4.5.

1815.4.1 Ultimate bond strength. The average ultimate bond strength along the interface between anchor grout and the ground shall be determined by a generally accepted means of analysis and confirmed by load testing performed in accordance with Section 1815.5.

1815.4.2 Applicable strata. The bonded zone of anchors shall not be formed in soils designated as Class 6 or Class 7.

1815.4.3 Bonded zone.  The bonded zone of anchors shall be fully located within materials of similar character and strength.

1815.4.4 Group capacity.  Group capacity of anchors shall be determined by a generally accepted means of analysis and shall:

1.	Ignore any contribution from soil or rock materials located beyond the property limits of the proposed structure.

2.	Not exceed that of the sum of all individual anchor loads.

1815.4.5 Structural aspects.

1.	Anchors design loads shall be based upon the load combinations specified in Section 1605.3.

2.	Anchor design, lock-off, and test loads shall be in accordance with PTI DC35.1.

3.	The cross section of the anchor tendons shall not be considered to contribute to the sliding or lateral resistance of any foundation element by means of shear friction.

4.	Anchor design and lock-off loads shall consider the effects of long-term creep or changes in prestress resulting from deformation.

1815.5 Load testing.  Load testing shall be in accordance with PTI DC35.1.  Extended creep tests shall be performed for any anchors designed with bonded zones located within materials designated as Class 1d, Class 4 or Class 5.

1815.6 Installation. Installation procedures shall comply with the following:

1.	Anchors shall be installed through fully cased boreholes.  Open hole drilling shall only be permitted through stable bedrock.

2.	Anchors having bond zones formed in soil shall be pressure grouted to at least 1.5 times the total stress at the midpoint of the bond zone.

1815.7 Grout sampling and testing.  Sampling and testing of grout shall be performed in accordance with Section 1812.1.1.2.

1815.8 Special inspection.  The installation and testing of prestressed rock and soil anchors shall be subject to special inspection in accordance with the requirements of Section 1705.19.

SECTION BC [1813] 1816
LIQUEFACTION ANALYSIS

[1813.1] 1816.1 General. An assessment of the liquefaction potential shall be determined for each building site except Structural Occupancy/Risk Category I structures. The evaluation of liquefaction potential shall include the following considerations:

1.	Noncohesive granular soils below groundwater table and less than 50 feet (15 240 mm) below the ground surface shall be considered to have potential for liquefaction.

2.	The potential for liquefaction on level ground shall be determined on the basis of the risk categories associated with the [standard penetration resistance normalized to an energy of 60 percent efficiency (N60)] values of N60 at the site, as defined in Figure [1813.1] 1816.1, or a site-specific analysis performed by a geotechnical engineer.

3.	Clays, silts and clayey silts below the groundwater table and less than 50 feet (15 240 mm) below the ground surface with a plasticity index less than 20 shall be considered to have potential for liquefaction. The susceptibility of the fine grained soils shall be evaluated in accordance with generally accepted engineering practice or a site-specific analysis performed by a geotechnical engineer.

FIGURE [1813.1] 1816.1
LIQUEFACTION ASSESSMENT DIAGRAM

[1813.2] 1816.2 Site-specific analyses. In evaluating liquefaction potential, the analysis shall consider the following parameters: peak ground acceleration, earthquake magnitude, magnitude scaling factor, effective [overburden pressure] stress, hammer energy, cone penetration resistance (where applicable), and fines content. If a site response analysis is conducted, bedrock acceleration time histories and a shear wave velocity profile based on in-situ measurements may be utilized. These analyses may consider the results of laboratory cyclic shear tests.  Where borings are drilled for the purpose of site-specific analyses and for the purpose of evaluating liquefaction potential, the drilling and sampling procedures and apparatus shall be in accordance with ASTM D6066.

[1813.2.1] 1816.2.1 Peak ground acceleration.  Peak ground acceleration shall be determined based on either (1) a site-specific study taking into account soil amplification effects as specified in Section [11.4.7] 11.4.8 of ASCE 7[-10] or (2) the Maximum Considered Geometric Mean peak ground acceleration adjusted for [Site Class] site class effects PGAM as provided in Table [1813.2.1] 1816.2.1 without adjustment for targeted risk.

| TABLE [1813.2.1] 1816.2.1 VALUES OF MAXIMUM CONSIDERED EARTHQUAKE MEAN (MCEG) PEAK GROUND ACCELERATIONS ADJUSTED FOR SITE CLASS EFFECTS, PGAM |
| --- |
| Site Class | PGAM(g) |
| A | [0.14] 0.15 |
| B (m) | 0.17 |
| B (un-m) | 0.18 |
| C | [0.20] 0.22 |
| D | [0.24] 0.26 |
| E | [0.33] 0.36 |

[1813.3] 1816.3 Foundation design analysis. The foundation design analysis shall consider an assessment of the potential consequences of any liquefaction and soil strength loss, including an estimation of total and differential settlement, lateral movement or reduction in foundation soil-bearing capacity, and may incorporate the potential benefits of any proposed mitigation measures. Such measures may be given consideration in the design of the structure and may include, but are not limited to, ground improvement, pore pressure dissipation, selection of appropriate foundation type and depths, selection of appropriate structural systems to accommodate anticipated displacements, or any combination of these measures.

In evaluating the potential for liquefaction, the effect of settlements induced by seismic motions and loss of soil strength shall be considered. The analysis performed shall incorporate the effects of the maximum considered earthquake (MCE) peak ground acceleration, appropriate earthquake magnitudes and duration consistent with the design earthquake ground motions as well as uncertainty and variability of soil properties across the site. The MCE peak ground acceleration, seismically induced cyclic stress ratios and pore pressure development may be determined from a site-specific study taking into account soil amplification effects and design ground motions appropriate for the seismic hazard. Other recognized methods of analysis may be used in the evaluation process subject to the approval of the commissioner. Effects of liquefaction shall be considered in the design except when the following conditions exist:

1.	Structures classified as Risk Category I.

2.	When the calculated cyclic resistance ratio (CRR) is greater than or equal to the calculated cyclic stress ratio (CSR) for Risk Category II and III structures.

3.	When the calculated CRR is greater than 1.2 times the calculated CSR for Risk Category IV structures.

[1813.4] 1816.4 Design considerations. Where liquefaction is determined to be probable, the following considerations shall be addressed in the design:

1.	Liquefiable soils shall be considered to have no passive (lateral) resistance or bearing capacity value for the design earthquake, unless shown otherwise by accepted methods of analysis. The engineer shall submit an analysis for review and approval by the commissioner, demonstrating that the proposed construction is safe against the effects of soil liquefaction.

2.	Where liquefiable soils are present in sloped ground or over sloped nonliquefiable substrata and where lateral displacement is possible, the engineer shall submit a stability analysis for review and approval by the commissioner, demonstrating that the proposed construction is safe against failure of the soil and that the effects of potential lateral displacements are acceptable.

SECTION BC [1814] 1817
UNDERPINNING AND ALTERNATE METHODS OF SUPPORT OF BUILDINGS AND ADJACENT PROPERTY

[1814.1] 1817.1 General. Where the [protection and/or support of a structure or property adjacent to an excavation is required, an engineer shall prepare a preconstruction report summarizing the condition of the structure or property.  The preconstruction report shall be prepared based on an examination of the structure or property, the review of available documents and, if necessary, the excavation of test pits. The engineer shall determine the requirements for underpinning or other protection and prepare site and structure-specific plans, including details and sequence of work for submission to the commissioner. Such protection may be provided by underpinning, sheeting, and bracing, or by other means acceptable to the commissioner.] proposed work may disturb, displace or otherwise affect the lateral or vertical support of property or buildings, an engineer shall evaluate the need for and methods to maintain the stability and integrity of the building(s), utilities or soil adjacent to such activity.

[1814.1.1 Underpinning and bracing. Underpinning piers, walls, piles and footings shall be designed as permanent structural elements and installed in accordance with provisions of this chapter and Chapter 33 and shall be inspected in accordance with the provisions of Chapter 17. Underpinning shall be designed and installed in such manner so as to limit the lateral and vertical displacement of the adjacent structure to permissible values as established in accordance with Section 1814.3. The sequence of installation and the requirements for sheeting, preloading, wedging with steel wedges, jacking or dry packing shall be identified in the design. The design shall take in account the effects on foundation and structure produced by the lateral earth pressure exerted on the underpinning. Lateral support for underpinning, if needed, shall be accounted for during the design of the new construction. The design and construction sequence of temporary lateral supports used prior to the installation of the foundation walls shall be included on the design drawings.]

1817.2 Minimum requirements for undeveloped adjacent property. The minimum requirements for construction documents for support of adjacent property which does not contain a building, such as, but not limited to, empty lots, court yards, front yards, or rear yards, shall include the following information:

1.	Existing grade of the adjacent property.

2.	Plans, cross-sections, and elevations as necessary, to illustrate all unique conditions of the support of excavation, including the depth of the proposed excavation, the subsurface conditions, surcharge loading, the proposed method of support, sequence of construction, required material properties, and additional details as required by Section 3304.

3.	Details and criteria for monitoring, including but not limited to criteria and thresholds for movements, and dewatering as specified in Chapters 17, 18 and 33.

4.	The elevation of the water table, need for dewatering as noted in the Geotechnical Report, and the maximum permissible drawdown outside of the project site.

1817.3 Evaluation of adjacent buildings for suitable method of support. At the time of foundation plan approval, an engineer shall submit an evaluation report to the department assessing the condition of the existing building and the subsurface conditions of the construction site and adjacent property. The report shall also identify acceptable method(s) of support, including underpinning or alternate methods of support, for the building. This evaluation shall be performed in accordance with the requirements of Section 1817.3.1 through 1817.3.6.

1817.3.1 Assessment of the building and the subsurface conditions: The engineer shall assess the condition of the existing building, and the subsurface conditions of the construction site and adjacent property, to an extent sufficient for determining acceptable method(s) of support, including underpinning or alternate methods of support. As necessary, the assessment shall be based on visual observations, calculations, review of the geotechnical report prepared for the project in accordance with Section 1803.6 and review of other available documentation.  The investigation shall include, as necessary, but need not be limited to, the following items:

1.	An evaluation of the vertical load path of the building as it relates to the location of the proposed underpinning or alternate method of support.

2.	An evaluation of the lateral load path of the building as it relates to the location of the proposed underpinning or alternate method of support.

3.	Calculations of the vertical and lateral loads at the foundations to be underpinned or supported by an alternate method of support.

4.	A determination of the type and condition of the above grade elements to be supported or potentially affected by the work.

5.	A survey of deviations from plumb or horizontal position of the building.

6.	Identification of conspicuous structural defects, including but not limited to: bowing, significant cracking, structural degradation or unusual slenderness. A detailed description of such items shall be provided, with photographs and mapping if possible.

7.	A determination of acceptable thresholds for maximum vertical and lateral movement, maximum permissible vibrations, the required monitoring and the protocols for exceedances.

8.	A determination of the type and condition of the foundation elements to be supported or potentially affected by the work.

9.	A test pit at each substantial change in foundation type or building geometry.  Records of the test pits shall include the following:

a.	A description of the construction materials and condition of the footing, foundation wall and/or foundation system.

b.	The bottom elevation of the wall(s) and/or footing(s).

c.	The classification of the soil or rock the foundation bears upon.

d.	Photographs and sketches of the test pit.

10.	An assessment of the allowable bearing pressure of the soils supporting the existing foundation(s) per Section 1806.

11.	An assessment of potential reductions to the allowable bearing pressure due to the proposed excavation.

12.	The lateral earth, surcharge, and water pressures that will be present on the elements of the proposed underpinning or alternate method of support.

13.	An analysis of the subsurface conditions and their potential impacts on the underpinning or alternate method of support work such as, but not limited to: high water table and need for dewatering, loose soils, potentially running soils, presence of boulders, or other factors that could impact the design or construction of the underpinning or alternate method of support.

14.	An assessment of the allowable bearing pressure of the soils supporting the underpinning or alternate method of support during the installation sequence and in the permanent condition.

15.	An assessment of the anticipated settlement during the underpinning or alternate method of support, and soil and foundation work.

16.	Any additional information requested by the commissioner.

1817.3.2 Additional requirements for buildings with rubble foundation elements. For buildings with rubble foundation elements, an assessment of the condition of the rubble element shall be performed.  If the rubble foundation elements are in poor condition, recommendations for addressing the poor conditions shall be provided.

1817.3.3 Additional requirements for unreinforced masonry buildings. Where the building being supported is of unreinforced masonry construction, the lateral stability of the masonry walls and their ability to resist the loads imposed shall be verified.

Exception: If it is not possible to verify the lateral stability of the masonry walls, lateral support shall be provided at the floor levels of the adjacent building prior to installation of the underpinning or alternate method of support.  Such lateral support shall be shown on the construction documents.

1817.3.4 Additional requirements for use of rock support. Where in situ Class 1a, 1b, or 1c rock is proposed for use in place of constructed methods of support, a subsurface investigation shall be conducted to assess the properties of the rock. Site-specific data shall be obtained to determine the predominant strike and dip of the joints, foliation, and/or other discontinuities in the rock. Recommendations for any rock stabilization necessary for the proposed work shall be provided.

1817.3.5 Evaluation report. The evaluation report shall include the following items:

1.	The address of the property.

2.	A description of the acceptable method(s) of support, including underpinning or alternate methods of support, that were evaluated and found to be feasible.

3.	A description of any required modifications to reinforce the existing building prior to the start of the underpinning or alternate method of support work.

4.	A summary of the assessment required by Sections 1817.3.1 through 1817.3.4, including all test pit records, where performed, and any additional items deemed necessary by the engineer.

5.	A list of all assumptions made in preparation of the evaluation report and a detailed plan for the verification of such assumptions.

6.	If the engineer determined that specific items listed in Sections 1817.3.1 through 1817.3.4 were not required, a statement shall be included explaining the basis for that determination for each item that was not included.

1817.3.6 Responsibility for the report. If more than one engineer participates in performing the required assessments of the building and subsurface conditions, and the author of the evaluation report is relying on the work of these additional engineer(s) in preparing the evaluation report, the findings of the additional engineer(s) shall be included as signed and sealed appendices to the evaluation report.

1817.4 Suitable Methods of Support. Where a method of support for an existing building is required, such underpinning or alternate method of support shall be designed as a permanent structural element specific to the building using the methods described in Sections 1817.4.1 through 1817.4.3. The underpinning or alternate method of support shall be installed in accordance with provisions of this chapter and Chapter 33 and shall be inspected in accordance with the provisions of Chapter 17.

1817.4.1 Underpinning. If the foundation loads are to be transferred to a lower bearing level, underpinning consisting of concrete piers, drilled piles, jacked piles, bracket piles, or similar engineered systems to transfer the existing building loads below the bottom of the proposed excavation shall be installed.

The bearing pressure at the base of the underpinning shall be computed accounting for all vertical loads and any overturning moments present due to lateral earth and water pressures,  and shall be less than or equal to the allowable bearing pressure of the bearing stratum.

1817.4.2 Alternate methods of support. In lieu of underpinning, an excavation support system and/or lateral bracing designed to restrict the movements of the adjacent buildings within the established threshold levels may be installed. Such excavation support systems may consist of secant piles, slurry walls, tangent pile walls, jet grouting, pressed-in continuous sheeting, or similar engineered system.

[1814.2] 1817.4.3 Use of rock support. Existing structures founded at a level above the level of adjacent new construction may be supported on Class 1a, [and] 1b, and 1c rock in lieu of underpinning, [sheeting and bracing or retaining walls,] provided [that a report by the engineer substantiates the safety of the proposed construction. The engineer shall also certify that the he or she has inspected the exposed rock and the jointing therein and has determined whether supplemental support of the rock face is required.] the requirements of Section 1817.3.4 are satisfied.

1817.5 Design requirements. The underpinning or alternate method of support for adjacent buildings shall be designed by an engineer and plans filed with the department for approval prior to the commencement of the work.

1817.5.1 New construction. Materials and design shall be in accordance with the requirements of this code for new construction.

1817.5.2 Incorporation of the evaluation report. The design shall incorporate the findings of the evaluation report and any additional evaluation and investigation deemed necessary by the engineer performing the design. If the evaluation report did not conclusively demonstrate the suitability of an underpinning or alternate method of support, such method of support shall not be used.

1817.5.3 Deviations from the evaluation report. The engineer designing the method of support may be an engineer other than the engineer who submitted the evaluation report. If the engineer designing the method of support does not accept the evaluation report or finds it insufficient, a new evaluation report shall be submitted to the department. Similarly, if a method of support other than one(s) determined to be suitable in the evaluation report is proposed for use, an additional evaluation report shall be submitted to the department justifying the suitability of the method of support now proposed.  The revised report may be submitted along with the construction documents for the design of the method of support. Alternatively, minor exceptions to the report may be incorporated into the design documents if explicitly indicated on the design documents along with the engineer’s reason for override.

1817.5.4 Design loads and load combinations. Underpinning, alternate methods of support and any associated lateral support system, shall be designed for the loads and load combinations listed in Sections 1817.5.4.1 and 1817.5.4.2.

1817.5.4.1 Loads from the existing building. A computation shall be performed to establish the vertical and lateral loads on the elements of the method of support from the existing building.  Loads and load combinations shall be computed in accordance with the requirements of Chapter 16 or where permitted for loads of prior codes for prior code buildings.

1817.5.4.1.1 Unconfirmed load path. Where the evaluation of Section 1817.3 is unable to visually confirm the load path from the existing building, pit-pier underpinning where all horizontal loads are transferred directly to a raker or tension anchor bracing system that braces every pit-pier is permissible.

Exception: Raker bracing or tension anchors need not be installed where it is demonstrated by calculation, according to data provided by the investigation per Section 1817.3.1, that the underpinning system, analyzed independently as a retaining wall that supports the soil and water behind it, calculated both (a) with and (b) without accounting for vertical loads from the structure above, has satisfactory bearing pressures and is stable with a 1.5 factor of safety against overturning and sliding. This exception shall not be utilized in unreinforced masonry buildings in which access to verify the lateral stability of masonry walls is not possible as per Section 1817.3.3.

1817.5.4.2 Soil and water pressures. The design shall include at rest soil pressures, water pressures, and any surcharge pressures that arise from the adjacent portions of the building being underpinned or supported by an alternate method of support.

1817.5.5 Anticipated deflection. A calculation shall be performed for the anticipated deflection of the method of support system and its effect on the supported building.

1817.5.6 Factor of safety. Methods of support shall be designed to provide a minimum factor of safety of 1.5 for sliding and overturning for all loads and all anticipated interim conditions.

1817.5.7 Sequence. The design of the method of support shall account for the means and methods of installation, sequence of operations, and all the load transfers and associated support conditions for all phases of the work.

1817.6 Minimum requirements for construction documents. Construction documents for methods of support of adjacent buildings shall include the following information:

1.	Indicate the type of adjacent foundation, including type of material.

2.	The bearing elevation(s) of the adjacent building foundation and its soil classification.

3.	For deep foundations, type and location including top and bottom elevations of deep foundation elements.

4.	The elevations of all floor levels at grade and below in the adjacent building.

5.	Plans, cross-sections, and elevations views as necessary, to illustrate all conditions of the adjacent building relevant to the operation, including the below grade portions and the depth of the proposed excavation.

6.	Details and criteria for monitoring the building or wall being supported, including but not limited to criteria and thresholds for movements as specified in Section 1817.9 and Chapters 17 and 33.

7.	A fully detailed design of the method of support including any required bracing.

a.	For pit-pier underpinning, a detailed design for the timber shoring of the pit excavations shall also be provided.

8.	A step by step procedure describing the installation of the elements of the method of support.

a.	For pit-pier underpinning, the procedure shall include a diagram indicating the sequence of the pit installation and a detailed procedure of the installation of the shoring for the pit excavations.

9.	The elevation of the water table, need for dewatering as noted in the evaluation report, and the maximum permissible drawdown.

10.	References alerting the contractor and the special inspector to review the evaluation report of the adjacent building prior to the start of work.

11.	Plans, sections, and elevation views of all methods of support.

12.	Soil classification of the required bearing stratum for the elements of the method of support.

a.	For pit-pier underpinning, also include the required allowable bearing pressure below the pier.

13.	A load table or diagram shall be provided to indicate the following:

a.	Total gravity load in underpinning pier or alternate method of support.

b.	Total lateral load in underpinning piers or alternate method of support.

1817.7 Additional requirements for pit-pier underpinning. When the method of support selected is pit-pier underpinning, the design shall meet the following minimum criteria:

1.	After installation of each pit-pier, the approach pit shall be back filled.

2.	In no case shall the general site excavation expose more than one third of the total height of a pit-pier, unless:

2.1.	A pit-pier bracing system designed by the engineer is installed or;

2.2.	The calculated capacity of the individual pit-pier to resist lateral loading at a greater depth is identified on the drawings.

3.	Pit-piers shall be preloaded by wedging, use of permanent jacks, or by other means designed by the engineer.

4.	Any voids between the bottom of the foundation and the top of the pit-pier shall be filled with dry-pack or equivalent. Dry-pack shall be composed of nonshrink material and be no more than 3 inches in thickness.

5.	The need for jacking and all associated jacking requirements shall be determined by the engineer responsible for the underpinning design.

6.	The width of pit-piers shall not exceed 4 feet unless the calculations determine that a wider pit-pier is acceptable.

7.	Shear transfer shall be designed and installed between adjacent pit-piers.

8.	The bottom of pit-pier elevation shall be a minimum of one foot below the bottom of the future adjacent excavation.

1817.7.1 Pit-pier excavation. Pit-pier excavation shall be subject to the requirements of Section 1817.7.1.1 through 1817.7.1.8.

1817.7.1.1 Excavation Methods.  Pit-pier excavations shall be performed using hand held tools.  Excavation using backhoes or other mechanical means to excavate the pit-piers is prohibited.

1817.7.1.2 Clear distance between open pits. Clear distance between open pits shall be determined by the evaluation report and shall not be less than 12 feet (3658 mm).

1817.7.1.3 Pit Excavation below the lowest installed lagging board. Lagging boards shall be installed as the excavation proceeds to limit soil loss.  In no case shall excavation proceed more than 2 feet (610 mm) below the lowest installed lagging board.  At completion of pit excavation, the pit shall be fully lagged.

1817.7.1.4 Backpacking. Backpacking of any voids shall be performed at each excavation lift.

1817.7.1.5 Excavation below the water table. Pit excavation shall not proceed below the water table.  If the depth of the underpinning requires excavation below the existing water table, a dewatering system shall be installed prior to the start of the excavation.  The dewatering system shall be tested via test pit or piezometer to confirm that the water table has been sufficiently drawn down prior to the start of the pit underpinning work.

1817.7.1.6 Variable depth pits. Where construction requires adjacent pits to be excavated to differing depths, the deeper pit-pier shall be constructed first.

1817.7.1.7 Multi-tier pit pier underpinning. Where multi-tier pit-pier underpinning is utilized, the upper piers shall be braced prior to the excavation of the lower pier and the installation of upper and lower piers staggered, unless the design per Section 1817.5 and drawings include explicit methods that will ensure that the installation of lower tiers shall not displace the tiers above.

1817.7.1.8 Use of tension anchors. When tension anchors are utilized, the effects of vertical and horizontal force components shall be accounted for including any potential additional displacements.

1817.8 Additional requirements for deep foundation elements used in underpinning. Where the method of support includes deep foundation systems such as pile supported underpinning or tie anchors, the requirements of Chapter 18 and Sections 1817.8.1 through 1817.8.5 shall be met.

1817.8.1 Pile design.  Piles used for underpinning shall be designed in accordance with Sections 1810.3 and 1810.4.

1817.8.2 Load testing of underpinning piles.  Piles used for underpinning are subject to the load testing criteria of Section 1810.4.

1817.8.3 Eccentric pile loads. Piles used for underpinning shall be designed to sustain all moments that are generated due to any eccentricities of the load on the pile.

1817.8.4 Spanning between piles. Unless new grade beams are provided, calculations shall be performed to confirm that the existing foundation can support the required loads spanning between the pile supports.

1817.8.5 Piles used as excavation support elements. If underpinning piles are to be used as excavation support elements, a calculation of the anticipated pile deflection shall be performed and its impacts on the supported building shall be assessed by the engineer.

[1814.3] 1817.9 Monitoring. When excavation, foundation construction, [or] underpinning, or an alternate method of support is required, adjacent structures and properties shall be monitored in accordance with a plan prepared by the engineer.  The engineer shall develop the scope of the monitoring program, including location and type of instruments, frequency and duration of readings, frequency of reporting, maximum allowable time to report readings (timely reporting), reporting requirements, and permissible movement and vibration criteria. This scope shall take into account the [structures] buildings or property to be monitored and the conditions thereof.  The monitoring program shall include necessary actions to address exceedances. These actions shall include notification of the commissioner.  Monitoring of historic and landmarked structures shall be subject to special requirements as determined by the department. Where the building to be monitored is subject to underpinning or alternate methods of support, the monitoring plan shall be determined by the engineer designing such work.

1817.10 Special Inspection. Special inspection shall be conducted in accordance with Chapter 17.

SECTION BC 1818
GEOTECHNICAL PEER REVIEW

1818.1 General. The provisions of this section specify where geotechnical peer review is required, how and by whom it is to be performed.

1818.2 Where required.  A geotechnical peer review shall be performed and a report shall be required in the following instances:

1. Where structural peer review is required pursuant to Section 1616.

2. For structures of Risk Category III or IV where the seismic site class is Site Class F.

3. Where performance based foundation design is utilized.

4. As required by the commissioner.

1818.3 Geotechnical peer review qualifications:  The geotechnical peer review shall be performed by a qualified independent geotechnical engineer who has been retained by or on behalf of the owner. A geotechnical peer reviewer shall meet the requirements of the rules of the department.

1818.3.1 Independence. In order to satisfy the requirement that the peer reviewer be independent, the department requires that the peer reviewer must not engage in any activities that may conflict with their objective judgment and integrity, including but not limited to having a financial and/or other interest in the design, construction, installation, manufacture or maintenance of structures or components that they are reviewing.

1818.4 Extent of Geotechnical Peer Review.  The extent of the geotechnical peer review shall be performed in accordance with Section 1818.4.1.

1818.4.1 Scope. The geotechnical peer reviewer shall review the plans and specifications submitted with the permit application for general compliance with the foundation design provisions of this code. The reviewing engineer shall perform the following tasks at a minimum:

1.	Confirm that the subsurface investigation meets the requirements of this code

2.	Confirm that the geotechnical report and supplemental reports, including foundation recommendations and testing, meet the requirements of this code.

3.	Provide independent check on foundation capacities. This check must include the structural and geotechnical capacity of the foundation element, if not covered by the structural peer review.

4.	Where uplift resistance is required, provide independent check on prestressed anchor or pile design.

5.	Perform independent settlement calculations.

6.	Confirm the design assumptions made by the geotechnical and structural engineers pertaining to the soil-foundation structure interaction are coordinated and consistent.

7.	Confirm that potential impacts on adjacent structures due to foundation construction have been addressed in accordance with this code.

8.	Review seismic analysis including any site-specific analysis, associated mitigation methods, and analyses pertaining to liquefaction for conformance with codes.

1818.5 Geotechnical peer review report. The geotechnical peer review report shall comply with Section 1818.5.1 through 1818.5.3.

1818.5.1 General. The reviewing engineer shall submit a report to the department stating whether or not the geotechnical design shown on the plans, reports and specifications generally conforms to the requirements of this code.

1818.5.2 Contents. The report shall demonstrate, at a minimum, compliance with Items 1 through 8 of Section 1818.4.1. In addition, the report shall also include the following:

1.	The codes and standards used in the geotechnical design of the project.

2.	The basis for design criteria that are not specified directly in applicable codes and standards. This should include reports by consultants such as geotechnical reports and site specific seismic studies. Generally, the report should confirm that existing conditions at the site have been investigated appropriately and that the design of the proposed foundations is in general conformance with these conditions.

3.	Basis of performance based design and its appropriateness of use.

4.	A statement that the qualification and independence of the peer reviewer is in accordance with Section 1818.3.

5.	Peer review reports shall provide an unconditional statement that must be either an acceptance or rejection of code compliance of the geotechnical design required to be reviewed by this section.

1818.5.3 Phased submission. If an application is submitted for a permit for the construction of foundations or any other part of a building before the construction documents for the whole building have been submitted, then the geotechnical peer review and report shall be phased. The geotechnical peer reviewer shall be provided with sufficient information on which to make a geotechnical peer review of the phased submission. In addition to the requirements of this section, phased submission of the report shall include any changes made to the initial geotechnical peer review evaluation. The geotechnical peer review report need not be submitted concurrently with the structural peer review report.

1818.6 Responsibility. Responsibility shall be as provided for in Section 1818.6.1 through 1818.6.4.

1818.6.1 Engineer of record. The engineer of record for the foundation design shall retain sole responsibility for the geotechnical design. The activities and reports of the geotechnical peer reviewer shall not relieve the engineer of record for the foundation design of this responsibility.

1818.6.2 Geotechnical peer reviewer. The geotechnical peer reviewer’s report states his or her opinion regarding the design by the engineer of record for the foundation design. The standard of care to which the geotechnical peer reviewer shall be held in the performance of the geotechnical peer review and report is that level of skill and care are consistent with geotechnical peer review services performed by professional engineers licensed in the State of New York for similar type projects. The geotechnical peer reviewer shall not be responsible for the accuracy of the subsurface investigation data or the conclusions of the structural peer review reports.

1818.6.3 Revisions of design. The engineer of record for the foundation design shall identify that a new review is required based upon changes to the design documents relevant to the scope of the peer review.  The geotechnical peer reviewer shall review the items that have been affected and shall revise the geotechnical peer review report.

1818.6.4 Disputes. When a dispute arises between the applicant of record and the peer reviewer regarding compliance with Section 1818 that cannot be resolved by these parties, such dispute shall be reported to the department in the form of a letter from the applicant of record. The department may make a final decision or may accept a change of the peer reviewer.

1818.7 Change to peer reviewer. The peer reviewer cannot be changed without the express consent of the department. The current peer reviewer must submit both a written letter to the borough commissioner detailing the reason for the withdrawal request and a report of the geotechnical peer review findings to date. If a change of peer reviewer is approved, a revised PW1 must be submitted indicating the replacement peer reviewer.

§ 20. Chapter 19 of the New York city building code, as amended by local law number 141 for the year 2013, is amended to read as follows:

CHAPTER 19
CONCRETE

SECTION BC 1901
GENERAL

1901.1 Scope. The provisions of this chapter shall govern the materials, quality control, design and construction of concrete used in structures.

1901.1.1 Referenced standards. Where this code makes reference to the nationally recognized standard ACI 318, such standard shall be as modified for New York City in accordance with Section 1908 of this code. Where sections within ACI 318 are referenced in other chapters and appendices of ACI 318, the provisions of this chapter shall apply.

1901.2 Plain and reinforced concrete. Structural concrete shall be designed and constructed in accordance with the requirements of this chapter and ACI 318 as amended in Section 1908 of this code. Except for the provisions of Sections 1904 and 1910, the design and construction of slabs on grade shall not be governed by this chapter unless they transmit vertical loads or lateral forces from other parts of the structure to the soil. Precast concrete diaphragms in buildings assigned to Seismic Design Category C or D shall be designed in accordance with the requirements of ASCE 7, Section 14.2.4.

[1901.3 Source and applicability. Sections 1902 through 1907 of this chapter are derived from the provisions for structural concrete in ACI 318. Where sections within Chapters 2 through 7 of ACI 318 are referenced in other chapters and appendices of ACI 318, the provisions of Sections 1902 through 1907 of this code shall apply.]

1901.3 Anchoring to concrete. Anchoring to concrete shall be in accordance with ACI 318 as amended in Section 1908, and applies to cast-in (headed bolts, headed studs and hooked J- or L-bolts), post-installed expansion (torque-controlled and displacement-controlled), undercut and adhesive anchors.

1901.4 Composite structural steel and concrete structures. Systems of structural steel acting compositely with reinforced concrete shall be designed in accordance with Section 2206.

[1901.4] 1901.5 Construction documents. The construction documents for structural concrete construction shall include:

- [Specified] The specified compressive strength of concrete at the stated ages or stages of construction for which each concrete element is designed.

- [Specified] The specified strength or grade of reinforcement.

- [Size] The size and location of structural elements, reinforcement[,] and anchors.

- Provision for dimensional changes resulting from creep, shrinkage and temperature.

- [Magnitude] The magnitude and location of prestressing forces.

- Anchorage length of reinforcement and location and length of lap splices.

- Type and location of mechanical and welded splices of reinforcement.

- Details and location of contraction or isolation joints specified for plain concrete.

- Minimum concrete compressive strength at time of posttensioning.

- Stressing sequence for posttensioning tendons.

- For structures assigned to Seismic Design Category D, a statement if slab on grade is designed as a structural diaphragm [(see Section 2112.3.4 of ACI 318)].

- Exposure classes per ACI 318, Section 19.3.1, and Section 1904.2 of this code [chapter and Section 4.2 of ACI 318].

- Areas of mass-concrete where a thermal control plan is required.

[1901.5] 1901.6 Special [inspection] inspections and tests. [The special inspection] Special inspections and tests of concrete elements of buildings and structures, and concreting operations, shall be [in accordance with] as required by Chapter 17.

SECTION BC 1902
DEFINITIONS

1902.1 [General] Definitions. The [words and terms] following term is defined in [this section and ACI 318 shall, for the purposes of this chapter and as used elsewhere in this code for concrete construction, have the meanings shown herein and in ACI 318, as modified by Section 1908.1.1 of this chapter.] Chapter 2:

MASS CONCRETE. [Any volume of concrete with dimensions large enough to require that measures be taken to cope with generation of heat from hydration of the cement and attendant volume change to minimize cracking, reduction of compressive strength, and/or delayed ettringite formation.]

SECTION BC 1903
SPECIFICATIONS FOR TESTS AND MATERIALS

1903.1 General. Materials used to produce concrete, concrete itself and testing thereof shall comply with the applicable standards listed in ACI 318 and this section.[Where required, special inspections and tests shall be in accordance with Chapter 17.]

1903.2 [Cemetitious materials. Cementitious materials used to produce concrete shall comply with ACI 318, Section 3.2.] Special inspections. Where required, special inspections and tests shall be in accordance with Chapter 17.

1903.3 [Aggregates. Aggregates used in concrete shall comply with ACI 318, Section 3.3.]

Glass fiber-reinforced concrete. Glass fiber-reinforced concrete (GFRC) and the materials used in such concrete shall be in accordance with the PCI MNL 128 standard.

1903.4 Flat wall insulating concrete form (ICF) systems. Insulating concrete form material used for forming flat concrete walls shall conform to ASTM E 2634.

1903.5 Water. Water used in mixing concrete shall be clean and free from injurious amounts of oils, acids, alkalis, salts, organic materials or other substances that are deleterious to concrete or steel reinforcement and shall comply with ACI 318, Section [3.4] 26.4.1.3.

[1903.5] 1903.6 Steel reinforcement. Reinforcement and welding of reinforcement to be placed in concrete construction shall conform to the requirements of ACI 318, [Section 3.5] Chapter 20, and this section.

[1903.5.1] 1903.6.1 Reinforcement type. Steel reinforcement used in concrete construction shall comply with ACI 318, [Section 3.5] Chapter 20.

[1903.5.2] 1903.6.2 Welding. Welding of reinforcing bars shall conform to AWS D1.4 and ACI 318, Section [3.5.2] 26.6.4. Type and location of welded splices and other required welding of reinforcing bars shall be indicated on the construction documents or in the project specifications. The ASTM reinforcing bar specifications, except for ASTM A 706, shall be supplemented to require a report of material properties necessary to conform to the requirements in AWS D1.4. A written welding procedure shall be provided to the registered design professional of record for approval prior to any welding. All welding shall be subject to special inspection by a special inspection agency.

[1903.6] 1903.7 Admixtures. Admixtures to be used in concrete shall be subject to prior approval by the registered design professional of record and shall comply with ACI 318, Section [3.6] 26.4.1.4.  Admixtures shall be included in the concrete design mix submittals.

[1903.7] 1903.8 Storage of materials. The storage of materials for use in concrete shall comply with ACI 318, Section [3.7] 26.5.1, and the provisions of Sections [1903.7.1] 1903.8.1 and [1903.7.2] 1903.8.2 of this chapter.

[1903.7.1] 1903.8.1 Manner of storage. Cementitious materials and aggregates shall be stored in such a manner as to prevent deterioration or intrusion of foreign matter.

[1903.7.2] 1903.8.2 Unacceptable material. Any material that has deteriorated or has been contaminated shall not be used for concrete.

[1903.8 Glass fiber reinforced concrete. Glass fiber-reinforced concrete (GFRC) and the materials used in such concrete shall be in accordance with the PCI MNL 128 standard.]

[1903.9 Flat wall insulating concrete form (ICF) systems. Insulating concrete form material used for forming flat concrete walls shall conform to ASTM E 2634.]

SECTION BC 1904
DURABILITY REQUIREMENTS

1904.1 General. Concrete shall be designed and proportioned to comply with the durability, strength, exposure, and other requirements as specified in [Section 4.1 of] ACI 318 and Sections 1904.2 through 1904.5 of this chapter.

1904.2 Exposure categories and classes. Concrete shall be assigned to exposure classes in accordance with ACI 318, Section [4.2] 19.3.1, based on:

1.	Exposure to freezing and thawing in a moist condition or exposure to deicing chemicals;

2.	Exposure to sulfates in water or soil;

3.	Exposure to water where the concrete is intended to have low permeability; and

4.	Exposure to chlorides from deicing chemicals, salt, saltwater, brackish water, seawater or spray from these sources, where the concrete has steel reinforcement.

1904.3 Concrete properties. Concrete mixtures shall conform to the most restrictive [maximum water-cementitious materials ratios and minimum specified concrete compressive strength] requirements of ACI 318, Section [4.3] 19.3.2, based on the exposure classes assigned in Section 1904.2 of this chapter.

Exception: For occupancies and appurtenances thereto in Group R occupancies that are in buildings less than four stories above grade plane, normal-weight aggregate concrete is permitted to comply with the requirements of Table 1904.3 of this chapter in lieu of the requirements of ACI 318, Table [4.3.1] 19.3.2.1.

TABLE 1904.3
MINIMUM SPECIFIED COMPRESSIVE STRENGTH (f’c)

| TYPE OR LOCATION OF CONCRETE CONSTRUCTION | MINIMUM SPECIFIED COMPRESSIVE STRENGTH (f’c at 28 days, psi) |
| --- | --- |
| Basement walls , foundation walls, exterior walls and other vertical concrete surfaces, basement slabs, interior slabs on grade except for garage floor slabs, and foundations not exposed to the weather | 3,000a |
| Driveways, curbs, walks, patios, porches, carport slabs, steps and other flatwork exposed to the weather, and garage floor slabs | 3,500b |
| Structural concrete exposed to weather | 4,500 |

For SI: 1 pound per square inch = 0.00689 MPa.

- Concrete in these locations that can be subjected to freezing and thawing during construction shall be of air-entrained concrete in accordance with Section 1904.2.

- Concrete shall be air entrained in accordance with Section 1904.4.1.

1904.4 Freezing and thawing exposures. Concrete that will be exposed to freezing and thawing, in the presence of moisture, with or without deicing chemicals being present, shall comply with ACI 318, Section 19.3.3, and Sections 1904.4.1 and 1904.4.2 of this code.

1904.4.1 Air entrainment. Concrete exposed to freezing and thawing while moist shall be air entrained in accordance with ACI 318, [Section 4.4.1] Sections 19.3.3.1 and 19.3.3.3.

1904.4.2 Deicing chemicals. For concrete exposed to freezing and thawing in the presence of moisture and deicing chemicals, the maximum weight of fly ash, other pozzolans, silica fume or slag that is included in the concrete shall not exceed the percentages of the total weight of cementitious materials permitted by Table 1904.4.2.

TABLE 1904.4.2
REQUIREMENTS FOR CONCRETE EXPOSED TO DEICING CHEMICALS

| CEMENTITIOUS MATERIALS | MAXIMUM PERCENT OF TOTAL CEMENTITIOUS MATERIALS BY WEIGHTa,b |
| --- | --- |
| Fly ash or other pozzolans conforming to ASTM C 618 | 25d |
| Slag conforming to ASTM C 989 | 50 |
| Silica fume conforming to ASTM C 1240 | 10 |
| Total of fly ash or other pozzolans, slag and silica fume | 50c |
| Total of fly ash or other pozzolans and silica fume | 35c |

a.	The total cementitious material also includes ASTM C 150, ASTM C 595, ASTM C 845 and ASTM C 1157 cement.

b.	The maximum percentages shall include:

- Fly ash or other pozzolans present in Type IP or I (PM) blended cement, ASTM C 595, or ASTM C 1157.

- Slag used in the manufacture of an IS or I (SM) blended cement, ASTM C 595, or ASTM C 1157.

- Silica fume, ASTM C 1240, present in a blended cement.

c.	Fly ash or other pozzolans and silica fume shall constitute no more than 25 and 10 percent, respectively, of the total weight of the cementitious materials.  The amount of fly ash or other pozzolans conforming to ASTM C 618 shall be permitted to be increased in accordance with footnote d, provided the maximum percentage of supplemental cementitious materials does not exceed the maximum values stated in Table 1904.4.2 when combining multiple types of supplemental cementitious materials.

d.	Amount of fly ash or other pozzolans conforming to ASTM C 618 in a given concrete mixture can be increased to 35% provided that the concrete is not placed during cold weather as defined by ACI 306 or that the concrete is membrane cured and protected from freezing until the concrete has attained 3,500 psi.

1904.5 Alternative cementitious materials for sulfate exposure. Combinations of cementitious materials for use in sulfate-resistant concrete that are alternative to those listed in ACI 318, [Table 4.3.1] Table 19.3.2.1, shall be permitted in accordance with ACI 318, Section [4.5.1] 26.4.2.2.

SECTION BC 1905
CONCRETE QUALITY, MIXING AND PLACING

1905.1 General. The required strength and durability of concrete shall be governed by compliance with the proportioning, testing, mixing and placing provisions of Sections 1905.1.1 through 1905.13 of this code and ACI 318.

1905.1.1 Strength. Concrete shall be proportioned to provide an average compressive strength in accordance with Section 1905.3, and shall satisfy the durability criteria of Section 1904. Concrete shall be produced to minimize the frequency of strengths below f’c in compliance with Section 1905.6.3.3. For concrete designed and constructed in accordance with this chapter, f’c shall not be less than 2,500 psi (17.22 MPa). No maximum specified compressive strength shall apply unless restricted by a specific provision of this code or ACI 318.

1905.1.2 Cylinder tests. Requirements for f’c shall be based on tests of cylinders made and tested in accordance with Section 1905.6.3.

1905.1.3 Basis of f’c . Unless otherwise specified, f’c shall be based on 28-day tests. If other than 28 days, test age for f’c shall be as indicated in construction documents. If at any time during the concrete operations, the concrete is not in conformance with ASTM C 94 or is otherwise compromised, it shall be rejected. If it is placed, the location of the load shall be recorded and a pair of cylinders shall be molded from the load per ASTM C 31 and included in the average f’c.

1905.1.4 Lightweight aggregate concrete. Where design criteria in ACI 318, [Sections 8.6.1, 9.5.2.3, 11.2, 12.2.4, and 22.2.4, provide] Section 19.2.4, provides for use of a splitting tensile strength value of concrete (f’ct), laboratory tests shall be made in accordance with ASTM C 330 to establish the value of f’ct corresponding to the specified value of f’c.

1905.1.5 Field acceptance. Splitting tensile strength tests shall not be used as a basis for field acceptance of concrete.

1905.2 Selection of concrete proportions. Concrete proportions shall be determined in accordance with ACI 318 and the provisions of Sections 1905.2.1 through 1905.2.4 of this code.

1905.2.1 General. Proportions of materials for concrete shall be established to provide:

- Workability and consistency to permit concrete to be worked readily into forms and around reinforcement under the conditions of placement to be employed, without segregation or excessive bleeding.

- Resistance to special exposures as required by Section 1904.

- Conformance with the strength test requirements of Section 1905.6.

1905.2.2 Different materials. Where different materials are to be used for different portions of proposed work, each combination shall be evaluated.

1905.2.3 Basis of proportions. Concrete proportions shall be established in accordance with Section 1905.3 or Section 1905.4, and shall comply with the applicable requirements of Section 1904.

1905.2.4 Mass concrete. For areas of high-strength mass concrete, including but not limited to, 8,000 psi (55 158 kPa) or greater and the least dimension being equal to or greater than 36 inches (914 mm), as indicated on the construction documents, a thermal control plan complying with ACI 301, Section 8.1 and acceptable to the registered design professional of record shall be submitted by the contractor.

1905.3 Proportioning on the basis of field experience and/or trial mixtures. Concrete proportioning determined on the basis of field experience or trial mixtures shall be done in accordance with ACI 318, [Section 5.3] Sections 26.4.3 and 26.4.4, and Sections 1905.3.1 through 1905.3.5 of this chapter.[. If the required f’c is obtained for trial batch mixes prior to the date specified, the trial mix design may be approved. All mixes shall be approved by the registered design professional of record. prior to construction.]

1905.3.1 Required Strength. If the required [f’ct] f’cr is obtained for trial batch mixes prior to the date specified, the trial mix design may be approved by the registered design professional of record for the structural design.

1905.3.2 Performance and approval. Concrete mix designs shall be performed by an approved agency or by a concrete producer [who is] approved by the department as an approved fabricator [authorized] in accordance with Section 1704.2.2, and approved in accordance with the requirements of Sections 1905.3.2.1 through 1905.3.2.3.

1905.3.2.1 Certification. All mix designs submitted for review and approval in accordance with Section 1905.3.2.2 shall be certified by the director of the approved agency or the quality control manager of the approved [fabricator] concrete producer that performed the tests used to substantiate the mix design. In addition, all mix designs shall be signed by an owner or officer of the concrete production facility.

1905.3.2.2 Review and approval. All mixes shall be approved by the registered design professional of record and filed with the department prior to use in construction.

1905.3.2.3 Distribution. Copies of the approved mix design(s) shall be maintained at the construction site by the contractor and made available to the department upon request. A copy of the approved mix design(s) shall be provided by the contractor to the licensed concrete testing laboratory performing the acceptance testing of the concrete at the construction site.

1905.3.3. Test records and trial mixtures. Field strength test records or trial mixtures used to determine f’cr shall not be more than 24 months old measured from the date of batching, provided the materials are the same as those proposed for use and the concrete producer provides a written statement confirming the materials are the same as those proposed for use.

# Exceptions:

1.	Coarse aggregates may be acquired from an alternative source provided the nominal maximum size and the volume of coarse aggregate used remain unchanged.

2.	Fine aggregates may be acquired from an alternative source provided the volume of fine aggregate used remains unchanged.

1905.3.4 Materials. The type and source of the materials used in the concrete shall be identified in the proposed concrete mix design. In order for materials in field strength test records or trial mixtures to be considered the same as those proposed for use, the materials shall, at a minimum, comply with the following:

- Cementitious materials. Cementitious materials shall be used in the same quantities for each individual component and shall be of the same type and shall be from the same source and mill. Upon request, the concrete producer shall provide mill certificates for the cementitious materials proposed for use and cementitious materials represented by the field strength test records or trial mixtures to the registered design professional of record and the department.

- Aggregates. Coarse and fine aggregates shall be the same nominal maximum size and shall be used in the same volume for each individual component. The aggregate supplier shall attest that the aggregates proposed are not alkali-silica reactive. The aggregate supplier is permitted to rely on New York State Department of Transportation approval of the supplier’s aggregate source.

- Admixtures. Admixtures shall meet the requirements of the same admixture type in accordance with ASTM C 494 or ASTM C 260 and there shall be no change in air content or water content from the previously specified mix.

Exception: Addition or removal of retarding or accelerating admixtures as described in Section 1905.3.5 is acceptable.

- Additional testing. Differences or changes in materials that are proposed for use, not meeting the requirements of Items 1 through 3 above, shall require new testing demonstrated by either field strength test records or trial mixtures.

Exception: Field changes to concrete proportions specified in Section 1905.3.5.

1905.3.5 Field changes to concrete proportions. Based on test data and observations during the course of construction, the following changes described in Sections 1905.3.5.1 and 1905.3.5.2 are permitted without requiring additional trial mixtures or field strength test records, provided:

- There are no changes to the type and source of materials described in [Section] Sections 1905.3.3 and 1905.3.4, except as permitted in Sections 1905.3.5.1 and 1905.3.5.2;

- Documentation of these changes are maintained by the concrete producer and the concrete contractor;

- The changes described in Section 1905.3.5 cannot be used for the submission of an initial mix design to demonstrate that a previously prepared mix design meets strength or air content requirements that differ from the required concrete properties without new field strength test records or new trial mix designs;

- Where required in Section 1905.3.5, documentation of these changes shall be submitted for acceptance to the registered design professional of record for the structural design by the concrete producer prior to use;

- Copies of the revised mixtures shall be maintained at the construction site and provided to the licensed concrete testing laboratory performing the acceptance testing of concrete in accordance with Item 4 of Table [1704.4] 1705.3 of this code; and

- The documentation required by Items 2 and 5 above shall be made available to the commissioner upon request.

1905.3.5.1 Changes that do not require prior approval of the registered design professional of record for the structure. The following admixture modifications to concrete proportions can be made without requiring prior acceptance by the registered design professional of record:

- Air-entraining admixtures. Air-entraining admixture dosages can be increased or decreased as needed to obtain the air content specified in the construction documents.

- Water reducing admixtures. Water reducing admixture dosages can be increased or decreased to produce the specified workability, provided that the design water is not exceeded and the changes do not segregate the concrete mix.

1905.3.5.2 Changes that require prior approval of the registered design professional of record for the structure. The following modifications to concrete proportions can be made only with prior acceptance by the registered design professional of record. Any added materials and the final mix proportions shall be indicated in a revised mix design submitted to the registered design professional of record prior to use:

1.	Retarding and accelerating admixtures. Retarding and accelerating admixtures may be added to concrete mixtures or the dosage may be modified as needed to maintain practical set times.

2.	Pigment. Pigment dosage may be adjusted to maintain uniform concrete color.

3.	Fibers. Synthetic, glass or natural fibers may be added to the mix within the manufacturer recommended range. Any loss in workability shall be compensated with a water reducer.

Exception: Steel fibers may not be added to a concrete mixture without the performance of a new mix design.

4.	Corrosion inhibitor. Corrosion inhibiting admixtures may be added, provided the corresponding adjustment of mix water remains within the limits of the required water/cementitious material ratio. The added materials and the revised design mix shall be submitted for review by the registered design professional of record for the structure prior to use.

5.	Cementitious content and [water-cementitous] water-cementitious material ratio (w/cm). The cementitious content may be increased by a maximum of 12 percent, or the w/cm ratio may be decreased while maintaining the same cementitious content, but the w/cm and air content shall not be increased. Aggregate quantities shall be adjusted, as required, to maintain the mix proportion and yield.

6.	Hydration control. Admixture may be added for the purpose of delaying hydration and maintaining a workable mix.

7.	Source of aggregate. Change to the source of aggregate may be approved by the registered design professional of record without providing additional test data only when the original aggregate source is no longer producing the required aggregates or the quality of the aggregates produced no longer meets the requirements of ASTM C 33 or the New York State Department of Transportation, provided:

7.1.	The new aggregate source is approved by the New York State Department of Transportation;

7.2.	A modulus of elasticity is not specified;

7.3.	The volume of both the fine and coarse aggregates remains the same and the nominal maximum size of coarse aggregates is unchanged;

7.4.	Lightweight aggregate shall not be substituted for dense, nor dense aggregate for lightweight, where lightweight aggregates are defined as having a specific gravity less than 2.5; and

7.5.	The registered design professional of record is informed of the reason necessitating the change of aggregate.

8.	Cementitious materials. Any change to cementitious materials shall require an additional laboratory testing trial batch. The new cementitious material shall maintain the same air and water cementitious ratio (w/cm) as the original mix and meet the strength requirements of ACI 301, Table 4.2.3.3 b. Approval of the registered design professional of record and submittal of data from either a three- or seven-day compressive strength test shall be required prior to the placement of concrete.

1905.4 Proportioning without field experience or trial mixtures. Concrete proportioning determined without field experience or trial mixtures shall be done in accordance with ACI 318, Section [5.4] 26.4.4.1(b). This method of proportioning shall not be permitted for:

1.	Load-carrying structural concrete where the total volume of concrete on a given project exceeds 50 cubic yards (38 m3); or

2.	Structural or non-structural concrete mix proportions that will be exposed to exposure classes S1, P1, or C2.

1905.5 Average strength reduction. As data [become] becomes available during construction, it is permissible to reduce the amount by which the average compressive strength (f ‘ c) is required to exceed the specified value of f’ c in accordance with ACI 318, Section [5.5] 26.4.4.1(c).  A new mix design shall be submitted to the registered design professional of record for approval prior to use.

1905.6 Evaluation and acceptance of concrete. The criteria for evaluation and acceptance of concrete shall be as specified in ACI 318, Sections 26.12 and 26.13, and Sections [1905.6.2] 1905.6.1 through [1905.6.5.5] 1905.6.5 of this code.

1905.6.1 Acceptance testing. Concrete shall be tested in accordance with the requirements in Sections 1905.6.2 through 1905.6.5. Concrete sampling and testing for acceptance shall be deemed a special inspection performed by a licensed concrete testing laboratory as an approved agency.  An approved agency shall perform tests on fresh concrete at the job site, prepare specimens required for curing under field conditions, prepare specimens required for testing in the laboratory and record the temperature of the fresh concrete when preparing specimens for strength tests. All field sampling and testing, including the testing of aggregates, concrete mixes, and strength testing of specimens, shall be subject to special inspection by an approved agency. All testing laboratories shall be approved agencies and shall employ qualified special inspectors to perform all required field and laboratory tests. Test results shall be promptly distributed by the testing laboratory to the registered design professional of record, concrete producer, owner and contractor to allow for corrective action where the concrete is found to be noncompliant with the mix design or noncompliant with the requirements otherwise specified in this code.  Unless more prompt action is required, test results shall be reported no [less] more than 7 business days after the date the respective tests were performed.

1905.6.2 Frequency of testing. The frequency of conducting strength tests of concrete shall be as specified in Sections 1905.6.2.1 through 1905.6.2.4.

1905.6.2.1 Minimum frequency. For the first 250 cubic yards of each class of concrete placed each day, samples for strength tests of each such class shall be taken: (i) not less than once a day; (ii) not less than once for each 50 cubic yards (38 m3) of concrete; and (iii) not less than once for each 5,000 square feet (465 m2) of surface area for slabs or walls. After the first 250 cubic yards (191 m3), samples for strength tests of each class of concrete placed each day shall be taken once for each additional 150 cubic yards (115 m3).  For structural concrete exposed to exposure class C2, additional field testing of the concrete for water content per AASHTO T 318 shall be required. At the discretion of the registered design professional of record, the frequency of testing may be reduced, but not less than once for each 150 cubic yards (115 m3).

1905.6.2.2 Minimum number. On a given project, if the total volume of concrete is such that the frequency of testing required by Section 1905.6.2.1 would provide less than five strength tests for a given class of concrete, tests shall be made from at least five randomly selected batches or from each batch if fewer than five batches are used.

1905.6.2.3 Small volume. When the total volume of concrete is less than 50 cubic yards (38 m3) on a given project, testing may be waived by the registered design professional of record.

1905.6.2.4 Strength test. A strength test shall be the average of the strengths of two 6 inch by 12 inch (152 mm by 3048 mm) or two 4 inch by 8 inch (102 mm by 203mm) cylinders made from the same sample of concrete and tested at 28 days or at the test age designated for the determination of f’c. Consideration shall be given specifying an f’c at 56 days or later for concrete utilizing pozzolans in the mix proportions. At the discretion of the registered design professional of record or the approved agency performing the testing, additional pairs of test cylinders may be taken at the time of sampling for testing at a later date. The additional cylinders may be tested at a later date should the strength at the specified date not meet the required f’c.

1905.6.3 Standard-cured specimens. Standard-cured specimens shall comply with the provisions of Sections 1905.6.3.1 through 1905.6.3.9.

1905.6.3.1 Mix Design. The special inspector shall verify that the proportions indicated on the batch ticket for the concrete delivered to the construction site are as per the approved concrete mix design prior to concrete placement (see Table [1704.4] 1705.3 of this code). Concrete that does not meet the requirements of the approved concrete mix design shall be rejected.

1905.6.3.2 Sampling. Samples for strength tests shall be taken in accordance with ASTM C 172.

1905.6.3.3 Cylinders. Cylinders for strength tests shall be molded and standard-cured in accordance with ASTM C 31.

1905.6.3.3.1 On-site curing. The [Contractor] contractor shall be responsible for providing the specified field storage curing facility and for monitoring the temperature of the cylinders as defined in ASTM C 31.

1905.6.3.3.2 Final curing. Cylinders shall be placed in final curing conditions meeting the requirements of ASTM C 511. Cylinders shall be transported to final curing conditions by the licensed concrete testing laboratory within 48 hours of casting the cylinders.

1905.6.3.3.3 Compressive strength testing. The cylinders shall be tested in accordance with ASTM C 39.

1905.6.3.4 Evaluation of results. The strength level of an individual class of concrete shall be considered satisfactory if both of the following requirements are met:

- Every arithmetic average of any three consecutive strength tests equals or exceeds f’c.

- No individual strength test (average of two cylinders) falls below f’c by more than 500 psi (3.45 MPa) when f’c is 5,000 psi (34.50 MPa) or less, or by more than 0.10 f’c when f’c is more than 5,000 psi (34.50 MPa).

1905.6.3.5 Correction. If either of the requirements of Section [1905.6.3.3] 1905.6.3.4 is not met, steps shall be taken to increase the average of subsequent strength test results. The requirements of Section 1905.6.5 shall govern if the requirement of Section [1905.6.3.6] 1905.6.3.4, Item 2, is not met.

1905.6.3.6 Field testing. Each time concrete is sampled for strength testing, the tests set forth in Items 1 through 5 shall be performed by the approved agency:

- Temperature in accordance with ASTM C 1064.

- Slump in accordance with ASTM C 143.

- Unit weight in accordance with ASTM C 138.

- Air content in accordance with ASTM C 173 or C 231. Testing in accordance with ASTM C 173 must be used for concretes made with lightweight aggregates, and other instances where ASTM C 231 is not applicable.

5. 	Water content per AASHTO T 318 when required by Section 1905.6.2.1 of this code.

1905.6.3.7 Mass concrete. For mass concrete sections identified as requiring monitoring, install temperature devices that are capable of measuring the temperature of the concrete continuously and record temperature data in increments that do not exceed 30 minutes for a minimum period of seven days per ACI 301, Section 8.3 or as otherwise directed by the registered design professional of record. In lieu of monitoring a concrete placement for core and outside face temperatures, a computer simulated thermal study may be substituted, if approved by the registered design professional of record. The computer simulated thermal study shall be of the largest section placed for a specific concrete mix proportion and reflect the thermal properties for the specific cementitious materials and quantities in the mix. The thermal study shall include the maximum temperature at which concrete may be placed and the ambient temperature range for concrete placement.
