Int. No. 994

By Council Member Garodnick, the Speaker (Council Member Quinn), and Council Members Fidler, Gentile, Gonzalez, James, Koppell, Liu, Nelson, Recchia Jr., Sanders Jr., Seabrook, Weprin, Baez, White Jr. and Gerson (in conjunction with the Mayor).

..Title

A Local Law to amend the administrative code of the city of New York and the New York city building code, in relation to requiring painting of dedicated standpipes and sprinklers.

..Body

Be it enacted by the Council as follows:

Section 1. Section BC 903 of the New York city building code of chapter 7 of title 28 of the administrative code of the city of New York is amended by adding a new subsection 903.6 to read as follows:

903.6  Painting of dedicated sprinklers.  Dedicated sprinklers shall be painted in accordance with Sections 903.6.1 through 903.6.4.

Exceptions:

1. Attachments, gauges, valves and other operable parts of sprinkler systems.

2.  Horizontal branch lines.

903.6.1	New buildings.  Cross connections and risers in new buildings, including buildings constructed pursuant to Section 28-101.4.2 of the Administrative Code, shall be painted green prior to the hydrostatic pressure test regardless of whether they will be enclosed at a later point in time.

Exception:   Where a standpipe system is used as a combination standpipe and sprinkler system, the sprinkler risers and cross connections that are also used for the standpipe system shall be painted red.

903.6.2	 Alterations.  Cross connections and risers for independent (stand-alone) existing sprinkler systems that are exposed during alterations, including alterations pursuant to Section 28-101.4.2 of the Administrative Code, shall be painted green prior to the hydrostatic pressure test.

Exception:   Where a standpipe system is used as a combination standpipe and sprinkler system, the sprinkler risers and cross connections that are also used for the standpipe system shall be painted red.

903.6.3	 Retroactive requirement for completed buildings.  Notwithstanding any other provision of law, all exposed risers and cross connections of completed buildings in existence on July 1, 2009 shall be painted green on or before October 1, 2009.

Exception:   Where a standpipe system is used as a combination standpipe and sprinkler system, the sprinkler risers and cross connections that are also used for the standpipe system shall be painted red.

903.6.4 Buildings under construction on July 1, 2009.  Notwithstanding any other provision of law, where construction documents were approved and permits issued for the construction of new buildings or alterations of existing buildings prior to July 1, 2009 and the work is not signed off by the department prior to such date, all exposed cross connections and risers shall be painted green prior to the hydrostatic pressure test, including cross connections and risers that will be enclosed at a later point in time.

Exceptions:   1. Where a standpipe system is used as a combination standpipe and sprinkler system, the sprinkler risers and cross connections that are also used for the standpipe system shall be painted red.

2.  Cross connections and risers enclosed prior to July 1, 2009 need not be painted.

§2.  Section BC 905 of the New York city building code of chapter 7 of title 28 of the administrative code of the city of New York is amended by adding a new subsection 905.11 to read as follows:

905.11  Painting of dedicated standpipes.  Dedicated standpipes shall be painted in accordance with Sections 905.11.1 through 905.11.5.

Exception:  Attachments, gauges, valves and other operable 				parts of standpipes.

905.11.1	 New buildings.  All portions of a standpipe system in new buildings, including buildings constructed pursuant to Section 28-101.4.2 of the Administrative Code, shall be painted red prior to the hydrostatic pressure test, whether or not they are intended to be enclosed at the end of construction.

905.11.2	   Alterations.  Existing unpainted standpipe risers that are exposed during alterations, including alterations pursuant to Section 28-101.4.2 of the Administrative Code, shall be painted red prior to the hydrostatic pressure test.

905.11.3 Retroactive requirement for completed buildings.  Notwithstanding any other provision of law, all portions of exposed standpipe systems of completed buildings in existence on July 1, 2009 shall be painted red on or before October 1, 2009.

905.11.4  Buildings under construction on July 1, 2009. Notwithstanding any other provision of law, where construction documents were approved and permits issued for the construction of new buildings or alterations of existing buildings prior to July 1, 2009 and the work is not signed off by the department prior to such date, all exposed portions of the standpipe system shall be painted red prior to the hydrostatic pressure test, including portions that will be enclosed at a later point in time.

Exception.  Portions of the standpipe system enclosed prior to July 1, 2009 need not be painted.

905.11.5 Combination standpipe and sprinkler systems.  Where a standpipe system that is used as a combination standpipe and sprinkler system is required to be painted pursuant to Section 905.11.1, 905.11.2, 905.11.3 or 905.11.4, the sprinkler risers and cross connections that are also used for the standpipe system shall be painted red.

§3.  This local law shall take effect on July 1, 2009 except that the commissioner of buildings may promulgate rules or take other administrative actions for the implementation of this local law prior to such effective date.

RCC

BKH

05/07/09

7:00 p.m.

LS # 6546